## Configuration
Configuration
PEL Transfer, Version 2.8.15973
Recording status
Session name | MCCY
Report start | 5/1/2026 11:30:00 AM
Report end | 5/11/2026 6:15:00 AM
Report duration | 9 days, 18:45:00 (h:min:s)
Recording start | 5/1/2026 11:28:21 AM
Recording end | 5/11/2026 6:13:21 AM
Recording duration | 9 days, 18:45:00 (h:min:s)
1 s trend | No
200 ms trend | No
1 s harmonics | No
Aggregated harmonics | No
Instrument ID
PEL model | PEL113
PEL serial number | 108822AAH
PEL name | PEL113-108822AAH
PEL location | St Josephs
Firmware DSP version | 1.96
Firmware microprocessor version | 1.14
Hardware version
Measurement configuration and status
Aggregation period | 15 min
Electrical hook-up | 3-phase 4-wire Y
Nominal frequency | Auto
Primary nominal voltage | - - -
Secondary nominal voltage | - - -
Current sensor I1 | MA193/MA194/A193/A196
Current sensor I2 | MA193/MA194/A193/A196
Current sensor I3 | MA193/MA194/A193/A196
Line flexible sensor range | 400 A
Line flexible sensor wraps | 1

## Event Log
Event Log
Date | Time | Event
5/1/2026 | 11:28:21 AM | Start of recording
5/1/2026 | 11:35:01 AM | The power supply has been lost, instrument on battery.
5/1/2026 | 11:35:10 AM | Instrument turned on, power supply restored.

## Total Energies and Costs
Total Energies and Costs
Name | Value | Cost | Cost per kWh, kvarh or kVAh
Ep+ Total (Wh) | 900.78 kWh
Ep- Total (Wh) | 0 kWh
Ep Total (Wh) | 900.78 kWh
Eq/q1 Total (varh) | 353.296 kvarh
Eq/q2 Total (varh) | 0 kvarh
Eq/q3 Total (varh) | 0 kvarh
Eq/q4 Total (varh) | 0 kvarh
Eq Total (varh) | 353.296 kvarh
Es+ Total (VAh) | 1.026 MVAh
Es- Total (VAh) | 0 kVAh
Es Total (VAh) | 1.026 MVAh
Positive-sequence active energy Ep⁺ | 1.279 kWh
Unbalance active energy Epu | 900.951 kWh
Harmonic active energy EpH | -1.45 kWh
Reactive energy Net/Total Eq | 353.296 kvarh
Distortion energy Net/Total Ed | 335.246 kvarh
MAX 15 min Summary I1 | 20.7162 A |  |  | 5/7/2026 | 7:30:00 PM
MAX 15 min Summary I2 | 20.1293 A |  |  | 5/7/2026 | 7:30:00 PM
MAX 15 min Summary I3 | 18.7485 A |  |  | 5/7/2026 | 7:30:00 PM
MAX 15 min Summary IN | 4.2026 A |  |  | 5/6/2026 | 6:00:00 PM
MAX 15 min Summary PFT+ | 0.912 |  |  | 5/3/2026 | 7:30:00 AM
MAX 15 min Summary PFT- |  |  |  | - - - | - - -
MAX 15 min Summary PT | 7.984 kW |  |  | 5/7/2026 | 7:30:00 PM
MAX 15 min Summary QT | 7.721 kvar |  |  | 5/7/2026 | 7:30:00 PM
MAX 15 min Summary ST | 11.611 kVA |  |  | 5/7/2026 | 7:30:00 PM

## Summary
Summary
Date | Time | V1 (15 min) | V2 (15 min) | V3 (15 min) | U12 (15 min) | U23 (15 min) | U31 (15 min) | I1 (15 min) | I2 (15 min) | I3 (15 min) | IN (15 min) | V1ᴄꜰ (15 min) | V2ᴄꜰ (15 min) | V3ᴄꜰ (15 min) | I1ᴄꜰ (15 min) | I2ᴄꜰ (15 min) | I3ᴄꜰ (15 min) | u₂ (15 min) | F (Hz) (15 min) | P1 (15 min) | P2 (15 min) | P3 (15 min) | PT (15 min) | P1- (15 min) | P2- (15 min) | P3- (15 min) | PT- (15 min) | P1+ (15 min) | P2+ (15 min) | P3+ (15 min) | PT+ (15 min) | Q1 (15 min) | Q2 (15 min) | Q3 (15 min) | QT (15 min) | Q1- (15 min) | Q2- (15 min) | Q3- (15 min) | QT- (15 min) | Q1+ (15 min) | Q2+ (15 min) | Q3+ (15 min) | QT+ (15 min) | S1 (15 min) | S2 (15 min) | S3 (15 min) | ST (15 min) | PF1- (15 min) | PF2- (15 min) | PF3- (15 min) | PFT- (15 min) | PF1+ (15 min) | PF2+ (15 min) | PF3+ (15 min) | PFT+ (15 min) | Cos φ1- (15 min) | Cos φ2- (15 min) | Cos φ3- (15 min) | Cos φT- (15 min) | Cos φ1+ (15 min) | Cos φ2+ (15 min) | Cos φ3+ (15 min) | Cos φT+ (15 min) | Tan Φ- (15 min) | Tan Φ+ (15 min) | V1ᴛʜᴅ (15 min) | V2ᴛʜᴅ (15 min) | V3ᴛʜᴅ (15 min) | U12ᴛʜᴅ (15 min) | U23ᴛʜᴅ (15 min) | U31ᴛʜᴅ (15 min) | I1ᴛʜᴅ (15 min) | I2ᴛʜᴅ (15 min) | I3ᴛʜᴅ (15 min) | INᴛʜᴅ (15 min) | S1- (15 min) | S2- (15 min) | S3- (15 min) | ST- (15 min) | S1+ (15 min) | S2+ (15 min) | S3+ (15 min) | ST+ (15 min) | i₂ (15 min) | N1 (15 min) | N2 (15 min) | N3 (15 min) | NT (15 min) | D1 (15 min) | D2 (15 min) | D3 (15 min) | DT (15 min) | Pᵳ1 (15 min) | Pᵳ2 (15 min) | Pᵳ3 (15 min) | PᵳT (15 min) | Pᵳ1+ (15 min) | Pᵳ2+ (15 min) | Pᵳ3+ (15 min) | PᵳT+ (15 min) | Pᵳ1- (15 min) | Pᵳ2- (15 min) | Pᵳ3- (15 min) | PᵳT- (15 min)
|  | V | V | V | V | V | V | A | A | A | A | [6 empty] | % | Hz | W | W | W | W | W | W | W | W | W | W | W | W | var | var | var | var | var | var | var | var | var | var | var | var | VA | VA | VA | VA | [18 empty] | % | % | % | % | % | % | % | % | % | % | VA | VA | VA | VA | VA | VA | VA | VA | % | var | var | var | var | var | var | var | var | W | W | W | W | W | W | W | W | W | W | W | W
5/1/2026 | 11:45:00 AM | 282.28 | 279.37 | 278.05 | 487.81 | 480.91 | 485.66 | 4.8078 | 4.0164 | 5.4453 | 4.1012 | 1.427 | 1.428 | 1.425 | 1.494 | 1.432 | 1.348 | Over-range | 60.01 | 1104 | 812 | 1489 | 3405 | - - - | - - - | - - - | - - - | 1104 | 812 | 1489 | 3405 | 771 | 744 | 0 | 1515 | - - - | - - - | - - - | - - - | 771 | 744 | 0 | 1515 | 1356 | 1119 | 1514 | 3988 | # # # | # # # | # # # | # # # | 0.814 | 0.726 | 0.983 | 0.854 | # # # | # # # | # # # | - - - | 0.82 | 0.735 | 0.999 | 0.864 | - - - | 0.445 | 1.76 | 1.73 | 1.68 | 1.56 | 1.67 | 1.68 | 10.14 | 15.6 | 17.81 | 0 | - - - | - - - | - - - | - - - | 1356 | 1119 | 1514 | 3988 | Over-range | 787 | 764 | 275 | 2075 | 157 | 176 | 269 | 1418 | 1105 | 811 | 1490 | 3407 | 1105 | 811 | 1490 | 3407 | - - - | - - - | - - - | - - -
5/1/2026 | 12:00:00 PM | 282.14 | 279.21 | 277.97 | 487.58 | 480.62 | 485.52 | 5.4338 | 5.0434 | 5.7704 | 4.1025 | 1.426 | 1.428 | 1.425 | 1.505 | 1.448 | 1.281 | Over-range | 60.01 | 1208 | 1183 | 1571 | 3962 | - - - | - - - | - - - | - - - | 1208 | 1183 | 1571 | 3962 | 931 | 738 | -164 | 1503 | - - - | - - - | - - - | - - - | 931 | 738 | -164 | 1503 | 1533 | 1407 | 1604 | 4544 | # # # | # # # | # # # | # # # | 0.788 | 0.841 | 0.98 | 0.872 | # # # | # # # | # # # | - - - | 0.793 | 0.849 | 0.994 | 0.881 | - - - | 0.379 | 1.74 | 1.69 | 1.67 | 1.54 | 1.64 | 1.66 | 8.99 | 13.05 | 17.21 | 0 | - - - | - - - | - - - | - - - | 1533 | 1407 | 1604 | 4544 | Over-range | 944 | 761 | 321 | 2225 | 158 | 187 | 274 | 1640 | 1211 | 1182 | 1571 | 3964 | 1211 | 1182 | 1571 | 3964 | - - - | - - - | - - - | - - -
5/1/2026 | 12:15:00 PM | 282.45 | 279.62 | 278.31 | 488.18 | 481.33 | 486.05 | 5.2144 | 4.6623 | 5.6626 | 4.118 | 1.427 | 1.428 | 1.425 | 1.5 | 1.426 | 1.299 | Over-range | 60 | 1172 | 1045 | 1547 | 3764 | - - - | - - - | - - - | - - - | 1172 | 1045 | 1547 | 3764 | 875 | 745 | -99 | 1521 | - - - | - - - | - - - | - - - | 875 | 745 | -99 | 1521 | 1471 | 1300 | 1576 | 4347 | # # # | # # # | # # # | # # # | 0.797 | 0.804 | 0.982 | 0.866 | # # # | # # # | # # # | - - - | 0.802 | 0.812 | 0.997 | 0.875 | - - - | 0.404 | 1.75 | 1.73 | 1.69 | 1.56 | 1.65 | 1.68 | 9.46 | 13.91 | 17.45 | 0 | - - - | - - - | - - - | - - - | 1471 | 1300 | 1576 | 4347 | Over-range | 889 | 768 | 296 | 2172 | 155 | 185 | 273 | 1550 | 1176 | 1043 | 1547 | 3767 | 1176 | 1043 | 1547 | 3767 | - - - | - - - | - - - | - - -
5/1/2026 | 12:30:00 PM | 282.34 | 279.47 | 278.16 | 487.94 | 481.15 | 485.78 | 4.4458 | 3.4675 | 5.2446 | 4.1293 | 1.427 | 1.428 | 1.425 | 1.49 | 1.46 | 1.403 | Over-range | 60.01 | 1048 | 568 | 1428 | 3045 | - - - | - - - | - - - | - - - | 1048 | 568 | 1428 | 3045 | 666 | 750 | 107 | 1523 | - - - | - - - | - - - | - - - | 666 | 750 | 107 | 1523 | 1254 | 966 | 1459 | 3678 | # # # | # # # | # # # | # # # | 0.836 | 0.589 | 0.979 | 0.828 | # # # | # # # | # # # | - - - | 0.844 | 0.599 | 0.996 | 0.84 | - - - | 0.5 | 1.75 | 1.72 | 1.67 | 1.56 | 1.65 | 1.68 | 11.18 | 17.32 | 18.28 | 0 | - - - | - - - | - - - | - - - | 1254 | 966 | 1459 | 3678 | Over-range | 687 | 773 | 295 | 2060 | 169 | 186 | 269 | 1387 | 1052 | 568 | 1427 | 3047 | 1052 | 568 | 1427 | 3047 | - - - | - - - | - - - | - - -
5/1/2026 | 12:45:00 PM | 282.1 | 279.17 | 277.92 | 487.49 | 480.58 | 485.43 | 4.83 | 4.0093 | 5.442 | 4.1234 | 1.427 | 1.428 | 1.425 | 1.494 | 1.435 | 1.346 | Over-range | 60 | 1112 | 810 | 1487 | 3409 | - - - | - - - | - - - | - - - | 1112 | 810 | 1487 | 3409 | 771 | 745 | 0 | 1515 | - - - | - - - | - - - | - - - | 771 | 745 | 0 | 1515 | 1362 | 1116 | 1512 | 3990 | # # # | # # # | # # # | # # # | 0.816 | 0.726 | 0.984 | 0.854 | # # # | # # # | # # # | - - - | 0.822 | 0.735 | 0.999 | 0.865 | - - - | 0.444 | 1.78 | 1.75 | 1.7 | 1.58 | 1.69 | 1.71 | 10.16 | 15.47 | 17.82 | 0 | - - - | - - - | - - - | - - - | 1362 | 1116 | 1512 | 3990 | Over-range | 786 | 764 | 273 | 2073 | 153 | 172 | 268 | 1414 | 1114 | 811 | 1485 | 3409 | 1114 | 811 | 1485 | 3409 | - - - | - - - | - - - | - - -
5/1/2026 | 1:00:00 PM | 282.06 | 279.18 | 277.87 | 487.48 | 480.54 | 485.34 | 4.8211 | 3.9872 | 5.4215 | 4.1189 | 1.427 | 1.428 | 1.425 | 1.493 | 1.431 | 1.349 | Over-range | 60 | 1110 | 807 | 1482 | 3399 | - - - | - - - | - - - | - - - | 1110 | 807 | 1482 | 3399 | 768 | 744 | 0 | 1512 | - - - | - - - | - - - | - - - | 768 | 744 | 0 | 1512 | 1360 | 1112 | 1506 | 3978 | # # # | # # # | # # # | # # # | 0.817 | 0.725 | 0.984 | 0.854 | # # # | # # # | # # # | - - - | 0.822 | 0.734 | 1 | 0.865 | - - - | 0.445 | 1.78 | 1.76 | 1.7 | 1.59 | 1.68 | 1.71 | 10.15 | 15.56 | 17.93 | 0 | - - - | - - - | - - - | - - - | 1360 | 1112 | 1506 | 3978 | Over-range | 784 | 764 | 271 | 2067 | 157 | 177 | 269 | 1409 | 1112 | 805 | 1484 | 3401 | 1112 | 805 | 1484 | 3401 | - - - | - - - | - - - | - - -
5/1/2026 | 1:15:00 PM | 282.25 | 279.45 | 278.21 | 487.78 | 481.19 | 485.78 | 5.4727 | 4.9395 | 5.7739 | 4.1227 | 1.427 | 1.428 | 1.425 | 1.498 | 1.435 | 1.296 | Over-range | 60.01 | 1223 | 1144 | 1576 | 3942 | - - - | - - - | - - - | - - - | 1223 | 1144 | 1576 | 3942 | 923 | 742 | -121 | 1544 | - - - | - - - | - - - | - - - | 923 | 742 | -121 | 1544 | 1541 | 1378 | 1606 | 4525 | # # # | # # # | # # # | # # # | 0.793 | 0.83 | 0.981 | 0.871 | # # # | # # # | # # # | - - - | 0.79 | 0.83 | 0.986 | 0.872 | - - - | 0.392 | 1.8 | 1.77 | 1.71 | 1.6 | 1.68 | 1.72 | 9.17 | 13.46 | 17.33 | 0 | - - - | - - - | - - - | - - - | 1541 | 1378 | 1606 | 4525 | Over-range | 938 | 766 | 311 | 2221 | 158 | 183 | 274 | 1591 | 1239 | 1150 | 1602 | 3991 | 1239 | 1150 | 1602 | 3991 | - - - | - - - | - - - | - - -
5/1/2026 | 1:30:00 PM | 282.17 | 279.35 | 278.08 | 487.69 | 480.94 | 485.58 | 5.4622 | 5.0915 | 5.7984 | 4.1191 | 1.427 | 1.428 | 1.425 | 1.502 | 1.439 | 1.288 | Over-range | 60 | 1213 | 1194 | 1579 | 3986 | - - - | - - - | - - - | - - - | 1213 | 1194 | 1579 | 3986 | 937 | 742 | -169 | 1510 | - - - | - - - | - - - | - - - | 937 | 742 | -169 | 1510 | 1540 | 1420 | 1612 | 4572 | # # # | # # # | # # # | # # # | 0.787 | 0.841 | 0.98 | 0.872 | # # # | # # # | # # # | - - - | 0.792 | 0.849 | 0.994 | 0.88 | - - - | 0.379 | 1.81 | 1.78 | 1.72 | 1.61 | 1.7 | 1.74 | 9 | 12.86 | 17.16 | 0 | - - - | - - - | - - - | - - - | 1540 | 1420 | 1612 | 4572 | Over-range | 950 | 765 | 324 | 2239 | 156 | 186 | 274 | 1653 | 1215 | 1195 | 1576 | 3986 | 1215 | 1195 | 1576 | 3986 | - - - | - - - | - - - | - - -
5/1/2026 | 1:45:00 PM | 282.1 | 279.31 | 278.09 | 487.57 | 480.93 | 485.55 | 5.2775 | 4.7526 | 5.7023 | 4.1242 | 1.427 | 1.428 | 1.425 | 1.502 | 1.424 | 1.282 | Over-range | 60.01 | 1184 | 1085 | 1557 | 3827 | - - - | - - - | - - - | - - - | 1184 | 1085 | 1557 | 3827 | 888 | 743 | -121 | 1509 | - - - | - - - | - - - | - - - | 888 | 743 | -121 | 1509 | 1489 | 1327 | 1586 | 4402 | # # # | # # # | # # # | # # # | 0.795 | 0.817 | 0.982 | 0.869 | # # # | # # # | # # # | - - - | 0.8 | 0.825 | 0.997 | 0.878 | - - - | 0.394 | 1.8 | 1.77 | 1.73 | 1.61 | 1.69 | 1.73 | 9.32 | 13.6 | 17.3 | 0 | - - - | - - - | - - - | - - - | 1489 | 1327 | 1586 | 4402 | Over-range | 902 | 765 | 298 | 2176 | 162 | 180 | 272 | 1567 | 1184 | 1086 | 1557 | 3827 | 1184 | 1086 | 1557 | 3827 | - - - | - - - | - - - | - - -
5/1/2026 | 2:00:00 PM | 282.12 | 279.28 | 278.02 | 487.59 | 480.81 | 485.49 | 4.6502 | 3.8141 | 5.3451 | 4.1275 | 1.427 | 1.428 | 1.425 | 1.49 | 1.455 | 1.377 | Over-range | 60 | 1079 | 683 | 1454 | 3215 | - - - | - - - | - - - | - - - | 1079 | 683 | 1454 | 3215 | 716 | 747 | 55 | 1518 | - - - | - - - | - - - | - - - | 716 | 747 | 55 | 1518 | 1306 | 1048 | 1485 | 3838 | # # # | # # # | # # # | # # # | 0.826 | 0.651 | 0.979 | 0.838 | # # # | # # # | # # # | - - - | 0.833 | 0.66 | 0.995 | 0.848 | - - - | 0.472 | 1.8 | 1.78 | 1.74 | 1.61 | 1.7 | 1.74 | 10.78 | 16.6 | 18.1 | 0 | - - - | - - - | - - - | - - - | 1306 | 1048 | 1485 | 3838 | Over-range | 733 | 767 | 300 | 2087 | 155 | 174 | 268 | 1431 | 1081 | 681 | 1455 | 3217 | 1081 | 681 | 1455 | 3217 | - - - | - - - | - - - | - - -
5/1/2026 | 2:15:00 PM | 282.39 | 279.65 | 278.37 | 488.12 | 481.51 | 485.99 | 4.7704 | 3.9232 | 5.4234 | 4.135 | 1.427 | 1.428 | 1.424 | 1.493 | 1.434 | 1.356 | Over-range | 60.01 | 1102 | 771 | 1484 | 3356 | - - - | - - - | - - - | - - - | 1102 | 771 | 1484 | 3356 | 756 | 751 | 20 | 1526 | - - - | - - - | - - - | - - - | 756 | 751 | 20 | 1526 | 1346 | 1094 | 1509 | 3949 | # # # | # # # | # # # | # # # | 0.819 | 0.705 | 0.983 | 0.85 | # # # | # # # | # # # | - - - | 0.825 | 0.713 | 0.999 | 0.861 | - - - | 0.455 | 1.83 | 1.77 | 1.74 | 1.63 | 1.7 | 1.75 | 10.36 | 16.17 | 18.09 | 0 | - - - | - - - | - - - | - - - | 1346 | 1094 | 1509 | 3949 | Over-range | 773 | 772 | 277 | 2080 | 159 | 179 | 272 | 1413 | 1103 | 769 | 1486 | 3358 | 1103 | 769 | 1486 | 3358 | - - - | - - - | - - - | - - -
5/1/2026 | 2:30:00 PM | 282.2 | 279.4 | 278.15 | 487.75 | 481.04 | 485.68 | 4.7813 | 3.9194 | 5.4032 | 4.1283 | 1.427 | 1.428 | 1.425 | 1.492 | 1.433 | 1.355 | Over-range | 60 | 1104 | 780 | 1478 | 3362 | - - - | - - - | - - - | - - - | 1104 | 780 | 1478 | 3362 | 760 | 748 | 13 | 1521 | - - - | - - - | - - - | - - - | 760 | 748 | 13 | 1521 | 1349 | 1095 | 1503 | 3947 | # # # | # # # | # # # | # # # | 0.818 | 0.712 | 0.984 | 0.852 | # # # | # # # | # # # | - - - | 0.824 | 0.721 | 1 | 0.862 | - - - | 0.452 | 1.82 | 1.78 | 1.73 | 1.62 | 1.7 | 1.74 | 10.27 | 15.89 | 18.14 | 0 | - - - | - - - | - - - | - - - | 1349 | 1095 | 1503 | 3947 | Over-range | 775 | 768 | 272 | 2067 | 152 | 176 | 271 | 1400 | 1108 | 779 | 1477 | 3364 | 1108 | 779 | 1477 | 3364 | - - - | - - - | - - - | - - -
5/1/2026 | 2:45:00 PM | 282.24 | 279.47 | 278.13 | 487.91 | 481.08 | 485.65 | 5.2233 | 4.6789 | 5.6712 | 4.128 | 1.426 | 1.428 | 1.424 | 1.499 | 1.429 | 1.303 | Over-range | 60 | 1174 | 1046 | 1548 | 3768 | - - - | - - - | - - - | - - - | 1174 | 1046 | 1548 | 3768 | 874 | 746 | -102 | 1517 | - - - | - - - | - - - | - - - | 874 | 746 | -102 | 1517 | 1472 | 1301 | 1577 | 4351 | # # # | # # # | # # # | # # # | 0.797 | 0.804 | 0.982 | 0.866 | # # # | # # # | # # # | - - - | 0.802 | 0.812 | 0.997 | 0.875 | - - - | 0.403 | 1.78 | 1.76 | 1.7 | 1.59 | 1.67 | 1.71 | 9.44 | 14.12 | 17.53 | 0 | - - - | - - - | - - - | - - - | 1472 | 1301 | 1577 | 4351 | Over-range | 888 | 768 | 300 | 2174 | 157 | 184 | 274 | 1555 | 1176 | 1046 | 1546 | 3769 | 1176 | 1046 | 1546 | 3769 | - - - | - - - | - - - | - - -
5/1/2026 | 3:00:00 PM | 282.22 | 279.52 | 278.19 | 487.88 | 481.27 | 485.63 | 5.5713 | 5.285 | 5.8652 | 4.1241 | 1.426 | 1.427 | 1.424 | 1.504 | 1.45 | 1.288 | Over-range | 60.01 | 1230 | 1259 | 1595 | 4083 | - - - | - - - | - - - | - - - | 1230 | 1259 | 1595 | 4083 | 965 | 744 | -197 | 1511 | - - - | - - - | - - - | - - - | 965 | 744 | -197 | 1511 | 1572 | 1475 | 1631 | 4678 | # # # | # # # | # # # | # # # | 0.782 | 0.854 | 0.978 | 0.873 | # # # | # # # | # # # | - - - | 0.786 | 0.861 | 0.992 | 0.881 | - - - | 0.37 | 1.8 | 1.75 | 1.71 | 1.6 | 1.67 | 1.71 | 8.85 | 12.62 | 17.15 | 0 | - - - | - - - | - - - | - - - | 1572 | 1475 | 1631 | 4678 | Over-range | 979 | 767 | 342 | 2282 | 163 | 185 | 276 | 1709 | 1229 | 1261 | 1592 | 4083 | 1229 | 1261 | 1592 | 4083 | - - - | - - - | - - - | - - -
5/1/2026 | 3:15:00 PM | 282.39 | 279.78 | 278.29 | 488.33 | 481.52 | 485.84 | 5.0044 | 4.3282 | 5.5508 | 4.1324 | 1.427 | 1.428 | 1.425 | 1.493 | 1.426 | 1.321 | Over-range | 60.01 | 1138 | 910 | 1517 | 3565 | - - - | - - - | - - - | - - - | 1138 | 910 | 1517 | 3565 | 815 | 751 | -42 | 1523 | - - - | - - - | - - - | - - - | 815 | 751 | -42 | 1523 | 1410 | 1204 | 1544 | 4158 | # # # | # # # | # # # | # # # | 0.807 | 0.756 | 0.982 | 0.857 | # # # | # # # | # # # | - - - | 0.813 | 0.764 | 0.997 | 0.867 | - - - | 0.427 | 1.78 | 1.71 | 1.68 | 1.58 | 1.64 | 1.69 | 9.96 | 14.75 | 17.67 | 0 | - - - | - - - | - - - | - - - | 1410 | 1204 | 1544 | 4158 | Over-range | 831 | 771 | 289 | 2135 | 163 | 176 | 271 | 1495 | 1138 | 910 | 1517 | 3565 | 1138 | 910 | 1517 | 3565 | - - - | - - - | - - - | - - -
5/1/2026 | 3:30:00 PM | 282.35 | 279.7 | 278.18 | 488.24 | 481.34 | 485.74 | 4.62 | 3.5896 | 5.3175 | 4.1328 | 1.427 | 1.428 | 1.424 | 1.486 | 1.452 | 1.398 | Over-range | 60.01 | 1085 | 624 | 1444 | 3154 | - - - | - - - | - - - | - - - | 1085 | 624 | 1444 | 3154 | 701 | 754 | 105 | 1559 | - - - | - - - | - - - | - - - | 701 | 754 | 105 | 1559 | 1302 | 1000 | 1479 | 3781 | # # # | # # # | # # # | # # # | 0.833 | 0.624 | 0.977 | 0.834 | # # # | # # # | # # # | - - - | 0.832 | 0.628 | 0.982 | 0.837 | - - - | 0.494 | 1.77 | 1.71 | 1.68 | 1.57 | 1.64 | 1.68 | 10.76 | 17.17 | 18.36 | 0 | - - - | - - - | - - - | - - - | 1302 | 1000 | 1479 | 3781 | Over-range | 719 | 773 | 308 | 2083 | 159 | 171 | 272 | 1378 | 1094 | 627 | 1456 | 3177 | 1094 | 627 | 1456 | 3177 | - - - | - - - | - - - | - - -
5/1/2026 | 3:45:00 PM | 282.35 | 279.61 | 278.15 | 488.11 | 481.26 | 485.72 | 4.8391 | 4.0244 | 5.4546 | 4.1364 | 1.427 | 1.428 | 1.425 | 1.49 | 1.435 | 1.345 | Over-range | 60.01 | 1114 | 813 | 1492 | 3418 | - - - | - - - | - - - | - - - | 1114 | 813 | 1492 | 3418 | 774 | 751 | 0 | 1524 | - - - | - - - | - - - | - - - | 774 | 751 | 0 | 1524 | 1365 | 1122 | 1517 | 4005 | # # # | # # # | # # # | # # # | 0.816 | 0.724 | 0.984 | 0.854 | # # # | # # # | # # # | - - - | 0.821 | 0.734 | 0.999 | 0.864 | - - - | 0.446 | 1.77 | 1.74 | 1.69 | 1.58 | 1.65 | 1.7 | 10.19 | 15.5 | 17.92 | 0 | - - - | - - - | - - - | - - - | 1365 | 1122 | 1517 | 4005 | Over-range | 790 | 770 | 274 | 2085 | 155 | 172 | 270 | 1422 | 1114 | 815 | 1489 | 3418 | 1114 | 815 | 1489 | 3418 | - - - | - - - | - - - | - - -
5/1/2026 | 4:00:00 PM | 282.37 | 279.69 | 278.18 | 488.21 | 481.33 | 485.78 | 5.3028 | 4.8177 | 5.6992 | 4.1242 | 1.427 | 1.428 | 1.425 | 1.497 | 1.434 | 1.296 | Over-range | 59.99 | 1186 | 1094 | 1554 | 3835 | - - - | - - - | - - - | - - - | 1186 | 1094 | 1554 | 3835 | 895 | 748 | -124 | 1519 | - - - | - - - | - - - | - - - | 895 | 748 | -124 | 1519 | 1495 | 1341 | 1585 | 4422 | # # # | # # # | # # # | # # # | 0.793 | 0.816 | 0.981 | 0.867 | # # # | # # # | # # # | - - - | 0.798 | 0.824 | 0.996 | 0.876 | - - - | 0.396 | 1.76 | 1.73 | 1.69 | 1.58 | 1.65 | 1.69 | 9.32 | 13.76 | 17.55 | 0 | - - - | - - - | - - - | - - - | 1495 | 1341 | 1585 | 4422 | Over-range | 910 | 770 | 309 | 2201 | 163 | 184 | 276 | 1591 | 1187 | 1094 | 1554 | 3835 | 1187 | 1094 | 1554 | 3835 | - - - | - - - | - - - | - - -
5/1/2026 | 4:15:00 PM | 282.56 | 279.85 | 278.35 | 488.54 | 481.58 | 486.09 | 5.4731 | 5.1114 | 5.819 | 4.1279 | 1.427 | 1.428 | 1.425 | 1.501 | 1.439 | 1.284 | Over-range | 60.01 | 1214 | 1200 | 1586 | 4000 | - - - | - - - | - - - | - - - | 1214 | 1200 | 1586 | 4000 | 942 | 747 | -168 | 1521 | - - - | - - - | - - - | - - - | 942 | 747 | -168 | 1521 | 1546 | 1427 | 1619 | 4592 | # # # | # # # | # # # | # # # | 0.785 | 0.841 | 0.98 | 0.871 | # # # | # # # | # # # | - - - | 0.791 | 0.847 | 0.994 | 0.879 | - - - | 0.38 | 1.77 | 1.72 | 1.68 | 1.57 | 1.64 | 1.68 | 9.05 | 12.9 | 17.08 | 0 | - - - | - - - | - - - | - - - | 1546 | 1427 | 1619 | 4592 | Over-range | 957 | 771 | 325 | 2256 | 164 | 188 | 274 | 1665 | 1217 | 1197 | 1588 | 4002 | 1217 | 1197 | 1588 | 4002 | - - - | - - - | - - - | - - -
5/1/2026 | 4:30:00 PM | 282.63 | 280.09 | 278.51 | 488.77 | 482.04 | 486.22 | 4.8984 | 4.2138 | 5.4857 | 4.1315 | 1.429 | 1.429 | 1.426 | 1.492 | 1.44 | 1.344 | Over-range | 59.99 | 1118 | 834 | 1495 | 3447 | - - - | - - - | - - - | - - - | 1118 | 834 | 1495 | 3447 | 786 | 756 | -5 | 1536 | - - - | - - - | - - - | - - - | 786 | 756 | -5 | 1536 | 1377 | 1163 | 1526 | 4067 | # # # | # # # | # # # | # # # | 0.811 | 0.717 | 0.98 | 0.848 | # # # | # # # | # # # | - - - | 0.818 | 0.725 | 0.996 | 0.858 | - - - | 0.446 | 1.78 | 1.75 | 1.67 | 1.59 | 1.65 | 1.7 | 10.33 | 15.49 | 18 | 0 | - - - | - - - | - - - | - - - | 1377 | 1163 | 1526 | 4067 | Over-range | 803 | 777 | 303 | 2147 | 160 | 179 | 272 | 1498 | 1120 | 832 | 1497 | 3449 | 1120 | 832 | 1497 | 3449 | - - - | - - - | - - - | - - -
5/1/2026 | 4:45:00 PM | 282.81 | 280.27 | 278.7 | 489.07 | 482.37 | 486.55 | 4.6898 | 3.825 | 5.3905 | 4.1401 | 1.428 | 1.428 | 1.425 | 1.49 | 1.444 | 1.368 | Over-range | 60.02 | 1089 | 718 | 1474 | 3281 | - - - | - - - | - - - | - - - | 1089 | 718 | 1474 | 3281 | 737 | 760 | 46 | 1542 | - - - | - - - | - - - | - - - | 737 | 760 | 46 | 1542 | 1324 | 1066 | 1502 | 3892 | # # # | # # # | # # # | # # # | 0.822 | 0.674 | 0.982 | 0.843 | # # # | # # # | # # # | - - - | 0.828 | 0.683 | 0.999 | 0.854 | - - - | 0.47 | 1.78 | 1.75 | 1.64 | 1.58 | 1.63 | 1.69 | 10.6 | 16.6 | 18.28 | 0 | - - - | - - - | - - - | - - - | 1324 | 1066 | 1502 | 3892 | Over-range | 753 | 780 | 285 | 2091 | 156 | 176 | 273 | 1412 | 1090 | 719 | 1473 | 3282 | 1090 | 719 | 1473 | 3282 | - - - | - - - | - - - | - - -
5/1/2026 | 5:00:00 PM | 282.61 | 279.97 | 278.38 | 488.7 | 481.74 | 486.13 | 4.8889 | 4.1103 | 5.4776 | 4.1285 | 1.428 | 1.429 | 1.425 | 1.491 | 1.429 | 1.339 | Over-range | 60.01 | 1122 | 847 | 1500 | 3469 | - - - | - - - | - - - | - - - | 1122 | 847 | 1500 | 3469 | 790 | 755 | -13 | 1531 | - - - | - - - | - - - | - - - | 790 | 755 | -13 | 1531 | 1381 | 1149 | 1525 | 4055 | # # # | # # # | # # # | # # # | 0.812 | 0.737 | 0.984 | 0.855 | # # # | # # # | # # # | - - - | 0.818 | 0.746 | 0.999 | 0.865 | - - - | 0.441 | 1.77 | 1.7 | 1.66 | 1.57 | 1.62 | 1.68 | 10.1 | 15.37 | 17.96 | 0 | - - - | - - - | - - - | - - - | 1381 | 1149 | 1525 | 4055 | Over-range | 806 | 775 | 275 | 2101 | 161 | 175 | 272 | 1438 | 1121 | 848 | 1499 | 3469 | 1121 | 848 | 1499 | 3469 | - - - | - - - | - - - | - - -
5/1/2026 | 5:15:00 PM | 282.99 | 280.43 | 278.81 | 489.42 | 482.6 | 486.75 | 5.6266 | 5.2418 | 5.8674 | 4.1246 | 1.428 | 1.428 | 1.427 | 1.498 | 1.445 | 1.291 | Over-range | 60.03 | 1247 | 1242 | 1601 | 4090 | - - - | - - - | - - - | - - - | 1247 | 1242 | 1601 | 4090 | 969 | 755 | -162 | 1561 | - - - | - - - | - - - | - - - | 969 | 755 | -162 | 1561 | 1589 | 1467 | 1635 | 4691 | # # # | # # # | # # # | # # # | 0.785 | 0.847 | 0.979 | 0.872 | # # # | # # # | # # # | - - - | 0.782 | 0.847 | 0.984 | 0.873 | - - - | 0.382 | 1.71 | 1.66 | 1.62 | 1.54 | 1.59 | 1.64 | 9 | 13 | 17.4 | 0 | - - - | - - - | - - - | - - - | 1589 | 1467 | 1635 | 4691 | Over-range | 984 | 778 | 334 | 2297 | 167 | 185 | 280 | 1680 | 1259 | 1261 | 1626 | 4146 | 1259 | 1261 | 1626 | 4146 | - - - | - - - | - - - | - - -
5/1/2026 | 5:30:00 PM | 282.78 | 280.19 | 278.65 | 488.98 | 482.31 | 486.43 | 5.1544 | 4.5468 | 5.6382 | 4.14 | 1.428 | 1.428 | 1.427 | 1.497 | 1.417 | 1.303 | Over-range | 60.01 | 1164 | 1008 | 1544 | 3717 | - - - | - - - | - - - | - - - | 1164 | 1008 | 1544 | 3717 | 862 | 755 | -82 | 1534 | - - - | - - - | - - - | - - - | 862 | 755 | -82 | 1534 | 1457 | 1273 | 1571 | 4302 | # # # | # # # | # # # | # # # | 0.799 | 0.792 | 0.983 | 0.864 | # # # | # # # | # # # | - - - | 0.804 | 0.8 | 0.998 | 0.873 | - - - | 0.413 | 1.7 | 1.65 | 1.59 | 1.52 | 1.57 | 1.61 | 9.62 | 14.26 | 17.65 | 0 | - - - | - - - | - - - | - - - | 1457 | 1273 | 1571 | 4302 | Over-range | 877 | 777 | 288 | 2166 | 161 | 185 | 276 | 1529 | 1166 | 1006 | 1546 | 3719 | 1166 | 1006 | 1546 | 3719 | - - - | - - - | - - - | - - -
5/1/2026 | 5:45:00 PM | 282.72 | 280.18 | 278.56 | 489.01 | 482.18 | 486.25 | 5.1524 | 4.5873 | 5.6213 | 4.1327 | 1.428 | 1.429 | 1.428 | 1.499 | 1.428 | 1.307 | Over-range | 60.01 | 1161 | 999 | 1535 | 3695 | - - - | - - - | - - - | - - - | 1161 | 999 | 1535 | 3695 | 857 | 754 | -79 | 1532 | - - - | - - - | - - - | - - - | 857 | 754 | -79 | 1532 | 1453 | 1277 | 1565 | 4295 | # # # | # # # | # # # | # # # | 0.799 | 0.782 | 0.981 | 0.86 | # # # | # # # | # # # | - - - | 0.804 | 0.79 | 0.997 | 0.87 | - - - | 0.415 | 1.7 | 1.66 | 1.58 | 1.53 | 1.57 | 1.61 | 9.73 | 14.52 | 17.83 | 0 | - - - | - - - | - - - | - - - | 1453 | 1277 | 1565 | 4295 | Over-range | 872 | 777 | 305 | 2184 | 160 | 187 | 277 | 1556 | 1164 | 997 | 1536 | 3697 | 1164 | 997 | 1536 | 3697 | - - - | - - - | - - - | - - -
5/1/2026 | 6:00:00 PM | 282.89 | 280.35 | 278.8 | 489.26 | 482.58 | 486.62 | 4.4894 | 3.5694 | 5.3056 | 4.1313 | 1.427 | 1.427 | 1.426 | 1.491 | 1.462 | 1.395 | Over-range | 60.01 | 1053 | 611 | 1450 | 3113 | - - - | - - - | - - - | - - - | 1053 | 611 | 1450 | 3113 | 690 | 762 | 92 | 1544 | - - - | - - - | - - - | - - - | 690 | 762 | 92 | 1544 | 1269 | 998 | 1479 | 3745 | # # # | # # # | # # # | # # # | 0.83 | 0.612 | 0.98 | 0.831 | # # # | # # # | # # # | - - - | 0.837 | 0.621 | 0.997 | 0.843 | - - - | 0.496 | 1.6 | 1.53 | 1.44 | 1.43 | 1.44 | 1.47 | 11.17 | 17.32 | 18.43 | 0 | - - - | - - - | - - - | - - - | 1269 | 998 | 1479 | 3745 | Over-range | 707 | 782 | 292 | 2080 | 156 | 175 | 272 | 1393 | 1054 | 610 | 1451 | 3115 | 1054 | 610 | 1451 | 3115 | - - - | - - - | - - - | - - -
5/1/2026 | 6:15:00 PM | 283.78 | 281.27 | 279.73 | 490.79 | 484.25 | 488.16 | 4.7898 | 3.9714 | 5.4354 | 4.1476 | 1.428 | 1.426 | 1.425 | 1.498 | 1.446 | 1.363 | Over-range | 60.03 | 1108 | 783 | 1494 | 3384 | - - - | - - - | - - - | - - - | 1108 | 783 | 1494 | 3384 | 770 | 773 | 21 | 1564 | - - - | - - - | - - - | - - - | 770 | 773 | 21 | 1564 | 1359 | 1116 | 1520 | 3995 | # # # | # # # | # # # | # # # | 0.815 | 0.702 | 0.983 | 0.847 | # # # | # # # | # # # | - - - | 0.821 | 0.711 | 0.999 | 0.858 | - - - | 0.462 | 1.54 | 1.46 | 1.38 | 1.39 | 1.37 | 1.4 | 10.59 | 16.08 | 18.5 | 0 | - - - | - - - | - - - | - - - | 1359 | 1116 | 1520 | 3995 | Over-range | 787 | 793 | 282 | 2122 | 162 | 179 | 279 | 1435 | 1107 | 783 | 1494 | 3385 | 1107 | 783 | 1494 | 3385 | - - - | - - - | - - - | - - -
5/1/2026 | 6:30:00 PM | 283.68 | 281.18 | 279.52 | 490.71 | 483.92 | 487.86 | 4.8205 | 4.0121 | 5.4624 | 4.1496 | 1.428 | 1.426 | 1.424 | 1.499 | 1.443 | 1.36 | Over-range | 60 | 1112 | 802 | 1501 | 3414 | - - - | - - - | - - - | - - - | 1112 | 802 | 1501 | 3414 | 780 | 772 | 15 | 1567 | - - - | - - - | - - - | - - - | 780 | 772 | 15 | 1567 | 1367 | 1128 | 1527 | 4022 | # # # | # # # | # # # | # # # | 0.813 | 0.711 | 0.983 | 0.849 | # # # | # # # | # # # | - - - | 0.819 | 0.72 | 1 | 0.86 | - - - | 0.459 | 1.53 | 1.47 | 1.38 | 1.4 | 1.39 | 1.4 | 10.5 | 15.9 | 18.35 | 0 | - - - | - - - | - - - | - - - | 1367 | 1128 | 1527 | 4022 | Over-range | 796 | 793 | 279 | 2126 | 159 | 184 | 279 | 1437 | 1114 | 800 | 1503 | 3416 | 1114 | 800 | 1503 | 3416 | - - - | - - - | - - - | - - -
5/1/2026 | 6:45:00 PM | 283.7 | 281.13 | 279.53 | 490.65 | 483.85 | 487.97 | 5.3182 | 4.8544 | 5.7385 | 4.1447 | 1.429 | 1.427 | 1.425 | 1.507 | 1.428 | 1.303 | Over-range | 60 | 1190 | 1101 | 1573 | 3865 | - - - | - - - | - - - | - - - | 1190 | 1101 | 1573 | 3865 | 910 | 767 | -116 | 1560 | - - - | - - - | - - - | - - - | 910 | 767 | -116 | 1560 | 1507 | 1359 | 1604 | 4470 | # # # | # # # | # # # | # # # | 0.79 | 0.81 | 0.981 | 0.865 | # # # | # # # | # # # | - - - | 0.795 | 0.818 | 0.996 | 0.874 | - - - | 0.404 | 1.56 | 1.49 | 1.39 | 1.41 | 1.41 | 1.42 | 9.52 | 13.85 | 17.77 | 0 | - - - | - - - | - - - | - - - | 1507 | 1359 | 1604 | 4470 | Over-range | 924 | 791 | 312 | 2245 | 160 | 192 | 282 | 1613 | 1194 | 1099 | 1573 | 3866 | 1194 | 1099 | 1573 | 3866 | - - - | - - - | - - - | - - -
5/1/2026 | 7:00:00 PM | 283.79 | 281.22 | 279.55 | 490.86 | 483.94 | 488.02 | 5.4045 | 5.5936 | 5.7774 | 3.4432 | 1.428 | 1.426 | 1.424 | 1.51 | 1.446 | 1.293 | Over-range | 60 | 1205 | 1388 | 1583 | 4176 | - - - | - - - | - - - | - - - | 1205 | 1388 | 1583 | 4176 | 933 | 696 | -142 | 1487 | - - - | - - - | - - - | - - - | 933 | 696 | -142 | 1487 | 1533 | 1568 | 1615 | 4716 | # # # | # # # | # # # | # # # | 0.786 | 0.885 | 0.98 | 0.886 | # # # | # # # | # # # | - - - | 0.791 | 0.89 | 0.996 | 0.894 | - - - | 0.356 | 1.54 | 1.46 | 1.36 | 1.39 | 1.37 | 1.39 | 9.4 | 10.55 | 17.65 | 0 | - - - | - - - | - - - | - - - | 1533 | 1568 | 1615 | 4716 | Over-range | 947 | 716 | 319 | 2185 | 162 | 169 | 282 | 1600 | 1208 | 1386 | 1583 | 4177 | 1208 | 1386 | 1583 | 4177 | - - - | - - - | - - - | - - -
5/1/2026 | 7:15:00 PM | 283.79 | 281.3 | 279.68 | 490.9 | 484.18 | 488.1 | 4.9978 | 5.2932 | 5.5655 | 2.743 | 1.427 | 1.425 | 1.423 | 1.505 | 1.437 | 1.335 | Over-range | 60 | 1141 | 1332 | 1531 | 4003 | - - - | - - - | - - - | - - - | 1141 | 1332 | 1531 | 4003 | 827 | 647 | -33 | 1440 | - - - | - - - | - - - | - - - | 827 | 647 | -33 | 1440 | 1418 | 1488 | 1556 | 4462 | # # # | # # # | # # # | # # # | 0.804 | 0.895 | 0.983 | 0.897 | # # # | # # # | # # # | - - - | 0.81 | 0.9 | 0.999 | 0.905 | - - - | 0.36 | 1.5 | 1.43 | 1.34 | 1.37 | 1.34 | 1.36 | 10.18 | 9.51 | 18.14 | 0 | - - - | - - - | - - - | - - - | 1418 | 1488 | 1556 | 4462 | Over-range | 842 | 663 | 283 | 1973 | 160 | 144 | 280 | 1347 | 1141 | 1334 | 1528 | 4003 | 1141 | 1334 | 1528 | 4003 | - - - | - - - | - - - | - - -
5/1/2026 | 7:30:00 PM | 283.99 | 281.59 | 279.93 | 491.32 | 484.66 | 488.48 | 5.3319 | 5.778 | 5.711 | 2.7488 | 1.428 | 1.425 | 1.424 | 1.507 | 1.452 | 1.321 | Over-range | 60 | 1201 | 1475 | 1566 | 4242 | - - - | - - - | - - - | - - - | 1201 | 1475 | 1566 | 4242 | 902 | 651 | -73 | 1479 | - - - | - - - | - - - | - - - | 902 | 651 | -73 | 1479 | 1512 | 1621 | 1598 | 4731 | # # # | # # # | # # # | # # # | 0.795 | 0.91 | 0.98 | 0.897 | # # # | # # # | # # # | - - - | 0.792 | 0.908 | 0.983 | 0.896 | - - - | 0.349 | 1.51 | 1.43 | 1.33 | 1.37 | 1.34 | 1.36 | 9.63 | 9.09 | 18.05 | 0 | - - - | - - - | - - - | - - - | 1512 | 1621 | 1598 | 4731 | Over-range | 917 | 668 | 317 | 2093 | 160 | 153 | 286 | 1468 | 1213 | 1485 | 1578 | 4276 | 1213 | 1485 | 1578 | 4276 | - - - | - - - | - - - | - - -
5/1/2026 | 7:45:00 PM | 284 | 281.53 | 279.88 | 491.29 | 484.54 | 488.44 | 5.415 | 6.1011 | 5.8058 | 2.7556 | 1.428 | 1.426 | 1.424 | 1.511 | 1.464 | 1.298 | Over-range | 60 | 1207 | 1577 | 1592 | 4376 | - - - | - - - | - - - | - - - | 1207 | 1577 | 1592 | 4376 | 937 | 648 | -141 | 1444 | - - - | - - - | - - - | - - - | 937 | 648 | -141 | 1444 | 1536 | 1713 | 1624 | 4874 | # # # | # # # | # # # | # # # | 0.785 | 0.921 | 0.98 | 0.898 | # # # | # # # | # # # | - - - | 0.79 | 0.924 | 0.996 | 0.905 | - - - | 0.33 | 1.52 | 1.44 | 1.33 | 1.37 | 1.35 | 1.36 | 9.43 | 8.66 | 17.64 | 0 | - - - | - - - | - - - | - - - | 1536 | 1713 | 1624 | 4874 | Over-range | 951 | 666 | 321 | 2146 | 160 | 153 | 283 | 1585 | 1208 | 1578 | 1589 | 4376 | 1208 | 1578 | 1589 | 4376 | - - - | - - - | - - - | - - -
5/1/2026 | 8:00:00 PM | 284.12 | 281.63 | 279.95 | 491.45 | 484.73 | 488.61 | 4.5172 | 4.3838 | 5.3082 | 2.7622 | 1.428 | 1.426 | 1.424 | 1.498 | 1.458 | 1.409 | Over-range | 60 | 1061 | 1018 | 1453 | 3532 | - - - | - - - | - - - | - - - | 1061 | 1018 | 1453 | 3532 | 698 | 658 | 102 | 1458 | - - - | - - - | - - - | - - - | 698 | 658 | 102 | 1458 | 1281 | 1225 | 1485 | 3991 | # # # | # # # | # # # | # # # | 0.829 | 0.831 | 0.978 | 0.885 | # # # | # # # | # # # | - - - | 0.835 | 0.837 | 0.996 | 0.895 | - - - | 0.413 | 1.51 | 1.44 | 1.32 | 1.37 | 1.34 | 1.36 | 11.5 | 11.62 | 18.88 | 0 | - - - | - - - | - - - | - - - | 1281 | 1225 | 1485 | 3991 | Over-range | 716 | 673 | 308 | 1856 | 159 | 142 | 279 | 1144 | 1061 | 1020 | 1450 | 3532 | 1061 | 1020 | 1450 | 3532 | - - - | - - - | - - - | - - -
5/1/2026 | 8:15:00 PM | 284.18 | 281.73 | 280.01 | 491.66 | 484.81 | 488.7 | 4.7873 | 4.8733 | 5.4569 | 2.7622 | 1.428 | 1.426 | 1.424 | 1.506 | 1.426 | 1.368 | Over-range | 60 | 1107 | 1194 | 1501 | 3802 | - - - | - - - | - - - | - - - | 1107 | 1194 | 1501 | 3802 | 774 | 657 | 28 | 1458 | - - - | - - - | - - - | - - - | 774 | 657 | 28 | 1458 | 1360 | 1371 | 1528 | 4259 | # # # | # # # | # # # | # # # | 0.814 | 0.871 | 0.982 | 0.893 | # # # | # # # | # # # | - - - | 0.819 | 0.876 | 0.999 | 0.902 | - - - | 0.384 | 1.51 | 1.44 | 1.31 | 1.37 | 1.34 | 1.36 | 10.72 | 10.52 | 18.65 | 0 | - - - | - - - | - - - | - - - | 1360 | 1371 | 1528 | 4259 | Over-range | 790 | 673 | 286 | 1920 | 160 | 146 | 282 | 1248 | 1107 | 1196 | 1498 | 3802 | 1107 | 1196 | 1498 | 3802 | - - - | - - - | - - - | - - -
5/1/2026 | 8:30:00 PM | 284 | 281.54 | 279.85 | 491.32 | 484.51 | 488.42 | 4.768 | 4.8342 | 5.4369 | 2.7578 | 1.429 | 1.427 | 1.424 | 1.505 | 1.425 | 1.37 | Over-range | 60 | 1103 | 1184 | 1495 | 3782 | - - - | - - - | - - - | - - - | 1103 | 1184 | 1495 | 3782 | 769 | 654 | 31 | 1454 | - - - | - - - | - - - | - - - | 769 | 654 | 31 | 1454 | 1354 | 1361 | 1521 | 4236 | # # # | # # # | # # # | # # # | 0.815 | 0.87 | 0.983 | 0.893 | # # # | # # # | # # # | - - - | 0.821 | 0.876 | 0.999 | 0.902 | - - - | 0.385 | 1.52 | 1.45 | 1.35 | 1.38 | 1.36 | 1.38 | 10.71 | 10.49 | 18.6 | 0 | - - - | - - - | - - - | - - - | 1354 | 1361 | 1521 | 4236 | Over-range | 785 | 670 | 283 | 1908 | 157 | 149 | 281 | 1235 | 1106 | 1183 | 1494 | 3783 | 1106 | 1183 | 1494 | 3783 | - - - | - - - | - - - | - - -
5/1/2026 | 8:45:00 PM | 283.81 | 281.41 | 279.59 | 491.07 | 484.22 | 487.95 | 5.1552 | 5.5988 | 5.6483 | 2.7535 | 1.429 | 1.427 | 1.424 | 1.513 | 1.454 | 1.317 | Over-range | 60 | 1164 | 1420 | 1550 | 4134 | - - - | - - - | - - - | - - - | 1164 | 1420 | 1550 | 4134 | 868 | 648 | -73 | 1442 | - - - | - - - | - - - | - - - | 868 | 648 | -73 | 1442 | 1462 | 1570 | 1579 | 4610 | # # # | # # # | # # # | # # # | 0.797 | 0.905 | 0.982 | 0.897 | # # # | # # # | # # # | - - - | 0.802 | 0.909 | 0.998 | 0.905 | - - - | 0.349 | 1.55 | 1.44 | 1.35 | 1.39 | 1.36 | 1.38 | 9.9 | 9.46 | 18.2 | 0 | - - - | - - - | - - - | - - - | 1462 | 1570 | 1579 | 4610 | Over-range | 883 | 666 | 301 | 2039 | 163 | 154 | 285 | 1439 | 1167 | 1418 | 1551 | 4136 | 1167 | 1418 | 1551 | 4136 | - - - | - - - | - - - | - - -
5/1/2026 | 9:00:00 PM | 284.3 | 281.85 | 280.1 | 491.87 | 484.99 | 488.88 | 5.4357 | 6.1359 | 5.8196 | 2.7572 | 1.429 | 1.427 | 1.424 | 1.516 | 1.466 | 1.288 | Over-range | 59.99 | 1210 | 1590 | 1597 | 4397 | - - - | - - - | - - - | - - - | 1210 | 1590 | 1597 | 4397 | 946 | 654 | -143 | 1456 | - - - | - - - | - - - | - - - | 946 | 654 | -143 | 1456 | 1545 | 1727 | 1630 | 4901 | # # # | # # # | # # # | # # # | 0.783 | 0.921 | 0.98 | 0.897 | # # # | # # # | # # # | - - - | 0.788 | 0.925 | 0.996 | 0.905 | - - - | 0.331 | 1.56 | 1.46 | 1.36 | 1.41 | 1.38 | 1.4 | 9.45 | 8.76 | 17.76 | 0 | - - - | - - - | - - - | - - - | 1545 | 1727 | 1630 | 4901 | Over-range | 960 | 672 | 323 | 2165 | 165 | 156 | 286 | 1601 | 1212 | 1589 | 1598 | 4398 | 1212 | 1589 | 1598 | 4398 | - - - | - - - | - - - | - - -
5/1/2026 | 9:15:00 PM | 284.33 | 281.87 | 280.21 | 491.86 | 485.11 | 489.04 | 5.1072 | 5.4875 | 5.61 | 2.7543 | 1.429 | 1.427 | 1.425 | 1.51 | 1.449 | 1.322 | Over-range | 60 | 1158 | 1389 | 1544 | 4091 | - - - | - - - | - - - | - - - | 1158 | 1389 | 1544 | 4091 | 860 | 656 | -56 | 1459 | - - - | - - - | - - - | - - - | 860 | 656 | -56 | 1459 | 1451 | 1544 | 1572 | 4567 | # # # | # # # | # # # | # # # | 0.798 | 0.9 | 0.982 | 0.896 | # # # | # # # | # # # | - - - | 0.803 | 0.904 | 0.999 | 0.904 | - - - | 0.357 | 1.56 | 1.46 | 1.39 | 1.42 | 1.39 | 1.41 | 10.07 | 9.59 | 18.3 | 0 | - - - | - - - | - - - | - - - | 1451 | 1544 | 1572 | 4567 | Over-range | 875 | 673 | 294 | 2031 | 159 | 152 | 285 | 1411 | 1160 | 1390 | 1541 | 4091 | 1160 | 1390 | 1541 | 4091 | - - - | - - - | - - - | - - -
5/1/2026 | 9:30:00 PM | 284.76 | 282.37 | 280.65 | 492.64 | 486.01 | 489.73 | 4.936 | 5.1468 | 5.5427 | 2.7716 | 1.429 | 1.427 | 1.425 | 1.506 | 1.431 | 1.347 | Over-range | 60 | 1131 | 1283 | 1529 | 3943 | - - - | - - - | - - - | - - - | 1131 | 1283 | 1529 | 3943 | 819 | 665 | -3 | 1480 | - - - | - - - | - - - | - - - | 819 | 665 | -3 | 1480 | 1406 | 1453 | 1556 | 4414 | # # # | # # # | # # # | # # # | 0.805 | 0.883 | 0.983 | 0.893 | # # # | # # # | # # # | - - - | 0.81 | 0.888 | 1 | 0.902 | - - - | 0.375 | 1.61 | 1.47 | 1.39 | 1.44 | 1.4 | 1.43 | 10.49 | 10.17 | 18.51 | 0 | - - - | - - - | - - - | - - - | 1406 | 1453 | 1556 | 4414 | Over-range | 835 | 682 | 286 | 1985 | 160 | 152 | 286 | 1323 | 1133 | 1284 | 1526 | 3943 | 1133 | 1284 | 1526 | 3943 | - - - | - - - | - - - | - - -
5/1/2026 | 9:45:00 PM | 285.02 | 282.64 | 280.9 | 493.11 | 486.46 | 490.17 | 5.365 | 5.806 | 5.7298 | 2.7605 | 1.429 | 1.427 | 1.425 | 1.508 | 1.456 | 1.312 | Over-range | 60.01 | 1208 | 1490 | 1578 | 4276 | - - - | - - - | - - - | - - - | 1208 | 1490 | 1578 | 4276 | 918 | 666 | -70 | 1513 | - - - | - - - | - - - | - - - | 918 | 666 | -70 | 1513 | 1527 | 1640 | 1609 | 4776 | # # # | # # # | # # # | # # # | 0.791 | 0.909 | 0.98 | 0.895 | # # # | # # # | # # # | - - - | 0.788 | 0.906 | 0.985 | 0.894 | - - - | 0.354 | 1.61 | 1.49 | 1.39 | 1.44 | 1.41 | 1.44 | 9.7 | 9.38 | 18.34 | 0 | - - - | - - - | - - - | - - - | 1527 | 1640 | 1609 | 4776 | Over-range | 934 | 683 | 316 | 2128 | 171 | 154 | 293 | 1488 | 1221 | 1501 | 1591 | 4314 | 1221 | 1501 | 1591 | 4314 | - - - | - - - | - - - | - - -
5/1/2026 | 10:00:00 PM | 285.29 | 282.91 | 281.14 | 493.63 | 486.85 | 490.61 | 5.3235 | 5.897 | 5.7583 | 2.7678 | 1.429 | 1.427 | 1.425 | 1.512 | 1.459 | 1.292 | Over-range | 60.01 | 1193 | 1521 | 1589 | 4303 | - - - | - - - | - - - | - - - | 1193 | 1521 | 1589 | 4303 | 924 | 668 | -104 | 1487 | - - - | - - - | - - - | - - - | 924 | 668 | -104 | 1487 | 1519 | 1668 | 1619 | 4806 | # # # | # # # | # # # | # # # | 0.786 | 0.911 | 0.982 | 0.895 | # # # | # # # | # # # | - - - | 0.791 | 0.916 | 0.997 | 0.903 | - - - | 0.345 | 1.61 | 1.46 | 1.42 | 1.45 | 1.42 | 1.45 | 9.79 | 9.27 | 18.18 | 0 | - - - | - - - | - - - | - - - | 1519 | 1668 | 1619 | 4806 | Over-range | 940 | 686 | 310 | 2141 | 173 | 157 | 291 | 1541 | 1193 | 1520 | 1590 | 4303 | 1193 | 1520 | 1590 | 4303 | - - - | - - - | - - - | - - -
5/1/2026 | 10:15:00 PM | 285.29 | 282.79 | 281.11 | 493.51 | 486.68 | 490.65 | 4.9823 | 5.2939 | 5.5605 | 2.7656 | 1.429 | 1.427 | 1.424 | 1.506 | 1.474 | 1.349 | Over-range | 60 | 1133 | 1288 | 1527 | 3948 | - - - | - - - | - - - | - - - | 1133 | 1288 | 1527 | 3948 | 825 | 671 | -4 | 1491 | - - - | - - - | - - - | - - - | 825 | 671 | -4 | 1491 | 1413 | 1471 | 1561 | 4445 | # # # | # # # | # # # | # # # | 0.802 | 0.876 | 0.978 | 0.888 | # # # | # # # | # # # | - - - | 0.808 | 0.881 | 0.995 | 0.898 | - - - | 0.378 | 1.6 | 1.5 | 1.39 | 1.45 | 1.41 | 1.44 | 10.76 | 10.69 | 18.65 | 0 | - - - | - - - | - - - | - - - | 1413 | 1471 | 1561 | 4445 | Over-range | 842 | 688 | 322 | 2039 | 169 | 152 | 288 | 1380 | 1133 | 1290 | 1526 | 3948 | 1133 | 1290 | 1526 | 3948 | - - - | - - - | - - - | - - -
5/1/2026 | 10:30:00 PM | 284.7 | 282.21 | 280.47 | 492.55 | 485.62 | 489.53 | 4.647 | 4.607 | 5.3921 | 2.772 | 1.429 | 1.427 | 1.425 | 1.503 | 1.438 | 1.391 | Over-range | 60.02 | 1084 | 1103 | 1483 | 3669 | - - - | - - - | - - - | - - - | 1084 | 1103 | 1483 | 3669 | 740 | 663 | 72 | 1475 | - - - | - - - | - - - | - - - | 740 | 663 | 72 | 1475 | 1322 | 1297 | 1512 | 4131 | # # # | # # # | # # # | # # # | 0.82 | 0.85 | 0.981 | 0.888 | # # # | # # # | # # # | - - - | 0.826 | 0.855 | 0.999 | 0.898 | - - - | 0.402 | 1.63 | 1.5 | 1.42 | 1.45 | 1.42 | 1.46 | 11.18 | 11.25 | 18.8 | 0 | - - - | - - - | - - - | - - - | 1322 | 1297 | 1512 | 4131 | Over-range | 757 | 680 | 296 | 1897 | 161 | 150 | 283 | 1192 | 1086 | 1101 | 1483 | 3670 | 1086 | 1101 | 1483 | 3670 | - - - | - - - | - - - | - - -
5/1/2026 | 10:45:00 PM | 284.67 | 282.09 | 280.41 | 492.4 | 485.41 | 489.54 | 4.7225 | 4.7434 | 5.4073 | 2.7604 | 1.429 | 1.427 | 1.424 | 1.503 | 1.423 | 1.382 | Over-range | 60 | 1096 | 1152 | 1488 | 3737 | - - - | - - - | - - - | - - - | 1096 | 1152 | 1488 | 3737 | 761 | 661 | 49 | 1472 | - - - | - - - | - - - | - - - | 761 | 661 | 49 | 1472 | 1344 | 1337 | 1516 | 4198 | # # # | # # # | # # # | # # # | 0.816 | 0.862 | 0.982 | 0.89 | # # # | # # # | # # # | - - - | 0.823 | 0.867 | 0.999 | 0.9 | - - - | 0.394 | 1.62 | 1.5 | 1.42 | 1.45 | 1.43 | 1.46 | 10.96 | 10.86 | 18.8 | 0 | - - - | - - - | - - - | - - - | 1344 | 1337 | 1516 | 4198 | Over-range | 778 | 678 | 289 | 1913 | 162 | 151 | 284 | 1221 | 1099 | 1150 | 1490 | 3738 | 1099 | 1150 | 1490 | 3738 | - - - | - - - | - - - | - - -
5/1/2026 | 11:00:00 PM | 285.06 | 282.46 | 280.75 | 493.06 | 485.99 | 490.19 | 5.0207 | 5.3132 | 5.5831 | 2.7679 | 1.429 | 1.427 | 1.424 | 1.509 | 1.44 | 1.337 | Over-range | 60 | 1144 | 1331 | 1539 | 4015 | - - - | - - - | - - - | - - - | 1144 | 1331 | 1539 | 4015 | 842 | 663 | -24 | 1481 | - - - | - - - | - - - | - - - | 842 | 663 | -24 | 1481 | 1430 | 1497 | 1567 | 4494 | # # # | # # # | # # # | # # # | 0.8 | 0.889 | 0.982 | 0.893 | # # # | # # # | # # # | - - - | 0.806 | 0.894 | 0.999 | 0.902 | - - - | 0.369 | 1.65 | 1.5 | 1.42 | 1.47 | 1.44 | 1.47 | 10.35 | 10.12 | 18.52 | 0 | - - - | - - - | - - - | - - - | 1430 | 1497 | 1567 | 4494 | Over-range | 858 | 682 | 293 | 2019 | 164 | 157 | 288 | 1371 | 1147 | 1329 | 1540 | 4016 | 1147 | 1329 | 1540 | 4016 | - - - | - - - | - - - | - - -
5/1/2026 | 11:15:00 PM | 285.15 | 282.51 | 280.74 | 493.21 | 486.03 | 490.22 | 5.3607 | 5.9661 | 5.7546 | 2.7625 | 1.429 | 1.428 | 1.425 | 1.511 | 1.46 | 1.293 | Over-range | 60 | 1199 | 1538 | 1584 | 4320 | - - - | - - - | - - - | - - - | 1199 | 1538 | 1584 | 4320 | 933 | 662 | -115 | 1479 | - - - | - - - | - - - | - - - | 933 | 662 | -115 | 1479 | 1528 | 1683 | 1615 | 4826 | # # # | # # # | # # # | # # # | 0.785 | 0.914 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.79 | 0.918 | 0.997 | 0.903 | - - - | 0.342 | 1.66 | 1.53 | 1.48 | 1.49 | 1.47 | 1.51 | 9.72 | 9.14 | 18.14 | 0 | - - - | - - - | - - - | - - - | 1528 | 1683 | 1615 | 4826 | Over-range | 947 | 681 | 315 | 2149 | 162 | 161 | 290 | 1558 | 1202 | 1537 | 1582 | 4321 | 1202 | 1537 | 1582 | 4321 | - - - | - - - | - - - | - - -
5/1/2026 | 11:30:00 PM | 285.49 | 282.86 | 281.12 | 493.82 | 486.61 | 490.87 | 4.5962 | 4.5217 | 5.3722 | 2.7779 | 1.429 | 1.427 | 1.424 | 1.499 | 1.458 | 1.401 | Over-range | 60 | 1074 | 1059 | 1477 | 3610 | - - - | - - - | - - - | - - - | 1074 | 1059 | 1477 | 3610 | 730 | 674 | 98 | 1502 | - - - | - - - | - - - | - - - | 730 | 674 | 98 | 1502 | 1309 | 1269 | 1510 | 4088 | # # # | # # # | # # # | # # # | 0.82 | 0.835 | 0.978 | 0.883 | # # # | # # # | # # # | - - - | 0.827 | 0.84 | 0.996 | 0.893 | - - - | 0.416 | 1.64 | 1.54 | 1.46 | 1.49 | 1.46 | 1.49 | 11.62 | 11.78 | 18.88 | 0 | - - - | - - - | - - - | - - - | 1309 | 1269 | 1510 | 4088 | Over-range | 748 | 691 | 310 | 1917 | 162 | 152 | 284 | 1188 | 1077 | 1059 | 1475 | 3611 | 1077 | 1059 | 1475 | 3611 | - - - | - - - | - - - | - - -
5/1/2026 | 11:45:00 PM | 285.92 | 283.34 | 281.5 | 494.66 | 487.37 | 491.53 | 4.7292 | 4.7537 | 5.421 | 2.7709 | 1.43 | 1.428 | 1.425 | 1.503 | 1.433 | 1.384 | Over-range | 60.01 | 1097 | 1148 | 1496 | 3741 | - - - | - - - | - - - | - - - | 1097 | 1148 | 1496 | 3741 | 772 | 679 | 63 | 1514 | - - - | - - - | - - - | - - - | 772 | 679 | 63 | 1514 | 1351 | 1344 | 1526 | 4221 | # # # | # # # | # # # | # # # | 0.812 | 0.854 | 0.981 | 0.886 | # # # | # # # | # # # | - - - | 0.818 | 0.86 | 0.999 | 0.896 | - - - | 0.405 | 1.68 | 1.56 | 1.49 | 1.52 | 1.5 | 1.54 | 11.25 | 11.3 | 19.09 | 0 | - - - | - - - | - - - | - - - | 1351 | 1344 | 1526 | 4221 | Over-range | 789 | 697 | 299 | 1956 | 165 | 157 | 290 | 1237 | 1100 | 1146 | 1497 | 3742 | 1100 | 1146 | 1497 | 3742 | - - - | - - - | - - - | - - -
5/2/2026 | 12:00:00 AM | 285.94 | 283.41 | 281.6 | 494.66 | 487.61 | 491.61 | 4.8304 | 4.7513 | 5.4626 | 2.7762 | 1.429 | 1.427 | 1.424 | 1.499 | 1.422 | 1.392 | Over-range | 60 | 1121 | 1152 | 1506 | 3779 | - - - | - - - | - - - | - - - | 1121 | 1152 | 1506 | 3779 | 784 | 679 | 88 | 1551 | - - - | - - - | - - - | - - - | 784 | 679 | 88 | 1551 | 1378 | 1346 | 1538 | 4263 | # # # | # # # | # # # | # # # | 0.814 | 0.856 | 0.979 | 0.886 | # # # | # # # | # # # | - - - | 0.812 | 0.854 | 0.988 | 0.888 | - - - | 0.411 | 1.69 | 1.54 | 1.48 | 1.51 | 1.49 | 1.52 | 11.09 | 11.19 | 18.91 | 0 | - - - | - - - | - - - | - - - | 1378 | 1346 | 1538 | 4263 | Over-range | 801 | 697 | 310 | 1973 | 166 | 156 | 290 | 1212 | 1134 | 1159 | 1515 | 3808 | 1134 | 1159 | 1515 | 3808 | - - - | - - - | - - - | - - -
5/2/2026 | 12:15:00 AM | 286.16 | 283.49 | 281.73 | 495 | 487.71 | 491.9 | 4.8794 | 5.0317 | 5.5108 | 2.7744 | 1.428 | 1.425 | 1.423 | 1.506 | 1.427 | 1.364 | Over-range | 60.01 | 1122 | 1240 | 1524 | 3886 | - - - | - - - | - - - | - - - | 1122 | 1240 | 1524 | 3886 | 814 | 680 | 25 | 1519 | - - - | - - - | - - - | - - - | 814 | 680 | 25 | 1519 | 1396 | 1424 | 1552 | 4372 | # # # | # # # | # # # | # # # | 0.804 | 0.871 | 0.982 | 0.889 | # # # | # # # | # # # | - - - | 0.81 | 0.876 | 0.999 | 0.898 | - - - | 0.391 | 1.7 | 1.53 | 1.46 | 1.51 | 1.48 | 1.51 | 10.91 | 10.78 | 18.89 | 0 | - - - | - - - | - - - | - - - | 1396 | 1424 | 1552 | 4372 | Over-range | 830 | 698 | 295 | 2003 | 165 | 157 | 291 | 1305 | 1124 | 1241 | 1521 | 3886 | 1124 | 1241 | 1521 | 3886 | - - - | - - - | - - - | - - -
5/2/2026 | 12:30:00 AM | 286.38 | 283.57 | 281.92 | 495.25 | 487.93 | 492.29 | 5.3999 | 6.0317 | 5.7928 | 2.7665 | 1.426 | 1.424 | 1.422 | 1.513 | 1.451 | 1.294 | Over-range | 59.99 | 1205 | 1559 | 1602 | 4366 | - - - | - - - | - - - | - - - | 1205 | 1559 | 1602 | 4366 | 953 | 679 | -112 | 1519 | - - - | - - - | - - - | - - - | 953 | 679 | -112 | 1519 | 1546 | 1709 | 1633 | 4887 | # # # | # # # | # # # | # # # | 0.78 | 0.913 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.785 | 0.917 | 0.998 | 0.902 | - - - | 0.348 | 1.7 | 1.55 | 1.49 | 1.51 | 1.5 | 1.53 | 9.85 | 9.29 | 18.3 | 0 | - - - | - - - | - - - | - - - | 1546 | 1709 | 1633 | 4887 | Over-range | 968 | 698 | 317 | 2196 | 171 | 161 | 295 | 1585 | 1206 | 1561 | 1599 | 4366 | 1206 | 1561 | 1599 | 4366 | - - - | - - - | - - - | - - -
5/2/2026 | 12:45:00 AM | 286.63 | 283.76 | 282.14 | 495.59 | 488.31 | 492.72 | 5.1846 | 5.6076 | 5.6734 | 2.7754 | 1.427 | 1.425 | 1.422 | 1.512 | 1.438 | 1.319 | Over-range | 60 | 1171 | 1427 | 1572 | 4170 | - - - | - - - | - - - | - - - | 1171 | 1427 | 1572 | 4170 | 898 | 684 | -53 | 1528 | - - - | - - - | - - - | - - - | 898 | 684 | -53 | 1528 | 1486 | 1591 | 1601 | 4677 | # # # | # # # | # # # | # # # | 0.788 | 0.897 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.793 | 0.901 | 0.999 | 0.9 | - - - | 0.367 | 1.71 | 1.57 | 1.49 | 1.53 | 1.51 | 1.54 | 10.33 | 9.91 | 18.57 | 0 | - - - | - - - | - - - | - - - | 1486 | 1591 | 1601 | 4677 | Over-range | 915 | 703 | 300 | 2118 | 175 | 159 | 294 | 1466 | 1171 | 1426 | 1573 | 4171 | 1171 | 1426 | 1573 | 4171 | - - - | - - - | - - - | - - -
5/2/2026 | 1:00:00 AM | 286.87 | 284.1 | 282.39 | 496.12 | 488.83 | 493.1 | 4.5076 | 4.3567 | 5.3409 | 2.7837 | 1.427 | 1.425 | 1.423 | 1.499 | 1.47 | 1.419 | Over-range | 60.01 | 1060 | 1001 | 1472 | 3532 | - - - | - - - | - - - | - - - | 1060 | 1001 | 1472 | 3532 | 717 | 693 | 136 | 1546 | - - - | - - - | - - - | - - - | 717 | 693 | 136 | 1546 | 1291 | 1231 | 1508 | 4030 | # # # | # # # | # # # | # # # | 0.821 | 0.813 | 0.976 | 0.876 | # # # | # # # | # # # | - - - | 0.828 | 0.82 | 0.995 | 0.887 | - - - | 0.438 | 1.72 | 1.6 | 1.49 | 1.53 | 1.52 | 1.55 | 12.16 | 12.65 | 19.37 | 0 | - - - | - - - | - - - | - - - | 1291 | 1231 | 1508 | 4030 | Over-range | 737 | 711 | 328 | 1939 | 171 | 156 | 290 | 1168 | 1059 | 1001 | 1473 | 3532 | 1059 | 1001 | 1473 | 3532 | - - - | - - - | - - - | - - -
5/2/2026 | 1:15:00 AM | 287.13 | 284.39 | 282.73 | 496.56 | 489.4 | 493.63 | 4.7778 | 4.8353 | 5.4699 | 2.7835 | 1.427 | 1.425 | 1.422 | 1.506 | 1.428 | 1.383 | Over-range | 59.99 | 1104 | 1171 | 1516 | 3791 | - - - | - - - | - - - | - - - | 1104 | 1171 | 1516 | 3791 | 794 | 699 | 65 | 1558 | - - - | - - - | - - - | - - - | 794 | 699 | 65 | 1558 | 1371 | 1373 | 1546 | 4291 | # # # | # # # | # # # | # # # | 0.805 | 0.853 | 0.98 | 0.883 | # # # | # # # | # # # | - - - | 0.812 | 0.859 | 0.999 | 0.894 | - - - | 0.411 | 1.73 | 1.59 | 1.51 | 1.54 | 1.53 | 1.56 | 11.4 | 11.62 | 19.37 | 0 | - - - | - - - | - - - | - - - | 1371 | 1373 | 1546 | 4291 | Over-range | 813 | 716 | 306 | 2010 | 174 | 158 | 297 | 1269 | 1103 | 1173 | 1515 | 3791 | 1103 | 1173 | 1515 | 3791 | - - - | - - - | - - - | - - -
5/2/2026 | 1:30:00 AM | 285.12 | 282.45 | 280.71 | 493.16 | 485.98 | 490.12 | 4.7314 | 4.759 | 5.4083 | 2.7547 | 1.427 | 1.425 | 1.422 | 1.506 | 1.42 | 1.382 | Over-range | 60.01 | 1098 | 1158 | 1490 | 3746 | - - - | - - - | - - - | - - - | 1098 | 1158 | 1490 | 3746 | 766 | 666 | 51 | 1483 | - - - | - - - | - - - | - - - | 766 | 666 | 51 | 1483 | 1349 | 1344 | 1518 | 4211 | # # # | # # # | # # # | # # # | 0.814 | 0.862 | 0.982 | 0.889 | # # # | # # # | # # # | - - - | 0.819 | 0.867 | 0.999 | 0.899 | - - - | 0.396 | 1.72 | 1.57 | 1.52 | 1.54 | 1.53 | 1.56 | 11.03 | 10.98 | 18.98 | 0 | - - - | - - - | - - - | - - - | 1349 | 1344 | 1518 | 4211 | Over-range | 784 | 682 | 290 | 1924 | 166 | 148 | 286 | 1226 | 1097 | 1159 | 1489 | 3746 | 1097 | 1159 | 1489 | 3746 | - - - | - - - | - - - | - - -
5/2/2026 | 1:45:00 AM | 285.29 | 282.64 | 280.89 | 493.44 | 486.34 | 490.41 | 4.7202 | 4.7643 | 5.4507 | 2.7645 | 1.427 | 1.424 | 1.422 | 1.505 | 1.421 | 1.383 | Over-range | 60.02 | 1096 | 1156 | 1503 | 3755 | - - - | - - - | - - - | - - - | 1096 | 1156 | 1503 | 3755 | 765 | 672 | 54 | 1491 | - - - | - - - | - - - | - - - | 765 | 672 | 54 | 1491 | 1347 | 1346 | 1531 | 4224 | # # # | # # # | # # # | # # # | 0.814 | 0.859 | 0.982 | 0.889 | # # # | # # # | # # # | - - - | 0.82 | 0.865 | 0.999 | 0.899 | - - - | 0.397 | 1.72 | 1.58 | 1.52 | 1.54 | 1.53 | 1.57 | 11.09 | 11.01 | 18.9 | 0 | - - - | - - - | - - - | - - - | 1347 | 1346 | 1531 | 4224 | Over-range | 782 | 690 | 293 | 1934 | 164 | 154 | 288 | 1232 | 1097 | 1158 | 1500 | 3755 | 1097 | 1158 | 1500 | 3755 | - - - | - - - | - - - | - - -
5/2/2026 | 2:00:00 AM | 285.18 | 282.46 | 280.83 | 493.19 | 486.08 | 490.31 | 5.0921 | 5.4583 | 5.6184 | 2.7561 | 1.427 | 1.425 | 1.422 | 1.512 | 1.443 | 1.33 | Over-range | 60 | 1155 | 1377 | 1549 | 4082 | - - - | - - - | - - - | - - - | 1155 | 1377 | 1549 | 4082 | 862 | 664 | -42 | 1482 | - - - | - - - | - - - | - - - | 862 | 664 | -42 | 1482 | 1451 | 1538 | 1577 | 4566 | # # # | # # # | # # # | # # # | 0.796 | 0.896 | 0.982 | 0.894 | # # # | # # # | # # # | - - - | 0.802 | 0.9 | 0.999 | 0.903 | - - - | 0.363 | 1.73 | 1.59 | 1.54 | 1.55 | 1.54 | 1.58 | 10.22 | 10.04 | 18.62 | 0 | - - - | - - - | - - - | - - - | 1451 | 1538 | 1577 | 4566 | Over-range | 878 | 682 | 298 | 2047 | 167 | 155 | 290 | 1410 | 1155 | 1379 | 1547 | 4081 | 1155 | 1379 | 1547 | 4081 | - - - | - - - | - - - | - - -
5/2/2026 | 2:15:00 AM | 284.97 | 282.25 | 280.66 | 492.79 | 485.79 | 489.99 | 5.2754 | 5.6269 | 5.6837 | 2.7506 | 1.427 | 1.425 | 1.422 | 1.508 | 1.447 | 1.327 | Over-range | 60 | 1194 | 1434 | 1565 | 4192 | - - - | - - - | - - - | - - - | 1194 | 1434 | 1565 | 4192 | 894 | 660 | -42 | 1510 | - - - | - - - | - - - | - - - | 894 | 660 | -42 | 1510 | 1501 | 1586 | 1595 | 4682 | # # # | # # # | # # # | # # # | 0.795 | 0.904 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.793 | 0.901 | 0.985 | 0.895 | - - - | 0.36 | 1.71 | 1.6 | 1.56 | 1.55 | 1.55 | 1.58 | 9.86 | 9.57 | 18.31 | 0 | - - - | - - - | - - - | - - - | 1501 | 1586 | 1595 | 4682 | Over-range | 909 | 677 | 308 | 2085 | 167 | 153 | 289 | 1428 | 1204 | 1445 | 1576 | 4226 | 1204 | 1445 | 1576 | 4226 | - - - | - - - | - - - | - - -
5/2/2026 | 2:30:00 AM | 284.89 | 282.17 | 280.58 | 492.61 | 485.7 | 489.83 | 4.809 | 4.9494 | 5.473 | 2.7569 | 1.427 | 1.425 | 1.423 | 1.505 | 1.463 | 1.37 | Over-range | 60.01 | 1107 | 1194 | 1503 | 3804 | - - - | - - - | - - - | - - - | 1107 | 1194 | 1503 | 3804 | 779 | 661 | 35 | 1475 | - - - | - - - | - - - | - - - | 779 | 661 | 35 | 1475 | 1365 | 1380 | 1535 | 4280 | # # # | # # # | # # # | # # # | 0.811 | 0.865 | 0.98 | 0.889 | # # # | # # # | # # # | - - - | 0.817 | 0.87 | 0.997 | 0.898 | - - - | 0.388 | 1.72 | 1.6 | 1.54 | 1.55 | 1.54 | 1.58 | 11 | 11 | 18.63 | 0 | - - - | - - - | - - - | - - - | 1365 | 1380 | 1535 | 4280 | Over-range | 796 | 678 | 306 | 1958 | 164 | 149 | 283 | 1281 | 1107 | 1196 | 1501 | 3804 | 1107 | 1196 | 1501 | 3804 | - - - | - - - | - - - | - - -
5/2/2026 | 2:45:00 AM | 285.25 | 282.58 | 280.95 | 493.33 | 486.35 | 490.44 | 4.5848 | 4.4959 | 5.3593 | 2.7551 | 1.427 | 1.424 | 1.422 | 1.504 | 1.437 | 1.403 | Over-range | 60.01 | 1074 | 1068 | 1475 | 3616 | - - - | - - - | - - - | - - - | 1074 | 1068 | 1475 | 3616 | 727 | 668 | 95 | 1490 | - - - | - - - | - - - | - - - | 727 | 668 | 95 | 1490 | 1307 | 1269 | 1506 | 4082 | # # # | # # # | # # # | # # # | 0.821 | 0.841 | 0.98 | 0.886 | # # # | # # # | # # # | - - - | 0.827 | 0.848 | 0.997 | 0.896 | - - - | 0.412 | 1.74 | 1.58 | 1.55 | 1.55 | 1.54 | 1.59 | 11.46 | 11.67 | 19.06 | 0 | - - - | - - - | - - - | - - - | 1307 | 1269 | 1506 | 4082 | Over-range | 746 | 684 | 303 | 1893 | 166 | 148 | 285 | 1167 | 1072 | 1069 | 1474 | 3616 | 1072 | 1069 | 1474 | 3616 | - - - | - - - | - - - | - - -
5/2/2026 | 3:00:00 AM | 285.28 | 282.53 | 280.97 | 493.3 | 486.31 | 490.51 | 4.6793 | 4.6654 | 5.404 | 2.7548 | 1.427 | 1.424 | 1.421 | 1.504 | 1.425 | 1.39 | Over-range | 60.01 | 1090 | 1126 | 1489 | 3705 | - - - | - - - | - - - | - - - | 1090 | 1126 | 1489 | 3705 | 753 | 667 | 69 | 1489 | - - - | - - - | - - - | - - - | 753 | 667 | 69 | 1489 | 1335 | 1317 | 1518 | 4170 | # # # | # # # | # # # | # # # | 0.816 | 0.855 | 0.981 | 0.888 | # # # | # # # | # # # | - - - | 0.823 | 0.86 | 0.999 | 0.898 | - - - | 0.402 | 1.71 | 1.58 | 1.53 | 1.54 | 1.53 | 1.57 | 11.19 | 11.2 | 18.95 | 0 | - - - | - - - | - - - | - - - | 1335 | 1317 | 1518 | 4170 | Over-range | 771 | 683 | 295 | 1914 | 166 | 148 | 286 | 1203 | 1089 | 1127 | 1489 | 3705 | 1089 | 1127 | 1489 | 3705 | - - - | - - - | - - - | - - -
5/2/2026 | 3:15:00 AM | 285.42 | 282.84 | 281.15 | 493.67 | 486.83 | 490.71 | 4.9158 | 5.1173 | 5.5284 | 2.7577 | 1.427 | 1.424 | 1.422 | 1.508 | 1.429 | 1.357 | Over-range | 60.01 | 1127 | 1272 | 1526 | 3925 | - - - | - - - | - - - | - - - | 1127 | 1272 | 1526 | 3925 | 817 | 668 | 7 | 1492 | - - - | - - - | - - - | - - - | 817 | 668 | 7 | 1492 | 1402 | 1445 | 1554 | 4402 | # # # | # # # | # # # | # # # | 0.804 | 0.88 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.809 | 0.884 | 1 | 0.901 | - - - | 0.38 | 1.71 | 1.57 | 1.54 | 1.54 | 1.53 | 1.57 | 10.66 | 10.58 | 18.86 | 0 | - - - | - - - | - - - | - - - | 1402 | 1445 | 1554 | 4402 | Over-range | 834 | 686 | 293 | 1993 | 170 | 153 | 290 | 1319 | 1126 | 1272 | 1527 | 3925 | 1126 | 1272 | 1527 | 3925 | - - - | - - - | - - - | - - -
5/2/2026 | 3:30:00 AM | 285.39 | 282.72 | 281.02 | 493.62 | 486.48 | 490.63 | 5.2599 | 5.7848 | 5.7134 | 2.75 | 1.426 | 1.423 | 1.421 | 1.512 | 1.444 | 1.306 | Over-range | 60 | 1182 | 1483 | 1576 | 4241 | - - - | - - - | - - - | - - - | 1182 | 1483 | 1576 | 4241 | 908 | 665 | -85 | 1487 | - - - | - - - | - - - | - - - | 908 | 665 | -85 | 1487 | 1500 | 1633 | 1605 | 4739 | # # # | # # # | # # # | # # # | 0.788 | 0.908 | 0.982 | 0.895 | # # # | # # # | # # # | - - - | 0.793 | 0.912 | 0.998 | 0.903 | - - - | 0.351 | 1.72 | 1.57 | 1.5 | 1.53 | 1.52 | 1.56 | 9.95 | 9.42 | 18.27 | 0 | - - - | - - - | - - - | - - - | 1500 | 1633 | 1605 | 4739 | Over-range | 924 | 683 | 305 | 2114 | 172 | 155 | 290 | 1501 | 1182 | 1482 | 1577 | 4241 | 1182 | 1482 | 1577 | 4241 | - - - | - - - | - - - | - - -
5/2/2026 | 3:45:00 AM | 285.36 | 282.73 | 281.04 | 493.6 | 486.54 | 490.6 | 5.2109 | 5.6839 | 5.6834 | 2.7521 | 1.427 | 1.424 | 1.422 | 1.513 | 1.446 | 1.311 | Over-range | 60.01 | 1174 | 1453 | 1569 | 4197 | - - - | - - - | - - - | - - - | 1174 | 1453 | 1569 | 4197 | 896 | 664 | -71 | 1488 | - - - | - - - | - - - | - - - | 896 | 664 | -71 | 1488 | 1487 | 1606 | 1597 | 4690 | # # # | # # # | # # # | # # # | 0.79 | 0.905 | 0.982 | 0.895 | # # # | # # # | # # # | - - - | 0.796 | 0.909 | 0.999 | 0.904 | - - - | 0.355 | 1.72 | 1.58 | 1.54 | 1.55 | 1.54 | 1.57 | 10.03 | 9.57 | 18.38 | 0 | - - - | - - - | - - - | - - - | 1487 | 1606 | 1597 | 4690 | Over-range | 912 | 683 | 300 | 2094 | 167 | 159 | 290 | 1473 | 1177 | 1451 | 1570 | 4198 | 1177 | 1451 | 1570 | 4198 | - - - | - - - | - - - | - - -
5/2/2026 | 4:00:00 AM | 285.67 | 283.02 | 281.31 | 494.11 | 487.01 | 491.12 | 4.5605 | 4.4819 | 5.3535 | 2.7593 | 1.426 | 1.423 | 1.42 | 1.5 | 1.464 | 1.41 | Over-range | 60 | 1066 | 1040 | 1470 | 3577 | - - - | - - - | - - - | - - - | 1066 | 1040 | 1470 | 3577 | 722 | 674 | 112 | 1508 | - - - | - - - | - - - | - - - | 722 | 674 | 112 | 1508 | 1299 | 1254 | 1505 | 4058 | # # # | # # # | # # # | # # # | 0.821 | 0.829 | 0.977 | 0.881 | # # # | # # # | # # # | - - - | 0.829 | 0.835 | 0.995 | 0.892 | - - - | 0.422 | 1.73 | 1.58 | 1.51 | 1.54 | 1.52 | 1.56 | 11.77 | 12.09 | 19.08 | 0 | - - - | - - - | - - - | - - - | 1299 | 1254 | 1505 | 4058 | Over-range | 740 | 691 | 321 | 1916 | 162 | 154 | 285 | 1177 | 1070 | 1039 | 1469 | 3578 | 1070 | 1039 | 1469 | 3578 | - - - | - - - | - - - | - - -
5/2/2026 | 4:15:00 AM | 285.74 | 283.08 | 281.4 | 494.22 | 487.14 | 491.24 | 4.7552 | 4.8124 | 5.4447 | 2.7595 | 1.427 | 1.424 | 1.421 | 1.505 | 1.43 | 1.381 | Over-range | 60 | 1100 | 1168 | 1503 | 3771 | - - - | - - - | - - - | - - - | 1100 | 1168 | 1503 | 3771 | 779 | 675 | 56 | 1510 | - - - | - - - | - - - | - - - | 779 | 675 | 56 | 1510 | 1358 | 1359 | 1532 | 4249 | # # # | # # # | # # # | # # # | 0.81 | 0.86 | 0.981 | 0.888 | # # # | # # # | # # # | - - - | 0.816 | 0.865 | 0.999 | 0.897 | - - - | 0.4 | 1.71 | 1.6 | 1.54 | 1.55 | 1.54 | 1.57 | 11.14 | 11.13 | 19.02 | 0 | - - - | - - - | - - - | - - - | 1358 | 1359 | 1532 | 4249 | Over-range | 796 | 692 | 298 | 1957 | 163 | 154 | 288 | 1244 | 1102 | 1169 | 1501 | 3772 | 1102 | 1169 | 1501 | 3772 | - - - | - - - | - - - | - - -
5/2/2026 | 4:30:00 AM | 285.67 | 283.05 | 281.37 | 494.13 | 487.13 | 491.14 | 5.1009 | 5.2789 | 5.5873 | 2.7558 | 1.426 | 1.423 | 1.421 | 1.506 | 1.431 | 1.357 | Over-range | 60.01 | 1164 | 1320 | 1543 | 4027 | - - - | - - - | - - - | - - - | 1164 | 1320 | 1543 | 4027 | 852 | 672 | 14 | 1538 | - - - | - - - | - - - | - - - | 852 | 672 | 14 | 1538 | 1452 | 1491 | 1572 | 4515 | # # # | # # # | # # # | # # # | 0.801 | 0.886 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.798 | 0.883 | 0.978 | 0.889 | - - - | 0.382 | 1.72 | 1.57 | 1.52 | 1.54 | 1.52 | 1.56 | 10.4 | 10.34 | 18.8 | 0 | - - - | - - - | - - - | - - - | 1452 | 1491 | 1572 | 4515 | Over-range | 868 | 690 | 301 | 2042 | 168 | 156 | 293 | 1338 | 1180 | 1332 | 1567 | 4079 | 1180 | 1332 | 1567 | 4079 | - - - | - - - | - - - | - - -
5/2/2026 | 4:45:00 AM | 285.51 | 282.89 | 281.18 | 493.87 | 486.79 | 490.83 | 5.2064 | 5.6838 | 5.6793 | 2.7459 | 1.426 | 1.423 | 1.421 | 1.512 | 1.443 | 1.314 | Over-range | 60.01 | 1173 | 1452 | 1568 | 4193 | - - - | - - - | - - - | - - - | 1173 | 1452 | 1568 | 4193 | 895 | 667 | -70 | 1492 | - - - | - - - | - - - | - - - | 895 | 667 | -70 | 1492 | 1486 | 1606 | 1597 | 4688 | # # # | # # # | # # # | # # # | 0.79 | 0.904 | 0.982 | 0.894 | # # # | # # # | # # # | - - - | 0.795 | 0.908 | 0.999 | 0.903 | - - - | 0.356 | 1.7 | 1.6 | 1.55 | 1.55 | 1.55 | 1.58 | 10.07 | 9.59 | 18.37 | 0 | - - - | - - - | - - - | - - - | 1486 | 1606 | 1597 | 4688 | Over-range | 912 | 685 | 300 | 2097 | 173 | 155 | 289 | 1473 | 1173 | 1451 | 1570 | 4194 | 1173 | 1451 | 1570 | 4194 | - - - | - - - | - - - | - - -
5/2/2026 | 5:00:00 AM | 285.67 | 283.02 | 281.39 | 494.09 | 487.11 | 491.19 | 5.1456 | 5.5748 | 5.6514 | 2.7502 | 1.427 | 1.424 | 1.422 | 1.511 | 1.454 | 1.324 | Over-range | 60.01 | 1162 | 1406 | 1560 | 4128 | - - - | - - - | - - - | - - - | 1162 | 1406 | 1560 | 4128 | 879 | 669 | -47 | 1501 | - - - | - - - | - - - | - - - | 879 | 669 | -47 | 1501 | 1467 | 1569 | 1590 | 4626 | # # # | # # # | # # # | # # # | 0.792 | 0.896 | 0.981 | 0.892 | # # # | # # # | # # # | - - - | 0.798 | 0.901 | 0.998 | 0.901 | - - - | 0.364 | 1.73 | 1.62 | 1.56 | 1.56 | 1.57 | 1.6 | 10.29 | 10.05 | 18.47 | 0 | - - - | - - - | - - - | - - - | 1467 | 1569 | 1590 | 4626 | Over-range | 895 | 688 | 306 | 2087 | 166 | 160 | 291 | 1447 | 1165 | 1405 | 1559 | 4129 | 1165 | 1405 | 1559 | 4129 | - - - | - - - | - - - | - - -
5/2/2026 | 5:15:00 AM | 285.8 | 283.23 | 281.58 | 494.38 | 487.48 | 491.43 | 4.4894 | 4.3299 | 5.3267 | 2.7569 | 1.427 | 1.424 | 1.422 | 1.495 | 1.455 | 1.419 | Over-range | 60.01 | 1056 | 1003 | 1465 | 3525 | - - - | - - - | - - - | - - - | 1056 | 1003 | 1465 | 3525 | 707 | 680 | 132 | 1519 | - - - | - - - | - - - | - - - | 707 | 680 | 132 | 1519 | 1282 | 1223 | 1500 | 4005 | # # # | # # # | # # # | # # # | 0.824 | 0.82 | 0.977 | 0.88 | # # # | # # # | # # # | - - - | 0.831 | 0.827 | 0.995 | 0.891 | - - - | 0.431 | 1.77 | 1.66 | 1.6 | 1.6 | 1.6 | 1.64 | 11.86 | 12.41 | 19.19 | 0 | - - - | - - - | - - - | - - - | 1282 | 1223 | 1500 | 4005 | Over-range | 726 | 697 | 318 | 1901 | 165 | 152 | 286 | 1142 | 1057 | 1005 | 1463 | 3524 | 1057 | 1005 | 1463 | 3524 | - - - | - - - | - - - | - - -
5/2/2026 | 5:30:00 AM | 285.61 | 283.11 | 281.42 | 494.13 | 487.23 | 491.11 | 4.715 | 4.741 | 5.4254 | 2.7481 | 1.426 | 1.424 | 1.422 | 1.501 | 1.426 | 1.387 | Over-range | 60.01 | 1094 | 1148 | 1497 | 3739 | - - - | - - - | - - - | - - - | 1094 | 1148 | 1497 | 3739 | 767 | 674 | 67 | 1509 | - - - | - - - | - - - | - - - | 767 | 674 | 67 | 1509 | 1346 | 1341 | 1527 | 4214 | # # # | # # # | # # # | # # # | 0.812 | 0.856 | 0.981 | 0.887 | # # # | # # # | # # # | - - - | 0.818 | 0.862 | 0.999 | 0.897 | - - - | 0.404 | 1.77 | 1.63 | 1.64 | 1.59 | 1.61 | 1.65 | 11.18 | 11.32 | 18.96 | 0 | - - - | - - - | - - - | - - - | 1346 | 1341 | 1527 | 4214 | Over-range | 785 | 691 | 297 | 1943 | 166 | 152 | 288 | 1223 | 1093 | 1150 | 1496 | 3739 | 1093 | 1150 | 1496 | 3739 | - - - | - - - | - - - | - - -
5/2/2026 | 5:45:00 AM | 285.57 | 282.99 | 281.3 | 494 | 487 | 491 | 4.6675 | 4.6494 | 5.4015 | 2.7455 | 1.425 | 1.423 | 1.421 | 1.501 | 1.424 | 1.392 | Over-range | 60 | 1086 | 1120 | 1490 | 3696 | - - - | - - - | - - - | - - - | 1086 | 1120 | 1490 | 3696 | 754 | 674 | 80 | 1508 | - - - | - - - | - - - | - - - | 754 | 674 | 80 | 1508 | 1333 | 1316 | 1519 | 4168 | # # # | # # # | # # # | # # # | 0.815 | 0.851 | 0.981 | 0.887 | # # # | # # # | # # # | - - - | 0.821 | 0.857 | 0.999 | 0.897 | - - - | 0.408 | 1.73 | 1.62 | 1.56 | 1.55 | 1.56 | 1.6 | 11.29 | 11.37 | 18.95 | 0 | - - - | - - - | - - - | - - - | 1333 | 1316 | 1519 | 4168 | Over-range | 773 | 690 | 298 | 1927 | 168 | 150 | 286 | 1199 | 1085 | 1120 | 1491 | 3696 | 1085 | 1120 | 1491 | 3696 | - - - | - - - | - - - | - - -
5/2/2026 | 6:00:00 AM | 285.18 | 282.56 | 280.9 | 493.3 | 486.26 | 490.32 | 4.9309 | 5.1578 | 5.5294 | 2.7406 | 1.425 | 1.423 | 1.421 | 1.504 | 1.428 | 1.354 | Over-range | 60 | 1127 | 1282 | 1525 | 3935 | - - - | - - - | - - - | - - - | 1127 | 1282 | 1525 | 3935 | 822 | 663 | 5 | 1491 | - - - | - - - | - - - | - - - | 822 | 663 | 5 | 1491 | 1405 | 1453 | 1553 | 4411 | # # # | # # # | # # # | # # # | 0.802 | 0.882 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.808 | 0.887 | 0.999 | 0.901 | - - - | 0.379 | 1.73 | 1.61 | 1.56 | 1.55 | 1.57 | 1.6 | 10.51 | 10.46 | 18.65 | 0 | - - - | - - - | - - - | - - - | 1405 | 1453 | 1553 | 4411 | Over-range | 838 | 682 | 293 | 1994 | 161 | 158 | 288 | 1322 | 1131 | 1280 | 1525 | 3936 | 1131 | 1280 | 1525 | 3936 | - - - | - - - | - - - | - - -
5/2/2026 | 6:15:00 AM | 285.07 | 282.49 | 280.79 | 493.12 | 486.17 | 490.09 | 5.164 | 5.6057 | 5.655 | 2.7365 | 1.425 | 1.423 | 1.421 | 1.509 | 1.445 | 1.317 | Over-range | 59.99 | 1165 | 1428 | 1560 | 4153 | - - - | - - - | - - - | - - - | 1165 | 1428 | 1560 | 4153 | 883 | 662 | -58 | 1486 | - - - | - - - | - - - | - - - | 883 | 662 | -58 | 1486 | 1472 | 1582 | 1588 | 4641 | # # # | # # # | # # # | # # # | 0.792 | 0.903 | 0.983 | 0.895 | # # # | # # # | # # # | - - - | 0.797 | 0.907 | 0.999 | 0.903 | - - - | 0.358 | 1.72 | 1.58 | 1.58 | 1.54 | 1.56 | 1.59 | 10.05 | 9.6 | 18.25 | 0 | - - - | - - - | - - - | - - - | 1472 | 1582 | 1588 | 4641 | Over-range | 899 | 680 | 295 | 2072 | 165 | 156 | 287 | 1442 | 1167 | 1427 | 1560 | 4154 | 1167 | 1427 | 1560 | 4154 | - - - | - - - | - - - | - - -
5/2/2026 | 6:30:00 AM | 284.94 | 282.38 | 280.68 | 492.92 | 485.98 | 489.87 | 4.8437 | 5.0237 | 5.4896 | 2.742 | 1.425 | 1.423 | 1.421 | 1.503 | 1.462 | 1.363 | Over-range | 60 | 1111 | 1220 | 1509 | 3840 | - - - | - - - | - - - | - - - | 1111 | 1220 | 1509 | 3840 | 793 | 661 | 30 | 1484 | - - - | - - - | - - - | - - - | 793 | 661 | 30 | 1484 | 1375 | 1403 | 1540 | 4319 | # # # | # # # | # # # | # # # | 0.808 | 0.87 | 0.98 | 0.889 | # # # | # # # | # # # | - - - | 0.814 | 0.875 | 0.997 | 0.899 | - - - | 0.387 | 1.68 | 1.56 | 1.55 | 1.52 | 1.53 | 1.56 | 10.88 | 10.74 | 18.45 | 0 | - - - | - - - | - - - | - - - | 1375 | 1403 | 1540 | 4319 | Over-range | 810 | 679 | 304 | 1973 | 163 | 154 | 283 | 1294 | 1114 | 1218 | 1511 | 3842 | 1114 | 1218 | 1511 | 3842 | - - - | - - - | - - - | - - -
5/2/2026 | 6:45:00 AM | 284.76 | 282.26 | 280.57 | 492.65 | 485.82 | 489.6 | 4.6582 | 4.469 | 5.3769 | 2.7436 | 1.425 | 1.423 | 1.422 | 1.495 | 1.435 | 1.411 | Over-range | 60.01 | 1091 | 1059 | 1473 | 3624 | - - - | - - - | - - - | - - - | 1091 | 1059 | 1473 | 3624 | 731 | 662 | 124 | 1516 | - - - | - - - | - - - | - - - | 731 | 662 | 124 | 1516 | 1324 | 1259 | 1508 | 4091 | # # # | # # # | # # # | # # # | 0.825 | 0.841 | 0.977 | 0.886 | # # # | # # # | # # # | - - - | 0.823 | 0.84 | 0.98 | 0.886 | - - - | 0.419 | 1.68 | 1.58 | 1.56 | 1.52 | 1.54 | 1.57 | 11.17 | 11.62 | 18.89 | 0 | - - - | - - - | - - - | - - - | 1324 | 1259 | 1508 | 4091 | Over-range | 749 | 679 | 319 | 1899 | 160 | 152 | 284 | 1135 | 1104 | 1064 | 1488 | 3656 | 1104 | 1064 | 1488 | 3656 | - - - | - - - | - - - | - - -
5/2/2026 | 7:00:00 AM | 284.72 | 282.2 | 280.51 | 492.55 | 485.71 | 489.53 | 4.6608 | 4.6399 | 5.3882 | 2.7382 | 1.426 | 1.424 | 1.422 | 1.496 | 1.42 | 1.387 | Over-range | 60.01 | 1084 | 1120 | 1483 | 3688 | - - - | - - - | - - - | - - - | 1084 | 1120 | 1483 | 3688 | 748 | 660 | 73 | 1480 | - - - | - - - | - - - | - - - | 748 | 660 | 73 | 1480 | 1327 | 1309 | 1511 | 4147 | # # # | # # # | # # # | # # # | 0.817 | 0.856 | 0.981 | 0.889 | # # # | # # # | # # # | - - - | 0.824 | 0.862 | 0.999 | 0.899 | - - - | 0.402 | 1.73 | 1.61 | 1.58 | 1.55 | 1.57 | 1.61 | 11.07 | 11.14 | 18.74 | 0 | - - - | - - - | - - - | - - - | 1327 | 1309 | 1511 | 4147 | Over-range | 764 | 676 | 292 | 1897 | 159 | 149 | 282 | 1186 | 1087 | 1120 | 1481 | 3688 | 1087 | 1120 | 1481 | 3688 | - - - | - - - | - - - | - - -
5/2/2026 | 7:15:00 AM | 284.58 | 282.09 | 280.32 | 492.36 | 485.46 | 489.2 | 4.6714 | 4.6617 | 5.394 | 2.7354 | 1.425 | 1.424 | 1.422 | 1.496 | 1.42 | 1.386 | Over-range | 60 | 1086 | 1128 | 1484 | 3698 | - - - | - - - | - - - | - - - | 1086 | 1128 | 1484 | 3698 | 749 | 659 | 69 | 1478 | - - - | - - - | - - - | - - - | 749 | 659 | 69 | 1478 | 1329 | 1315 | 1512 | 4156 | # # # | # # # | # # # | # # # | 0.817 | 0.858 | 0.981 | 0.89 | # # # | # # # | # # # | - - - | 0.823 | 0.863 | 0.999 | 0.899 | - - - | 0.4 | 1.75 | 1.63 | 1.65 | 1.57 | 1.61 | 1.65 | 11.01 | 11.1 | 18.7 | 0 | - - - | - - - | - - - | - - - | 1329 | 1315 | 1512 | 4156 | Over-range | 766 | 675 | 291 | 1897 | 161 | 147 | 282 | 1189 | 1087 | 1129 | 1482 | 3698 | 1087 | 1129 | 1482 | 3698 | - - - | - - - | - - - | - - -
5/2/2026 | 7:30:00 AM | 284.49 | 281.97 | 280.18 | 492.21 | 485.21 | 489.01 | 5.1068 | 5.5096 | 5.6192 | 2.7245 | 1.425 | 1.424 | 1.423 | 1.503 | 1.446 | 1.324 | Over-range | 60.01 | 1156 | 1396 | 1546 | 4099 | - - - | - - - | - - - | - - - | 1156 | 1396 | 1546 | 4099 | 862 | 653 | -49 | 1465 | - - - | - - - | - - - | - - - | 862 | 653 | -49 | 1465 | 1452 | 1550 | 1574 | 4576 | # # # | # # # | # # # | # # # | 0.796 | 0.901 | 0.982 | 0.896 | # # # | # # # | # # # | - - - | 0.801 | 0.905 | 0.999 | 0.904 | - - - | 0.358 | 1.77 | 1.66 | 1.66 | 1.59 | 1.63 | 1.67 | 10.03 | 9.76 | 18.25 | 0 | - - - | - - - | - - - | - - - | 1452 | 1550 | 1574 | 4576 | Over-range | 878 | 670 | 294 | 2034 | 166 | 151 | 285 | 1409 | 1155 | 1398 | 1545 | 4099 | 1155 | 1398 | 1545 | 4099 | - - - | - - - | - - - | - - -
5/2/2026 | 7:45:00 AM | 284.43 | 281.88 | 280.13 | 492.02 | 485.09 | 488.94 | 5.0103 | 5.3147 | 5.5628 | 2.7222 | 1.425 | 1.424 | 1.422 | 1.499 | 1.44 | 1.337 | Over-range | 60 | 1140 | 1339 | 1532 | 4012 | - - - | - - - | - - - | - - - | 1140 | 1339 | 1532 | 4012 | 839 | 652 | -22 | 1468 | - - - | - - - | - - - | - - - | 839 | 652 | -22 | 1468 | 1425 | 1498 | 1558 | 4481 | # # # | # # # | # # # | # # # | 0.8 | 0.894 | 0.983 | 0.895 | # # # | # # # | # # # | - - - | 0.806 | 0.899 | 1 | 0.904 | - - - | 0.366 | 1.78 | 1.69 | 1.69 | 1.62 | 1.65 | 1.7 | 10.24 | 9.89 | 18.18 | 0 | - - - | - - - | - - - | - - - | 1425 | 1498 | 1558 | 4481 | Over-range | 855 | 669 | 283 | 1995 | 164 | 152 | 281 | 1351 | 1142 | 1337 | 1534 | 4013 | 1142 | 1337 | 1534 | 4013 | - - - | - - - | - - - | - - -
5/2/2026 | 8:00:00 AM | 284.16 | 281.68 | 279.88 | 491.64 | 484.7 | 488.48 | 4.4365 | 4.2468 | 5.2779 | 2.7266 | 1.425 | 1.424 | 1.422 | 1.491 | 1.458 | 1.422 | Over-range | 60.01 | 1045 | 979 | 1443 | 3467 | - - - | - - - | - - - | - - - | 1045 | 979 | 1443 | 3467 | 682 | 652 | 133 | 1468 | - - - | - - - | - - - | - - - | 682 | 652 | 133 | 1468 | 1259 | 1189 | 1477 | 3925 | # # # | # # # | # # # | # # # | 0.831 | 0.823 | 0.977 | 0.883 | # # # | # # # | # # # | - - - | 0.838 | 0.829 | 0.994 | 0.894 | - - - | 0.423 | 1.82 | 1.71 | 1.7 | 1.63 | 1.68 | 1.73 | 11.67 | 12.2 | 18.65 | 0 | - - - | - - - | - - - | - - - | 1259 | 1189 | 1477 | 3925 | Over-range | 700 | 669 | 313 | 1837 | 157 | 149 | 275 | 1102 | 1049 | 977 | 1443 | 3469 | 1049 | 977 | 1443 | 3469 | - - - | - - - | - - - | - - -
5/2/2026 | 8:15:00 AM | 283.63 | 281.11 | 279.4 | 490.65 | 483.79 | 487.64 | 4.6338 | 4.5996 | 5.3649 | 2.718 | 1.425 | 1.425 | 1.422 | 1.496 | 1.429 | 1.391 | Over-range | 60 | 1079 | 1110 | 1471 | 3660 | - - - | - - - | - - - | - - - | 1079 | 1110 | 1471 | 3660 | 734 | 643 | 72 | 1448 | - - - | - - - | - - - | - - - | 734 | 643 | 72 | 1448 | 1314 | 1292 | 1499 | 4105 | # # # | # # # | # # # | # # # | 0.821 | 0.859 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.828 | 0.865 | 0.999 | 0.902 | - - - | 0.396 | 1.81 | 1.72 | 1.72 | 1.64 | 1.69 | 1.74 | 10.9 | 11.14 | 18.49 | 0 | - - - | - - - | - - - | - - - | 1314 | 1292 | 1499 | 4105 | Over-range | 750 | 660 | 287 | 1858 | 157 | 149 | 277 | 1164 | 1082 | 1108 | 1472 | 3662 | 1082 | 1108 | 1472 | 3662 | - - - | - - - | - - - | - - -
5/2/2026 | 8:30:00 AM | 283.15 | 280.49 | 278.78 | 489.73 | 482.61 | 486.77 | 4.6102 | 4.5505 | 5.3424 | 2.7137 | 1.425 | 1.425 | 1.422 | 1.496 | 1.424 | 1.392 | Over-range | 60.01 | 1075 | 1098 | 1463 | 3636 | - - - | - - - | - - - | - - - | 1075 | 1098 | 1463 | 3636 | 724 | 634 | 71 | 1428 | - - - | - - - | - - - | - - - | 724 | 634 | 71 | 1428 | 1305 | 1276 | 1489 | 4071 | # # # | # # # | # # # | # # # | 0.824 | 0.86 | 0.982 | 0.893 | # # # | # # # | # # # | - - - | 0.831 | 0.866 | 0.999 | 0.903 | - - - | 0.393 | 1.78 | 1.72 | 1.71 | 1.62 | 1.68 | 1.72 | 10.85 | 10.98 | 18.32 | 0 | - - - | - - - | - - - | - - - | 1305 | 1276 | 1489 | 4071 | Over-range | 740 | 651 | 281 | 1831 | 154 | 146 | 272 | 1146 | 1079 | 1096 | 1463 | 3637 | 1079 | 1096 | 1463 | 3637 | - - - | - - - | - - - | - - -
5/2/2026 | 8:45:00 AM | 282.91 | 280.24 | 278.55 | 489.28 | 482.22 | 486.37 | 4.6884 | 4.7024 | 5.3791 | 2.7099 | 1.425 | 1.426 | 1.422 | 1.498 | 1.435 | 1.38 | Over-range | 60.01 | 1088 | 1148 | 1472 | 3708 | - - - | - - - | - - - | - - - | 1088 | 1148 | 1472 | 3708 | 743 | 630 | 47 | 1420 | - - - | - - - | - - - | - - - | 743 | 630 | 47 | 1420 | 1326 | 1318 | 1498 | 4142 | # # # | # # # | # # # | # # # | 0.82 | 0.871 | 0.983 | 0.895 | # # # | # # # | # # # | - - - | 0.827 | 0.876 | 0.999 | 0.905 | - - - | 0.383 | 1.8 | 1.74 | 1.72 | 1.63 | 1.69 | 1.73 | 10.62 | 10.72 | 18.28 | 0 | - - - | - - - | - - - | - - - | 1326 | 1318 | 1498 | 4142 | Over-range | 759 | 647 | 277 | 1846 | 153 | 147 | 273 | 1180 | 1092 | 1146 | 1472 | 3709 | 1092 | 1146 | 1472 | 3709 | - - - | - - - | - - - | - - -
5/2/2026 | 9:00:00 AM | 282.98 | 280.3 | 278.62 | 489.37 | 482.36 | 486.46 | 5.2121 | 5.5395 | 5.6272 | 2.709 | 1.425 | 1.426 | 1.423 | 1.5 | 1.467 | 1.33 | Over-range | 60 | 1179 | 1408 | 1540 | 4127 | - - - | - - - | - - - | - - - | 1179 | 1408 | 1540 | 4127 | 864 | 628 | -42 | 1448 | - - - | - - - | - - - | - - - | 864 | 628 | -42 | 1448 | 1471 | 1550 | 1567 | 4588 | # # # | # # # | # # # | # # # | 0.802 | 0.909 | 0.982 | 0.9 | # # # | # # # | # # # | - - - | 0.799 | 0.905 | 0.99 | 0.899 | - - - | 0.351 | 1.81 | 1.75 | 1.72 | 1.64 | 1.7 | 1.74 | 9.6 | 9.49 | 17.86 | 0 | - - - | - - - | - - - | - - - | 1471 | 1550 | 1567 | 4588 | Over-range | 879 | 646 | 293 | 2005 | 161 | 151 | 279 | 1380 | 1192 | 1416 | 1552 | 4160 | 1192 | 1416 | 1552 | 4160 | - - - | - - - | - - - | - - -
5/2/2026 | 9:15:00 AM | 282.65 | 279.98 | 278.2 | 488.88 | 481.66 | 485.82 | 4.9453 | 5.2032 | 5.5111 | 2.7024 | 1.423 | 1.424 | 1.421 | 1.501 | 1.452 | 1.341 | Over-range | 60 | 1129 | 1307 | 1508 | 3945 | - - - | - - - | - - - | - - - | 1129 | 1307 | 1508 | 3945 | 808 | 626 | -24 | 1409 | - - - | - - - | - - - | - - - | 808 | 626 | -24 | 1409 | 1398 | 1456 | 1533 | 4387 | # # # | # # # | # # # | # # # | 0.808 | 0.898 | 0.984 | 0.899 | # # # | # # # | # # # | - - - | 0.814 | 0.902 | 0.999 | 0.908 | - - - | 0.357 | 1.73 | 1.69 | 1.68 | 1.58 | 1.65 | 1.67 | 10.07 | 9.64 | 17.82 | 0 | - - - | - - - | - - - | - - - | 1398 | 1456 | 1533 | 4387 | Over-range | 823 | 642 | 274 | 1919 | 158 | 142 | 272 | 1303 | 1130 | 1309 | 1506 | 3945 | 1130 | 1309 | 1506 | 3945 | - - - | - - - | - - - | - - -
5/2/2026 | 9:30:00 AM | 282.43 | 279.62 | 277.94 | 488.36 | 481.05 | 485.49 | 4.6053 | 4.5932 | 5.3391 | 2.6976 | 1.424 | 1.425 | 1.421 | 1.497 | 1.465 | 1.391 | Over-range | 59.99 | 1071 | 1088 | 1453 | 3612 | - - - | - - - | - - - | - - - | 1071 | 1088 | 1453 | 3612 | 711 | 623 | 69 | 1403 | - - - | - - - | - - - | - - - | 711 | 623 | 69 | 1403 | 1296 | 1268 | 1483 | 4047 | # # # | # # # | # # # | # # # | 0.826 | 0.858 | 0.98 | 0.892 | # # # | # # # | # # # | - - - | 0.832 | 0.863 | 0.997 | 0.902 | - - - | 0.388 | 1.74 | 1.72 | 1.67 | 1.58 | 1.65 | 1.68 | 10.92 | 11.11 | 18.07 | 0 | - - - | - - - | - - - | - - - | 1296 | 1268 | 1483 | 4047 | Over-range | 728 | 639 | 295 | 1824 | 157 | 141 | 268 | 1158 | 1071 | 1087 | 1455 | 3613 | 1071 | 1087 | 1455 | 3613 | - - - | - - - | - - - | - - -
5/2/2026 | 9:45:00 AM | 282.1 | 279.19 | 277.47 | 487.74 | 480.22 | 484.81 | 4.5517 | 4.2479 | 5.309 | 3.1789 | 1.423 | 1.425 | 1.421 | 1.498 | 1.447 | 1.392 | Over-range | 60.01 | 1063 | 951 | 1446 | 3460 | - - - | - - - | - - - | - - - | 1063 | 951 | 1446 | 3460 | 702 | 654 | 69 | 1425 | - - - | - - - | - - - | - - - | 702 | 654 | 69 | 1425 | 1283 | 1177 | 1473 | 3934 | # # # | # # # | # # # | # # # | 0.828 | 0.808 | 0.982 | 0.88 | # # # | # # # | # # # | - - - | 0.835 | 0.814 | 0.999 | 0.889 | - - - | 0.412 | 1.68 | 1.66 | 1.63 | 1.53 | 1.62 | 1.63 | 10.78 | 12.53 | 18.06 | 0 | - - - | - - - | - - - | - - - | 1283 | 1177 | 1473 | 3934 | Over-range | 719 | 670 | 278 | 1860 | 153 | 147 | 267 | 1193 | 1064 | 950 | 1448 | 3462 | 1064 | 950 | 1448 | 3462 | - - - | - - - | - - - | - - -
5/2/2026 | 10:00:00 AM | 282.25 | 279.47 | 277.73 | 488.11 | 480.76 | 485.09 | 4.5785 | 3.6212 | 5.3128 | 4.1115 | 1.424 | 1.425 | 1.422 | 1.497 | 1.453 | 1.392 | Over-range | 60 | 1070 | 663 | 1449 | 3183 | - - - | - - - | - - - | - - - | 1070 | 663 | 1449 | 3183 | 708 | 745 | 69 | 1522 | - - - | - - - | - - - | - - - | 708 | 745 | 69 | 1522 | 1292 | 1012 | 1476 | 3780 | # # # | # # # | # # # | # # # | 0.828 | 0.655 | 0.982 | 0.842 | # # # | # # # | # # # | - - - | 0.834 | 0.664 | 0.999 | 0.853 | - - - | 0.478 | 1.72 | 1.67 | 1.65 | 1.56 | 1.63 | 1.65 | 10.75 | 16.53 | 18.08 | 0 | - - - | - - - | - - - | - - - | 1292 | 1012 | 1476 | 3780 | Over-range | 724 | 764 | 276 | 2039 | 153 | 169 | 267 | 1357 | 1072 | 662 | 1450 | 3184 | 1072 | 662 | 1450 | 3184 | - - - | - - - | - - - | - - -
5/2/2026 | 10:15:00 AM | 282.02 | 279.16 | 277.57 | 487.6 | 480.33 | 484.82 | 4.6308 | 3.7235 | 5.3474 | 4.0956 | 1.424 | 1.425 | 1.422 | 1.499 | 1.444 | 1.383 | Over-range | 60 | 1076 | 708 | 1459 | 3243 | - - - | - - - | - - - | - - - | 1076 | 708 | 1459 | 3243 | 724 | 741 | 48 | 1513 | - - - | - - - | - - - | - - - | 724 | 741 | 48 | 1513 | 1306 | 1039 | 1484 | 3830 | # # # | # # # | # # # | # # # | 0.824 | 0.681 | 0.983 | 0.847 | # # # | # # # | # # # | - - - | 0.83 | 0.69 | 0.999 | 0.858 | - - - | 0.467 | 1.71 | 1.65 | 1.65 | 1.54 | 1.62 | 1.64 | 10.57 | 16.33 | 18.02 | 0 | - - - | - - - | - - - | - - - | 1306 | 1039 | 1484 | 3830 | Over-range | 740 | 761 | 272 | 2037 | 153 | 174 | 268 | 1365 | 1078 | 706 | 1461 | 3245 | 1078 | 706 | 1461 | 3245 | - - - | - - - | - - - | - - -
5/2/2026 | 10:30:00 AM | 281.82 | 278.99 | 277.37 | 487.3 | 480 | 484.46 | 5.0056 | 4.3085 | 5.5378 | 4.1026 | 1.424 | 1.425 | 1.422 | 1.505 | 1.426 | 1.331 | Over-range | 60.01 | 1139 | 926 | 1510 | 3574 | - - - | - - - | - - - | - - - | 1139 | 926 | 1510 | 3574 | 815 | 735 | -50 | 1499 | - - - | - - - | - - - | - - - | 815 | 735 | -50 | 1499 | 1410 | 1198 | 1536 | 4143 | # # # | # # # | # # # | # # # | 0.808 | 0.773 | 0.983 | 0.863 | # # # | # # # | # # # | - - - | 0.814 | 0.781 | 0.999 | 0.873 | - - - | 0.419 | 1.67 | 1.64 | 1.62 | 1.52 | 1.6 | 1.6 | 9.79 | 14.88 | 17.73 | 0 | - - - | - - - | - - - | - - - | 1410 | 1198 | 1536 | 4143 | Over-range | 830 | 757 | 282 | 2095 | 159 | 180 | 271 | 1464 | 1140 | 924 | 1512 | 3576 | 1140 | 924 | 1512 | 3576 | - - - | - - - | - - - | - - -
5/2/2026 | 10:45:00 AM | 281.45 | 278.5 | 276.95 | 486.5 | 479.21 | 483.83 | 5.1982 | 4.6235 | 5.6427 | 4.1031 | 1.424 | 1.425 | 1.422 | 1.507 | 1.428 | 1.304 | Over-range | 60.01 | 1170 | 1043 | 1535 | 3748 | - - - | - - - | - - - | - - - | 1170 | 1043 | 1535 | 3748 | 864 | 727 | -106 | 1484 | - - - | - - - | - - - | - - - | 864 | 727 | -106 | 1484 | 1462 | 1285 | 1563 | 4310 | # # # | # # # | # # # | # # # | 0.8 | 0.812 | 0.983 | 0.87 | # # # | # # # | # # # | - - - | 0.806 | 0.819 | 0.997 | 0.879 | - - - | 0.396 | 1.67 | 1.65 | 1.62 | 1.52 | 1.6 | 1.61 | 9.35 | 13.65 | 17.24 | 0 | - - - | - - - | - - - | - - - | 1462 | 1285 | 1563 | 4310 | Over-range | 878 | 748 | 291 | 2128 | 155 | 179 | 268 | 1525 | 1173 | 1041 | 1536 | 3750 | 1173 | 1041 | 1536 | 3750 | - - - | - - - | - - - | - - -
5/2/2026 | 11:00:00 AM | 281.39 | 278.44 | 276.92 | 486.42 | 479.1 | 483.76 | 4.8308 | 4.0581 | 5.4249 | 4.0993 | 1.424 | 1.424 | 1.422 | 1.503 | 1.434 | 1.357 | Over-range | 60 | 1108 | 810 | 1474 | 3391 | - - - | - - - | - - - | - - - | 1108 | 810 | 1474 | 3391 | 762 | 730 | -4 | 1487 | - - - | - - - | - - - | - - - | 762 | 730 | -4 | 1487 | 1355 | 1119 | 1501 | 3976 | # # # | # # # | # # # | # # # | 0.818 | 0.723 | 0.982 | 0.853 | # # # | # # # | # # # | - - - | 0.823 | 0.731 | 0.997 | 0.863 | - - - | 0.439 | 1.68 | 1.64 | 1.63 | 1.53 | 1.61 | 1.62 | 10.22 | 15.25 | 17.69 | 0 | - - - | - - - | - - - | - - - | 1355 | 1119 | 1501 | 3976 | Over-range | 778 | 750 | 285 | 2067 | 154 | 172 | 266 | 1435 | 1110 | 808 | 1475 | 3394 | 1110 | 808 | 1475 | 3394 | - - - | - - - | - - - | - - -
5/2/2026 | 11:15:00 AM | 280.97 | 278.06 | 276.48 | 485.73 | 478.39 | 483.01 | 4.5767 | 3.4786 | 5.284 | 4.1079 | 1.424 | 1.425 | 1.421 | 1.495 | 1.45 | 1.411 | Over-range | 60.01 | 1076 | 607 | 1430 | 3114 | - - - | - - - | - - - | - - - | 1076 | 607 | 1430 | 3114 | 679 | 729 | 104 | 1512 | - - - | - - - | - - - | - - - | 679 | 729 | 104 | 1512 | 1282 | 965 | 1461 | 3708 | # # # | # # # | # # # | # # # | 0.84 | 0.629 | 0.979 | 0.84 | # # # | # # # | # # # | - - - | 0.837 | 0.633 | 0.986 | 0.842 | - - - | 0.485 | 1.66 | 1.65 | 1.6 | 1.51 | 1.59 | 1.6 | 10.68 | 16.95 | 17.97 | 0 | - - - | - - - | - - - | - - - | 1282 | 965 | 1461 | 3708 | Over-range | 696 | 747 | 291 | 2012 | 153 | 162 | 263 | 1324 | 1086 | 613 | 1440 | 3139 | 1086 | 613 | 1440 | 3139 | - - - | - - - | - - - | - - -
5/2/2026 | 11:30:00 AM | 280.47 | 277.53 | 275.94 | 484.82 | 477.48 | 482.11 | 4.6488 | 3.7064 | 5.3373 | 4.1048 | 1.424 | 1.425 | 1.422 | 1.5 | 1.437 | 1.378 | Over-range | 60 | 1081 | 712 | 1449 | 3241 | - - - | - - - | - - - | - - - | 1081 | 712 | 1449 | 3241 | 713 | 719 | 32 | 1463 | - - - | - - - | - - - | - - - | 713 | 719 | 32 | 1463 | 1303 | 1027 | 1473 | 3803 | # # # | # # # | # # # | # # # | 0.829 | 0.693 | 0.984 | 0.852 | # # # | # # # | # # # | - - - | 0.836 | 0.703 | 0.999 | 0.863 | - - - | 0.452 | 1.66 | 1.63 | 1.59 | 1.5 | 1.59 | 1.59 | 10.33 | 16.01 | 17.71 | 0 | - - - | - - - | - - - | - - - | 1303 | 1027 | 1473 | 3803 | Over-range | 729 | 738 | 265 | 1989 | 151 | 168 | 261 | 1347 | 1083 | 711 | 1450 | 3243 | 1083 | 711 | 1450 | 3243 | - - - | - - - | - - - | - - -
5/2/2026 | 11:45:00 AM | 280.47 | 277.67 | 276.04 | 484.93 | 477.75 | 482.16 | 4.7079 | 3.828 | 5.3807 | 4.0971 | 1.425 | 1.425 | 1.423 | 1.502 | 1.43 | 1.365 | Over-range | 60.01 | 1087 | 762 | 1462 | 3311 | - - - | - - - | - - - | - - - | 1087 | 762 | 1462 | 3311 | 733 | 721 | 9 | 1463 | - - - | - - - | - - - | - - - | 733 | 721 | 9 | 1463 | 1320 | 1063 | 1485 | 3868 | # # # | # # # | # # # | # # # | 0.824 | 0.717 | 0.984 | 0.856 | # # # | # # # | # # # | - - - | 0.829 | 0.725 | 1 | 0.866 | - - - | 0.442 | 1.63 | 1.62 | 1.56 | 1.49 | 1.56 | 1.57 | 10.17 | 15.77 | 17.76 | 0 | - - - | - - - | - - - | - - - | 1320 | 1063 | 1485 | 3868 | Over-range | 749 | 741 | 264 | 2000 | 151 | 169 | 263 | 1364 | 1088 | 761 | 1462 | 3312 | 1088 | 761 | 1462 | 3312 | - - - | - - - | - - - | - - -
5/2/2026 | 12:00:00 PM | 280.78 | 277.86 | 276.29 | 485.39 | 478.06 | 482.7 | 5.2539 | 4.7424 | 5.6823 | 4.1062 | 1.424 | 1.425 | 1.422 | 1.509 | 1.43 | 1.307 | Over-range | 60.01 | 1177 | 1076 | 1540 | 3793 | - - - | - - - | - - - | - - - | 1177 | 1076 | 1540 | 3793 | 871 | 721 | -127 | 1464 | - - - | - - - | - - - | - - - | 871 | 721 | -127 | 1464 | 1473 | 1311 | 1569 | 4353 | # # # | # # # | # # # | # # # | 0.799 | 0.821 | 0.981 | 0.871 | # # # | # # # | # # # | - - - | 0.804 | 0.829 | 0.995 | 0.88 | - - - | 0.386 | 1.65 | 1.62 | 1.59 | 1.5 | 1.59 | 1.58 | 9.21 | 13.64 | 17.16 | 0 | - - - | - - - | - - - | - - - | 1473 | 1311 | 1569 | 4353 | Over-range | 885 | 743 | 303 | 2137 | 159 | 179 | 268 | 1555 | 1178 | 1076 | 1540 | 3794 | 1178 | 1076 | 1540 | 3794 | - - - | - - - | - - - | - - -
5/2/2026 | 12:15:00 PM | 282.31 | 279.33 | 277.76 | 487.99 | 480.55 | 485.33 | 5.3587 | 4.9406 | 5.7464 | 4.1039 | 1.425 | 1.426 | 1.424 | 1.509 | 1.428 | 1.291 | Over-range | 59.98 | 1192 | 1147 | 1565 | 3904 | - - - | - - - | - - - | - - - | 1192 | 1147 | 1565 | 3904 | 917 | 741 | -148 | 1510 | - - - | - - - | - - - | - - - | 917 | 741 | -148 | 1510 | 1512 | 1379 | 1596 | 4487 | # # # | # # # | # # # | # # # | 0.789 | 0.832 | 0.981 | 0.87 | # # # | # # # | # # # | - - - | 0.794 | 0.839 | 0.996 | 0.879 | - - - | 0.387 | 1.58 | 1.58 | 1.53 | 1.45 | 1.52 | 1.51 | 9.15 | 13.05 | 17.26 | 0 | - - - | - - - | - - - | - - - | 1512 | 1379 | 1596 | 4487 | Over-range | 930 | 764 | 313 | 2211 | 155 | 185 | 274 | 1615 | 1196 | 1145 | 1565 | 3906 | 1196 | 1145 | 1565 | 3906 | - - - | - - - | - - - | - - -
5/2/2026 | 12:30:00 PM | 282.23 | 279.25 | 277.63 | 487.85 | 480.4 | 485.14 | 5.1009 | 4.4652 | 5.5967 | 4.1241 | 1.425 | 1.425 | 1.423 | 1.506 | 1.43 | 1.321 | Over-range | 59.99 | 1155 | 979 | 1527 | 3661 | - - - | - - - | - - - | - - - | 1155 | 979 | 1527 | 3661 | 842 | 743 | -75 | 1509 | - - - | - - - | - - - | - - - | 842 | 743 | -75 | 1509 | 1439 | 1244 | 1554 | 4236 | # # # | # # # | # # # | # # # | 0.803 | 0.787 | 0.983 | 0.864 | # # # | # # # | # # # | - - - | 0.808 | 0.794 | 0.998 | 0.873 | - - - | 0.412 | 1.57 | 1.58 | 1.5 | 1.43 | 1.5 | 1.5 | 9.66 | 14.08 | 17.49 | 0 | - - - | - - - | - - - | - - - | 1439 | 1244 | 1554 | 4236 | Over-range | 857 | 764 | 285 | 2130 | 161 | 177 | 271 | 1503 | 1155 | 978 | 1528 | 3662 | 1155 | 978 | 1528 | 3662 | - - - | - - - | - - - | - - -
5/2/2026 | 12:45:00 PM | 282.12 | 279.08 | 277.54 | 487.58 | 480.12 | 485.02 | 4.9384 | 4.1694 | 5.5012 | 4.1283 | 1.425 | 1.426 | 1.424 | 1.502 | 1.428 | 1.342 | Over-range | 59.99 | 1130 | 880 | 1503 | 3512 | - - - | - - - | - - - | - - - | 1130 | 880 | 1503 | 3512 | 800 | 743 | -33 | 1508 | - - - | - - - | - - - | - - - | 800 | 743 | -33 | 1508 | 1393 | 1164 | 1527 | 4084 | # # # | # # # | # # # | # # # | 0.811 | 0.756 | 0.984 | 0.86 | # # # | # # # | # # # | - - - | 0.816 | 0.765 | 0.999 | 0.87 | - - - | 0.429 | 1.6 | 1.59 | 1.52 | 1.45 | 1.52 | 1.52 | 9.93 | 14.73 | 17.66 | 0 | - - - | - - - | - - - | - - - | 1393 | 1164 | 1527 | 4084 | Over-range | 815 | 762 | 271 | 2083 | 156 | 170 | 269 | 1437 | 1130 | 882 | 1500 | 3512 | 1130 | 882 | 1500 | 3512 | - - - | - - - | - - - | - - -
5/2/2026 | 1:00:00 PM | 282.3 | 279.3 | 277.72 | 487.91 | 480.5 | 485.31 | 5.2867 | 4.7962 | 5.6948 | 4.1215 | 1.425 | 1.425 | 1.423 | 1.508 | 1.429 | 1.312 | Over-range | 59.99 | 1185 | 1088 | 1551 | 3823 | - - - | - - - | - - - | - - - | 1185 | 1088 | 1551 | 3823 | 890 | 744 | -125 | 1508 | - - - | - - - | - - - | - - - | 890 | 744 | -125 | 1508 | 1491 | 1333 | 1581 | 4405 | # # # | # # # | # # # | # # # | 0.795 | 0.816 | 0.981 | 0.868 | # # # | # # # | # # # | - - - | 0.799 | 0.824 | 0.996 | 0.877 | - - - | 0.395 | 1.54 | 1.52 | 1.46 | 1.39 | 1.46 | 1.44 | 9.35 | 13.53 | 17.47 | 0 | - - - | - - - | - - - | - - - | 1491 | 1333 | 1581 | 4405 | Over-range | 904 | 766 | 307 | 2187 | 161 | 179 | 274 | 1582 | 1184 | 1090 | 1549 | 3823 | 1184 | 1090 | 1549 | 3823 | - - - | - - - | - - - | - - -
5/2/2026 | 1:15:00 PM | 282.3 | 279.31 | 277.77 | 487.86 | 480.61 | 485.37 | 5.5042 | 5.008 | 5.7993 | 4.1331 | 1.426 | 1.426 | 1.424 | 1.508 | 1.432 | 1.302 | Over-range | 59.99 | 1228 | 1167 | 1579 | 3974 | - - - | - - - | - - - | - - - | 1228 | 1167 | 1579 | 3974 | 933 | 742 | -137 | 1536 | - - - | - - - | - - - | - - - | 933 | 742 | -137 | 1536 | 1550 | 1396 | 1611 | 4557 | # # # | # # # | # # # | # # # | 0.792 | 0.836 | 0.981 | 0.872 | # # # | # # # | # # # | - - - | 0.789 | 0.836 | 0.984 | 0.872 | - - - | 0.387 | 1.51 | 1.48 | 1.43 | 1.38 | 1.42 | 1.42 | 9.16 | 13.09 | 17.28 | 0 | - - - | - - - | - - - | - - - | 1550 | 1396 | 1611 | 4557 | Over-range | 946 | 764 | 315 | 2230 | 155 | 181 | 274 | 1611 | 1241 | 1185 | 1606 | 4032 | 1241 | 1185 | 1606 | 4032 | - - - | - - - | - - - | - - -
5/2/2026 | 1:30:00 PM | 282.38 | 279.32 | 277.83 | 487.99 | 480.58 | 485.52 | 4.9236 | 4.2604 | 5.4946 | 4.1313 | 1.427 | 1.427 | 1.425 | 1.503 | 1.444 | 1.351 | Over-range | 59.99 | 1123 | 848 | 1493 | 3465 | - - - | - - - | - - - | - - - | 1123 | 848 | 1493 | 3465 | 788 | 747 | -20 | 1513 | - - - | - - - | - - - | - - - | 788 | 747 | -20 | 1513 | 1382 | 1169 | 1525 | 4076 | # # # | # # # | # # # | # # # | 0.812 | 0.726 | 0.979 | 0.85 | # # # | # # # | # # # | - - - | 0.818 | 0.735 | 0.995 | 0.86 | - - - | 0.437 | 1.52 | 1.53 | 1.43 | 1.4 | 1.44 | 1.44 | 10.29 | 15.29 | 17.87 | 0 | - - - | - - - | - - - | - - - | 1382 | 1169 | 1525 | 4076 | Over-range | 803 | 767 | 308 | 2136 | 154 | 174 | 271 | 1506 | 1125 | 850 | 1491 | 3465 | 1125 | 850 | 1491 | 3465 | - - - | - - - | - - - | - - -
5/2/2026 | 1:45:00 PM | 282.46 | 279.41 | 277.85 | 488.18 | 480.68 | 485.58 | 4.6389 | 3.7224 | 5.3566 | 4.1409 | 1.427 | 1.426 | 1.424 | 1.503 | 1.452 | 1.384 | Over-range | 59.99 | 1082 | 692 | 1462 | 3236 | - - - | - - - | - - - | - - - | 1082 | 692 | 1462 | 3236 | 722 | 750 | 50 | 1521 | - - - | - - - | - - - | - - - | 722 | 750 | 50 | 1521 | 1310 | 1038 | 1488 | 3836 | # # # | # # # | # # # | # # # | 0.826 | 0.667 | 0.982 | 0.844 | # # # | # # # | # # # | - - - | 0.833 | 0.676 | 0.999 | 0.855 | - - - | 0.47 | 1.53 | 1.5 | 1.41 | 1.4 | 1.43 | 1.42 | 10.7 | 16.58 | 18.19 | 0 | - - - | - - - | - - - | - - - | 1310 | 1038 | 1488 | 3836 | Over-range | 738 | 770 | 279 | 2059 | 152 | 175 | 271 | 1386 | 1085 | 692 | 1461 | 3237 | 1085 | 692 | 1461 | 3237 | - - - | - - - | - - - | - - -
5/2/2026 | 2:00:00 PM | 282.29 | 279.21 | 277.73 | 487.79 | 480.43 | 485.36 | 4.7517 | 3.8771 | 5.3897 | 4.1371 | 1.427 | 1.426 | 1.424 | 1.507 | 1.442 | 1.369 | Over-range | 59.99 | 1101 | 764 | 1472 | 3337 | - - - | - - - | - - - | - - - | 1101 | 764 | 1472 | 3337 | 751 | 745 | 14 | 1510 | - - - | - - - | - - - | - - - | 751 | 745 | 14 | 1510 | 1341 | 1082 | 1497 | 3920 | # # # | # # # | # # # | # # # | 0.821 | 0.706 | 0.983 | 0.851 | # # # | # # # | # # # | - - - | 0.827 | 0.716 | 1 | 0.862 | - - - | 0.452 | 1.51 | 1.46 | 1.35 | 1.37 | 1.39 | 1.37 | 10.33 | 16.01 | 18.25 | 0 | - - - | - - - | - - - | - - - | 1341 | 1082 | 1497 | 3920 | Over-range | 766 | 766 | 273 | 2057 | 151 | 176 | 272 | 1397 | 1104 | 764 | 1471 | 3339 | 1104 | 764 | 1471 | 3339 | - - - | - - - | - - - | - - -
5/2/2026 | 2:15:00 PM | 282.43 | 279.32 | 277.9 | 488 | 480.65 | 485.66 | 5.0509 | 4.3716 | 5.5719 | 4.1403 | 1.427 | 1.426 | 1.423 | 1.513 | 1.428 | 1.325 | Over-range | 59.99 | 1149 | 945 | 1522 | 3616 | - - - | - - - | - - - | - - - | 1149 | 945 | 1522 | 3616 | 830 | 745 | -63 | 1510 | - - - | - - - | - - - | - - - | 830 | 745 | -63 | 1510 | 1426 | 1218 | 1548 | 4192 | # # # | # # # | # # # | # # # | 0.806 | 0.776 | 0.983 | 0.863 | # # # | # # # | # # # | - - - | 0.811 | 0.784 | 0.999 | 0.872 | - - - | 0.418 | 1.48 | 1.44 | 1.37 | 1.37 | 1.38 | 1.36 | 9.78 | 14.7 | 17.81 | 0 | - - - | - - - | - - - | - - - | 1426 | 1218 | 1548 | 4192 | Over-range | 844 | 766 | 285 | 2121 | 153 | 180 | 274 | 1489 | 1151 | 946 | 1518 | 3616 | 1151 | 946 | 1518 | 3616 | - - - | - - - | - - - | - - -
5/2/2026 | 2:30:00 PM | 282.42 | 279.27 | 277.9 | 487.93 | 480.6 | 485.69 | 5.4219 | 5.0141 | 5.7751 | 4.1297 | 1.427 | 1.426 | 1.423 | 1.518 | 1.432 | 1.295 | Over-range | 59.98 | 1208 | 1172 | 1572 | 3952 | - - - | - - - | - - - | - - - | 1208 | 1172 | 1572 | 3952 | 928 | 741 | -163 | 1505 | - - - | - - - | - - - | - - - | 928 | 741 | -163 | 1505 | 1531 | 1400 | 1605 | 4536 | # # # | # # # | # # # | # # # | 0.789 | 0.837 | 0.98 | 0.871 | # # # | # # # | # # # | - - - | 0.794 | 0.845 | 0.994 | 0.88 | - - - | 0.381 | 1.47 | 1.47 | 1.33 | 1.35 | 1.37 | 1.34 | 9.1 | 13.01 | 17.36 | 0 | - - - | - - - | - - - | - - - | 1531 | 1400 | 1605 | 4536 | Over-range | 941 | 764 | 322 | 2225 | 154 | 187 | 276 | 1639 | 1212 | 1171 | 1571 | 3954 | 1212 | 1171 | 1571 | 3954 | - - - | - - - | - - - | - - -
5/2/2026 | 2:45:00 PM | 282.14 | 279 | 277.66 | 487.43 | 480.15 | 485.26 | 4.8511 | 4.1235 | 5.4657 | 4.1363 | 1.427 | 1.426 | 1.423 | 1.508 | 1.443 | 1.356 | Over-range | 59.98 | 1112 | 810 | 1486 | 3408 | - - - | - - - | - - - | - - - | 1112 | 810 | 1486 | 3408 | 768 | 741 | -6 | 1502 | - - - | - - - | - - - | - - - | 768 | 741 | -6 | 1502 | 1362 | 1134 | 1516 | 4012 | # # # | # # # | # # # | # # # | 0.817 | 0.714 | 0.98 | 0.849 | # # # | # # # | # # # | - - - | 0.822 | 0.723 | 0.996 | 0.86 | - - - | 0.441 | 1.46 | 1.44 | 1.32 | 1.33 | 1.36 | 1.32 | 10.36 | 15.45 | 17.78 | 0 | - - - | - - - | - - - | - - - | 1362 | 1134 | 1516 | 4012 | Over-range | 784 | 762 | 298 | 2107 | 156 | 177 | 269 | 1476 | 1114 | 808 | 1488 | 3410 | 1114 | 808 | 1488 | 3410 | - - - | - - - | - - - | - - -
5/2/2026 | 3:00:00 PM | 282.49 | 279.4 | 277.98 | 488.08 | 480.81 | 485.79 | 4.7813 | 3.8199 | 5.4103 | 4.1448 | 1.427 | 1.426 | 1.422 | 1.504 | 1.446 | 1.382 | Over-range | 59.98 | 1112 | 729 | 1474 | 3315 | - - - | - - - | - - - | - - - | 1112 | 729 | 1474 | 3315 | 744 | 748 | 52 | 1544 | - - - | - - - | - - - | - - - | 744 | 748 | 52 | 1544 | 1348 | 1063 | 1504 | 3915 | # # # | # # # | # # # | # # # | 0.825 | 0.686 | 0.98 | 0.847 | # # # | # # # | # # # | - - - | 0.823 | 0.689 | 0.987 | 0.85 | - - - | 0.466 | 1.47 | 1.43 | 1.32 | 1.34 | 1.35 | 1.33 | 10.41 | 16.34 | 18.2 | 0 | - - - | - - - | - - - | - - - | 1348 | 1063 | 1504 | 3915 | Over-range | 761 | 769 | 294 | 2081 | 160 | 174 | 274 | 1391 | 1123 | 733 | 1498 | 3354 | 1123 | 733 | 1498 | 3354 | - - - | - - - | - - - | - - -
5/2/2026 | 3:15:00 PM | 282.2 | 279.06 | 277.67 | 487.58 | 480.19 | 485.29 | 4.7582 | 3.8926 | 5.3913 | 4.1335 | 1.427 | 1.426 | 1.423 | 1.507 | 1.444 | 1.366 | Over-range | 60 | 1102 | 769 | 1472 | 3343 | - - - | - - - | - - - | - - - | 1102 | 769 | 1472 | 3343 | 750 | 743 | 9 | 1502 | - - - | - - - | - - - | - - - | 750 | 743 | 9 | 1502 | 1342 | 1084 | 1497 | 3923 | # # # | # # # | # # # | # # # | 0.821 | 0.709 | 0.983 | 0.852 | # # # | # # # | # # # | - - - | 0.826 | 0.719 | 0.999 | 0.862 | - - - | 0.449 | 1.46 | 1.43 | 1.33 | 1.33 | 1.35 | 1.33 | 10.36 | 15.77 | 18.15 | 0 | - - - | - - - | - - - | - - - | 1342 | 1084 | 1497 | 3923 | Over-range | 766 | 762 | 274 | 2054 | 155 | 169 | 271 | 1401 | 1101 | 771 | 1470 | 3342 | 1101 | 771 | 1470 | 3342 | - - - | - - - | - - - | - - -
5/2/2026 | 3:30:00 PM | 282.18 | 279.08 | 277.59 | 487.61 | 480.13 | 485.18 | 5.0932 | 4.458 | 5.6004 | 4.1331 | 1.426 | 1.425 | 1.423 | 1.512 | 1.428 | 1.322 | Over-range | 59.99 | 1155 | 973 | 1527 | 3655 | - - - | - - - | - - - | - - - | 1155 | 973 | 1527 | 3655 | 838 | 743 | -78 | 1501 | - - - | - - - | - - - | - - - | 838 | 743 | -78 | 1501 | 1436 | 1240 | 1554 | 4230 | # # # | # # # | # # # | # # # | 0.805 | 0.785 | 0.982 | 0.864 | # # # | # # # | # # # | - - - | 0.809 | 0.794 | 0.998 | 0.874 | - - - | 0.411 | 1.49 | 1.44 | 1.32 | 1.34 | 1.36 | 1.34 | 9.66 | 14.48 | 17.73 | 0 | - - - | - - - | - - - | - - - | 1436 | 1240 | 1554 | 4230 | Over-range | 853 | 764 | 290 | 2128 | 159 | 179 | 274 | 1507 | 1155 | 975 | 1525 | 3655 | 1155 | 975 | 1525 | 3655 | - - - | - - - | - - - | - - -
5/2/2026 | 3:45:00 PM | 282.3 | 279.21 | 277.75 | 487.78 | 480.47 | 485.37 | 5.5293 | 5.2159 | 5.8556 | 4.1303 | 1.426 | 1.425 | 1.422 | 1.519 | 1.44 | 1.301 | Over-range | 59.98 | 1225 | 1238 | 1591 | 4053 | - - - | - - - | - - - | - - - | 1225 | 1238 | 1591 | 4053 | 953 | 742 | -193 | 1500 | - - - | - - - | - - - | - - - | 953 | 742 | -193 | 1500 | 1561 | 1455 | 1626 | 4642 | # # # | # # # | # # # | # # # | 0.785 | 0.851 | 0.978 | 0.873 | # # # | # # # | # # # | - - - | 0.789 | 0.858 | 0.993 | 0.882 | - - - | 0.37 | 1.47 | 1.44 | 1.33 | 1.34 | 1.35 | 1.33 | 8.94 | 12.7 | 17.17 | 0 | - - - | - - - | - - - | - - - | 1561 | 1455 | 1626 | 4642 | Over-range | 967 | 764 | 338 | 2263 | 165 | 184 | 276 | 1694 | 1224 | 1240 | 1590 | 4053 | 1224 | 1240 | 1590 | 4053 | - - - | - - - | - - - | - - -
5/2/2026 | 4:00:00 PM | 282.13 | 278.98 | 277.58 | 487.46 | 480.06 | 485.12 | 5.0442 | 4.3649 | 5.5579 | 4.1305 | 1.426 | 1.425 | 1.422 | 1.51 | 1.43 | 1.326 | Over-range | 59.98 | 1148 | 944 | 1517 | 3609 | - - - | - - - | - - - | - - - | 1148 | 944 | 1517 | 3609 | 825 | 743 | -66 | 1502 | - - - | - - - | - - - | - - - | 825 | 743 | -66 | 1502 | 1422 | 1216 | 1543 | 4181 | # # # | # # # | # # # | # # # | 0.807 | 0.777 | 0.983 | 0.863 | # # # | # # # | # # # | - - - | 0.812 | 0.786 | 0.999 | 0.873 | - - - | 0.416 | 1.49 | 1.44 | 1.31 | 1.34 | 1.35 | 1.33 | 9.77 | 14.36 | 17.74 | 0 | - - - | - - - | - - - | - - - | 1422 | 1216 | 1543 | 4181 | Over-range | 840 | 763 | 282 | 2111 | 157 | 174 | 272 | 1483 | 1147 | 947 | 1514 | 3608 | 1147 | 947 | 1514 | 3608 | - - - | - - - | - - - | - - -
5/2/2026 | 4:15:00 PM | 282.16 | 279.06 | 277.55 | 487.57 | 480.07 | 485.14 | 4.9418 | 4.1894 | 5.5127 | 4.134 | 1.426 | 1.425 | 1.423 | 1.508 | 1.432 | 1.338 | Over-range | 59.99 | 1132 | 885 | 1505 | 3522 | - - - | - - - | - - - | - - - | 1132 | 885 | 1505 | 3522 | 799 | 743 | -40 | 1500 | - - - | - - - | - - - | - - - | 799 | 743 | -40 | 1500 | 1394 | 1169 | 1530 | 4093 | # # # | # # # | # # # | # # # | 0.812 | 0.757 | 0.984 | 0.861 | # # # | # # # | # # # | - - - | 0.816 | 0.766 | 0.999 | 0.87 | - - - | 0.426 | 1.49 | 1.41 | 1.31 | 1.34 | 1.35 | 1.33 | 9.93 | 14.83 | 17.75 | 0 | - - - | - - - | - - - | - - - | 1394 | 1169 | 1530 | 4093 | Over-range | 814 | 763 | 274 | 2085 | 160 | 175 | 271 | 1449 | 1130 | 886 | 1506 | 3522 | 1130 | 886 | 1506 | 3522 | - - - | - - - | - - - | - - -
5/2/2026 | 4:30:00 PM | 282.11 | 278.99 | 277.53 | 487.44 | 480.04 | 485.07 | 5.3428 | 4.8894 | 5.7339 | 4.1257 | 1.426 | 1.425 | 1.422 | 1.517 | 1.426 | 1.295 | Over-range | 59.97 | 1195 | 1128 | 1560 | 3883 | - - - | - - - | - - - | - - - | 1195 | 1128 | 1560 | 3883 | 904 | 741 | -147 | 1497 | - - - | - - - | - - - | - - - | 904 | 741 | -147 | 1497 | 1507 | 1363 | 1591 | 4461 | # # # | # # # | # # # | # # # | 0.793 | 0.828 | 0.98 | 0.87 | # # # | # # # | # # # | - - - | 0.798 | 0.835 | 0.996 | 0.879 | - - - | 0.385 | 1.46 | 1.45 | 1.3 | 1.34 | 1.34 | 1.33 | 9.19 | 13.33 | 17.49 | 0 | - - - | - - - | - - - | - - - | 1507 | 1363 | 1591 | 4461 | Over-range | 919 | 764 | 314 | 2197 | 164 | 186 | 276 | 1608 | 1195 | 1127 | 1562 | 3884 | 1195 | 1127 | 1562 | 3884 | - - - | - - - | - - - | - - -
5/2/2026 | 4:45:00 PM | 281.96 | 278.86 | 277.36 | 487.19 | 479.81 | 484.77 | 5.2861 | 4.6844 | 5.6794 | 4.1359 | 1.426 | 1.425 | 1.423 | 1.509 | 1.434 | 1.32 | Over-range | 59.99 | 1190 | 1033 | 1542 | 3765 | - - - | - - - | - - - | - - - | 1190 | 1033 | 1542 | 3765 | 870 | 738 | -86 | 1522 | - - - | - - - | - - - | - - - | 870 | 738 | -86 | 1522 | 1484 | 1295 | 1574 | 4353 | # # # | # # # | # # # | # # # | 0.802 | 0.797 | 0.98 | 0.865 | # # # | # # # | # # # | - - - | 0.799 | 0.799 | 0.984 | 0.866 | - - - | 0.404 | 1.47 | 1.43 | 1.33 | 1.35 | 1.35 | 1.34 | 9.42 | 13.84 | 17.43 | 0 | - - - | - - - | - - - | - - - | 1484 | 1295 | 1574 | 4353 | Over-range | 885 | 760 | 314 | 2179 | 156 | 179 | 273 | 1553 | 1202 | 1042 | 1554 | 3797 | 1202 | 1042 | 1554 | 3797 | - - - | - - - | - - - | - - -
5/2/2026 | 5:00:00 PM | 282.02 | 278.88 | 277.37 | 487.32 | 479.75 | 484.85 | 4.5047 | 3.5308 | 5.2865 | 4.1416 | 1.425 | 1.424 | 1.422 | 1.501 | 1.456 | 1.404 | Over-range | 59.99 | 1060 | 610 | 1438 | 3109 | - - - | - - - | - - - | - - - | 1060 | 610 | 1438 | 3109 | 681 | 744 | 80 | 1505 | - - - | - - - | - - - | - - - | 681 | 744 | 80 | 1505 | 1269 | 982 | 1466 | 3718 | # # # | # # # | # # # | # # # | 0.835 | 0.622 | 0.981 | 0.836 | # # # | # # # | # # # | - - - | 0.842 | 0.631 | 0.998 | 0.847 | - - - | 0.484 | 1.48 | 1.45 | 1.33 | 1.35 | 1.36 | 1.34 | 10.93 | 17.1 | 18.26 | 0 | - - - | - - - | - - - | - - - | 1269 | 982 | 1466 | 3718 | Over-range | 698 | 763 | 283 | 2036 | 150 | 171 | 267 | 1372 | 1063 | 610 | 1437 | 3110 | 1063 | 610 | 1437 | 3110 | - - - | - - - | - - - | - - -
5/2/2026 | 5:15:00 PM | 282.32 | 279.25 | 277.81 | 487.83 | 480.53 | 485.48 | 4.8005 | 3.9674 | 5.4203 | 4.1347 | 1.427 | 1.425 | 1.423 | 1.509 | 1.438 | 1.361 | Over-range | 60 | 1109 | 795 | 1480 | 3383 | - - - | - - - | - - - | - - - | 1109 | 795 | 1480 | 3383 | 762 | 745 | 0 | 1507 | - - - | - - - | - - - | - - - | 762 | 745 | 0 | 1507 | 1355 | 1106 | 1506 | 3966 | # # # | # # # | # # # | # # # | 0.818 | 0.719 | 0.983 | 0.853 | # # # | # # # | # # # | - - - | 0.825 | 0.728 | 1 | 0.864 | - - - | 0.446 | 1.51 | 1.45 | 1.34 | 1.38 | 1.38 | 1.36 | 10.26 | 15.8 | 18.22 | 0 | - - - | - - - | - - - | - - - | 1355 | 1106 | 1506 | 3966 | Over-range | 778 | 766 | 276 | 2069 | 156 | 180 | 273 | 1416 | 1111 | 793 | 1482 | 3386 | 1111 | 793 | 1482 | 3386 | - - - | - - - | - - - | - - -
5/2/2026 | 5:30:00 PM | 282.14 | 279.15 | 277.63 | 487.6 | 480.35 | 485.1 | 5.2423 | 4.7113 | 5.6919 | 4.138 | 1.427 | 1.425 | 1.423 | 1.517 | 1.426 | 1.304 | Over-range | 59.97 | 1178 | 1063 | 1550 | 3792 | - - - | - - - | - - - | - - - | 1178 | 1063 | 1550 | 3792 | 878 | 742 | -116 | 1503 | - - - | - - - | - - - | - - - | 878 | 742 | -116 | 1503 | 1478 | 1312 | 1580 | 4370 | # # # | # # # | # # # | # # # | 0.797 | 0.811 | 0.981 | 0.868 | # # # | # # # | # # # | - - - | 0.802 | 0.818 | 0.997 | 0.877 | - - - | 0.396 | 1.49 | 1.47 | 1.34 | 1.37 | 1.37 | 1.35 | 9.4 | 14.02 | 17.63 | 0 | - - - | - - - | - - - | - - - | 1478 | 1312 | 1580 | 4370 | Over-range | 892 | 766 | 304 | 2172 | 161 | 187 | 276 | 1567 | 1180 | 1062 | 1552 | 3794 | 1180 | 1062 | 1552 | 3794 | - - - | - - - | - - - | - - -
5/2/2026 | 5:45:00 PM | 282.45 | 279.35 | 277.91 | 488.07 | 480.67 | 485.66 | 5.212 | 4.6451 | 5.651 | 4.13 | 1.427 | 1.425 | 1.422 | 1.518 | 1.419 | 1.301 | Over-range | 60 | 1175 | 1047 | 1542 | 3764 | - - - | - - - | - - - | - - - | 1175 | 1047 | 1542 | 3764 | 872 | 744 | -108 | 1506 | - - - | - - - | - - - | - - - | 872 | 744 | -108 | 1506 | 1472 | 1297 | 1570 | 4340 | # # # | # # # | # # # | # # # | 0.798 | 0.807 | 0.982 | 0.867 | # # # | # # # | # # # | - - - | 0.803 | 0.814 | 0.997 | 0.877 | - - - | 0.4 | 1.5 | 1.45 | 1.33 | 1.37 | 1.37 | 1.34 | 9.47 | 13.95 | 17.71 | 0 | - - - | - - - | - - - | - - - | 1472 | 1297 | 1570 | 4340 | Over-range | 887 | 766 | 297 | 2161 | 161 | 185 | 276 | 1549 | 1176 | 1045 | 1544 | 3765 | 1176 | 1045 | 1544 | 3765 | - - - | - - - | - - - | - - -
5/2/2026 | 6:00:00 PM | 282.09 | 278.98 | 277.51 | 487.45 | 480 | 485 | 4.4359 | 3.4476 | 5.2524 | 4.143 | 1.426 | 1.425 | 1.422 | 1.501 | 1.464 | 1.415 | Over-range | 59.98 | 1048 | 564 | 1427 | 3039 | - - - | - - - | - - - | - - - | 1048 | 564 | 1427 | 3039 | 662 | 745 | 101 | 1508 | - - - | - - - | - - - | - - - | 662 | 745 | 101 | 1508 | 1250 | 958 | 1457 | 3664 | # # # | # # # | # # # | # # # | 0.839 | 0.589 | 0.98 | 0.83 | # # # | # # # | # # # | - - - | 0.845 | 0.598 | 0.996 | 0.841 | - - - | 0.496 | 1.48 | 1.45 | 1.36 | 1.36 | 1.37 | 1.35 | 11.21 | 17.34 | 18.26 | 0 | - - - | - - - | - - - | - - - | 1250 | 958 | 1457 | 3664 | Over-range | 680 | 764 | 292 | 2043 | 154 | 171 | 266 | 1378 | 1049 | 563 | 1429 | 3042 | 1049 | 563 | 1429 | 3042 | - - - | - - - | - - - | - - -
5/2/2026 | 6:15:00 PM | 282.38 | 279.35 | 277.81 | 488 | 480.65 | 485.46 | 4.7664 | 3.9103 | 5.4183 | 4.1435 | 1.427 | 1.425 | 1.422 | 1.508 | 1.442 | 1.367 | Over-range | 59.99 | 1103 | 771 | 1480 | 3354 | - - - | - - - | - - - | - - - | 1103 | 771 | 1480 | 3354 | 753 | 747 | 12 | 1512 | - - - | - - - | - - - | - - - | 753 | 747 | 12 | 1512 | 1345 | 1090 | 1505 | 3941 | # # # | # # # | # # # | # # # | 0.82 | 0.708 | 0.983 | 0.851 | # # # | # # # | # # # | - - - | 0.826 | 0.717 | 0.999 | 0.862 | - - - | 0.451 | 1.51 | 1.45 | 1.35 | 1.38 | 1.38 | 1.36 | 10.38 | 15.92 | 18.15 | 0 | - - - | - - - | - - - | - - - | 1345 | 1090 | 1505 | 3941 | Over-range | 770 | 767 | 276 | 2068 | 159 | 176 | 272 | 1410 | 1103 | 771 | 1481 | 3355 | 1103 | 771 | 1481 | 3355 | - - - | - - - | - - - | - - -
5/2/2026 | 6:30:00 PM | 282.56 | 279.39 | 277.92 | 488.24 | 480.67 | 485.77 | 5.2461 | 4.5714 | 5.6364 | 4.1373 | 1.426 | 1.425 | 1.422 | 1.512 | 1.43 | 1.33 | Over-range | 59.99 | 1186 | 1010 | 1537 | 3733 | - - - | - - - | - - - | - - - | 1186 | 1010 | 1537 | 3733 | 867 | 744 | -71 | 1539 | - - - | - - - | - - - | - - - | 867 | 744 | -71 | 1539 | 1478 | 1272 | 1566 | 4315 | # # # | # # # | # # # | # # # | 0.803 | 0.794 | 0.982 | 0.865 | # # # | # # # | # # # | - - - | 0.8 | 0.796 | 0.987 | 0.867 | - - - | 0.412 | 1.5 | 1.47 | 1.35 | 1.37 | 1.38 | 1.36 | 9.49 | 14.33 | 17.84 | 0 | - - - | - - - | - - - | - - - | 1478 | 1272 | 1566 | 4315 | Over-range | 881 | 767 | 299 | 2164 | 155 | 186 | 278 | 1516 | 1200 | 1025 | 1559 | 3784 | 1200 | 1025 | 1559 | 3784 | - - - | - - - | - - - | - - -
5/2/2026 | 6:45:00 PM | 282.82 | 279.69 | 278.13 | 488.77 | 481.1 | 486.15 | 5.3019 | 4.8067 | 5.7193 | 4.1391 | 1.426 | 1.424 | 1.422 | 1.515 | 1.426 | 1.305 | Over-range | 59.99 | 1189 | 1095 | 1560 | 3844 | - - - | - - - | - - - | - - - | 1189 | 1095 | 1560 | 3844 | 899 | 748 | -125 | 1521 | - - - | - - - | - - - | - - - | 899 | 748 | -125 | 1521 | 1498 | 1341 | 1590 | 4430 | # # # | # # # | # # # | # # # | 0.793 | 0.816 | 0.981 | 0.868 | # # # | # # # | # # # | - - - | 0.799 | 0.824 | 0.996 | 0.877 | - - - | 0.396 | 1.51 | 1.48 | 1.33 | 1.37 | 1.38 | 1.36 | 9.37 | 13.5 | 17.44 | 0 | - - - | - - - | - - - | - - - | 1498 | 1341 | 1590 | 4430 | Over-range | 912 | 771 | 307 | 2201 | 154 | 185 | 275 | 1590 | 1193 | 1094 | 1558 | 3845 | 1193 | 1094 | 1558 | 3845 | - - - | - - - | - - - | - - -
5/2/2026 | 7:00:00 PM | 283.14 | 280.01 | 278.51 | 489.28 | 481.77 | 486.75 | 4.5317 | 3.6064 | 5.2896 | 4.1476 | 1.426 | 1.424 | 1.422 | 1.501 | 1.464 | 1.406 | Over-range | 60.01 | 1064 | 614 | 1442 | 3120 | - - - | - - - | - - - | - - - | 1064 | 614 | 1442 | 3120 | 693 | 757 | 85 | 1535 | - - - | - - - | - - - | - - - | 693 | 757 | 85 | 1535 | 1280 | 1002 | 1472 | 3754 | # # # | # # # | # # # | # # # | 0.831 | 0.613 | 0.979 | 0.831 | # # # | # # # | # # # | - - - | 0.838 | 0.622 | 0.997 | 0.842 | - - - | 0.492 | 1.52 | 1.44 | 1.36 | 1.38 | 1.38 | 1.36 | 11.18 | 16.99 | 18.42 | 0 | - - - | - - - | - - - | - - - | 1280 | 1002 | 1472 | 3754 | Over-range | 710 | 776 | 297 | 2082 | 153 | 169 | 271 | 1406 | 1067 | 615 | 1440 | 3121 | 1067 | 615 | 1440 | 3121 | - - - | - - - | - - - | - - -
5/2/2026 | 7:15:00 PM | 283.43 | 280.6 | 278.95 | 490.07 | 482.76 | 487.24 | 4.6638 | 3.7701 | 5.3802 | 4.1532 | 1.427 | 1.425 | 1.422 | 1.505 | 1.454 | 1.386 | Over-range | 59.99 | 1087 | 702 | 1473 | 3262 | - - - | - - - | - - - | - - - | 1087 | 702 | 1473 | 3262 | 734 | 767 | 53 | 1554 | - - - | - - - | - - - | - - - | 734 | 767 | 53 | 1554 | 1321 | 1056 | 1501 | 3878 | # # # | # # # | # # # | # # # | 0.823 | 0.665 | 0.982 | 0.841 | # # # | # # # | # # # | - - - | 0.829 | 0.675 | 0.999 | 0.852 | - - - | 0.476 | 1.52 | 1.45 | 1.33 | 1.39 | 1.36 | 1.36 | 10.83 | 16.57 | 18.48 | 0 | - - - | - - - | - - - | - - - | 1321 | 1056 | 1501 | 3878 | Over-range | 751 | 786 | 284 | 2096 | 159 | 174 | 276 | 1406 | 1087 | 704 | 1472 | 3263 | 1087 | 704 | 1472 | 3263 | - - - | - - - | - - - | - - -
5/2/2026 | 7:30:00 PM | 283.42 | 280.62 | 278.95 | 490.1 | 482.77 | 487.22 | 4.7795 | 3.94 | 5.4203 | 4.1457 | 1.427 | 1.425 | 1.422 | 1.507 | 1.444 | 1.37 | Over-range | 59.97 | 1105 | 775 | 1486 | 3366 | - - - | - - - | - - - | - - - | 1105 | 775 | 1486 | 3366 | 766 | 766 | 21 | 1553 | - - - | - - - | - - - | - - - | 766 | 766 | 21 | 1553 | 1354 | 1105 | 1512 | 3972 | # # # | # # # | # # # | # # # | 0.816 | 0.701 | 0.983 | 0.848 | # # # | # # # | # # # | - - - | 0.822 | 0.71 | 1 | 0.858 | - - - | 0.462 | 1.52 | 1.46 | 1.33 | 1.39 | 1.36 | 1.36 | 10.54 | 16.06 | 18.55 | 0 | - - - | - - - | - - - | - - - | 1354 | 1105 | 1512 | 3972 | Over-range | 783 | 787 | 280 | 2108 | 162 | 179 | 279 | 1424 | 1105 | 775 | 1487 | 3367 | 1105 | 775 | 1487 | 3367 | - - - | - - - | - - - | - - -
5/2/2026 | 7:45:00 PM | 283.51 | 280.74 | 278.98 | 490.27 | 482.91 | 487.31 | 5.3055 | 5.4036 | 5.7324 | 3.5439 | 1.428 | 1.425 | 1.423 | 1.516 | 1.44 | 1.297 | Over-range | 59.98 | 1189 | 1300 | 1569 | 4058 | - - - | - - - | - - - | - - - | 1189 | 1300 | 1569 | 4058 | 906 | 700 | -117 | 1488 | - - - | - - - | - - - | - - - | 906 | 700 | -117 | 1488 | 1503 | 1500 | 1599 | 4603 | # # # | # # # | # # # | # # # | 0.791 | 0.866 | 0.981 | 0.882 | # # # | # # # | # # # | - - - | 0.796 | 0.872 | 0.997 | 0.89 | - - - | 0.367 | 1.51 | 1.47 | 1.34 | 1.39 | 1.36 | 1.36 | 9.5 | 11.42 | 17.78 | 0 | - - - | - - - | - - - | - - - | 1503 | 1500 | 1599 | 4603 | Over-range | 920 | 721 | 308 | 2164 | 157 | 172 | 281 | 1570 | 1193 | 1299 | 1568 | 4059 | 1193 | 1299 | 1568 | 4059 | - - - | - - - | - - - | - - -
5/2/2026 | 8:00:00 PM | 283.67 | 280.99 | 279.14 | 490.66 | 483.32 | 487.53 | 5.1198 | 5.5471 | 5.612 | 2.7273 | 1.427 | 1.425 | 1.422 | 1.513 | 1.453 | 1.321 | Over-range | 59.97 | 1158 | 1403 | 1538 | 4099 | - - - | - - - | - - - | - - - | 1158 | 1403 | 1538 | 4099 | 858 | 640 | -64 | 1433 | - - - | - - - | - - - | - - - | 858 | 640 | -64 | 1433 | 1450 | 1552 | 1566 | 4569 | # # # | # # # | # # # | # # # | 0.799 | 0.904 | 0.982 | 0.897 | # # # | # # # | # # # | - - - | 0.804 | 0.909 | 0.998 | 0.906 | - - - | 0.35 | 1.52 | 1.44 | 1.31 | 1.38 | 1.34 | 1.34 | 9.95 | 9.17 | 18.07 | 0 | - - - | - - - | - - - | - - - | 1450 | 1552 | 1566 | 4569 | Over-range | 873 | 658 | 297 | 2017 | 157 | 150 | 281 | 1416 | 1162 | 1403 | 1536 | 4101 | 1162 | 1403 | 1536 | 4101 | - - - | - - - | - - - | - - -
5/2/2026 | 8:15:00 PM | 284.22 | 281.54 | 279.77 | 491.58 | 484.33 | 488.6 | 4.4704 | 4.2981 | 5.2994 | 2.7502 | 1.427 | 1.425 | 1.422 | 1.501 | 1.45 | 1.416 | Over-range | 59.97 | 1053 | 998 | 1450 | 3502 | - - - | - - - | - - - | - - - | 1053 | 998 | 1450 | 3502 | 690 | 655 | 117 | 1462 | - - - | - - - | - - - | - - - | 690 | 655 | 117 | 1462 | 1269 | 1206 | 1482 | 3957 | # # # | # # # | # # # | # # # | 0.83 | 0.828 | 0.978 | 0.885 | # # # | # # # | # # # | - - - | 0.837 | 0.833 | 0.996 | 0.895 | - - - | 0.418 | 1.54 | 1.44 | 1.37 | 1.4 | 1.37 | 1.37 | 11.57 | 11.69 | 18.8 | 0 | - - - | - - - | - - - | - - - | 1269 | 1206 | 1482 | 3957 | Over-range | 708 | 671 | 306 | 1842 | 159 | 147 | 278 | 1120 | 1056 | 996 | 1451 | 3503 | 1056 | 996 | 1451 | 3503 | - - - | - - - | - - - | - - -
5/2/2026 | 8:30:00 PM | 284.19 | 281.61 | 279.8 | 491.62 | 484.46 | 488.53 | 4.8389 | 4.8213 | 5.4596 | 2.7546 | 1.427 | 1.424 | 1.421 | 1.506 | 1.425 | 1.384 | Over-range | 59.98 | 1121 | 1176 | 1497 | 3794 | - - - | - - - | - - - | - - - | 1121 | 1176 | 1497 | 3794 | 775 | 655 | 60 | 1490 | - - - | - - - | - - - | - - - | 775 | 655 | 60 | 1490 | 1373 | 1355 | 1527 | 4256 | # # # | # # # | # # # | # # # | 0.817 | 0.868 | 0.98 | 0.891 | # # # | # # # | # # # | - - - | 0.815 | 0.866 | 0.982 | 0.891 | - - - | 0.393 | 1.54 | 1.43 | 1.35 | 1.39 | 1.36 | 1.37 | 10.65 | 10.54 | 18.57 | 0 | - - - | - - - | - - - | - - - | 1373 | 1355 | 1527 | 4256 | Over-range | 792 | 672 | 300 | 1928 | 163 | 150 | 283 | 1215 | 1133 | 1181 | 1515 | 3829 | 1133 | 1181 | 1515 | 3829 | - - - | - - - | - - - | - - -
5/2/2026 | 8:45:00 PM | 284.1 | 281.43 | 279.65 | 491.37 | 484.18 | 488.34 | 4.781 | 4.8716 | 5.4393 | 2.7469 | 1.427 | 1.425 | 1.423 | 1.508 | 1.428 | 1.371 | Over-range | 59.98 | 1104 | 1195 | 1494 | 3793 | - - - | - - - | - - - | - - - | 1104 | 1195 | 1494 | 3793 | 773 | 652 | 28 | 1453 | - - - | - - - | - - - | - - - | 773 | 652 | 28 | 1453 | 1358 | 1370 | 1521 | 4249 | # # # | # # # | # # # | # # # | 0.813 | 0.872 | 0.982 | 0.893 | # # # | # # # | # # # | - - - | 0.819 | 0.877 | 1 | 0.902 | - - - | 0.383 | 1.58 | 1.46 | 1.35 | 1.41 | 1.38 | 1.4 | 10.65 | 10.39 | 18.6 | 0 | - - - | - - - | - - - | - - - | 1358 | 1370 | 1521 | 4249 | Over-range | 790 | 669 | 284 | 1913 | 161 | 149 | 281 | 1244 | 1106 | 1193 | 1496 | 3795 | 1106 | 1193 | 1496 | 3795 | - - - | - - - | - - - | - - -
5/2/2026 | 9:00:00 PM | 284.27 | 281.66 | 279.86 | 491.76 | 484.54 | 488.66 | 5.2164 | 5.7164 | 5.689 | 2.7445 | 1.427 | 1.425 | 1.422 | 1.515 | 1.453 | 1.308 | Over-range | 59.98 | 1175 | 1462 | 1563 | 4200 | - - - | - - - | - - - | - - - | 1175 | 1462 | 1563 | 4200 | 888 | 653 | -86 | 1455 | - - - | - - - | - - - | - - - | 888 | 653 | -86 | 1455 | 1482 | 1608 | 1592 | 4683 | # # # | # # # | # # # | # # # | 0.792 | 0.909 | 0.982 | 0.897 | # # # | # # # | # # # | - - - | 0.798 | 0.913 | 0.998 | 0.905 | - - - | 0.346 | 1.53 | 1.47 | 1.34 | 1.39 | 1.37 | 1.38 | 9.78 | 9.19 | 18.11 | 0 | - - - | - - - | - - - | - - - | 1482 | 1608 | 1592 | 4683 | Over-range | 904 | 670 | 300 | 2072 | 169 | 150 | 285 | 1473 | 1175 | 1461 | 1565 | 4201 | 1175 | 1461 | 1565 | 4201 | - - - | - - - | - - - | - - -
5/2/2026 | 9:15:00 PM | 284.48 | 281.94 | 280.16 | 492.17 | 485.08 | 489.07 | 5.1633 | 5.6139 | 5.659 | 2.7464 | 1.427 | 1.425 | 1.422 | 1.515 | 1.453 | 1.315 | Over-range | 59.99 | 1166 | 1428 | 1557 | 4150 | - - - | - - - | - - - | - - - | 1166 | 1428 | 1557 | 4150 | 876 | 655 | -68 | 1462 | - - - | - - - | - - - | - - - | 876 | 655 | -68 | 1462 | 1468 | 1580 | 1585 | 4633 | # # # | # # # | # # # | # # # | 0.794 | 0.904 | 0.982 | 0.896 | # # # | # # # | # # # | - - - | 0.799 | 0.908 | 0.999 | 0.904 | - - - | 0.352 | 1.58 | 1.45 | 1.36 | 1.41 | 1.38 | 1.4 | 9.97 | 9.42 | 18.19 | 0 | - - - | - - - | - - - | - - - | 1468 | 1580 | 1585 | 4633 | Over-range | 892 | 673 | 298 | 2058 | 166 | 153 | 286 | 1447 | 1167 | 1426 | 1559 | 4152 | 1167 | 1426 | 1559 | 4152 | - - - | - - - | - - - | - - -
5/2/2026 | 9:30:00 PM | 284.68 | 282.09 | 280.3 | 492.42 | 485.41 | 489.33 | 4.4441 | 4.2394 | 5.2919 | 2.7619 | 1.427 | 1.425 | 1.422 | 1.498 | 1.458 | 1.42 | Over-range | 59.99 | 1050 | 977 | 1450 | 3477 | - - - | - - - | - - - | - - - | 1050 | 977 | 1450 | 3477 | 685 | 663 | 129 | 1478 | - - - | - - - | - - - | - - - | 685 | 663 | 129 | 1478 | 1264 | 1192 | 1483 | 3939 | # # # | # # # | # # # | # # # | 0.831 | 0.82 | 0.978 | 0.883 | # # # | # # # | # # # | - - - | 0.837 | 0.826 | 0.995 | 0.893 | - - - | 0.425 | 1.58 | 1.45 | 1.4 | 1.42 | 1.4 | 1.42 | 11.75 | 11.93 | 18.84 | 0 | - - - | - - - | - - - | - - - | 1264 | 1192 | 1483 | 3939 | Over-range | 704 | 678 | 311 | 1851 | 160 | 143 | 279 | 1113 | 1050 | 979 | 1447 | 3477 | 1050 | 979 | 1447 | 3477 | - - - | - - - | - - - | - - -
5/2/2026 | 9:45:00 PM | 285.25 | 282.71 | 280.82 | 493.57 | 486.31 | 490.25 | 4.7308 | 4.7696 | 5.431 | 2.7571 | 1.427 | 1.425 | 1.422 | 1.507 | 1.422 | 1.382 | Over-range | 59.99 | 1097 | 1159 | 1497 | 3753 | - - - | - - - | - - - | - - - | 1097 | 1159 | 1497 | 3753 | 768 | 670 | 55 | 1492 | - - - | - - - | - - - | - - - | 768 | 670 | 55 | 1492 | 1349 | 1347 | 1525 | 4221 | # # # | # # # | # # # | # # # | 0.813 | 0.86 | 0.981 | 0.889 | # # # | # # # | # # # | - - - | 0.819 | 0.866 | 0.999 | 0.898 | - - - | 0.398 | 1.59 | 1.46 | 1.4 | 1.42 | 1.4 | 1.42 | 11.07 | 10.87 | 18.86 | 0 | - - - | - - - | - - - | - - - | 1349 | 1347 | 1525 | 4221 | Over-range | 785 | 686 | 292 | 1933 | 166 | 147 | 286 | 1228 | 1096 | 1161 | 1495 | 3753 | 1096 | 1161 | 1495 | 3753 | - - - | - - - | - - - | - - -
5/2/2026 | 10:00:00 PM | 285.33 | 282.86 | 281.06 | 493.67 | 486.71 | 490.56 | 4.7253 | 4.7553 | 5.4333 | 2.7601 | 1.427 | 1.425 | 1.422 | 1.505 | 1.421 | 1.383 | Over-range | 60 | 1096 | 1155 | 1499 | 3750 | - - - | - - - | - - - | - - - | 1096 | 1155 | 1499 | 3750 | 767 | 672 | 58 | 1497 | - - - | - - - | - - - | - - - | 767 | 672 | 58 | 1497 | 1348 | 1345 | 1527 | 4220 | # # # | # # # | # # # | # # # | 0.813 | 0.859 | 0.982 | 0.889 | # # # | # # # | # # # | - - - | 0.819 | 0.865 | 0.999 | 0.898 | - - - | 0.399 | 1.61 | 1.46 | 1.39 | 1.43 | 1.41 | 1.43 | 11.05 | 10.95 | 18.85 | 0 | - - - | - - - | - - - | - - - | 1348 | 1345 | 1527 | 4220 | Over-range | 785 | 688 | 293 | 1935 | 167 | 148 | 286 | 1226 | 1095 | 1156 | 1499 | 3751 | 1095 | 1156 | 1499 | 3751 | - - - | - - - | - - - | - - -
5/2/2026 | 10:15:00 PM | 285.55 | 283.11 | 281.32 | 494.03 | 487.23 | 490.94 | 5.2022 | 5.6718 | 5.6924 | 2.7591 | 1.428 | 1.425 | 1.422 | 1.512 | 1.446 | 1.316 | Over-range | 59.98 | 1172 | 1446 | 1572 | 4190 | - - - | - - - | - - - | - - - | 1172 | 1446 | 1572 | 4190 | 895 | 674 | -65 | 1504 | - - - | - - - | - - - | - - - | 895 | 674 | -65 | 1504 | 1485 | 1604 | 1601 | 4690 | # # # | # # # | # # # | # # # | 0.789 | 0.902 | 0.982 | 0.893 | # # # | # # # | # # # | - - - | 0.794 | 0.906 | 0.999 | 0.902 | - - - | 0.359 | 1.61 | 1.46 | 1.42 | 1.44 | 1.42 | 1.45 | 10.04 | 9.69 | 18.49 | 0 | - - - | - - - | - - - | - - - | 1485 | 1604 | 1601 | 4690 | Over-range | 912 | 692 | 303 | 2106 | 173 | 156 | 293 | 1473 | 1171 | 1447 | 1573 | 4191 | 1171 | 1447 | 1573 | 4191 | - - - | - - - | - - - | - - -
5/2/2026 | 10:30:00 PM | 285.34 | 282.85 | 281.13 | 493.65 | 486.79 | 490.62 | 5.0989 | 5.4763 | 5.6278 | 2.7534 | 1.427 | 1.425 | 1.423 | 1.509 | 1.434 | 1.33 | Over-range | 59.98 | 1155 | 1384 | 1554 | 4094 | - - - | - - - | - - - | - - - | 1155 | 1384 | 1554 | 4094 | 866 | 671 | -40 | 1496 | - - - | - - - | - - - | - - - | 866 | 671 | -40 | 1496 | 1454 | 1546 | 1582 | 4582 | # # # | # # # | # # # | # # # | 0.795 | 0.895 | 0.983 | 0.893 | # # # | # # # | # # # | - - - | 0.8 | 0.899 | 0.999 | 0.902 | - - - | 0.366 | 1.6 | 1.49 | 1.42 | 1.43 | 1.42 | 1.45 | 10.26 | 9.77 | 18.42 | 0 | - - - | - - - | - - - | - - - | 1454 | 1546 | 1582 | 4582 | Over-range | 883 | 688 | 295 | 2058 | 169 | 151 | 289 | 1412 | 1155 | 1386 | 1553 | 4094 | 1155 | 1386 | 1553 | 4094 | - - - | - - - | - - - | - - -
5/2/2026 | 10:45:00 PM | 285.67 | 283.22 | 281.39 | 494.28 | 487.34 | 491.08 | 4.6635 | 4.6793 | 5.4136 | 2.7617 | 1.428 | 1.426 | 1.422 | 1.502 | 1.464 | 1.397 | Over-range | 60 | 1083 | 1102 | 1489 | 3673 | - - - | - - - | - - - | - - - | 1083 | 1102 | 1489 | 3673 | 749 | 678 | 87 | 1513 | - - - | - - - | - - - | - - - | 749 | 678 | 87 | 1513 | 1328 | 1310 | 1522 | 4160 | # # # | # # # | # # # | # # # | 0.816 | 0.841 | 0.978 | 0.883 | # # # | # # # | # # # | - - - | 0.822 | 0.848 | 0.995 | 0.893 | - - - | 0.412 | 1.65 | 1.51 | 1.43 | 1.46 | 1.45 | 1.48 | 11.48 | 11.7 | 18.98 | 0 | - - - | - - - | - - - | - - - | 1328 | 1310 | 1522 | 4160 | Over-range | 767 | 695 | 317 | 1950 | 165 | 151 | 287 | 1223 | 1083 | 1104 | 1486 | 3674 | 1083 | 1104 | 1486 | 3674 | - - - | - - - | - - - | - - -
5/2/2026 | 11:00:00 PM | 286.05 | 283.69 | 281.85 | 494.97 | 488.24 | 491.78 | 4.7377 | 4.6042 | 5.4312 | 2.7679 | 1.427 | 1.425 | 1.422 | 1.501 | 1.431 | 1.409 | Over-range | 59.99 | 1105 | 1098 | 1495 | 3698 | - - - | - - - | - - - | - - - | 1105 | 1098 | 1495 | 3698 | 761 | 685 | 117 | 1562 | - - - | - - - | - - - | - - - | 761 | 685 | 117 | 1562 | 1352 | 1304 | 1530 | 4187 | # # # | # # # | # # # | # # # | 0.817 | 0.842 | 0.977 | 0.883 | # # # | # # # | # # # | - - - | 0.815 | 0.842 | 0.984 | 0.885 | - - - | 0.423 | 1.65 | 1.49 | 1.43 | 1.46 | 1.43 | 1.47 | 11.27 | 11.73 | 19.28 | 0 | - - - | - - - | - - - | - - - | 1352 | 1304 | 1530 | 4187 | Over-range | 779 | 702 | 325 | 1963 | 168 | 153 | 294 | 1181 | 1117 | 1115 | 1516 | 3748 | 1117 | 1115 | 1516 | 3748 | - - - | - - - | - - - | - - -
5/2/2026 | 11:15:00 PM | 286.02 | 283.52 | 281.76 | 494.84 | 487.9 | 491.73 | 4.6583 | 4.6315 | 5.4081 | 2.7595 | 1.427 | 1.425 | 1.421 | 1.504 | 1.425 | 1.397 | Over-range | 59.98 | 1084 | 1111 | 1493 | 3688 | - - - | - - - | - - - | - - - | 1084 | 1111 | 1493 | 3688 | 755 | 683 | 87 | 1526 | - - - | - - - | - - - | - - - | 755 | 683 | 87 | 1526 | 1332 | 1313 | 1524 | 4169 | # # # | # # # | # # # | # # # | 0.814 | 0.846 | 0.98 | 0.885 | # # # | # # # | # # # | - - - | 0.821 | 0.852 | 0.998 | 0.895 | - - - | 0.414 | 1.64 | 1.49 | 1.43 | 1.45 | 1.43 | 1.47 | 11.4 | 11.52 | 19.22 | 0 | - - - | - - - | - - - | - - - | 1332 | 1313 | 1524 | 4169 | Over-range | 774 | 700 | 304 | 1943 | 169 | 153 | 291 | 1204 | 1084 | 1111 | 1494 | 3689 | 1084 | 1111 | 1494 | 3689 | - - - | - - - | - - - | - - -
5/2/2026 | 11:30:00 PM | 286.34 | 283.82 | 282.08 | 495.37 | 488.47 | 492.27 | 4.8137 | 4.9185 | 5.4865 | 2.7619 | 1.427 | 1.425 | 1.422 | 1.508 | 1.418 | 1.377 | Over-range | 59.99 | 1110 | 1203 | 1518 | 3831 | - - - | - - - | - - - | - - - | 1110 | 1203 | 1518 | 3831 | 799 | 686 | 50 | 1535 | - - - | - - - | - - - | - - - | 799 | 686 | 50 | 1535 | 1378 | 1394 | 1548 | 4320 | # # # | # # # | # # # | # # # | 0.806 | 0.863 | 0.981 | 0.887 | # # # | # # # | # # # | - - - | 0.812 | 0.869 | 0.999 | 0.897 | - - - | 0.401 | 1.63 | 1.51 | 1.45 | 1.47 | 1.46 | 1.49 | 11.06 | 11.14 | 19.23 | 0 | - - - | - - - | - - - | - - - | 1378 | 1394 | 1548 | 4320 | Over-range | 816 | 704 | 300 | 1995 | 165 | 157 | 295 | 1274 | 1111 | 1205 | 1515 | 3832 | 1111 | 1205 | 1515 | 3832 | - - - | - - - | - - - | - - -
5/2/2026 | 11:45:00 PM | 286.83 | 284.34 | 282.64 | 496.21 | 489.47 | 493.18 | 5.2536 | 5.7568 | 5.7248 | 2.7629 | 1.428 | 1.426 | 1.422 | 1.513 | 1.443 | 1.314 | Over-range | 59.98 | 1180 | 1472 | 1588 | 4241 | - - - | - - - | - - - | - - - | 1180 | 1472 | 1588 | 4241 | 920 | 692 | -62 | 1548 | - - - | - - - | - - - | - - - | 920 | 692 | -62 | 1548 | 1506 | 1635 | 1618 | 4760 | # # # | # # # | # # # | # # # | 0.784 | 0.9 | 0.982 | 0.891 | # # # | # # # | # # # | - - - | 0.788 | 0.905 | 0.999 | 0.9 | - - - | 0.365 | 1.67 | 1.52 | 1.46 | 1.49 | 1.47 | 1.51 | 10.22 | 9.92 | 18.77 | 0 | - - - | - - - | - - - | - - - | 1506 | 1635 | 1618 | 4760 | Over-range | 936 | 711 | 308 | 2161 | 173 | 163 | 300 | 1506 | 1180 | 1474 | 1587 | 4241 | 1180 | 1474 | 1587 | 4241 | - - - | - - - | - - - | - - -
5/3/2026 | 12:00:00 AM | 287.06 | 284.68 | 282.85 | 496.75 | 489.91 | 493.53 | 5.0212 | 5.3087 | 5.5995 | 2.7646 | 1.428 | 1.426 | 1.422 | 1.511 | 1.425 | 1.349 | Over-range | 59.99 | 1143 | 1331 | 1555 | 4029 | - - - | - - - | - - - | - - - | 1143 | 1331 | 1555 | 4029 | 861 | 697 | 2 | 1560 | - - - | - - - | - - - | - - - | 861 | 697 | 2 | 1560 | 1441 | 1511 | 1584 | 4536 | # # # | # # # | # # # | # # # | 0.793 | 0.881 | 0.982 | 0.888 | # # # | # # # | # # # | - - - | 0.799 | 0.885 | 1 | 0.898 | - - - | 0.387 | 1.66 | 1.54 | 1.47 | 1.49 | 1.47 | 1.51 | 10.78 | 10.58 | 19.07 | 0 | - - - | - - - | - - - | - - - | 1441 | 1511 | 1584 | 4536 | Over-range | 878 | 716 | 299 | 2085 | 175 | 161 | 299 | 1383 | 1143 | 1330 | 1557 | 4029 | 1143 | 1330 | 1557 | 4029 | - - - | - - - | - - - | - - -
5/3/2026 | 12:15:00 AM | 287.33 | 284.88 | 283.17 | 497.13 | 490.36 | 494.05 | 4.6164 | 4.5874 | 5.4096 | 2.7712 | 1.428 | 1.426 | 1.422 | 1.501 | 1.469 | 1.41 | Over-range | 59.98 | 1074 | 1065 | 1494 | 3632 | - - - | - - - | - - - | - - - | 1074 | 1065 | 1494 | 3632 | 751 | 706 | 122 | 1579 | - - - | - - - | - - - | - - - | 751 | 706 | 122 | 1579 | 1322 | 1294 | 1531 | 4147 | # # # | # # # | # # # | # # # | 0.812 | 0.823 | 0.976 | 0.876 | # # # | # # # | # # # | - - - | 0.819 | 0.83 | 0.994 | 0.886 | - - - | 0.435 | 1.65 | 1.55 | 1.48 | 1.5 | 1.48 | 1.51 | 12.04 | 12.46 | 19.54 | 0 | - - - | - - - | - - - | - - - | 1322 | 1294 | 1531 | 4147 | Over-range | 770 | 724 | 334 | 1999 | 172 | 158 | 297 | 1221 | 1074 | 1067 | 1491 | 3632 | 1074 | 1067 | 1491 | 3632 | - - - | - - - | - - - | - - -
5/3/2026 | 12:30:00 AM | 286.65 | 284.26 | 282.46 | 495.99 | 489.26 | 492.82 | 4.6712 | 4.6613 | 5.4247 | 2.7645 | 1.427 | 1.424 | 1.421 | 1.502 | 1.432 | 1.4 | Over-range | 59.98 | 1085 | 1114 | 1500 | 3699 | - - - | - - - | - - - | - - - | 1085 | 1114 | 1500 | 3699 | 765 | 695 | 95 | 1555 | - - - | - - - | - - - | - - - | 765 | 695 | 95 | 1555 | 1338 | 1323 | 1532 | 4193 | # # # | # # # | # # # | # # # | 0.811 | 0.842 | 0.979 | 0.882 | # # # | # # # | # # # | - - - | 0.818 | 0.848 | 0.997 | 0.892 | - - - | 0.42 | 1.68 | 1.52 | 1.45 | 1.48 | 1.47 | 1.5 | 11.52 | 11.79 | 19.45 | 0 | - - - | - - - | - - - | - - - | 1338 | 1323 | 1532 | 4193 | Over-range | 783 | 712 | 313 | 1976 | 167 | 158 | 295 | 1218 | 1087 | 1114 | 1498 | 3699 | 1087 | 1114 | 1498 | 3699 | - - - | - - - | - - - | - - -
5/3/2026 | 12:45:00 AM | 285.43 | 283.14 | 281.46 | 493.9 | 487.47 | 490.9 | 4.6621 | 4.6464 | 5.4092 | 2.7497 | 1.426 | 1.424 | 1.421 | 1.501 | 1.422 | 1.397 | Over-range | 59.99 | 1084 | 1118 | 1492 | 3695 | - - - | - - - | - - - | - - - | 1084 | 1118 | 1492 | 3695 | 754 | 675 | 83 | 1512 | - - - | - - - | - - - | - - - | 754 | 675 | 83 | 1512 | 1331 | 1316 | 1522 | 4169 | # # # | # # # | # # # | # # # | 0.815 | 0.85 | 0.98 | 0.886 | # # # | # # # | # # # | - - - | 0.821 | 0.855 | 0.998 | 0.896 | - - - | 0.409 | 1.67 | 1.52 | 1.48 | 1.48 | 1.48 | 1.52 | 11.21 | 11.37 | 19.09 | 0 | - - - | - - - | - - - | - - - | 1331 | 1316 | 1522 | 4169 | Over-range | 771 | 693 | 301 | 1930 | 165 | 155 | 289 | 1199 | 1086 | 1116 | 1494 | 3697 | 1086 | 1116 | 1494 | 3697 | - - - | - - - | - - - | - - -
5/3/2026 | 1:00:00 AM | 285.88 | 283.61 | 281.91 | 494.69 | 488.3 | 491.67 | 4.8281 | 4.966 | 5.4983 | 2.7521 | 1.428 | 1.425 | 1.422 | 1.505 | 1.422 | 1.373 | Over-range | 59.99 | 1111 | 1218 | 1520 | 3850 | - - - | - - - | - - - | - - - | 1111 | 1218 | 1520 | 3850 | 799 | 682 | 42 | 1524 | - - - | - - - | - - - | - - - | 799 | 682 | 42 | 1524 | 1379 | 1406 | 1550 | 4335 | # # # | # # # | # # # | # # # | 0.806 | 0.867 | 0.981 | 0.888 | # # # | # # # | # # # | - - - | 0.812 | 0.872 | 0.999 | 0.898 | - - - | 0.396 | 1.66 | 1.5 | 1.48 | 1.48 | 1.46 | 1.51 | 10.92 | 11.01 | 19.16 | 0 | - - - | - - - | - - - | - - - | 1379 | 1406 | 1550 | 4335 | Over-range | 817 | 700 | 300 | 1993 | 170 | 157 | 294 | 1283 | 1111 | 1217 | 1522 | 3850 | 1111 | 1217 | 1522 | 3850 | - - - | - - - | - - - | - - -
5/3/2026 | 1:15:00 AM | 285.79 | 283.46 | 281.77 | 494.49 | 488.05 | 491.47 | 5.1596 | 5.4106 | 5.6386 | 2.7518 | 1.428 | 1.426 | 1.422 | 1.505 | 1.437 | 1.348 | Over-range | 59.97 | 1173 | 1365 | 1558 | 4096 | - - - | - - - | - - - | - - - | 1173 | 1365 | 1558 | 4096 | 872 | 679 | 2 | 1553 | - - - | - - - | - - - | - - - | 872 | 679 | 2 | 1553 | 1472 | 1533 | 1589 | 4593 | # # # | # # # | # # # | # # # | 0.797 | 0.89 | 0.981 | 0.892 | # # # | # # # | # # # | - - - | 0.794 | 0.888 | 0.987 | 0.892 | - - - | 0.379 | 1.7 | 1.54 | 1.53 | 1.51 | 1.5 | 1.55 | 10.25 | 10.15 | 18.69 | 0 | - - - | - - - | - - - | - - - | 1472 | 1533 | 1589 | 4593 | Over-range | 889 | 697 | 307 | 2079 | 172 | 155 | 295 | 1374 | 1182 | 1375 | 1571 | 4128 | 1182 | 1375 | 1571 | 4128 | - - - | - - - | - - - | - - -
5/3/2026 | 1:30:00 AM | 285.82 | 283.35 | 281.67 | 494.5 | 487.73 | 491.47 | 4.5868 | 4.5365 | 5.379 | 2.7538 | 1.428 | 1.425 | 1.423 | 1.498 | 1.46 | 1.408 | Over-range | 59.99 | 1071 | 1060 | 1480 | 3610 | - - - | - - - | - - - | - - - | 1071 | 1060 | 1480 | 3610 | 731 | 681 | 109 | 1521 | - - - | - - - | - - - | - - - | 731 | 681 | 109 | 1521 | 1308 | 1274 | 1514 | 4096 | # # # | # # # | # # # | # # # | 0.819 | 0.832 | 0.977 | 0.881 | # # # | # # # | # # # | - - - | 0.826 | 0.838 | 0.995 | 0.892 | - - - | 0.421 | 1.71 | 1.55 | 1.52 | 1.52 | 1.52 | 1.55 | 11.69 | 12.02 | 19.06 | 0 | - - - | - - - | - - - | - - - | 1308 | 1274 | 1514 | 4096 | Over-range | 750 | 697 | 319 | 1933 | 166 | 151 | 287 | 1189 | 1071 | 1061 | 1479 | 3610 | 1071 | 1061 | 1479 | 3610 | - - - | - - - | - - - | - - -
5/3/2026 | 1:45:00 AM | 286.19 | 283.67 | 281.95 | 495.13 | 488.2 | 492.05 | 4.6283 | 4.6156 | 5.4218 | 2.7526 | 1.427 | 1.425 | 1.421 | 1.503 | 1.433 | 1.403 | Over-range | 59.99 | 1079 | 1099 | 1497 | 3675 | - - - | - - - | - - - | - - - | 1079 | 1099 | 1497 | 3675 | 749 | 687 | 95 | 1532 | - - - | - - - | - - - | - - - | 749 | 687 | 95 | 1532 | 1324 | 1307 | 1529 | 4160 | # # # | # # # | # # # | # # # | 0.815 | 0.841 | 0.979 | 0.883 | # # # | # # # | # # # | - - - | 0.822 | 0.847 | 0.998 | 0.894 | - - - | 0.417 | 1.68 | 1.54 | 1.5 | 1.5 | 1.5 | 1.53 | 11.51 | 11.69 | 19.31 | 0 | - - - | - - - | - - - | - - - | 1324 | 1307 | 1529 | 4160 | Over-range | 767 | 706 | 311 | 1949 | 164 | 162 | 294 | 1204 | 1082 | 1098 | 1497 | 3676 | 1082 | 1098 | 1497 | 3676 | - - - | - - - | - - - | - - -
5/3/2026 | 2:00:00 AM | 286.26 | 283.79 | 282.1 | 495.22 | 488.52 | 492.23 | 4.6393 | 4.5987 | 5.4029 | 2.7565 | 1.428 | 1.425 | 1.422 | 1.502 | 1.43 | 1.401 | Over-range | 60 | 1081 | 1100 | 1493 | 3674 | - - - | - - - | - - - | - - - | 1081 | 1100 | 1493 | 3674 | 753 | 685 | 97 | 1535 | - - - | - - - | - - - | - - - | 753 | 685 | 97 | 1535 | 1328 | 1305 | 1524 | 4157 | # # # | # # # | # # # | # # # | 0.814 | 0.843 | 0.98 | 0.884 | # # # | # # # | # # # | - - - | 0.821 | 0.849 | 0.997 | 0.894 | - - - | 0.418 | 1.68 | 1.52 | 1.5 | 1.5 | 1.49 | 1.53 | 11.49 | 11.7 | 19.25 | 0 | - - - | - - - | - - - | - - - | 1328 | 1305 | 1524 | 4157 | Over-range | 771 | 703 | 307 | 1946 | 165 | 158 | 292 | 1196 | 1084 | 1098 | 1493 | 3675 | 1084 | 1098 | 1493 | 3675 | - - - | - - - | - - - | - - -
5/3/2026 | 2:15:00 AM | 286.44 | 284 | 282.28 | 495.61 | 488.82 | 492.51 | 4.6669 | 4.6508 | 5.4152 | 2.7566 | 1.428 | 1.425 | 1.422 | 1.502 | 1.427 | 1.399 | Over-range | 59.99 | 1085 | 1116 | 1497 | 3698 | - - - | - - - | - - - | - - - | 1085 | 1116 | 1497 | 3698 | 763 | 688 | 91 | 1542 | - - - | - - - | - - - | - - - | 763 | 688 | 91 | 1542 | 1337 | 1320 | 1529 | 4186 | # # # | # # # | # # # | # # # | 0.812 | 0.845 | 0.98 | 0.884 | # # # | # # # | # # # | - - - | 0.819 | 0.851 | 0.998 | 0.894 | - - - | 0.417 | 1.69 | 1.54 | 1.5 | 1.5 | 1.5 | 1.53 | 11.46 | 11.65 | 19.3 | 0 | - - - | - - - | - - - | - - - | 1337 | 1320 | 1529 | 4186 | Over-range | 780 | 706 | 307 | 1960 | 164 | 156 | 293 | 1209 | 1088 | 1117 | 1494 | 3699 | 1088 | 1117 | 1494 | 3699 | - - - | - - - | - - - | - - -
5/3/2026 | 2:30:00 AM | 286.73 | 284.26 | 282.61 | 496.06 | 489.35 | 493.08 | 5.2116 | 5.6917 | 5.7013 | 2.7502 | 1.428 | 1.425 | 1.422 | 1.51 | 1.438 | 1.324 | Over-range | 59.98 | 1173 | 1448 | 1581 | 4201 | - - - | - - - | - - - | - - - | 1173 | 1448 | 1581 | 4201 | 908 | 690 | -49 | 1547 | - - - | - - - | - - - | - - - | 908 | 690 | -49 | 1547 | 1493 | 1613 | 1611 | 4717 | # # # | # # # | # # # | # # # | 0.786 | 0.898 | 0.981 | 0.891 | # # # | # # # | # # # | - - - | 0.79 | 0.902 | 0.999 | 0.899 | - - - | 0.368 | 1.71 | 1.56 | 1.51 | 1.52 | 1.52 | 1.55 | 10.25 | 10.08 | 18.88 | 0 | - - - | - - - | - - - | - - - | 1493 | 1613 | 1611 | 4717 | Over-range | 924 | 709 | 310 | 2145 | 171 | 164 | 300 | 1483 | 1173 | 1450 | 1578 | 4201 | 1173 | 1450 | 1578 | 4201 | - - - | - - - | - - - | - - -
5/3/2026 | 2:45:00 AM | 286.97 | 284.57 | 282.86 | 496.52 | 489.89 | 493.45 | 5.1963 | 5.6525 | 5.6936 | 2.7524 | 1.427 | 1.424 | 1.421 | 1.509 | 1.432 | 1.324 | Over-range | 59.99 | 1171 | 1441 | 1581 | 4193 | - - - | - - - | - - - | - - - | 1171 | 1441 | 1581 | 4193 | 907 | 694 | -44 | 1556 | - - - | - - - | - - - | - - - | 907 | 694 | -44 | 1556 | 1491 | 1608 | 1610 | 4709 | # # # | # # # | # # # | # # # | 0.785 | 0.896 | 0.982 | 0.89 | # # # | # # # | # # # | - - - | 0.791 | 0.901 | 1 | 0.899 | - - - | 0.371 | 1.67 | 1.54 | 1.49 | 1.49 | 1.49 | 1.52 | 10.35 | 10 | 18.85 | 0 | - - - | - - - | - - - | - - - | 1491 | 1608 | 1610 | 4709 | Over-range | 923 | 712 | 304 | 2143 | 173 | 161 | 300 | 1473 | 1171 | 1443 | 1580 | 4193 | 1171 | 1443 | 1580 | 4193 | - - - | - - - | - - - | - - -
5/3/2026 | 3:00:00 AM | 287 | 284.55 | 282.93 | 496.51 | 489.91 | 493.58 | 4.5755 | 4.5208 | 5.3881 | 2.755 | 1.427 | 1.424 | 1.422 | 1.496 | 1.467 | 1.414 | Over-range | 59.98 | 1067 | 1047 | 1486 | 3601 | - - - | - - - | - - - | - - - | 1067 | 1047 | 1486 | 3601 | 738 | 700 | 129 | 1567 | - - - | - - - | - - - | - - - | 738 | 700 | 129 | 1567 | 1310 | 1275 | 1524 | 4108 | # # # | # # # | # # # | # # # | 0.815 | 0.822 | 0.976 | 0.876 | # # # | # # # | # # # | - - - | 0.822 | 0.828 | 0.995 | 0.887 | - - - | 0.435 | 1.67 | 1.53 | 1.49 | 1.48 | 1.48 | 1.52 | 12.04 | 12.4 | 19.41 | 0 | - - - | - - - | - - - | - - - | 1310 | 1275 | 1524 | 4108 | Over-range | 758 | 717 | 333 | 1975 | 172 | 155 | 294 | 1198 | 1067 | 1049 | 1486 | 3601 | 1067 | 1049 | 1486 | 3601 | - - - | - - - | - - - | - - -
5/3/2026 | 3:15:00 AM | 286.96 | 284.61 | 282.93 | 496.54 | 489.97 | 493.51 | 4.7136 | 4.7328 | 5.4466 | 2.7525 | 1.427 | 1.424 | 1.421 | 1.502 | 1.432 | 1.397 | Over-range | 59.97 | 1092 | 1137 | 1508 | 3737 | - - - | - - - | - - - | - - - | 1092 | 1137 | 1508 | 3737 | 777 | 699 | 93 | 1569 | - - - | - - - | - - - | - - - | 777 | 699 | 93 | 1569 | 1352 | 1345 | 1541 | 4237 | # # # | # # # | # # # | # # # | 0.808 | 0.845 | 0.979 | 0.882 | # # # | # # # | # # # | - - - | 0.806 | 0.845 | 0.983 | 0.882 | - - - | 0.42 | 1.67 | 1.54 | 1.49 | 1.5 | 1.49 | 1.53 | 11.52 | 11.75 | 19.47 | 0 | - - - | - - - | - - - | - - - | 1352 | 1345 | 1541 | 4237 | Over-range | 796 | 717 | 315 | 1997 | 170 | 157 | 298 | 1233 | 1102 | 1147 | 1521 | 3770 | 1102 | 1147 | 1521 | 3770 | - - - | - - - | - - - | - - -
5/3/2026 | 3:30:00 AM | 287.05 | 284.75 | 283.07 | 496.69 | 490.31 | 493.67 | 4.7795 | 4.7039 | 5.4623 | 2.7606 | 1.427 | 1.424 | 1.421 | 1.495 | 1.429 | 1.405 | Over-range | 59.98 | 1109 | 1130 | 1511 | 3750 | - - - | - - - | - - - | - - - | 1109 | 1130 | 1511 | 3750 | 785 | 701 | 117 | 1603 | - - - | - - - | - - - | - - - | 785 | 701 | 117 | 1603 | 1369 | 1339 | 1546 | 4255 | # # # | # # # | # # # | # # # | 0.81 | 0.844 | 0.977 | 0.881 | # # # | # # # | # # # | - - - | 0.816 | 0.85 | 0.995 | 0.892 | - - - | 0.427 | 1.69 | 1.52 | 1.5 | 1.5 | 1.49 | 1.53 | 11.44 | 11.67 | 19.38 | 0 | - - - | - - - | - - - | - - - | 1369 | 1339 | 1546 | 4255 | Over-range | 803 | 719 | 325 | 2010 | 169 | 159 | 297 | 1207 | 1111 | 1131 | 1509 | 3751 | 1111 | 1131 | 1509 | 3751 | - - - | - - - | - - - | - - -
5/3/2026 | 3:45:00 AM | 287.16 | 284.82 | 283.18 | 496.87 | 490.4 | 493.91 | 4.9834 | 5.2516 | 5.5867 | 2.7569 | 1.428 | 1.425 | 1.422 | 1.508 | 1.425 | 1.356 | Over-range | 59.97 | 1135 | 1306 | 1552 | 3992 | - - - | - - - | - - - | - - - | 1135 | 1306 | 1552 | 3992 | 853 | 701 | 19 | 1573 | - - - | - - - | - - - | - - - | 853 | 701 | 19 | 1573 | 1430 | 1492 | 1582 | 4504 | # # # | # # # | # # # | # # # | 0.794 | 0.875 | 0.981 | 0.886 | # # # | # # # | # # # | - - - | 0.799 | 0.88 | 0.999 | 0.896 | - - - | 0.394 | 1.72 | 1.55 | 1.51 | 1.52 | 1.51 | 1.55 | 10.9 | 10.89 | 19.25 | 0 | - - - | - - - | - - - | - - - | 1430 | 1492 | 1582 | 4504 | Over-range | 870 | 720 | 306 | 2085 | 173 | 165 | 301 | 1366 | 1136 | 1304 | 1553 | 3993 | 1136 | 1304 | 1553 | 3993 | - - - | - - - | - - - | - - -
5/3/2026 | 4:00:00 AM | 287.27 | 284.96 | 283.28 | 497.08 | 490.62 | 494.08 | 5.2131 | 5.688 | 5.7059 | 2.7502 | 1.426 | 1.423 | 1.421 | 1.507 | 1.427 | 1.323 | Over-range | 59.98 | 1172 | 1451 | 1587 | 4210 | - - - | - - - | - - - | - - - | 1172 | 1451 | 1587 | 4210 | 914 | 701 | -42 | 1572 | - - - | - - - | - - - | - - - | 914 | 701 | -42 | 1572 | 1497 | 1620 | 1616 | 4733 | # # # | # # # | # # # | # # # | 0.783 | 0.896 | 0.982 | 0.889 | # # # | # # # | # # # | - - - | 0.788 | 0.9 | 0.999 | 0.898 | - - - | 0.373 | 1.69 | 1.53 | 1.49 | 1.49 | 1.49 | 1.53 | 10.4 | 10.05 | 18.92 | 0 | - - - | - - - | - - - | - - - | 1497 | 1620 | 1616 | 4733 | Over-range | 932 | 720 | 307 | 2164 | 178 | 164 | 302 | 1486 | 1172 | 1450 | 1588 | 4210 | 1172 | 1450 | 1588 | 4210 | - - - | - - - | - - - | - - -
5/3/2026 | 4:15:00 AM | 287.2 | 284.95 | 283.31 | 496.97 | 490.72 | 494.02 | 4.8796 | 5.0978 | 5.5447 | 2.7578 | 1.427 | 1.423 | 1.421 | 1.501 | 1.456 | 1.373 | Over-range | 59.99 | 1115 | 1230 | 1535 | 3880 | - - - | - - - | - - - | - - - | 1115 | 1230 | 1535 | 3880 | 819 | 703 | 53 | 1575 | - - - | - - - | - - - | - - - | 819 | 703 | 53 | 1575 | 1396 | 1434 | 1570 | 4400 | # # # | # # # | # # # | # # # | 0.799 | 0.857 | 0.978 | 0.882 | # # # | # # # | # # # | - - - | 0.805 | 0.863 | 0.996 | 0.892 | - - - | 0.406 | 1.7 | 1.53 | 1.49 | 1.5 | 1.49 | 1.54 | 11.36 | 11.5 | 19.21 | 0 | - - - | - - - | - - - | - - - | 1396 | 1434 | 1570 | 4400 | Over-range | 838 | 721 | 326 | 2072 | 174 | 162 | 299 | 1339 | 1115 | 1230 | 1535 | 3880 | 1115 | 1230 | 1535 | 3880 | - - - | - - - | - - - | - - -
5/3/2026 | 4:30:00 AM | 287.13 | 284.82 | 283.11 | 496.87 | 490.33 | 493.8 | 4.6099 | 4.5576 | 5.4037 | 2.7565 | 1.427 | 1.423 | 1.422 | 1.5 | 1.441 | 1.412 | Over-range | 59.99 | 1074 | 1076 | 1495 | 3645 | - - - | - - - | - - - | - - - | 1074 | 1076 | 1495 | 3645 | 754 | 702 | 120 | 1575 | - - - | - - - | - - - | - - - | 754 | 702 | 120 | 1575 | 1323 | 1296 | 1530 | 4149 | # # # | # # # | # # # | # # # | 0.812 | 0.83 | 0.977 | 0.879 | # # # | # # # | # # # | - - - | 0.82 | 0.837 | 0.996 | 0.889 | - - - | 0.432 | 1.68 | 1.53 | 1.49 | 1.49 | 1.48 | 1.52 | 11.8 | 12.21 | 19.67 | 0 | - - - | - - - | - - - | - - - | 1323 | 1296 | 1530 | 4149 | Over-range | 772 | 720 | 324 | 1980 | 166 | 162 | 298 | 1198 | 1078 | 1075 | 1493 | 3647 | 1078 | 1075 | 1493 | 3647 | - - - | - - - | - - - | - - -
5/3/2026 | 4:45:00 AM | 287.3 | 284.92 | 283.21 | 497.15 | 490.44 | 494.05 | 4.6723 | 4.6638 | 5.4292 | 2.7565 | 1.427 | 1.424 | 1.422 | 1.5 | 1.435 | 1.402 | Over-range | 59.99 | 1085 | 1115 | 1505 | 3705 | - - - | - - - | - - - | - - - | 1085 | 1115 | 1505 | 3705 | 771 | 703 | 103 | 1578 | - - - | - - - | - - - | - - - | 771 | 703 | 103 | 1578 | 1342 | 1328 | 1538 | 4208 | # # # | # # # | # # # | # # # | 0.809 | 0.84 | 0.979 | 0.88 | # # # | # # # | # # # | - - - | 0.815 | 0.845 | 0.997 | 0.891 | - - - | 0.426 | 1.7 | 1.54 | 1.5 | 1.51 | 1.49 | 1.54 | 11.7 | 11.86 | 19.49 | 0 | - - - | - - - | - - - | - - - | 1342 | 1328 | 1538 | 4208 | Over-range | 790 | 721 | 315 | 1995 | 169 | 160 | 297 | 1220 | 1087 | 1115 | 1503 | 3706 | 1087 | 1115 | 1503 | 3706 | - - - | - - - | - - - | - - -
5/3/2026 | 5:00:00 AM | 287.15 | 284.85 | 283.07 | 496.93 | 490.37 | 493.72 | 4.6965 | 4.7095 | 5.4445 | 2.7593 | 1.427 | 1.424 | 1.422 | 1.502 | 1.429 | 1.399 | Over-range | 59.98 | 1089 | 1132 | 1509 | 3730 | - - - | - - - | - - - | - - - | 1089 | 1132 | 1509 | 3730 | 777 | 702 | 96 | 1575 | - - - | - - - | - - - | - - - | 777 | 702 | 96 | 1575 | 1349 | 1341 | 1541 | 4231 | # # # | # # # | # # # | # # # | 0.808 | 0.844 | 0.979 | 0.881 | # # # | # # # | # # # | - - - | 0.814 | 0.85 | 0.998 | 0.892 | - - - | 0.422 | 1.69 | 1.52 | 1.51 | 1.51 | 1.49 | 1.53 | 11.61 | 11.76 | 19.46 | 0 | - - - | - - - | - - - | - - - | 1349 | 1341 | 1541 | 4231 | Over-range | 796 | 720 | 313 | 1998 | 170 | 162 | 298 | 1230 | 1091 | 1130 | 1510 | 3731 | 1091 | 1130 | 1510 | 3731 | - - - | - - - | - - - | - - -
5/3/2026 | 5:15:00 AM | 287.09 | 284.75 | 283.07 | 496.76 | 490.22 | 493.74 | 5.1004 | 5.4863 | 5.6462 | 2.7454 | 1.426 | 1.423 | 1.421 | 1.508 | 1.43 | 1.342 | Over-range | 60 | 1154 | 1382 | 1568 | 4104 | - - - | - - - | - - - | - - - | 1154 | 1382 | 1568 | 4104 | 882 | 696 | -14 | 1562 | - - - | - - - | - - - | - - - | 882 | 696 | -14 | 1562 | 1463 | 1558 | 1598 | 4618 | # # # | # # # | # # # | # # # | 0.789 | 0.887 | 0.981 | 0.889 | # # # | # # # | # # # | - - - | 0.795 | 0.892 | 0.999 | 0.898 | - - - | 0.381 | 1.67 | 1.53 | 1.48 | 1.49 | 1.47 | 1.52 | 10.56 | 10.46 | 19.12 | 0 | - - - | - - - | - - - | - - - | 1463 | 1558 | 1598 | 4618 | Over-range | 899 | 715 | 308 | 2118 | 174 | 166 | 302 | 1428 | 1156 | 1380 | 1570 | 4105 | 1156 | 1380 | 1570 | 4105 | - - - | - - - | - - - | - - -
5/3/2026 | 5:30:00 AM | 287.04 | 284.79 | 283.04 | 496.78 | 490.28 | 493.62 | 5.1724 | 5.6176 | 5.682 | 2.7456 | 1.426 | 1.423 | 1.421 | 1.507 | 1.429 | 1.33 | Over-range | 60 | 1166 | 1428 | 1579 | 4173 | - - - | - - - | - - - | - - - | 1166 | 1428 | 1579 | 4173 | 902 | 695 | -34 | 1562 | - - - | - - - | - - - | - - - | 902 | 695 | -34 | 1562 | 1484 | 1597 | 1608 | 4690 | # # # | # # # | # # # | # # # | 0.786 | 0.894 | 0.982 | 0.89 | # # # | # # # | # # # | - - - | 0.791 | 0.899 | 0.999 | 0.899 | - - - | 0.374 | 1.68 | 1.51 | 1.48 | 1.49 | 1.47 | 1.52 | 10.4 | 10.1 | 18.9 | 0 | - - - | - - - | - - - | - - - | 1484 | 1597 | 1608 | 4690 | Over-range | 918 | 715 | 306 | 2140 | 168 | 167 | 301 | 1461 | 1169 | 1427 | 1577 | 4174 | 1169 | 1427 | 1577 | 4174 | - - - | - - - | - - - | - - -
5/3/2026 | 5:45:00 AM | 286.9 | 284.57 | 282.85 | 496.42 | 489.94 | 493.36 | 4.5311 | 4.2624 | 5.3582 | 2.7561 | 1.427 | 1.423 | 1.421 | 1.492 | 1.472 | 1.441 | Over-range | 60 | 1070 | 970 | 1470 | 3509 | - - - | - - - | - - - | - - - | 1070 | 970 | 1470 | 3509 | 714 | 697 | 187 | 1598 | - - - | - - - | - - - | - - - | 714 | 697 | 187 | 1598 | 1297 | 1208 | 1515 | 4020 | # # # | # # # | # # # | # # # | 0.825 | 0.803 | 0.97 | 0.873 | # # # | # # # | # # # | - - - | 0.825 | 0.804 | 0.976 | 0.875 | - - - | 0.456 | 1.66 | 1.53 | 1.46 | 1.48 | 1.46 | 1.5 | 12.09 | 12.89 | 19.49 | 0 | - - - | - - - | - - - | - - - | 1297 | 1208 | 1515 | 4020 | Over-range | 733 | 715 | 360 | 1960 | 166 | 158 | 295 | 1127 | 1082 | 975 | 1481 | 3538 | 1082 | 975 | 1481 | 3538 | - - - | - - - | - - - | - - -
5/3/2026 | 6:00:00 AM | 286.82 | 284.53 | 282.8 | 496.37 | 489.81 | 493.23 | 4.6808 | 4.6888 | 5.4295 | 2.7475 | 1.427 | 1.423 | 1.422 | 1.5 | 1.43 | 1.4 | Over-range | 60.01 | 1087 | 1126 | 1503 | 3716 | - - - | - - - | - - - | - - - | 1087 | 1126 | 1503 | 3716 | 770 | 694 | 95 | 1558 | - - - | - - - | - - - | - - - | 770 | 694 | 95 | 1558 | 1342 | 1333 | 1535 | 4210 | # # # | # # # | # # # | # # # | 0.81 | 0.845 | 0.979 | 0.883 | # # # | # # # | # # # | - - - | 0.816 | 0.85 | 0.997 | 0.893 | - - - | 0.419 | 1.69 | 1.55 | 1.49 | 1.5 | 1.48 | 1.53 | 11.49 | 11.7 | 19.39 | 0 | - - - | - - - | - - - | - - - | 1342 | 1333 | 1535 | 4210 | Over-range | 787 | 712 | 312 | 1979 | 165 | 160 | 296 | 1219 | 1090 | 1125 | 1501 | 3717 | 1090 | 1125 | 1501 | 3717 | - - - | - - - | - - - | - - -
5/3/2026 | 6:15:00 AM | 286.5 | 284.12 | 282.42 | 495.74 | 489.08 | 492.67 | 4.6971 | 4.718 | 5.4297 | 2.7402 | 1.426 | 1.423 | 1.421 | 1.502 | 1.424 | 1.397 | Over-range | 60 | 1090 | 1140 | 1503 | 3732 | - - - | - - - | - - - | - - - | 1090 | 1140 | 1503 | 3732 | 772 | 687 | 85 | 1544 | - - - | - - - | - - - | - - - | 772 | 687 | 85 | 1544 | 1346 | 1340 | 1533 | 4220 | # # # | # # # | # # # | # # # | 0.81 | 0.851 | 0.98 | 0.884 | # # # | # # # | # # # | - - - | 0.816 | 0.856 | 0.998 | 0.894 | - - - | 0.414 | 1.64 | 1.52 | 1.47 | 1.47 | 1.45 | 1.5 | 11.36 | 11.41 | 19.28 | 0 | - - - | - - - | - - - | - - - | 1346 | 1340 | 1533 | 4220 | Over-range | 790 | 705 | 306 | 1968 | 166 | 158 | 293 | 1220 | 1092 | 1138 | 1503 | 3734 | 1092 | 1138 | 1503 | 3734 | - - - | - - - | - - - | - - -
5/3/2026 | 6:30:00 AM | 286.34 | 283.96 | 282.18 | 495.44 | 488.79 | 492.29 | 4.8012 | 4.9208 | 5.4838 | 2.7402 | 1.427 | 1.423 | 1.421 | 1.504 | 1.422 | 1.38 | Over-range | 60 | 1107 | 1205 | 1518 | 3830 | - - - | - - - | - - - | - - - | 1107 | 1205 | 1518 | 3830 | 796 | 684 | 54 | 1534 | - - - | - - - | - - - | - - - | 796 | 684 | 54 | 1534 | 1374 | 1395 | 1547 | 4317 | # # # | # # # | # # # | # # # | 0.805 | 0.864 | 0.981 | 0.887 | # # # | # # # | # # # | - - - | 0.811 | 0.869 | 0.999 | 0.897 | - - - | 0.401 | 1.64 | 1.49 | 1.45 | 1.46 | 1.44 | 1.48 | 11.07 | 11.03 | 19.16 | 0 | - - - | - - - | - - - | - - - | 1374 | 1395 | 1547 | 4317 | Over-range | 815 | 702 | 301 | 1992 | 171 | 156 | 294 | 1269 | 1106 | 1205 | 1520 | 3831 | 1106 | 1205 | 1520 | 3831 | - - - | - - - | - - - | - - -
5/3/2026 | 6:45:00 AM | 289.57 | 286.89 | 285.14 | 500.99 | 493.58 | 497.76 | 5.425 | 5.4789 | 6.2049 | 2.7096 | 1.428 | 1.424 | 1.418 | 1.484 | 1.422 | 1.366 | Over-range | 60.01 | 1299 | 1377 | 1717 | 4393 | - - - | - - - | - - - | - - - | 1299 | 1377 | 1717 | 4393 | 821 | 733 | 97 | 1651 | - - - | - - - | - - - | - - - | 821 | 733 | 97 | 1651 | 1564 | 1570 | 1754 | 4889 | # # # | # # # | # # # | # # # | 0.83 | 0.877 | 0.979 | 0.899 | # # # | # # # | # # # | - - - | 0.82 | 0.875 | 0.977 | 0.894 | - - - | 0.376 | 1.77 | 1.61 | 1.52 | 1.58 | 1.53 | 1.6 | 11.08 | 11.55 | 18.6 | 0 | - - - | - - - | - - - | - - - | 1564 | 1570 | 1754 | 4889 | Over-range | 842 | 753 | 356 | 2130 | 167 | 158 | 310 | 1333 | 1325 | 1396 | 1756 | 4477 | 1325 | 1396 | 1756 | 4477 | - - - | - - - | - - - | - - -
5/3/2026 | 7:00:00 AM | 290.09 | 287.41 | 285.65 | 501.9 | 494.42 | 498.68 | 5.2855 | 4.6777 | 6.5742 | 2.7053 | 1.428 | 1.423 | 1.417 | 1.431 | 1.474 | 1.448 | Over-range | 60.02 | 1396 | 1084 | 1819 | 4299 | - - - | - - - | - - - | - - - | 1396 | 1084 | 1819 | 4299 | 600 | 747 | 332 | 1679 | - - - | - - - | - - - | - - - | 600 | 747 | 332 | 1679 | 1531 | 1334 | 1878 | 4742 | # # # | # # # | # # # | # # # | 0.912 | 0.813 | 0.969 | 0.907 | # # # | # # # | # # # | - - - | 0.917 | 0.819 | 0.982 | 0.915 | - - - | 0.391 | 1.79 | 1.62 | 1.55 | 1.61 | 1.54 | 1.63 | 11.7 | 13.79 | 17.18 | 0 | - - - | - - - | - - - | - - - | 1531 | 1334 | 1878 | 4742 | Over-range | 626 | 766 | 458 | 1996 | 161 | 154 | 309 | 1079 | 1395 | 1084 | 1819 | 4298 | 1395 | 1084 | 1819 | 4298 | - - - | - - - | - - - | - - -
5/3/2026 | 7:15:00 AM | 289.45 | 286.74 | 284.93 | 500.78 | 493.2 | 497.51 | 5.3031 | 4.7067 | 6.555 | 2.7178 | 1.428 | 1.423 | 1.417 | 1.435 | 1.456 | 1.442 | Over-range | 60.01 | 1396 | 1113 | 1814 | 4323 | - - - | - - - | - - - | - - - | 1396 | 1113 | 1814 | 4323 | 612 | 737 | 309 | 1658 | - - - | - - - | - - - | - - - | 612 | 737 | 309 | 1658 | 1534 | 1347 | 1868 | 4749 | # # # | # # # | # # # | # # # | 0.91 | 0.826 | 0.971 | 0.91 | # # # | # # # | # # # | - - - | 0.916 | 0.832 | 0.986 | 0.92 | - - - | 0.384 | 1.77 | 1.63 | 1.56 | 1.61 | 1.55 | 1.63 | 10.56 | 12.49 | 16.79 | 0 | - - - | - - - | - - - | - - - | 1534 | 1347 | 1868 | 4749 | Over-range | 637 | 757 | 442 | 1965 | 175 | 171 | 314 | 1055 | 1397 | 1110 | 1817 | 4324 | 1397 | 1110 | 1817 | 4324 | - - - | - - - | - - - | - - -
5/3/2026 | 7:30:00 AM | 289.3 | 286.56 | 284.82 | 500.5 | 492.91 | 497.31 | 5.3067 | 4.7081 | 6.5466 | 2.7096 | 1.428 | 1.424 | 1.418 | 1.435 | 1.456 | 1.439 | Over-range | 60.03 | 1397 | 1119 | 1813 | 4329 | - - - | - - - | - - - | - - - | 1397 | 1119 | 1813 | 4329 | 612 | 734 | 304 | 1649 | - - - | - - - | - - - | - - - | 612 | 734 | 304 | 1649 | 1535 | 1349 | 1865 | 4749 | # # # | # # # | # # # | # # # | 0.91 | 0.83 | 0.972 | 0.912 | # # # | # # # | # # # | - - - | 0.916 | 0.836 | 0.986 | 0.921 | - - - | 0.381 | 1.82 | 1.67 | 1.58 | 1.64 | 1.58 | 1.67 | 10.46 | 12.3 | 16.61 | 0 | - - - | - - - | - - - | - - - | 1535 | 1349 | 1865 | 4749 | Over-range | 636 | 753 | 435 | 1951 | 175 | 166 | 311 | 1041 | 1396 | 1118 | 1815 | 4330 | 1396 | 1118 | 1815 | 4330 | - - - | - - - | - - - | - - -
5/3/2026 | 7:45:00 AM | 289.14 | 286.4 | 284.69 | 500.19 | 492.69 | 497.08 | 5.6543 | 4.9209 | 6.6912 | 3.4924 | 1.429 | 1.424 | 1.418 | 1.444 | 1.433 | 1.397 | Over-range | 60.02 | 1459 | 1139 | 1867 | 4465 | - - - | - - - | - - - | - - - | 1459 | 1139 | 1867 | 4465 | 715 | 794 | 198 | 1707 | - - - | - - - | - - - | - - - | 715 | 794 | 198 | 1707 | 1634 | 1408 | 1905 | 4947 | # # # | # # # | # # # | # # # | 0.893 | 0.809 | 0.98 | 0.903 | # # # | # # # | # # # | - - - | 0.898 | 0.817 | 0.994 | 0.912 | - - - | 0.382 | 1.82 | 1.68 | 1.59 | 1.65 | 1.6 | 1.69 | 9.65 | 13.64 | 16.6 | 0 | - - - | - - - | - - - | - - - | 1634 | 1408 | 1905 | 4947 | Over-range | 735 | 818 | 374 | 2122 | 172 | 196 | 315 | 1256 | 1462 | 1137 | 1867 | 4466 | 1462 | 1137 | 1867 | 4466 | - - - | - - - | - - - | - - -
5/3/2026 | 8:00:00 AM | 289.11 | 286.39 | 284.81 | 500.05 | 492.84 | 497.2 | 5.7274 | 4.4771 | 6.7085 | 4.0798 | 1.428 | 1.423 | 1.418 | 1.443 | 1.457 | 1.407 | Over-range | 60.03 | 1480 | 921 | 1869 | 4270 | - - - | - - - | - - - | - - - | 1480 | 921 | 1869 | 4270 | 713 | 856 | 227 | 1797 | - - - | - - - | - - - | - - - | 713 | 856 | 227 | 1797 | 1653 | 1280 | 1910 | 4842 | # # # | # # # | # # # | # # # | 0.896 | 0.72 | 0.978 | 0.882 | # # # | # # # | # # # | - - - | 0.889 | 0.722 | 0.981 | 0.882 | - - - | 0.421 | 1.82 | 1.68 | 1.62 | 1.66 | 1.61 | 1.7 | 10.42 | 17.03 | 16.83 | 0 | - - - | - - - | - - - | - - - | 1653 | 1280 | 1910 | 4842 | Over-range | 735 | 882 | 389 | 2281 | 156 | 192 | 306 | 1398 | 1495 | 926 | 1899 | 4321 | 1495 | 926 | 1899 | 4321 | - - - | - - - | - - - | - - -
5/3/2026 | 8:15:00 AM | 288.74 | 286.02 | 284.49 | 499.43 | 492.2 | 496.62 | 5.1055 | 3.655 | 6.454 | 4.0965 | 1.428 | 1.424 | 1.418 | 1.426 | 1.495 | 1.461 | Over-range | 60.01 | 1358 | 549 | 1772 | 3678 | - - - | - - - | - - - | - - - | 1358 | 549 | 1772 | 3678 | 544 | 860 | 363 | 1767 | - - - | - - - | - - - | - - - | 544 | 860 | 363 | 1767 | 1473 | 1044 | 1836 | 4353 | # # # | # # # | # # # | # # # | 0.921 | 0.526 | 0.965 | 0.845 | # # # | # # # | # # # | - - - | 0.928 | 0.536 | 0.979 | 0.856 | - - - | 0.48 | 1.85 | 1.67 | 1.62 | 1.66 | 1.62 | 1.7 | 10.83 | 18.84 | 16.58 | 0 | - - - | - - - | - - - | - - - | 1473 | 1044 | 1836 | 4353 | Over-range | 572 | 883 | 478 | 2325 | 176 | 202 | 308 | 1511 | 1357 | 550 | 1771 | 3678 | 1357 | 550 | 1771 | 3678 | - - - | - - - | - - - | - - -
5/3/2026 | 8:30:00 AM | 288.5 | 285.62 | 284.18 | 498.84 | 491.54 | 496.21 | 5.3877 | 4.0397 | 6.5573 | 4.0924 | 1.429 | 1.424 | 1.418 | 1.438 | 1.479 | 1.426 | Over-range | 60.01 | 1411 | 751 | 1818 | 3979 | - - - | - - - | - - - | - - - | 1411 | 751 | 1818 | 3979 | 630 | 850 | 270 | 1750 | - - - | - - - | - - - | - - - | 630 | 850 | 270 | 1750 | 1554 | 1153 | 1863 | 4571 | # # # | # # # | # # # | # # # | 0.908 | 0.652 | 0.975 | 0.871 | # # # | # # # | # # # | - - - | 0.913 | 0.662 | 0.989 | 0.881 | - - - | 0.44 | 1.81 | 1.7 | 1.61 | 1.65 | 1.61 | 1.69 | 10 | 17.31 | 16.47 | 0 | - - - | - - - | - - - | - - - | 1554 | 1153 | 1863 | 4571 | Over-range | 652 | 874 | 410 | 2248 | 169 | 201 | 308 | 1411 | 1412 | 753 | 1815 | 3979 | 1412 | 753 | 1815 | 3979 | - - - | - - - | - - - | - - -
5/3/2026 | 8:45:00 AM | 288.41 | 285.4 | 283.97 | 498.59 | 491.11 | 496.01 | 5.3792 | 4.0173 | 6.547 | 4.0914 | 1.429 | 1.425 | 1.419 | 1.44 | 1.48 | 1.427 | Over-range | 60.02 | 1409 | 748 | 1814 | 3972 | - - - | - - - | - - - | - - - | 1409 | 748 | 1814 | 3972 | 627 | 846 | 267 | 1740 | - - - | - - - | - - - | - - - | 627 | 846 | 267 | 1740 | 1551 | 1146 | 1859 | 4557 | # # # | # # # | # # # | # # # | 0.909 | 0.653 | 0.976 | 0.872 | # # # | # # # | # # # | - - - | 0.914 | 0.663 | 0.99 | 0.882 | - - - | 0.438 | 1.79 | 1.63 | 1.59 | 1.61 | 1.57 | 1.65 | 10.01 | 17.24 | 16.4 | 0 | - - - | - - - | - - - | - - - | 1551 | 1146 | 1859 | 4557 | Over-range | 648 | 868 | 406 | 2234 | 166 | 194 | 306 | 1401 | 1410 | 750 | 1812 | 3972 | 1410 | 750 | 1812 | 3972 | - - - | - - - | - - - | - - -
5/3/2026 | 9:00:00 AM | 287.07 | 283.95 | 282.63 | 496.13 | 488.68 | 493.75 | 5.4917 | 4.1813 | 6.5811 | 4.0956 | 1.428 | 1.424 | 1.42 | 1.443 | 1.461 | 1.413 | Over-range | 60.01 | 1427 | 824 | 1821 | 4072 | - - - | - - - | - - - | - - - | 1427 | 824 | 1821 | 4072 | 647 | 822 | 217 | 1687 | - - - | - - - | - - - | - - - | 647 | 822 | 217 | 1687 | 1575 | 1184 | 1860 | 4619 | # # # | # # # | # # # | # # # | 0.906 | 0.696 | 0.979 | 0.881 | # # # | # # # | # # # | - - - | 0.911 | 0.706 | 0.992 | 0.891 | - - - | 0.414 | 1.72 | 1.61 | 1.56 | 1.56 | 1.55 | 1.6 | 9.54 | 16.49 | 16.15 | 0 | - - - | - - - | - - - | - - - | 1575 | 1184 | 1860 | 4619 | Over-range | 668 | 844 | 376 | 2178 | 165 | 192 | 302 | 1378 | 1426 | 826 | 1819 | 4071 | 1426 | 826 | 1819 | 4071 | - - - | - - - | - - - | - - -
5/3/2026 | 9:15:00 AM | 284.13 | 281.47 | 279.94 | 491.25 | 484.58 | 488.68 | 5.8955 | 4.8317 | 6.7688 | 4.1386 | 1.428 | 1.426 | 1.425 | 1.449 | 1.418 | 1.353 | Over-range | 60.01 | 1494 | 1098 | 1870 | 4462 | - - - | - - - | - - - | - - - | 1494 | 1098 | 1870 | 4462 | 738 | 778 | 63 | 1580 | - - - | - - - | - - - | - - - | 738 | 778 | 63 | 1580 | 1675 | 1359 | 1895 | 4929 | # # # | # # # | # # # | # # # | 0.892 | 0.807 | 0.987 | 0.905 | # # # | # # # | # # # | - - - | 0.896 | 0.816 | 0.999 | 0.914 | - - - | 0.354 | 1.76 | 1.64 | 1.63 | 1.6 | 1.63 | 1.64 | 8.69 | 14.15 | 15.62 | 0 | - - - | - - - | - - - | - - - | 1675 | 1359 | 1895 | 4929 | Over-range | 757 | 801 | 305 | 2095 | 169 | 192 | 297 | 1376 | 1492 | 1098 | 1870 | 4461 | 1492 | 1098 | 1870 | 4461 | - - - | - - - | - - - | - - -
5/3/2026 | 9:30:00 AM | 284.04 | 281.2 | 279.79 | 490.95 | 484.12 | 488.56 | 5.4703 | 4.0915 | 6.5488 | 4.1392 | 1.428 | 1.427 | 1.424 | 1.447 | 1.449 | 1.406 | Over-range | 60 | 1416 | 801 | 1796 | 4012 | - - - | - - - | - - - | - - - | 1416 | 801 | 1796 | 4012 | 610 | 779 | 191 | 1580 | - - - | - - - | - - - | - - - | 610 | 779 | 191 | 1580 | 1551 | 1143 | 1832 | 4526 | # # # | # # # | # # # | # # # | 0.913 | 0.701 | 0.98 | 0.886 | # # # | # # # | # # # | - - - | 0.918 | 0.71 | 0.993 | 0.896 | - - - | 0.394 | 1.7 | 1.64 | 1.57 | 1.55 | 1.59 | 1.59 | 9.39 | 16.01 | 15.68 | 0 | - - - | - - - | - - - | - - - | 1551 | 1143 | 1832 | 4526 | Over-range | 632 | 799 | 356 | 2086 | 163 | 179 | 291 | 1361 | 1414 | 802 | 1795 | 4011 | 1414 | 802 | 1795 | 4011 | - - - | - - - | - - - | - - -
5/3/2026 | 9:45:00 AM | 284.13 | 281.35 | 279.91 | 491.19 | 484.35 | 488.71 | 5.176 | 3.5892 | 6.4133 | 4.1389 | 1.428 | 1.426 | 1.424 | 1.44 | 1.466 | 1.443 | Over-range | 60.01 | 1363 | 602 | 1749 | 3714 | - - - | - - - | - - - | - - - | 1363 | 602 | 1749 | 3714 | 526 | 783 | 280 | 1588 | - - - | - - - | - - - | - - - | 526 | 783 | 280 | 1588 | 1470 | 1008 | 1795 | 4273 | # # # | # # # | # # # | # # # | 0.928 | 0.597 | 0.974 | 0.869 | # # # | # # # | # # # | - - - | 0.932 | 0.608 | 0.987 | 0.879 | - - - | 0.428 | 1.66 | 1.57 | 1.52 | 1.5 | 1.51 | 1.54 | 9.73 | 17.73 | 15.82 | 0 | - - - | - - - | - - - | - - - | 1470 | 1008 | 1795 | 4273 | Over-range | 548 | 803 | 403 | 2108 | 156 | 176 | 287 | 1386 | 1363 | 604 | 1746 | 3714 | 1363 | 604 | 1746 | 3714 | - - - | - - - | - - - | - - -
5/3/2026 | 10:00:00 AM | 284.19 | 281.27 | 279.9 | 491.16 | 484.23 | 488.82 | 5.4028 | 3.9234 | 6.5103 | 4.1306 | 1.428 | 1.425 | 1.422 | 1.44 | 1.451 | 1.417 | Over-range | 60.03 | 1407 | 756 | 1786 | 3949 | - - - | - - - | - - - | - - - | 1407 | 756 | 1786 | 3949 | 593 | 777 | 215 | 1585 | - - - | - - - | - - - | - - - | 593 | 777 | 215 | 1585 | 1535 | 1102 | 1822 | 4458 | # # # | # # # | # # # | # # # | 0.917 | 0.687 | 0.98 | 0.886 | # # # | # # # | # # # | - - - | 0.913 | 0.691 | 0.984 | 0.887 | - - - | 0.401 | 1.62 | 1.51 | 1.48 | 1.46 | 1.46 | 1.49 | 9.24 | 16.38 | 15.62 | 0 | - - - | - - - | - - - | - - - | 1535 | 1102 | 1822 | 4458 | Over-range | 613 | 798 | 360 | 2069 | 156 | 182 | 286 | 1329 | 1420 | 761 | 1799 | 3980 | 1420 | 761 | 1799 | 3980 | - - - | - - - | - - - | - - -
5/3/2026 | 10:15:00 AM | 283.56 | 280.53 | 279.31 | 489.92 | 483.04 | 487.85 | 5.8374 | 4.6149 | 6.7048 | 4.0832 | 1.427 | 1.424 | 1.421 | 1.452 | 1.431 | 1.378 | Over-range | 60 | 1490 | 1021 | 1846 | 4357 | - - - | - - - | - - - | - - - | 1490 | 1021 | 1846 | 4357 | 699 | 760 | 110 | 1569 | - - - | - - - | - - - | - - - | 699 | 760 | 110 | 1569 | 1653 | 1289 | 1872 | 4815 | # # # | # # # | # # # | # # # | 0.901 | 0.792 | 0.986 | 0.905 | # # # | # # # | # # # | - - - | 0.904 | 0.798 | 0.996 | 0.911 | - - - | 0.36 | 1.59 | 1.5 | 1.44 | 1.44 | 1.44 | 1.46 | 10.51 | 16.5 | 16.29 | 0 | - - - | - - - | - - - | - - - | 1653 | 1289 | 1872 | 4815 | Over-range | 716 | 782 | 308 | 2049 | 120 | 148 | 269 | 1314 | 1490 | 1020 | 1845 | 4354 | 1490 | 1020 | 1845 | 4354 | - - - | - - - | - - - | - - -
5/3/2026 | 10:30:00 AM | 283.25 | 280.11 | 278.98 | 489.3 | 482.32 | 487.36 | 5.782 | 4.6247 | 6.6879 | 4.0803 | 1.426 | 1.424 | 1.421 | 1.452 | 1.427 | 1.369 | Over-range | 60.01 | 1475 | 1032 | 1844 | 4351 | - - - | - - - | - - - | - - - | 1475 | 1032 | 1844 | 4351 | 692 | 754 | 83 | 1529 | - - - | - - - | - - - | - - - | 692 | 754 | 83 | 1529 | 1637 | 1292 | 1866 | 4795 | # # # | # # # | # # # | # # # | 0.901 | 0.798 | 0.988 | 0.907 | # # # | # # # | # # # | - - - | 0.903 | 0.804 | 0.998 | 0.913 | - - - | 0.352 | 1.57 | 1.49 | 1.43 | 1.43 | 1.43 | 1.44 | 10.55 | 16.08 | 16.09 | 0 | - - - | - - - | - - - | - - - | 1637 | 1292 | 1866 | 4795 | Over-range | 709 | 775 | 283 | 2015 | 119 | 143 | 265 | 1312 | 1476 | 1030 | 1843 | 4349 | 1476 | 1030 | 1843 | 4349 | - - - | - - - | - - - | - - -
5/3/2026 | 10:45:00 AM | 283.36 | 280.27 | 279.14 | 489.49 | 482.66 | 487.56 | 4.7724 | 3.5559 | 5.7617 | 4.124 | 1.427 | 1.425 | 1.421 | 1.479 | 1.463 | 1.425 | Over-range | 60.01 | 1180 | 594 | 1564 | 3338 | - - - | - - - | - - - | - - - | 1180 | 594 | 1564 | 3338 | 614 | 760 | 172 | 1547 | - - - | - - - | - - - | - - - | 614 | 760 | 172 | 1547 | 1347 | 991 | 1601 | 3940 | # # # | # # # | # # # | # # # | 0.875 | 0.599 | 0.977 | 0.847 | # # # | # # # | # # # | - - - | 0.881 | 0.608 | 0.992 | 0.857 | - - - | 0.463 | 1.58 | 1.5 | 1.43 | 1.43 | 1.43 | 1.45 | 11.01 | 17.93 | 17.45 | 0 | - - - | - - - | - - - | - - - | 1347 | 991 | 1601 | 3940 | Over-range | 633 | 781 | 335 | 2081 | 145 | 169 | 271 | 1391 | 1181 | 593 | 1564 | 3338 | 1181 | 593 | 1564 | 3338 | - - - | - - - | - - - | - - -
5/3/2026 | 11:00:00 AM | 283.15 | 280.04 | 278.94 | 489.12 | 482.26 | 487.23 | 4.7178 | 3.8519 | 5.3976 | 4.1268 | 1.428 | 1.425 | 1.422 | 1.509 | 1.448 | 1.378 | Over-range | 60.01 | 1095 | 741 | 1479 | 3315 | - - - | - - - | - - - | - - - | 1095 | 741 | 1479 | 3315 | 747 | 755 | 36 | 1538 | - - - | - - - | - - - | - - - | 747 | 755 | 36 | 1538 | 1335 | 1076 | 1505 | 3916 | # # # | # # # | # # # | # # # | 0.821 | 0.689 | 0.983 | 0.847 | # # # | # # # | # # # | - - - | 0.826 | 0.698 | 0.999 | 0.857 | - - - | 0.464 | 1.59 | 1.51 | 1.43 | 1.44 | 1.44 | 1.47 | 10.6 | 16.49 | 18.32 | 0 | - - - | - - - | - - - | - - - | 1335 | 1076 | 1505 | 3916 | Over-range | 763 | 776 | 280 | 2083 | 154 | 181 | 274 | 1405 | 1098 | 739 | 1479 | 3317 | 1098 | 739 | 1479 | 3317 | - - - | - - - | - - - | - - -
5/3/2026 | 11:15:00 AM | 282.83 | 279.71 | 278.63 | 488.54 | 481.69 | 486.7 | 4.7474 | 3.8846 | 5.4096 | 4.1235 | 1.428 | 1.425 | 1.422 | 1.508 | 1.444 | 1.372 | Over-range | 60 | 1100 | 764 | 1482 | 3346 | - - - | - - - | - - - | - - - | 1100 | 764 | 1482 | 3346 | 754 | 751 | 23 | 1528 | - - - | - - - | - - - | - - - | 754 | 751 | 23 | 1528 | 1343 | 1086 | 1507 | 3936 | # # # | # # # | # # # | # # # | 0.819 | 0.703 | 0.983 | 0.85 | # # # | # # # | # # # | - - - | 0.826 | 0.712 | 1 | 0.861 | - - - | 0.457 | 1.57 | 1.5 | 1.44 | 1.43 | 1.44 | 1.46 | 10.46 | 16.16 | 18.21 | 0 | - - - | - - - | - - - | - - - | 1343 | 1086 | 1507 | 3936 | Over-range | 770 | 772 | 274 | 2073 | 153 | 180 | 273 | 1400 | 1103 | 762 | 1483 | 3348 | 1103 | 762 | 1483 | 3348 | - - - | - - - | - - - | - - -
5/3/2026 | 11:30:00 AM | 282.96 | 279.94 | 278.79 | 488.79 | 482.12 | 486.91 | 5.2933 | 4.8088 | 5.7218 | 4.1265 | 1.429 | 1.426 | 1.423 | 1.515 | 1.429 | 1.306 | Over-range | 60.02 | 1187 | 1093 | 1564 | 3845 | - - - | - - - | - - - | - - - | 1187 | 1093 | 1564 | 3845 | 896 | 748 | -120 | 1523 | - - - | - - - | - - - | - - - | 896 | 748 | -120 | 1523 | 1496 | 1341 | 1595 | 4432 | # # # | # # # | # # # | # # # | 0.793 | 0.815 | 0.981 | 0.868 | # # # | # # # | # # # | - - - | 0.799 | 0.823 | 0.996 | 0.877 | - - - | 0.396 | 1.58 | 1.5 | 1.46 | 1.44 | 1.45 | 1.47 | 9.42 | 14.03 | 17.64 | 0 | - - - | - - - | - - - | - - - | 1496 | 1341 | 1595 | 4432 | Over-range | 910 | 773 | 309 | 2205 | 159 | 192 | 278 | 1592 | 1190 | 1091 | 1565 | 3846 | 1190 | 1091 | 1565 | 3846 | - - - | - - - | - - - | - - -
5/3/2026 | 11:45:00 AM | 282.82 | 279.7 | 278.61 | 488.49 | 481.69 | 486.7 | 5.3313 | 4.8591 | 5.7355 | 4.1231 | 1.428 | 1.426 | 1.423 | 1.515 | 1.427 | 1.292 | Over-range | 60.02 | 1194 | 1119 | 1568 | 3882 | - - - | - - - | - - - | - - - | 1194 | 1119 | 1568 | 3882 | 906 | 746 | -135 | 1516 | - - - | - - - | - - - | - - - | 906 | 746 | -135 | 1516 | 1508 | 1358 | 1598 | 4464 | # # # | # # # | # # # | # # # | 0.792 | 0.824 | 0.981 | 0.87 | # # # | # # # | # # # | - - - | 0.797 | 0.832 | 0.996 | 0.878 | - - - | 0.391 | 1.58 | 1.49 | 1.46 | 1.44 | 1.44 | 1.47 | 9.33 | 13.48 | 17.43 | 0 | - - - | - - - | - - - | - - - | 1508 | 1358 | 1598 | 4464 | Over-range | 920 | 768 | 308 | 2204 | 158 | 184 | 275 | 1599 | 1195 | 1121 | 1566 | 3882 | 1195 | 1121 | 1566 | 3882 | - - - | - - - | - - - | - - -
5/3/2026 | 12:00:00 PM | 282.5 | 279.39 | 278.29 | 487.97 | 481.12 | 486.14 | 4.6598 | 3.8137 | 5.371 | 4.1324 | 1.429 | 1.426 | 1.423 | 1.503 | 1.45 | 1.387 | Over-range | 60.01 | 1083 | 694 | 1464 | 3242 | - - - | - - - | - - - | - - - | 1083 | 694 | 1464 | 3242 | 720 | 748 | 49 | 1517 | - - - | - - - | - - - | - - - | 720 | 748 | 49 | 1517 | 1311 | 1053 | 1494 | 3858 | # # # | # # # | # # # | # # # | 0.826 | 0.66 | 0.98 | 0.84 | # # # | # # # | # # # | - - - | 0.833 | 0.669 | 0.997 | 0.851 | - - - | 0.468 | 1.59 | 1.5 | 1.49 | 1.45 | 1.45 | 1.49 | 10.83 | 16.61 | 18.1 | 0 | - - - | - - - | - - - | - - - | 1311 | 1053 | 1494 | 3858 | Over-range | 737 | 767 | 295 | 2083 | 154 | 170 | 269 | 1427 | 1084 | 696 | 1462 | 3242 | 1084 | 696 | 1462 | 3242 | - - - | - - - | - - - | - - -
5/3/2026 | 12:15:00 PM | 282.53 | 279.43 | 278.34 | 488 | 481.24 | 486.19 | 4.7884 | 3.8191 | 5.4125 | 4.1343 | 1.429 | 1.427 | 1.424 | 1.505 | 1.446 | 1.387 | Over-range | 60 | 1115 | 732 | 1476 | 3323 | - - - | - - - | - - - | - - - | 1115 | 732 | 1476 | 3323 | 746 | 749 | 55 | 1549 | - - - | - - - | - - - | - - - | 746 | 749 | 55 | 1549 | 1351 | 1065 | 1506 | 3922 | # # # | # # # | # # # | # # # | 0.825 | 0.688 | 0.98 | 0.847 | # # # | # # # | # # # | - - - | 0.823 | 0.692 | 0.982 | 0.849 | - - - | 0.466 | 1.62 | 1.53 | 1.49 | 1.46 | 1.46 | 1.5 | 10.42 | 16.62 | 18.3 | 0 | - - - | - - - | - - - | - - - | 1351 | 1065 | 1506 | 3922 | Over-range | 762 | 769 | 294 | 2081 | 156 | 174 | 274 | 1384 | 1123 | 738 | 1489 | 3351 | 1123 | 738 | 1489 | 3351 | - - - | - - - | - - - | - - -
5/3/2026 | 12:30:00 PM | 282.4 | 279.38 | 278.24 | 487.87 | 481.13 | 485.96 | 4.7372 | 3.8546 | 5.4043 | 4.1351 | 1.429 | 1.426 | 1.423 | 1.507 | 1.443 | 1.372 | Over-range | 60.01 | 1099 | 756 | 1479 | 3334 | - - - | - - - | - - - | - - - | 1099 | 756 | 1479 | 3334 | 747 | 746 | 21 | 1514 | - - - | - - - | - - - | - - - | 747 | 746 | 21 | 1514 | 1338 | 1077 | 1504 | 3918 | # # # | # # # | # # # | # # # | 0.822 | 0.702 | 0.983 | 0.851 | # # # | # # # | # # # | - - - | 0.828 | 0.712 | 1 | 0.862 | - - - | 0.454 | 1.58 | 1.52 | 1.45 | 1.44 | 1.44 | 1.48 | 10.43 | 16.21 | 18.19 | 0 | - - - | - - - | - - - | - - - | 1338 | 1077 | 1504 | 3918 | Over-range | 762 | 766 | 273 | 2058 | 153 | 175 | 271 | 1394 | 1101 | 756 | 1478 | 3335 | 1101 | 756 | 1478 | 3335 | - - - | - - - | - - - | - - -
5/3/2026 | 12:45:00 PM | 282.29 | 279.23 | 278.12 | 487.64 | 480.89 | 485.78 | 4.9443 | 4.1968 | 5.5161 | 4.1301 | 1.429 | 1.426 | 1.424 | 1.51 | 1.429 | 1.341 | Over-range | 60.01 | 1132 | 884 | 1509 | 3525 | - - - | - - - | - - - | - - - | 1132 | 884 | 1509 | 3525 | 800 | 743 | -35 | 1508 | - - - | - - - | - - - | - - - | 800 | 743 | -35 | 1508 | 1395 | 1171 | 1534 | 4100 | # # # | # # # | # # # | # # # | 0.811 | 0.755 | 0.983 | 0.86 | # # # | # # # | # # # | - - - | 0.817 | 0.764 | 0.999 | 0.87 | - - - | 0.428 | 1.61 | 1.51 | 1.48 | 1.46 | 1.46 | 1.5 | 9.99 | 15.39 | 17.97 | 0 | - - - | - - - | - - - | - - - | 1395 | 1171 | 1534 | 4100 | Over-range | 816 | 765 | 278 | 2093 | 157 | 184 | 274 | 1452 | 1134 | 882 | 1510 | 3526 | 1134 | 882 | 1510 | 3526 | - - - | - - - | - - - | - - -
5/3/2026 | 1:00:00 PM | 282.12 | 279.08 | 277.95 | 487.34 | 480.62 | 485.47 | 5.487 | 5.1404 | 5.8168 | 4.1217 | 1.429 | 1.426 | 1.424 | 1.517 | 1.444 | 1.298 | Over-range | 60.01 | 1218 | 1212 | 1582 | 4011 | - - - | - - - | - - - | - - - | 1218 | 1212 | 1582 | 4011 | 940 | 736 | -182 | 1493 | - - - | - - - | - - - | - - - | 940 | 736 | -182 | 1493 | 1547 | 1432 | 1616 | 4595 | # # # | # # # | # # # | # # # | 0.787 | 0.846 | 0.978 | 0.873 | # # # | # # # | # # # | - - - | 0.792 | 0.853 | 0.993 | 0.881 | - - - | 0.372 | 1.62 | 1.53 | 1.5 | 1.47 | 1.47 | 1.51 | 9 | 12.99 | 17.3 | 0 | - - - | - - - | - - - | - - - | 1547 | 1432 | 1616 | 4595 | Over-range | 954 | 760 | 333 | 2242 | 164 | 188 | 276 | 1671 | 1219 | 1210 | 1583 | 4012 | 1219 | 1210 | 1583 | 4012 | - - - | - - - | - - - | - - -
5/3/2026 | 1:15:00 PM | 282.14 | 279.18 | 278.04 | 487.41 | 480.85 | 485.55 | 4.846 | 4.1114 | 5.4736 | 4.1393 | 1.43 | 1.427 | 1.425 | 1.505 | 1.442 | 1.357 | Over-range | 60.01 | 1112 | 806 | 1491 | 3409 | - - - | - - - | - - - | - - - | 1112 | 806 | 1491 | 3409 | 765 | 744 | -2 | 1506 | - - - | - - - | - - - | - - - | 765 | 744 | -2 | 1506 | 1361 | 1133 | 1520 | 4014 | # # # | # # # | # # # | # # # | 0.817 | 0.712 | 0.981 | 0.849 | # # # | # # # | # # # | - - - | 0.822 | 0.721 | 0.996 | 0.859 | - - - | 0.442 | 1.64 | 1.52 | 1.49 | 1.48 | 1.47 | 1.52 | 10.4 | 15.66 | 17.83 | 0 | - - - | - - - | - - - | - - - | 1361 | 1133 | 1520 | 4014 | Over-range | 782 | 764 | 297 | 2108 | 159 | 174 | 269 | 1474 | 1111 | 807 | 1491 | 3409 | 1111 | 807 | 1491 | 3409 | - - - | - - - | - - - | - - -
5/3/2026 | 1:30:00 PM | 282.07 | 279.13 | 277.98 | 487.34 | 480.71 | 485.44 | 4.6321 | 3.7131 | 5.3383 | 4.1359 | 1.429 | 1.426 | 1.424 | 1.505 | 1.447 | 1.39 | Over-range | 60.01 | 1081 | 688 | 1457 | 3225 | - - - | - - - | - - - | - - - | 1081 | 688 | 1457 | 3225 | 715 | 744 | 49 | 1507 | - - - | - - - | - - - | - - - | 715 | 744 | 49 | 1507 | 1305 | 1032 | 1484 | 3821 | # # # | # # # | # # # | # # # | 0.828 | 0.666 | 0.982 | 0.844 | # # # | # # # | # # # | - - - | 0.834 | 0.675 | 0.999 | 0.855 | - - - | 0.467 | 1.62 | 1.53 | 1.46 | 1.47 | 1.46 | 1.5 | 10.66 | 16.95 | 18.45 | 0 | - - - | - - - | - - - | - - - | 1305 | 1032 | 1484 | 3821 | Over-range | 731 | 765 | 282 | 2048 | 152 | 178 | 272 | 1386 | 1084 | 686 | 1457 | 3227 | 1084 | 686 | 1457 | 3227 | - - - | - - - | - - - | - - -
5/3/2026 | 1:45:00 PM | 281.66 | 278.72 | 277.58 | 486.6 | 480.03 | 484.74 | 4.9295 | 4.162 | 5.5059 | 4.1384 | 1.429 | 1.426 | 1.424 | 1.509 | 1.431 | 1.342 | Over-range | 60.01 | 1129 | 874 | 1503 | 3506 | - - - | - - - | - - - | - - - | 1129 | 874 | 1503 | 3506 | 792 | 736 | -35 | 1492 | - - - | - - - | - - - | - - - | 792 | 736 | -35 | 1492 | 1388 | 1158 | 1528 | 4074 | # # # | # # # | # # # | # # # | 0.814 | 0.754 | 0.984 | 0.861 | # # # | # # # | # # # | - - - | 0.819 | 0.764 | 0.999 | 0.871 | - - - | 0.426 | 1.61 | 1.55 | 1.48 | 1.47 | 1.46 | 1.5 | 9.94 | 15.21 | 17.87 | 0 | - - - | - - - | - - - | - - - | 1388 | 1158 | 1528 | 4074 | Over-range | 806 | 758 | 276 | 2074 | 150 | 179 | 271 | 1440 | 1133 | 873 | 1502 | 3507 | 1133 | 873 | 1502 | 3507 | - - - | - - - | - - - | - - -
5/3/2026 | 2:00:00 PM | 281.7 | 278.77 | 277.68 | 486.6 | 480.25 | 484.87 | 5.5382 | 5.2296 | 5.8693 | 4.1334 | 1.43 | 1.427 | 1.425 | 1.516 | 1.45 | 1.3 | Over-range | 60 | 1226 | 1243 | 1594 | 4062 | - - - | - - - | - - - | - - - | 1226 | 1243 | 1594 | 4062 | 951 | 732 | -197 | 1485 | - - - | - - - | - - - | - - - | 951 | 732 | -197 | 1485 | 1560 | 1456 | 1630 | 4645 | # # # | # # # | # # # | # # # | 0.786 | 0.854 | 0.978 | 0.875 | # # # | # # # | # # # | - - - | 0.791 | 0.861 | 0.993 | 0.883 | - - - | 0.366 | 1.62 | 1.56 | 1.49 | 1.49 | 1.48 | 1.52 | 8.89 | 12.81 | 17.09 | 0 | - - - | - - - | - - - | - - - | 1560 | 1456 | 1630 | 4645 | Over-range | 964 | 756 | 340 | 2253 | 157 | 191 | 275 | 1693 | 1229 | 1241 | 1594 | 4063 | 1229 | 1241 | 1594 | 4063 | - - - | - - - | - - - | - - -
5/3/2026 | 2:15:00 PM | 281.95 | 279.08 | 277.9 | 487.18 | 480.64 | 485.23 | 4.9433 | 4.1266 | 5.477 | 4.1368 | 1.43 | 1.427 | 1.424 | 1.503 | 1.442 | 1.369 | Over-range | 60.01 | 1134 | 812 | 1489 | 3435 | - - - | - - - | - - - | - - - | 1134 | 812 | 1489 | 3435 | 776 | 741 | 14 | 1531 | - - - | - - - | - - - | - - - | 776 | 741 | 14 | 1531 | 1384 | 1136 | 1521 | 4041 | # # # | # # # | # # # | # # # | 0.819 | 0.715 | 0.98 | 0.85 | # # # | # # # | # # # | - - - | 0.816 | 0.717 | 0.984 | 0.851 | - - - | 0.446 | 1.6 | 1.53 | 1.47 | 1.47 | 1.46 | 1.5 | 10.28 | 15.58 | 17.92 | 0 | - - - | - - - | - - - | - - - | 1384 | 1136 | 1521 | 4041 | Over-range | 792 | 763 | 304 | 2117 | 155 | 179 | 271 | 1456 | 1147 | 817 | 1505 | 3469 | 1147 | 817 | 1505 | 3469 | - - - | - - - | - - - | - - -
5/3/2026 | 2:30:00 PM | 282.02 | 279.17 | 278.05 | 487.29 | 480.86 | 485.44 | 4.6386 | 3.7238 | 5.3611 | 4.1428 | 1.43 | 1.427 | 1.425 | 1.504 | 1.446 | 1.388 | Over-range | 60 | 1082 | 692 | 1464 | 3237 | - - - | - - - | - - - | - - - | 1082 | 692 | 1464 | 3237 | 717 | 746 | 48 | 1511 | - - - | - - - | - - - | - - - | 717 | 746 | 48 | 1511 | 1307 | 1036 | 1490 | 3834 | # # # | # # # | # # # | # # # | 0.828 | 0.667 | 0.982 | 0.844 | # # # | # # # | # # # | - - - | 0.834 | 0.677 | 0.999 | 0.856 | - - - | 0.467 | 1.63 | 1.53 | 1.48 | 1.48 | 1.47 | 1.51 | 10.64 | 16.93 | 18.33 | 0 | - - - | - - - | - - - | - - - | 1307 | 1036 | 1490 | 3834 | Over-range | 733 | 767 | 281 | 2052 | 153 | 179 | 271 | 1389 | 1084 | 690 | 1465 | 3239 | 1084 | 690 | 1465 | 3239 | - - - | - - - | - - - | - - -
5/3/2026 | 2:45:00 PM | 281.74 | 278.9 | 277.76 | 486.77 | 480.47 | 484.9 | 4.7894 | 3.9332 | 5.4167 | 4.1405 | 1.43 | 1.427 | 1.424 | 1.505 | 1.439 | 1.364 | Over-range | 60.01 | 1107 | 788 | 1480 | 3374 | - - - | - - - | - - - | - - - | 1107 | 788 | 1480 | 3374 | 756 | 740 | 2 | 1499 | - - - | - - - | - - - | - - - | 756 | 740 | 2 | 1499 | 1349 | 1096 | 1504 | 3950 | # # # | # # # | # # # | # # # | 0.821 | 0.719 | 0.984 | 0.854 | # # # | # # # | # # # | - - - | 0.826 | 0.728 | 1 | 0.865 | - - - | 0.444 | 1.62 | 1.55 | 1.47 | 1.48 | 1.47 | 1.51 | 10.23 | 15.82 | 18.15 | 0 | - - - | - - - | - - - | - - - | 1349 | 1096 | 1504 | 3950 | Over-range | 771 | 761 | 272 | 2052 | 150 | 176 | 271 | 1402 | 1110 | 787 | 1479 | 3376 | 1110 | 787 | 1479 | 3376 | - - - | - - - | - - - | - - -
5/3/2026 | 3:00:00 PM | 281.8 | 279 | 277.84 | 486.96 | 480.59 | 485 | 4.9143 | 4.1408 | 5.5023 | 4.1409 | 1.43 | 1.427 | 1.425 | 1.507 | 1.43 | 1.341 | Over-range | 60.01 | 1127 | 865 | 1504 | 3496 | - - - | - - - | - - - | - - - | 1127 | 865 | 1504 | 3496 | 789 | 741 | -30 | 1499 | - - - | - - - | - - - | - - - | 789 | 741 | -30 | 1499 | 1384 | 1154 | 1529 | 4067 | # # # | # # # | # # # | # # # | 0.814 | 0.75 | 0.984 | 0.86 | # # # | # # # | # # # | - - - | 0.819 | 0.759 | 1 | 0.87 | - - - | 0.429 | 1.64 | 1.54 | 1.45 | 1.48 | 1.45 | 1.51 | 10 | 15.28 | 17.94 | 0 | - - - | - - - | - - - | - - - | 1384 | 1154 | 1529 | 4067 | Over-range | 804 | 762 | 275 | 2078 | 153 | 177 | 271 | 1438 | 1128 | 866 | 1502 | 3496 | 1128 | 866 | 1502 | 3496 | - - - | - - - | - - - | - - -
5/3/2026 | 3:15:00 PM | 281.42 | 278.52 | 277.43 | 486.2 | 479.77 | 484.4 | 5.4981 | 5.1607 | 5.829 | 4.1262 | 1.429 | 1.426 | 1.424 | 1.514 | 1.446 | 1.299 | Over-range | 60.01 | 1219 | 1220 | 1582 | 4021 | - - - | - - - | - - - | - - - | 1219 | 1220 | 1582 | 4021 | 938 | 731 | -191 | 1476 | - - - | - - - | - - - | - - - | 938 | 731 | -191 | 1476 | 1547 | 1435 | 1617 | 4598 | # # # | # # # | # # # | # # # | 0.788 | 0.85 | 0.978 | 0.874 | # # # | # # # | # # # | - - - | 0.792 | 0.858 | 0.992 | 0.882 | - - - | 0.367 | 1.63 | 1.52 | 1.48 | 1.46 | 1.45 | 1.5 | 8.93 | 12.76 | 17.13 | 0 | - - - | - - - | - - - | - - - | 1547 | 1435 | 1617 | 4598 | Over-range | 951 | 753 | 336 | 2231 | 160 | 181 | 273 | 1672 | 1218 | 1222 | 1579 | 4020 | 1218 | 1222 | 1579 | 4020 | - - - | - - - | - - - | - - -
5/3/2026 | 3:30:00 PM | 281.34 | 278.56 | 277.39 | 486.13 | 479.87 | 484.23 | 5.4924 | 5.1539 | 5.8398 | 4.1336 | 1.43 | 1.427 | 1.425 | 1.513 | 1.447 | 1.296 | Over-range | 60 | 1218 | 1217 | 1585 | 4019 | - - - | - - - | - - - | - - - | 1218 | 1217 | 1585 | 4019 | 936 | 732 | -189 | 1477 | - - - | - - - | - - - | - - - | 936 | 732 | -189 | 1477 | 1544 | 1433 | 1620 | 4597 | # # # | # # # | # # # | # # # | 0.789 | 0.849 | 0.978 | 0.874 | # # # | # # # | # # # | - - - | 0.793 | 0.857 | 0.992 | 0.883 | - - - | 0.368 | 1.63 | 1.52 | 1.48 | 1.48 | 1.45 | 1.5 | 8.94 | 12.73 | 17.04 | 0 | - - - | - - - | - - - | - - - | 1544 | 1433 | 1620 | 4597 | Over-range | 950 | 754 | 334 | 2230 | 162 | 181 | 272 | 1670 | 1217 | 1219 | 1583 | 4019 | 1217 | 1219 | 1583 | 4019 | - - - | - - - | - - - | - - -
5/3/2026 | 3:45:00 PM | 281.24 | 278.43 | 277.32 | 485.92 | 479.66 | 484.12 | 4.6798 | 3.8346 | 5.3808 | 4.142 | 1.43 | 1.428 | 1.425 | 1.501 | 1.445 | 1.377 | Over-range | 60.01 | 1086 | 710 | 1462 | 3259 | - - - | - - - | - - - | - - - | 1086 | 710 | 1462 | 3259 | 716 | 736 | 31 | 1483 | - - - | - - - | - - - | - - - | 716 | 736 | 31 | 1483 | 1311 | 1055 | 1491 | 3857 | # # # | # # # | # # # | # # # | 0.828 | 0.674 | 0.981 | 0.845 | # # # | # # # | # # # | - - - | 0.833 | 0.683 | 0.997 | 0.855 | - - - | 0.455 | 1.62 | 1.55 | 1.48 | 1.48 | 1.46 | 1.51 | 10.62 | 16.36 | 17.9 | 0 | - - - | - - - | - - - | - - - | 1311 | 1055 | 1491 | 3857 | Over-range | 733 | 755 | 289 | 2055 | 155 | 167 | 266 | 1421 | 1084 | 712 | 1462 | 3258 | 1084 | 712 | 1462 | 3258 | - - - | - - - | - - - | - - -
5/3/2026 | 4:00:00 PM | 281.19 | 278.39 | 277.2 | 485.89 | 479.5 | 483.95 | 4.8222 | 3.875 | 5.4066 | 4.1349 | 1.43 | 1.427 | 1.425 | 1.501 | 1.439 | 1.378 | Over-range | 60 | 1117 | 757 | 1470 | 3345 | - - - | - - - | - - - | - - - | 1117 | 757 | 1470 | 3345 | 744 | 735 | 30 | 1509 | - - - | - - - | - - - | - - - | 744 | 735 | 30 | 1509 | 1352 | 1074 | 1498 | 3924 | # # # | # # # | # # # | # # # | 0.827 | 0.705 | 0.981 | 0.852 | # # # | # # # | # # # | - - - | 0.824 | 0.709 | 0.982 | 0.853 | - - - | 0.451 | 1.63 | 1.53 | 1.49 | 1.48 | 1.46 | 1.51 | 10.22 | 16.15 | 18.14 | 0 | - - - | - - - | - - - | - - - | 1352 | 1074 | 1498 | 3924 | Over-range | 760 | 754 | 287 | 2050 | 157 | 171 | 271 | 1383 | 1126 | 764 | 1485 | 3375 | 1126 | 764 | 1485 | 3375 | - - - | - - - | - - - | - - -
5/3/2026 | 4:15:00 PM | 281.04 | 278.25 | 277.06 | 485.63 | 479.28 | 483.68 | 4.8137 | 3.9656 | 5.4427 | 4.1423 | 1.43 | 1.427 | 1.425 | 1.505 | 1.434 | 1.355 | Over-range | 60 | 1110 | 807 | 1484 | 3401 | - - - | - - - | - - - | - - - | 1110 | 807 | 1484 | 3401 | 758 | 732 | -11 | 1477 | - - - | - - - | - - - | - - - | 758 | 732 | -11 | 1477 | 1353 | 1103 | 1508 | 3964 | # # # | # # # | # # # | # # # | 0.821 | 0.732 | 0.984 | 0.858 | # # # | # # # | # # # | - - - | 0.827 | 0.742 | 1 | 0.869 | - - - | 0.434 | 1.62 | 1.51 | 1.46 | 1.47 | 1.45 | 1.5 | 10.12 | 15.56 | 17.9 | 0 | - - - | - - - | - - - | - - - | 1353 | 1103 | 1508 | 3964 | Over-range | 772 | 752 | 269 | 2035 | 150 | 171 | 268 | 1400 | 1112 | 809 | 1481 | 3401 | 1112 | 809 | 1481 | 3401 | - - - | - - - | - - - | - - -
5/3/2026 | 4:30:00 PM | 280.97 | 278.12 | 276.98 | 485.43 | 479.09 | 483.59 | 5.3184 | 4.8411 | 5.7177 | 4.1324 | 1.43 | 1.427 | 1.425 | 1.513 | 1.436 | 1.301 | Over-range | 59.99 | 1189 | 1110 | 1552 | 3851 | - - - | - - - | - - - | - - - | 1189 | 1110 | 1552 | 3851 | 889 | 726 | -145 | 1469 | - - - | - - - | - - - | - - - | 889 | 726 | -145 | 1469 | 1493 | 1342 | 1583 | 4418 | # # # | # # # | # # # | # # # | 0.797 | 0.828 | 0.98 | 0.872 | # # # | # # # | # # # | - - - | 0.802 | 0.835 | 0.995 | 0.881 | - - - | 0.382 | 1.61 | 1.53 | 1.47 | 1.47 | 1.44 | 1.5 | 9.18 | 13.57 | 17.44 | 0 | - - - | - - - | - - - | - - - | 1493 | 1342 | 1583 | 4418 | Over-range | 902 | 749 | 314 | 2165 | 153 | 184 | 273 | 1588 | 1192 | 1110 | 1550 | 3852 | 1192 | 1110 | 1550 | 3852 | - - - | - - - | - - - | - - -
5/3/2026 | 4:45:00 PM | 280.7 | 277.92 | 276.67 | 485.12 | 478.59 | 483.06 | 5.4244 | 5.0216 | 5.7923 | 4.1318 | 1.43 | 1.427 | 1.425 | 1.514 | 1.445 | 1.286 | Over-range | 59.99 | 1206 | 1178 | 1569 | 3953 | - - - | - - - | - - - | - - - | 1206 | 1178 | 1569 | 3953 | 916 | 722 | -175 | 1462 | - - - | - - - | - - - | - - - | 916 | 722 | -175 | 1462 | 1522 | 1395 | 1602 | 4519 | # # # | # # # | # # # | # # # | 0.792 | 0.845 | 0.979 | 0.875 | # # # | # # # | # # # | - - - | 0.797 | 0.852 | 0.994 | 0.883 | - - - | 0.37 | 1.62 | 1.56 | 1.49 | 1.49 | 1.47 | 1.52 | 8.98 | 12.95 | 17.1 | 0 | - - - | - - - | - - - | - - - | 1522 | 1395 | 1602 | 4519 | Over-range | 929 | 746 | 324 | 2190 | 152 | 186 | 271 | 1630 | 1210 | 1176 | 1568 | 3954 | 1210 | 1176 | 1568 | 3954 | - - - | - - - | - - - | - - -
5/3/2026 | 5:00:00 PM | 280.59 | 277.71 | 276.53 | 484.81 | 478.26 | 482.9 | 4.9362 | 4.2612 | 5.5159 | 4.1368 | 1.429 | 1.427 | 1.425 | 1.505 | 1.442 | 1.34 | Over-range | 60 | 1124 | 864 | 1493 | 3481 | - - - | - - - | - - - | - - - | 1124 | 864 | 1493 | 3481 | 779 | 723 | -40 | 1461 | - - - | - - - | - - - | - - - | 779 | 723 | -40 | 1461 | 1378 | 1164 | 1524 | 4065 | # # # | # # # | # # # | # # # | 0.816 | 0.742 | 0.98 | 0.856 | # # # | # # # | # # # | - - - | 0.822 | 0.75 | 0.995 | 0.866 | - - - | 0.42 | 1.62 | 1.53 | 1.45 | 1.47 | 1.46 | 1.5 | 10.03 | 15.03 | 17.49 | 0 | - - - | - - - | - - - | - - - | 1378 | 1164 | 1524 | 4065 | Over-range | 794 | 744 | 301 | 2089 | 152 | 175 | 264 | 1492 | 1127 | 862 | 1494 | 3483 | 1127 | 862 | 1494 | 3483 | - - - | - - - | - - - | - - -
5/3/2026 | 5:15:00 PM | 280.56 | 277.86 | 276.64 | 484.85 | 478.62 | 482.89 | 4.6728 | 3.762 | 5.3508 | 4.1389 | 1.429 | 1.426 | 1.425 | 1.503 | 1.44 | 1.378 | Over-range | 60 | 1086 | 718 | 1454 | 3258 | - - - | - - - | - - - | - - - | 1086 | 718 | 1454 | 3258 | 716 | 726 | 23 | 1466 | - - - | - - - | - - - | - - - | 716 | 726 | 23 | 1466 | 1309 | 1040 | 1480 | 3830 | # # # | # # # | # # # | # # # | 0.829 | 0.69 | 0.983 | 0.851 | # # # | # # # | # # # | - - - | 0.836 | 0.699 | 0.999 | 0.862 | - - - | 0.45 | 1.61 | 1.51 | 1.43 | 1.46 | 1.43 | 1.48 | 10.39 | 16.4 | 18.16 | 0 | - - - | - - - | - - - | - - - | 1309 | 1040 | 1480 | 3830 | Over-range | 732 | 747 | 275 | 2012 | 150 | 175 | 267 | 1378 | 1089 | 716 | 1455 | 3259 | 1089 | 716 | 1455 | 3259 | - - - | - - - | - - - | - - -
5/3/2026 | 5:30:00 PM | 280.27 | 277.56 | 276.4 | 484.35 | 478.11 | 482.46 | 4.8693 | 4.0656 | 5.4707 | 4.1364 | 1.429 | 1.427 | 1.425 | 1.504 | 1.431 | 1.344 | Over-range | 60 | 1117 | 842 | 1487 | 3446 | - - - | - - - | - - - | - - - | 1117 | 842 | 1487 | 3446 | 766 | 721 | -31 | 1456 | - - - | - - - | - - - | - - - | 766 | 721 | -31 | 1456 | 1364 | 1125 | 1512 | 4001 | # # # | # # # | # # # | # # # | 0.819 | 0.748 | 0.984 | 0.861 | # # # | # # # | # # # | - - - | 0.825 | 0.757 | 0.999 | 0.871 | - - - | 0.423 | 1.61 | 1.52 | 1.47 | 1.47 | 1.45 | 1.49 | 9.92 | 15.25 | 17.66 | 0 | - - - | - - - | - - - | - - - | 1364 | 1125 | 1512 | 4001 | Over-range | 782 | 742 | 273 | 2031 | 153 | 175 | 266 | 1416 | 1119 | 840 | 1488 | 3448 | 1119 | 840 | 1488 | 3448 | - - - | - - - | - - - | - - -
5/3/2026 | 5:45:00 PM | 280.38 | 277.78 | 276.6 | 484.63 | 478.53 | 482.68 | 5.5192 | 5.0587 | 5.804 | 4.1257 | 1.429 | 1.427 | 1.425 | 1.509 | 1.446 | 1.295 | Over-range | 60 | 1228 | 1190 | 1572 | 3989 | - - - | - - - | - - - | - - - | 1228 | 1190 | 1572 | 3989 | 924 | 720 | -164 | 1479 | - - - | - - - | - - - | - - - | 924 | 720 | -164 | 1479 | 1545 | 1403 | 1605 | 4553 | # # # | # # # | # # # | # # # | 0.795 | 0.848 | 0.979 | 0.876 | # # # | # # # | # # # | - - - | 0.792 | 0.841 | 0.973 | 0.871 | - - - | 0.371 | 1.62 | 1.5 | 1.45 | 1.47 | 1.44 | 1.49 | 8.94 | 12.91 | 17.17 | 0 | - - - | - - - | - - - | - - - | 1545 | 1403 | 1605 | 4553 | Over-range | 938 | 742 | 325 | 2195 | 157 | 179 | 271 | 1617 | 1240 | 1206 | 1598 | 4044 | 1240 | 1206 | 1598 | 4044 | - - - | - - - | - - - | - - -
5/3/2026 | 6:00:00 PM | 280.1 | 277.51 | 276.27 | 484.13 | 478.05 | 482.14 | 5.2178 | 4.654 | 5.6684 | 4.1393 | 1.429 | 1.426 | 1.425 | 1.508 | 1.434 | 1.299 | Over-range | 60 | 1173 | 1053 | 1537 | 3762 | - - - | - - - | - - - | - - - | 1173 | 1053 | 1537 | 3762 | 857 | 717 | -126 | 1447 | - - - | - - - | - - - | - - - | 857 | 717 | -126 | 1447 | 1460 | 1288 | 1566 | 4314 | # # # | # # # | # # # | # # # | 0.803 | 0.818 | 0.982 | 0.872 | # # # | # # # | # # # | - - - | 0.808 | 0.825 | 0.996 | 0.881 | - - - | 0.385 | 1.62 | 1.52 | 1.47 | 1.47 | 1.45 | 1.49 | 9.26 | 13.53 | 17.18 | 0 | - - - | - - - | - - - | - - - | 1460 | 1288 | 1566 | 4314 | Over-range | 870 | 738 | 299 | 2111 | 154 | 175 | 267 | 1536 | 1174 | 1053 | 1536 | 3763 | 1174 | 1053 | 1536 | 3763 | - - - | - - - | - - - | - - -
5/3/2026 | 6:15:00 PM | 280.3 | 277.38 | 276.19 | 484.3 | 477.64 | 482.36 | 4.9033 | 4.0984 | 5.4801 | 4.1344 | 1.428 | 1.426 | 1.424 | 1.504 | 1.431 | 1.337 | Over-range | 60 | 1124 | 864 | 1490 | 3478 | - - - | - - - | - - - | - - - | 1124 | 864 | 1490 | 3478 | 775 | 719 | -44 | 1450 | - - - | - - - | - - - | - - - | 775 | 719 | -44 | 1450 | 1374 | 1137 | 1514 | 4025 | # # # | # # # | # # # | # # # | 0.818 | 0.76 | 0.984 | 0.864 | # # # | # # # | # # # | - - - | 0.823 | 0.769 | 0.999 | 0.874 | - - - | 0.417 | 1.59 | 1.5 | 1.46 | 1.45 | 1.45 | 1.47 | 9.82 | 14.71 | 17.48 | 0 | - - - | - - - | - - - | - - - | 1374 | 1137 | 1514 | 4025 | Over-range | 791 | 738 | 267 | 2025 | 154 | 168 | 263 | 1413 | 1124 | 865 | 1489 | 3478 | 1124 | 865 | 1489 | 3478 | - - - | - - - | - - - | - - -
5/3/2026 | 6:30:00 PM | 280.52 | 277.63 | 276.35 | 484.74 | 478.01 | 482.65 | 5.2488 | 4.708 | 5.6697 | 4.1296 | 1.428 | 1.426 | 1.424 | 1.513 | 1.432 | 1.296 | Over-range | 60 | 1179 | 1072 | 1537 | 3788 | - - - | - - - | - - - | - - - | 1179 | 1072 | 1537 | 3788 | 867 | 719 | -135 | 1450 | - - - | - - - | - - - | - - - | 867 | 719 | -135 | 1450 | 1472 | 1305 | 1567 | 4343 | # # # | # # # | # # # | # # # | 0.801 | 0.822 | 0.981 | 0.872 | # # # | # # # | # # # | - - - | 0.805 | 0.829 | 0.996 | 0.881 | - - - | 0.383 | 1.58 | 1.49 | 1.44 | 1.44 | 1.43 | 1.45 | 9.23 | 13.52 | 17.31 | 0 | - - - | - - - | - - - | - - - | 1472 | 1305 | 1567 | 4343 | Over-range | 881 | 741 | 304 | 2124 | 159 | 179 | 269 | 1552 | 1179 | 1071 | 1538 | 3789 | 1179 | 1071 | 1538 | 3789 | - - - | - - - | - - - | - - -
5/3/2026 | 6:45:00 PM | 280.41 | 277.52 | 276.25 | 484.49 | 477.86 | 482.49 | 5.2636 | 4.7271 | 5.6962 | 4.1351 | 1.428 | 1.426 | 1.424 | 1.515 | 1.432 | 1.288 | Over-range | 59.99 | 1181 | 1082 | 1544 | 3807 | - - - | - - - | - - - | - - - | 1181 | 1082 | 1544 | 3807 | 871 | 718 | -138 | 1450 | - - - | - - - | - - - | - - - | 871 | 718 | -138 | 1450 | 1476 | 1311 | 1574 | 4360 | # # # | # # # | # # # | # # # | 0.8 | 0.825 | 0.981 | 0.873 | # # # | # # # | # # # | - - - | 0.805 | 0.833 | 0.996 | 0.882 | - - - | 0.381 | 1.57 | 1.49 | 1.43 | 1.43 | 1.43 | 1.44 | 9.18 | 13.37 | 17.13 | 0 | - - - | - - - | - - - | - - - | 1476 | 1311 | 1574 | 4360 | Over-range | 885 | 740 | 302 | 2126 | 159 | 178 | 267 | 1555 | 1182 | 1081 | 1546 | 3808 | 1182 | 1081 | 1546 | 3808 | - - - | - - - | - - - | - - -
5/3/2026 | 7:00:00 PM | 280.83 | 277.99 | 276.66 | 485.36 | 478.59 | 483.15 | 4.4678 | 3.4914 | 5.2448 | 4.14 | 1.428 | 1.426 | 1.424 | 1.5 | 1.458 | 1.411 | Over-range | 60 | 1051 | 584 | 1421 | 3056 | - - - | - - - | - - - | - - - | 1051 | 584 | 1421 | 3056 | 660 | 729 | 82 | 1471 | - - - | - - - | - - - | - - - | 660 | 729 | 82 | 1471 | 1251 | 961 | 1450 | 3663 | # # # | # # # | # # # | # # # | 0.84 | 0.607 | 0.98 | 0.834 | # # # | # # # | # # # | - - - | 0.846 | 0.616 | 0.996 | 0.845 | - - - | 0.481 | 1.57 | 1.49 | 1.42 | 1.43 | 1.42 | 1.44 | 11.02 | 17.19 | 18.2 | 0 | - - - | - - - | - - - | - - - | 1251 | 961 | 1450 | 3663 | Over-range | 677 | 749 | 290 | 2014 | 153 | 168 | 264 | 1375 | 1052 | 583 | 1423 | 3058 | 1052 | 583 | 1423 | 3058 | - - - | - - - | - - - | - - -
5/3/2026 | 7:15:00 PM | 280.75 | 278.05 | 276.59 | 485.37 | 478.6 | 482.95 | 4.8081 | 3.961 | 5.4373 | 4.1425 | 1.428 | 1.426 | 1.424 | 1.507 | 1.43 | 1.355 | Over-range | 60 | 1109 | 803 | 1479 | 3391 | - - - | - - - | - - - | - - - | 1109 | 803 | 1479 | 3391 | 753 | 728 | -13 | 1467 | - - - | - - - | - - - | - - - | 753 | 728 | -13 | 1467 | 1349 | 1099 | 1504 | 3953 | # # # | # # # | # # # | # # # | 0.822 | 0.731 | 0.984 | 0.858 | # # # | # # # | # # # | - - - | 0.827 | 0.739 | 0.999 | 0.868 | - - - | 0.433 | 1.56 | 1.5 | 1.38 | 1.43 | 1.4 | 1.42 | 10.1 | 15.71 | 17.92 | 0 | - - - | - - - | - - - | - - - | 1349 | 1099 | 1504 | 3953 | Over-range | 769 | 749 | 271 | 2030 | 157 | 173 | 268 | 1403 | 1108 | 803 | 1480 | 3391 | 1108 | 803 | 1480 | 3391 | - - - | - - - | - - - | - - -
5/3/2026 | 7:30:00 PM | 280.87 | 278.1 | 276.66 | 485.52 | 478.72 | 483.09 | 4.9277 | 4.0143 | 5.4563 | 4.1399 | 1.428 | 1.426 | 1.424 | 1.501 | 1.428 | 1.359 | Over-range | 59.99 | 1134 | 827 | 1483 | 3444 | - - - | - - - | - - - | - - - | 1134 | 827 | 1483 | 3444 | 772 | 729 | -3 | 1498 | - - - | - - - | - - - | - - - | 772 | 729 | -3 | 1498 | 1382 | 1116 | 1509 | 4007 | # # # | # # # | # # # | # # # | 0.821 | 0.741 | 0.983 | 0.86 | # # # | # # # | # # # | - - - | 0.818 | 0.744 | 0.99 | 0.862 | - - - | 0.435 | 1.57 | 1.51 | 1.41 | 1.44 | 1.42 | 1.44 | 9.89 | 15.37 | 17.95 | 0 | - - - | - - - | - - - | - - - | 1382 | 1116 | 1509 | 4007 | Over-range | 789 | 750 | 278 | 2048 | 158 | 174 | 270 | 1392 | 1144 | 832 | 1495 | 3471 | 1144 | 832 | 1495 | 3471 | - - - | - - - | - - - | - - -
5/3/2026 | 7:45:00 PM | 281.26 | 278.6 | 277.11 | 486.28 | 479.61 | 483.79 | 5.3501 | 5.6966 | 5.7557 | 3.2848 | 1.428 | 1.426 | 1.424 | 1.514 | 1.459 | 1.288 | Over-range | 60 | 1195 | 1408 | 1563 | 4166 | - - - | - - - | - - - | - - - | 1195 | 1408 | 1563 | 4166 | 900 | 648 | -151 | 1396 | - - - | - - - | - - - | - - - | 900 | 648 | -151 | 1396 | 1504 | 1570 | 1595 | 4669 | # # # | # # # | # # # | # # # | 0.795 | 0.897 | 0.98 | 0.892 | # # # | # # # | # # # | - - - | 0.799 | 0.902 | 0.995 | 0.9 | - - - | 0.335 | 1.54 | 1.48 | 1.42 | 1.43 | 1.41 | 1.42 | 9.17 | 10.16 | 17.32 | 0 | - - - | - - - | - - - | - - - | 1504 | 1570 | 1595 | 4669 | Over-range | 913 | 667 | 315 | 2101 | 154 | 158 | 273 | 1569 | 1197 | 1409 | 1560 | 4166 | 1197 | 1409 | 1560 | 4166 | - - - | - - - | - - - | - - -
5/3/2026 | 8:00:00 PM | 281.34 | 278.71 | 277.28 | 486.41 | 479.88 | 484.02 | 5.1235 | 5.5679 | 5.6028 | 2.7109 | 1.428 | 1.426 | 1.424 | 1.51 | 1.465 | 1.313 | Over-range | 60.01 | 1159 | 1414 | 1525 | 4098 | - - - | - - - | - - - | - - - | 1159 | 1414 | 1525 | 4098 | 842 | 610 | -90 | 1360 | - - - | - - - | - - - | - - - | 842 | 610 | -90 | 1360 | 1440 | 1548 | 1553 | 4541 | # # # | # # # | # # # | # # # | 0.804 | 0.914 | 0.982 | 0.903 | # # # | # # # | # # # | - - - | 0.81 | 0.918 | 0.997 | 0.91 | - - - | 0.332 | 1.56 | 1.51 | 1.42 | 1.44 | 1.42 | 1.43 | 9.57 | 8.87 | 17.68 | 0 | - - - | - - - | - - - | - - - | 1440 | 1548 | 1553 | 4541 | Over-range | 855 | 627 | 291 | 1956 | 151 | 145 | 272 | 1403 | 1162 | 1413 | 1523 | 4099 | 1162 | 1413 | 1523 | 4099 | - - - | - - - | - - - | - - -
5/3/2026 | 8:15:00 PM | 281.61 | 278.98 | 277.37 | 486.97 | 480.13 | 484.27 | 4.9276 | 5.1622 | 5.5121 | 2.7321 | 1.428 | 1.426 | 1.424 | 1.508 | 1.454 | 1.339 | Over-range | 59.99 | 1128 | 1293 | 1504 | 3926 | - - - | - - - | - - - | - - - | 1128 | 1293 | 1504 | 3926 | 793 | 618 | -36 | 1374 | - - - | - - - | - - - | - - - | 793 | 618 | -36 | 1374 | 1388 | 1440 | 1529 | 4356 | # # # | # # # | # # # | # # # | 0.813 | 0.898 | 0.984 | 0.901 | # # # | # # # | # # # | - - - | 0.818 | 0.902 | 1 | 0.909 | - - - | 0.35 | 1.56 | 1.5 | 1.41 | 1.43 | 1.42 | 1.42 | 9.96 | 9.44 | 17.83 | 0 | - - - | - - - | - - - | - - - | 1388 | 1440 | 1529 | 4356 | Over-range | 808 | 634 | 273 | 1889 | 155 | 139 | 271 | 1296 | 1129 | 1295 | 1502 | 3926 | 1129 | 1295 | 1502 | 3926 | - - - | - - - | - - - | - - -
5/3/2026 | 8:30:00 PM | 281.7 | 278.94 | 277.4 | 487.01 | 480.11 | 484.4 | 5.3097 | 5.9148 | 5.7144 | 2.725 | 1.428 | 1.426 | 1.423 | 1.515 | 1.475 | 1.289 | Over-range | 59.99 | 1189 | 1522 | 1554 | 4266 | - - - | - - - | - - - | - - - | 1189 | 1522 | 1554 | 4266 | 892 | 615 | -138 | 1368 | - - - | - - - | - - - | - - - | 892 | 615 | -138 | 1368 | 1495 | 1648 | 1585 | 4729 | # # # | # # # | # # # | # # # | 0.795 | 0.924 | 0.981 | 0.902 | # # # | # # # | # # # | - - - | 0.8 | 0.928 | 0.996 | 0.91 | - - - | 0.321 | 1.55 | 1.49 | 1.4 | 1.43 | 1.41 | 1.41 | 9.26 | 8.56 | 17.54 | 0 | - - - | - - - | - - - | - - - | 1495 | 1648 | 1585 | 4729 | Over-range | 906 | 631 | 310 | 2040 | 158 | 145 | 275 | 1512 | 1190 | 1525 | 1552 | 4266 | 1190 | 1525 | 1552 | 4266 | - - - | - - - | - - - | - - -
5/3/2026 | 8:45:00 PM | 281.39 | 278.57 | 276.98 | 486.49 | 479.33 | 483.79 | 5.0717 | 5.4844 | 5.5896 | 2.7269 | 1.428 | 1.426 | 1.423 | 1.51 | 1.48 | 1.321 | Over-range | 59.99 | 1148 | 1365 | 1516 | 4029 | - - - | - - - | - - - | - - - | 1148 | 1365 | 1516 | 4029 | 822 | 612 | -71 | 1362 | - - - | - - - | - - - | - - - | 822 | 612 | -71 | 1362 | 1421 | 1509 | 1547 | 4477 | # # # | # # # | # # # | # # # | 0.807 | 0.904 | 0.98 | 0.9 | # # # | # # # | # # # | - - - | 0.812 | 0.909 | 0.995 | 0.908 | - - - | 0.338 | 1.58 | 1.49 | 1.4 | 1.43 | 1.42 | 1.43 | 9.78 | 9.33 | 17.58 | 0 | - - - | - - - | - - - | - - - | 1421 | 1509 | 1547 | 4477 | Over-range | 837 | 628 | 305 | 1951 | 155 | 141 | 270 | 1389 | 1148 | 1367 | 1513 | 4029 | 1148 | 1367 | 1513 | 4029 | - - - | - - - | - - - | - - -
5/3/2026 | 9:00:00 PM | 281.67 | 278.96 | 277.28 | 487.12 | 479.97 | 484.2 | 4.5198 | 4.3758 | 5.2824 | 2.7351 | 1.428 | 1.426 | 1.423 | 1.501 | 1.437 | 1.401 | Over-range | 60.01 | 1062 | 1037 | 1437 | 3537 | - - - | - - - | - - - | - - - | 1062 | 1037 | 1437 | 3537 | 684 | 620 | 74 | 1377 | - - - | - - - | - - - | - - - | 684 | 620 | 74 | 1377 | 1272 | 1218 | 1465 | 3955 | # # # | # # # | # # # | # # # | 0.835 | 0.852 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.842 | 0.857 | 0.998 | 0.904 | - - - | 0.389 | 1.56 | 1.48 | 1.4 | 1.43 | 1.4 | 1.41 | 10.92 | 10.9 | 18.31 | 0 | - - - | - - - | - - - | - - - | 1272 | 1218 | 1465 | 3955 | Over-range | 700 | 635 | 281 | 1769 | 152 | 138 | 268 | 1109 | 1065 | 1036 | 1437 | 3538 | 1065 | 1036 | 1437 | 3538 | - - - | - - - | - - - | - - -
5/3/2026 | 9:15:00 PM | 281.69 | 279.05 | 277.42 | 487.13 | 480.26 | 484.35 | 4.7047 | 4.7213 | 5.3883 | 2.7419 | 1.428 | 1.426 | 1.424 | 1.504 | 1.436 | 1.373 | Over-range | 60.01 | 1092 | 1152 | 1470 | 3715 | - - - | - - - | - - - | - - - | 1092 | 1152 | 1470 | 3715 | 734 | 619 | 25 | 1379 | - - - | - - - | - - - | - - - | 734 | 619 | 25 | 1379 | 1325 | 1316 | 1495 | 4136 | # # # | # # # | # # # | # # # | 0.825 | 0.875 | 0.983 | 0.898 | # # # | # # # | # # # | - - - | 0.831 | 0.88 | 1 | 0.907 | - - - | 0.371 | 1.58 | 1.53 | 1.43 | 1.45 | 1.43 | 1.45 | 10.43 | 10.2 | 18.09 | 0 | - - - | - - - | - - - | - - - | 1325 | 1316 | 1495 | 4136 | Over-range | 750 | 635 | 272 | 1819 | 150 | 141 | 269 | 1185 | 1096 | 1151 | 1469 | 3716 | 1096 | 1151 | 1469 | 3716 | - - - | - - - | - - - | - - -
5/3/2026 | 9:30:00 PM | 282.15 | 279.52 | 277.85 | 487.99 | 480.98 | 485.12 | 4.7826 | 4.8682 | 5.416 | 2.7362 | 1.428 | 1.427 | 1.424 | 1.506 | 1.44 | 1.366 | Over-range | 60.02 | 1106 | 1200 | 1480 | 3785 | - - - | - - - | - - - | - - - | 1106 | 1200 | 1480 | 3785 | 758 | 625 | 7 | 1390 | - - - | - - - | - - - | - - - | 758 | 625 | 7 | 1390 | 1349 | 1360 | 1505 | 4214 | # # # | # # # | # # # | # # # | 0.82 | 0.882 | 0.983 | 0.898 | # # # | # # # | # # # | - - - | 0.826 | 0.887 | 0.999 | 0.907 | - - - | 0.367 | 1.61 | 1.52 | 1.43 | 1.46 | 1.43 | 1.46 | 10.31 | 10.06 | 18.22 | 0 | - - - | - - - | - - - | - - - | 1349 | 1360 | 1505 | 4214 | Over-range | 773 | 641 | 274 | 1853 | 152 | 143 | 273 | 1225 | 1109 | 1199 | 1477 | 3786 | 1109 | 1199 | 1477 | 3786 | - - - | - - - | - - - | - - -
5/3/2026 | 9:45:00 PM | 282.65 | 279.9 | 278.26 | 488.78 | 481.59 | 485.94 | 5.2843 | 5.853 | 5.7185 | 2.7397 | 1.428 | 1.427 | 1.423 | 1.515 | 1.471 | 1.292 | Over-range | 60.02 | 1187 | 1505 | 1562 | 4253 | - - - | - - - | - - - | - - - | 1187 | 1505 | 1562 | 4253 | 892 | 627 | -122 | 1396 | - - - | - - - | - - - | - - - | 892 | 627 | -122 | 1396 | 1493 | 1637 | 1591 | 4721 | # # # | # # # | # # # | # # # | 0.795 | 0.919 | 0.982 | 0.901 | # # # | # # # | # # # | - - - | 0.799 | 0.923 | 0.997 | 0.908 | - - - | 0.328 | 1.58 | 1.52 | 1.41 | 1.45 | 1.43 | 1.45 | 9.41 | 8.78 | 17.55 | 0 | - - - | - - - | - - - | - - - | 1493 | 1637 | 1591 | 4721 | Over-range | 906 | 644 | 304 | 2050 | 161 | 147 | 277 | 1501 | 1187 | 1505 | 1561 | 4253 | 1187 | 1505 | 1561 | 4253 | - - - | - - - | - - - | - - -
5/3/2026 | 10:00:00 PM | 282.9 | 280.14 | 278.44 | 489.19 | 481.99 | 486.31 | 5.1571 | 5.4142 | 5.593 | 2.7414 | 1.428 | 1.426 | 1.423 | 1.507 | 1.455 | 1.335 | Over-range | 60.02 | 1174 | 1371 | 1529 | 4075 | - - - | - - - | - - - | - - - | 1174 | 1371 | 1529 | 4075 | 848 | 630 | -38 | 1439 | - - - | - - - | - - - | - - - | 848 | 630 | -38 | 1439 | 1457 | 1516 | 1557 | 4530 | # # # | # # # | # # # | # # # | 0.806 | 0.904 | 0.982 | 0.899 | # # # | # # # | # # # | - - - | 0.803 | 0.901 | 0.988 | 0.899 | - - - | 0.353 | 1.6 | 1.53 | 1.43 | 1.46 | 1.44 | 1.46 | 9.71 | 9.26 | 17.91 | 0 | - - - | - - - | - - - | - - - | 1457 | 1516 | 1557 | 4530 | Over-range | 862 | 647 | 291 | 1980 | 156 | 148 | 277 | 1354 | 1191 | 1389 | 1552 | 4132 | 1191 | 1389 | 1552 | 4132 | - - - | - - - | - - - | - - -
5/3/2026 | 10:15:00 PM | 283.33 | 280.4 | 278.77 | 489.84 | 482.36 | 487.04 | 4.4571 | 4.2585 | 5.278 | 2.7534 | 1.428 | 1.427 | 1.423 | 1.499 | 1.457 | 1.418 | Over-range | 60 | 1052 | 986 | 1440 | 3477 | - - - | - - - | - - - | - - - | 1052 | 986 | 1440 | 3477 | 677 | 639 | 111 | 1426 | - - - | - - - | - - - | - - - | 677 | 639 | 111 | 1426 | 1261 | 1187 | 1471 | 3918 | # # # | # # # | # # # | # # # | 0.834 | 0.831 | 0.979 | 0.887 | # # # | # # # | # # # | - - - | 0.841 | 0.836 | 0.996 | 0.897 | - - - | 0.41 | 1.65 | 1.55 | 1.46 | 1.5 | 1.48 | 1.5 | 11.42 | 11.69 | 18.5 | 0 | - - - | - - - | - - - | - - - | 1261 | 1187 | 1471 | 3918 | Over-range | 694 | 655 | 300 | 1805 | 154 | 143 | 271 | 1104 | 1055 | 984 | 1439 | 3478 | 1055 | 984 | 1439 | 3478 | - - - | - - - | - - - | - - -
5/3/2026 | 10:30:00 PM | 283.62 | 280.73 | 279.06 | 490.4 | 482.9 | 487.52 | 4.6719 | 4.6523 | 5.3664 | 2.7424 | 1.428 | 1.427 | 1.423 | 1.506 | 1.429 | 1.388 | Over-range | 60.02 | 1088 | 1128 | 1471 | 3687 | - - - | - - - | - - - | - - - | 1088 | 1128 | 1471 | 3687 | 738 | 640 | 49 | 1427 | - - - | - - - | - - - | - - - | 738 | 640 | 49 | 1427 | 1325 | 1305 | 1498 | 4128 | # # # | # # # | # # # | # # # | 0.822 | 0.864 | 0.982 | 0.893 | # # # | # # # | # # # | - - - | 0.828 | 0.869 | 0.999 | 0.903 | - - - | 0.387 | 1.69 | 1.56 | 1.47 | 1.5 | 1.49 | 1.52 | 10.8 | 10.83 | 18.63 | 0 | - - - | - - - | - - - | - - - | 1325 | 1305 | 1498 | 4128 | Over-range | 755 | 657 | 283 | 1856 | 160 | 146 | 278 | 1186 | 1090 | 1125 | 1473 | 3688 | 1090 | 1125 | 1473 | 3688 | - - - | - - - | - - - | - - -
5/3/2026 | 10:45:00 PM | 283.94 | 281.04 | 279.29 | 490.94 | 483.42 | 487.96 | 4.6925 | 4.6849 | 5.3962 | 2.7559 | 1.427 | 1.426 | 1.422 | 1.507 | 1.422 | 1.383 | Over-range | 60.02 | 1092 | 1139 | 1481 | 3711 | - - - | - - - | - - - | - - - | 1092 | 1139 | 1481 | 3711 | 746 | 645 | 47 | 1438 | - - - | - - - | - - - | - - - | 746 | 645 | 47 | 1438 | 1332 | 1317 | 1507 | 4156 | # # # | # # # | # # # | # # # | 0.82 | 0.865 | 0.982 | 0.893 | # # # | # # # | # # # | - - - | 0.826 | 0.87 | 0.999 | 0.902 | - - - | 0.388 | 1.66 | 1.54 | 1.44 | 1.48 | 1.47 | 1.49 | 10.82 | 10.77 | 18.52 | 0 | - - - | - - - | - - - | - - - | 1332 | 1317 | 1507 | 4156 | Over-range | 763 | 661 | 282 | 1871 | 161 | 146 | 278 | 1197 | 1093 | 1136 | 1483 | 3712 | 1093 | 1136 | 1483 | 3712 | - - - | - - - | - - - | - - -
5/3/2026 | 11:00:00 PM | 284.25 | 281.2 | 279.5 | 491.41 | 483.62 | 488.45 | 4.8881 | 5.0676 | 5.4803 | 2.7442 | 1.428 | 1.427 | 1.422 | 1.511 | 1.437 | 1.357 | Over-range | 60.02 | 1124 | 1256 | 1505 | 3885 | - - - | - - - | - - - | - - - | 1124 | 1256 | 1505 | 3885 | 798 | 647 | -3 | 1441 | - - - | - - - | - - - | - - - | 798 | 647 | -3 | 1441 | 1389 | 1422 | 1532 | 4342 | # # # | # # # | # # # | # # # | 0.809 | 0.884 | 0.982 | 0.895 | # # # | # # # | # # # | - - - | 0.815 | 0.889 | 0.999 | 0.904 | - - - | 0.371 | 1.65 | 1.53 | 1.46 | 1.48 | 1.47 | 1.5 | 10.44 | 10.23 | 18.55 | 0 | - - - | - - - | - - - | - - - | 1389 | 1422 | 1532 | 4342 | Over-range | 815 | 663 | 286 | 1939 | 165 | 147 | 282 | 1295 | 1123 | 1256 | 1506 | 3885 | 1123 | 1256 | 1506 | 3885 | - - - | - - - | - - - | - - -
5/3/2026 | 11:15:00 PM | 284.04 | 280.99 | 279.32 | 491.02 | 483.29 | 488.13 | 5.2002 | 5.6711 | 5.6634 | 2.7416 | 1.428 | 1.427 | 1.422 | 1.513 | 1.457 | 1.307 | Over-range | 60 | 1174 | 1449 | 1554 | 4177 | - - - | - - - | - - - | - - - | 1174 | 1449 | 1554 | 4177 | 881 | 642 | -87 | 1436 | - - - | - - - | - - - | - - - | 881 | 642 | -87 | 1436 | 1477 | 1592 | 1582 | 4651 | # # # | # # # | # # # | # # # | 0.795 | 0.91 | 0.983 | 0.898 | # # # | # # # | # # # | - - - | 0.799 | 0.914 | 0.998 | 0.906 | - - - | 0.344 | 1.67 | 1.56 | 1.51 | 1.51 | 1.51 | 1.54 | 9.77 | 9.18 | 17.9 | 0 | - - - | - - - | - - - | - - - | 1477 | 1592 | 1582 | 4651 | Over-range | 896 | 659 | 295 | 2045 | 163 | 147 | 280 | 1456 | 1173 | 1451 | 1552 | 4177 | 1173 | 1451 | 1552 | 4177 | - - - | - - - | - - - | - - -
5/3/2026 | 11:30:00 PM | 284.23 | 281.21 | 279.61 | 491.29 | 483.83 | 488.54 | 4.5789 | 4.5012 | 5.3478 | 2.7558 | 1.427 | 1.426 | 1.422 | 1.501 | 1.461 | 1.401 | Over-range | 60.02 | 1072 | 1056 | 1463 | 3590 | - - - | - - - | - - - | - - - | 1072 | 1056 | 1463 | 3590 | 713 | 650 | 87 | 1449 | - - - | - - - | - - - | - - - | 713 | 650 | 87 | 1449 | 1298 | 1253 | 1495 | 4046 | # # # | # # # | # # # | # # # | 0.826 | 0.842 | 0.979 | 0.887 | # # # | # # # | # # # | - - - | 0.832 | 0.848 | 0.996 | 0.897 | - - - | 0.404 | 1.67 | 1.55 | 1.51 | 1.51 | 1.51 | 1.54 | 11.31 | 11.45 | 18.52 | 0 | - - - | - - - | - - - | - - - | 1298 | 1253 | 1495 | 4046 | Over-range | 731 | 665 | 303 | 1863 | 159 | 142 | 275 | 1165 | 1072 | 1057 | 1461 | 3590 | 1072 | 1057 | 1461 | 3590 | - - - | - - - | - - - | - - -
5/3/2026 | 11:45:00 PM | 284.77 | 281.8 | 280.18 | 492.31 | 484.8 | 489.47 | 4.6185 | 4.5527 | 5.3651 | 2.755 | 1.428 | 1.427 | 1.423 | 1.504 | 1.434 | 1.395 | Over-range | 60.02 | 1080 | 1089 | 1474 | 3643 | - - - | - - - | - - - | - - - | 1080 | 1089 | 1474 | 3643 | 731 | 656 | 77 | 1464 | - - - | - - - | - - - | - - - | 731 | 656 | 77 | 1464 | 1315 | 1281 | 1503 | 4098 | # # # | # # # | # # # | # # # | 0.821 | 0.85 | 0.981 | 0.889 | # # # | # # # | # # # | - - - | 0.828 | 0.855 | 0.998 | 0.898 | - - - | 0.402 | 1.66 | 1.56 | 1.51 | 1.51 | 1.5 | 1.54 | 11.19 | 11.24 | 18.73 | 0 | - - - | - - - | - - - | - - - | 1315 | 1281 | 1503 | 4098 | Over-range | 750 | 672 | 293 | 1877 | 163 | 146 | 280 | 1173 | 1080 | 1088 | 1475 | 3644 | 1080 | 1088 | 1475 | 3644 | - - - | - - - | - - - | - - -
5/4/2026 | 12:00:00 AM | 285.04 | 282.01 | 280.54 | 492.67 | 485.3 | 490.08 | 4.6461 | 4.5945 | 5.3626 | 2.7502 | 1.427 | 1.425 | 1.421 | 1.504 | 1.424 | 1.396 | Over-range | 60.02 | 1085 | 1105 | 1476 | 3666 | - - - | - - - | - - - | - - - | 1085 | 1105 | 1476 | 3666 | 742 | 660 | 72 | 1474 | - - - | - - - | - - - | - - - | 742 | 660 | 72 | 1474 | 1324 | 1296 | 1504 | 4124 | # # # | # # # | # # # | # # # | 0.819 | 0.853 | 0.981 | 0.889 | # # # | # # # | # # # | - - - | 0.826 | 0.859 | 0.999 | 0.899 | - - - | 0.402 | 1.67 | 1.59 | 1.48 | 1.5 | 1.51 | 1.54 | 11.1 | 11.18 | 18.9 | 0 | - - - | - - - | - - - | - - - | 1324 | 1296 | 1504 | 4124 | Over-range | 760 | 676 | 291 | 1890 | 160 | 148 | 282 | 1183 | 1087 | 1105 | 1475 | 3666 | 1087 | 1105 | 1475 | 3666 | - - - | - - - | - - - | - - -
5/4/2026 | 12:15:00 AM | 285.14 | 281.99 | 280.43 | 492.79 | 485.15 | 490.06 | 4.8559 | 4.9943 | 5.4848 | 2.7567 | 1.427 | 1.425 | 1.422 | 1.509 | 1.425 | 1.364 | Over-range | 59.99 | 1118 | 1232 | 1511 | 3861 | - - - | - - - | - - - | - - - | 1118 | 1232 | 1511 | 3861 | 798 | 659 | 17 | 1474 | - - - | - - - | - - - | - - - | 798 | 659 | 17 | 1474 | 1384 | 1406 | 1538 | 4328 | # # # | # # # | # # # | # # # | 0.808 | 0.876 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.814 | 0.881 | 0.999 | 0.901 | - - - | 0.382 | 1.69 | 1.56 | 1.51 | 1.52 | 1.52 | 1.54 | 10.68 | 10.57 | 18.64 | 0 | - - - | - - - | - - - | - - - | 1384 | 1406 | 1538 | 4328 | Over-range | 815 | 676 | 288 | 1955 | 167 | 148 | 285 | 1283 | 1117 | 1233 | 1511 | 3861 | 1117 | 1233 | 1511 | 3861 | - - - | - - - | - - - | - - -
5/4/2026 | 12:30:00 AM | 285.15 | 282.02 | 280.47 | 492.86 | 485.16 | 490.12 | 5.1581 | 5.3879 | 5.6114 | 2.7502 | 1.427 | 1.425 | 1.421 | 1.508 | 1.437 | 1.344 | Over-range | 60.01 | 1176 | 1360 | 1544 | 4080 | - - - | - - - | - - - | - - - | 1176 | 1360 | 1544 | 4080 | 862 | 658 | -13 | 1506 | - - - | - - - | - - - | - - - | 862 | 658 | -13 | 1506 | 1469 | 1518 | 1574 | 4560 | # # # | # # # | # # # | # # # | 0.801 | 0.896 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.799 | 0.893 | 0.984 | 0.894 | - - - | 0.369 | 1.69 | 1.56 | 1.49 | 1.51 | 1.52 | 1.54 | 10.06 | 9.78 | 18.25 | 0 | - - - | - - - | - - - | - - - | 1469 | 1518 | 1574 | 4560 | Over-range | 879 | 674 | 300 | 2036 | 169 | 148 | 286 | 1361 | 1185 | 1370 | 1560 | 4115 | 1185 | 1370 | 1560 | 4115 | - - - | - - - | - - - | - - -
5/4/2026 | 12:45:00 AM | 285.37 | 282.36 | 280.76 | 493.36 | 485.76 | 490.5 | 4.5236 | 4.4019 | 5.3283 | 2.7558 | 1.427 | 1.426 | 1.421 | 1.499 | 1.467 | 1.415 | Over-range | 60 | 1062 | 1019 | 1462 | 3543 | - - - | - - - | - - - | - - - | 1062 | 1019 | 1462 | 3543 | 708 | 667 | 114 | 1490 | - - - | - - - | - - - | - - - | 708 | 667 | 114 | 1490 | 1288 | 1232 | 1495 | 4015 | # # # | # # # | # # # | # # # | 0.825 | 0.827 | 0.977 | 0.882 | # # # | # # # | # # # | - - - | 0.832 | 0.833 | 0.995 | 0.892 | - - - | 0.421 | 1.7 | 1.56 | 1.56 | 1.53 | 1.54 | 1.57 | 11.73 | 11.98 | 18.82 | 0 | - - - | - - - | - - - | - - - | 1288 | 1232 | 1495 | 4015 | Over-range | 728 | 683 | 315 | 1888 | 165 | 146 | 280 | 1156 | 1061 | 1020 | 1461 | 3543 | 1061 | 1020 | 1461 | 3543 | - - - | - - - | - - - | - - -
5/4/2026 | 1:00:00 AM | 285.5 | 282.36 | 280.77 | 493.47 | 485.75 | 490.65 | 4.631 | 4.5689 | 5.3733 | 2.7591 | 1.427 | 1.425 | 1.421 | 1.505 | 1.435 | 1.398 | Over-range | 60.01 | 1082 | 1092 | 1479 | 3652 | - - - | - - - | - - - | - - - | 1082 | 1092 | 1479 | 3652 | 741 | 665 | 82 | 1488 | - - - | - - - | - - - | - - - | 741 | 665 | 82 | 1488 | 1321 | 1288 | 1509 | 4118 | # # # | # # # | # # # | # # # | 0.819 | 0.848 | 0.98 | 0.887 | # # # | # # # | # # # | - - - | 0.825 | 0.854 | 0.999 | 0.897 | - - - | 0.407 | 1.69 | 1.58 | 1.52 | 1.52 | 1.53 | 1.55 | 11.3 | 11.37 | 18.85 | 0 | - - - | - - - | - - - | - - - | 1321 | 1288 | 1509 | 4118 | Over-range | 759 | 681 | 297 | 1901 | 162 | 147 | 283 | 1182 | 1083 | 1093 | 1477 | 3652 | 1083 | 1093 | 1477 | 3652 | - - - | - - - | - - - | - - -
5/4/2026 | 1:15:00 AM | 285.38 | 282.15 | 280.68 | 493.17 | 485.44 | 490.56 | 4.6062 | 4.5207 | 5.3577 | 2.7523 | 1.427 | 1.425 | 1.421 | 1.504 | 1.433 | 1.4 | Over-range | 60 | 1078 | 1079 | 1475 | 3632 | - - - | - - - | - - - | - - - | 1078 | 1079 | 1475 | 3632 | 734 | 663 | 87 | 1485 | - - - | - - - | - - - | - - - | 734 | 663 | 87 | 1485 | 1315 | 1275 | 1504 | 4094 | # # # | # # # | # # # | # # # | 0.82 | 0.846 | 0.981 | 0.887 | # # # | # # # | # # # | - - - | 0.827 | 0.852 | 0.998 | 0.897 | - - - | 0.409 | 1.73 | 1.59 | 1.54 | 1.55 | 1.56 | 1.58 | 11.34 | 11.37 | 18.74 | 0 | - - - | - - - | - - - | - - - | 1315 | 1275 | 1504 | 4094 | Over-range | 752 | 679 | 294 | 1889 | 165 | 147 | 281 | 1168 | 1078 | 1079 | 1476 | 3633 | 1078 | 1079 | 1476 | 3633 | - - - | - - - | - - - | - - -
5/4/2026 | 1:30:00 AM | 285.15 | 281.92 | 280.46 | 492.75 | 485.03 | 490.17 | 4.6785 | 4.6635 | 5.3914 | 2.7458 | 1.427 | 1.425 | 1.421 | 1.508 | 1.426 | 1.388 | Over-range | 60 | 1089 | 1126 | 1484 | 3700 | - - - | - - - | - - - | - - - | 1089 | 1126 | 1484 | 3700 | 751 | 659 | 65 | 1475 | - - - | - - - | - - - | - - - | 751 | 659 | 65 | 1475 | 1334 | 1314 | 1512 | 4159 | # # # | # # # | # # # | # # # | 0.817 | 0.857 | 0.981 | 0.889 | # # # | # # # | # # # | - - - | 0.823 | 0.863 | 0.999 | 0.899 | - - - | 0.399 | 1.69 | 1.59 | 1.53 | 1.53 | 1.55 | 1.56 | 11.09 | 11.06 | 18.71 | 0 | - - - | - - - | - - - | - - - | 1334 | 1314 | 1512 | 4159 | Over-range | 769 | 675 | 290 | 1901 | 166 | 146 | 281 | 1198 | 1089 | 1126 | 1486 | 3700 | 1089 | 1126 | 1486 | 3700 | - - - | - - - | - - - | - - -
5/4/2026 | 1:45:00 AM | 285.41 | 282.18 | 280.79 | 493.12 | 485.64 | 490.66 | 5.0549 | 5.4091 | 5.618 | 2.7452 | 1.427 | 1.425 | 1.421 | 1.514 | 1.437 | 1.333 | Over-range | 60.01 | 1151 | 1363 | 1550 | 4064 | - - - | - - - | - - - | - - - | 1151 | 1363 | 1550 | 4064 | 853 | 663 | -37 | 1479 | - - - | - - - | - - - | - - - | 853 | 663 | -37 | 1479 | 1442 | 1524 | 1577 | 4544 | # # # | # # # | # # # | # # # | 0.798 | 0.894 | 0.983 | 0.894 | # # # | # # # | # # # | - - - | 0.803 | 0.899 | 0.999 | 0.903 | - - - | 0.364 | 1.72 | 1.6 | 1.56 | 1.55 | 1.57 | 1.59 | 10.26 | 9.89 | 18.39 | 0 | - - - | - - - | - - - | - - - | 1442 | 1524 | 1577 | 4544 | Over-range | 869 | 681 | 293 | 2032 | 165 | 156 | 288 | 1393 | 1151 | 1365 | 1547 | 4064 | 1151 | 1365 | 1547 | 4064 | - - - | - - - | - - - | - - -
5/4/2026 | 2:00:00 AM | 285.71 | 282.52 | 281.07 | 493.76 | 486.11 | 491.16 | 4.8275 | 4.95 | 5.4686 | 2.7486 | 1.427 | 1.425 | 1.421 | 1.508 | 1.43 | 1.368 | Over-range | 60.01 | 1113 | 1212 | 1508 | 3834 | - - - | - - - | - - - | - - - | 1113 | 1212 | 1508 | 3834 | 795 | 665 | 32 | 1492 | - - - | - - - | - - - | - - - | 795 | 665 | 32 | 1492 | 1378 | 1393 | 1537 | 4308 | # # # | # # # | # # # | # # # | 0.808 | 0.87 | 0.982 | 0.89 | # # # | # # # | # # # | - - - | 0.814 | 0.876 | 0.999 | 0.899 | - - - | 0.389 | 1.72 | 1.57 | 1.56 | 1.54 | 1.56 | 1.57 | 10.92 | 10.7 | 18.58 | 0 | - - - | - - - | - - - | - - - | 1378 | 1393 | 1537 | 4308 | Over-range | 811 | 682 | 292 | 1963 | 162 | 150 | 284 | 1274 | 1115 | 1214 | 1505 | 3834 | 1115 | 1214 | 1505 | 3834 | - - - | - - - | - - - | - - -
5/4/2026 | 2:15:00 AM | 285.57 | 282.34 | 281.02 | 493.39 | 485.91 | 491.07 | 4.4612 | 4.2636 | 5.2953 | 2.7509 | 1.426 | 1.424 | 1.421 | 1.501 | 1.458 | 1.422 | Over-range | 60.01 | 1053 | 986 | 1454 | 3493 | - - - | - - - | - - - | - - - | 1053 | 986 | 1454 | 3493 | 696 | 666 | 132 | 1494 | - - - | - - - | - - - | - - - | 696 | 666 | 132 | 1494 | 1273 | 1201 | 1488 | 3962 | # # # | # # # | # # # | # # # | 0.828 | 0.821 | 0.977 | 0.882 | # # # | # # # | # # # | - - - | 0.835 | 0.827 | 0.995 | 0.892 | - - - | 0.428 | 1.7 | 1.6 | 1.55 | 1.54 | 1.56 | 1.57 | 11.78 | 12.22 | 18.99 | 0 | - - - | - - - | - - - | - - - | 1273 | 1201 | 1488 | 3962 | Over-range | 714 | 682 | 314 | 1868 | 160 | 149 | 281 | 1120 | 1056 | 985 | 1452 | 3494 | 1056 | 985 | 1452 | 3494 | - - - | - - - | - - - | - - -
5/4/2026 | 2:30:00 AM | 285.6 | 282.43 | 281.06 | 493.47 | 486.12 | 491.07 | 4.6771 | 4.6577 | 5.3976 | 2.7487 | 1.426 | 1.424 | 1.421 | 1.508 | 1.427 | 1.391 | Over-range | 60.01 | 1089 | 1124 | 1488 | 3701 | - - - | - - - | - - - | - - - | 1089 | 1124 | 1488 | 3701 | 756 | 665 | 72 | 1492 | - - - | - - - | - - - | - - - | 756 | 665 | 72 | 1492 | 1336 | 1315 | 1517 | 4167 | # # # | # # # | # # # | # # # | 0.816 | 0.855 | 0.981 | 0.888 | # # # | # # # | # # # | - - - | 0.822 | 0.861 | 0.999 | 0.898 | - - - | 0.403 | 1.72 | 1.59 | 1.57 | 1.55 | 1.56 | 1.58 | 11.13 | 11.29 | 18.89 | 0 | - - - | - - - | - - - | - - - | 1336 | 1315 | 1517 | 4167 | Over-range | 773 | 682 | 295 | 1915 | 160 | 151 | 285 | 1199 | 1092 | 1124 | 1486 | 3702 | 1092 | 1124 | 1486 | 3702 | - - - | - - - | - - - | - - -
5/4/2026 | 2:45:00 AM | 285.84 | 282.65 | 281.31 | 493.91 | 486.46 | 491.51 | 4.6478 | 4.6006 | 5.3839 | 2.7475 | 1.427 | 1.425 | 1.421 | 1.508 | 1.428 | 1.394 | Over-range | 60 | 1085 | 1105 | 1485 | 3675 | - - - | - - - | - - - | - - - | 1085 | 1105 | 1485 | 3675 | 749 | 670 | 82 | 1501 | - - - | - - - | - - - | - - - | 749 | 670 | 82 | 1501 | 1329 | 1300 | 1515 | 4143 | # # # | # # # | # # # | # # # | 0.817 | 0.85 | 0.981 | 0.887 | # # # | # # # | # # # | - - - | 0.822 | 0.855 | 0.999 | 0.897 | - - - | 0.408 | 1.71 | 1.6 | 1.57 | 1.55 | 1.57 | 1.57 | 11.31 | 11.38 | 18.92 | 0 | - - - | - - - | - - - | - - - | 1329 | 1300 | 1515 | 4143 | Over-range | 767 | 686 | 297 | 1914 | 165 | 147 | 285 | 1188 | 1084 | 1107 | 1484 | 3674 | 1084 | 1107 | 1484 | 3674 | - - - | - - - | - - - | - - -
5/4/2026 | 3:00:00 AM | 285.94 | 282.87 | 281.47 | 494.19 | 486.85 | 491.69 | 4.6844 | 4.6748 | 5.4045 | 2.7464 | 1.427 | 1.425 | 1.421 | 1.508 | 1.423 | 1.389 | Over-range | 60.02 | 1091 | 1129 | 1492 | 3712 | - - - | - - - | - - - | - - - | 1091 | 1129 | 1492 | 3712 | 760 | 671 | 73 | 1504 | - - - | - - - | - - - | - - - | 760 | 671 | 73 | 1504 | 1339 | 1322 | 1521 | 4183 | # # # | # # # | # # # | # # # | 0.814 | 0.854 | 0.981 | 0.887 | # # # | # # # | # # # | - - - | 0.82 | 0.86 | 0.999 | 0.897 | - - - | 0.405 | 1.71 | 1.58 | 1.55 | 1.54 | 1.55 | 1.57 | 11.21 | 11.29 | 18.92 | 0 | - - - | - - - | - - - | - - - | 1339 | 1322 | 1521 | 4183 | Over-range | 778 | 688 | 296 | 1928 | 166 | 148 | 287 | 1206 | 1090 | 1131 | 1491 | 3712 | 1090 | 1131 | 1491 | 3712 | - - - | - - - | - - - | - - -
5/4/2026 | 3:15:00 AM | 285.88 | 282.88 | 281.52 | 494.06 | 486.99 | 491.68 | 5.1773 | 5.4266 | 5.6316 | 2.745 | 1.426 | 1.423 | 1.42 | 1.51 | 1.432 | 1.345 | Over-range | 60 | 1178 | 1368 | 1554 | 4100 | - - - | - - - | - - - | - - - | 1178 | 1368 | 1554 | 4100 | 874 | 669 | -3 | 1539 | - - - | - - - | - - - | - - - | 874 | 669 | -3 | 1539 | 1477 | 1532 | 1585 | 4594 | # # # | # # # | # # # | # # # | 0.798 | 0.893 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.795 | 0.891 | 0.984 | 0.892 | - - - | 0.375 | 1.7 | 1.58 | 1.54 | 1.53 | 1.55 | 1.56 | 10.15 | 10.11 | 18.6 | 0 | - - - | - - - | - - - | - - - | 1477 | 1532 | 1585 | 4594 | Over-range | 890 | 687 | 309 | 2071 | 171 | 154 | 293 | 1377 | 1187 | 1378 | 1569 | 4134 | 1187 | 1378 | 1569 | 4134 | - - - | - - - | - - - | - - -
5/4/2026 | 3:30:00 AM | 285.97 | 283.05 | 281.65 | 494.33 | 487.21 | 491.85 | 4.8838 | 5.0773 | 5.5106 | 2.7408 | 1.426 | 1.424 | 1.421 | 1.508 | 1.44 | 1.361 | Over-range | 60 | 1120 | 1246 | 1522 | 3888 | - - - | - - - | - - - | - - - | 1120 | 1246 | 1522 | 3888 | 811 | 673 | 25 | 1510 | - - - | - - - | - - - | - - - | 811 | 673 | 25 | 1510 | 1394 | 1429 | 1552 | 4374 | # # # | # # # | # # # | # # # | 0.804 | 0.873 | 0.981 | 0.889 | # # # | # # # | # # # | - - - | 0.809 | 0.877 | 0.999 | 0.898 | - - - | 0.388 | 1.7 | 1.57 | 1.55 | 1.53 | 1.55 | 1.56 | 10.88 | 10.7 | 18.63 | 0 | - - - | - - - | - - - | - - - | 1394 | 1429 | 1552 | 4374 | Over-range | 829 | 690 | 299 | 2002 | 169 | 152 | 287 | 1311 | 1120 | 1246 | 1524 | 3889 | 1120 | 1246 | 1524 | 3889 | - - - | - - - | - - - | - - -
5/4/2026 | 3:45:00 AM | 286.08 | 283.06 | 281.77 | 494.41 | 487.3 | 492.09 | 4.4745 | 4.2978 | 5.3116 | 2.7444 | 1.426 | 1.423 | 1.421 | 1.501 | 1.455 | 1.422 | Over-range | 60 | 1054 | 995 | 1462 | 3511 | - - - | - - - | - - - | - - - | 1054 | 995 | 1462 | 3511 | 705 | 675 | 138 | 1518 | - - - | - - - | - - - | - - - | 705 | 675 | 138 | 1518 | 1279 | 1214 | 1497 | 3990 | # # # | # # # | # # # | # # # | 0.824 | 0.82 | 0.977 | 0.88 | # # # | # # # | # # # | - - - | 0.832 | 0.826 | 0.995 | 0.891 | - - - | 0.432 | 1.68 | 1.55 | 1.56 | 1.51 | 1.54 | 1.56 | 11.87 | 12.33 | 19.12 | 0 | - - - | - - - | - - - | - - - | 1279 | 1214 | 1497 | 3990 | Over-range | 724 | 692 | 319 | 1893 | 163 | 154 | 285 | 1131 | 1057 | 993 | 1463 | 3513 | 1057 | 993 | 1463 | 3513 | - - - | - - - | - - - | - - -
5/4/2026 | 4:00:00 AM | 285.81 | 282.91 | 281.55 | 494.02 | 487.1 | 491.6 | 4.662 | 4.6355 | 5.3976 | 2.7455 | 1.425 | 1.423 | 1.421 | 1.505 | 1.429 | 1.395 | Over-range | 60 | 1085 | 1114 | 1490 | 3689 | - - - | - - - | - - - | - - - | 1085 | 1114 | 1490 | 3689 | 755 | 671 | 84 | 1510 | - - - | - - - | - - - | - - - | 755 | 671 | 84 | 1510 | 1332 | 1310 | 1520 | 4162 | # # # | # # # | # # # | # # # | 0.815 | 0.85 | 0.98 | 0.886 | # # # | # # # | # # # | - - - | 0.822 | 0.855 | 0.998 | 0.896 | - - - | 0.409 | 1.69 | 1.59 | 1.55 | 1.52 | 1.55 | 1.57 | 11.25 | 11.42 | 18.95 | 0 | - - - | - - - | - - - | - - - | 1332 | 1310 | 1520 | 4162 | Over-range | 772 | 689 | 300 | 1927 | 161 | 154 | 287 | 1195 | 1089 | 1112 | 1489 | 3690 | 1089 | 1112 | 1489 | 3690 | - - - | - - - | - - - | - - -
5/4/2026 | 4:15:00 AM | 286.1 | 283.19 | 281.79 | 494.58 | 487.47 | 492.06 | 4.6409 | 4.592 | 5.3867 | 2.742 | 1.425 | 1.424 | 1.421 | 1.501 | 1.429 | 1.398 | Over-range | 60 | 1082 | 1100 | 1488 | 3669 | - - - | - - - | - - - | - - - | 1082 | 1100 | 1488 | 3669 | 753 | 676 | 94 | 1523 | - - - | - - - | - - - | - - - | 753 | 676 | 94 | 1523 | 1328 | 1300 | 1518 | 4146 | # # # | # # # | # # # | # # # | 0.815 | 0.846 | 0.98 | 0.885 | # # # | # # # | # # # | - - - | 0.822 | 0.852 | 0.998 | 0.895 | - - - | 0.415 | 1.72 | 1.63 | 1.59 | 1.54 | 1.6 | 1.61 | 11.37 | 11.58 | 18.99 | 0 | - - - | - - - | - - - | - - - | 1328 | 1300 | 1518 | 4146 | Over-range | 770 | 694 | 302 | 1930 | 161 | 153 | 287 | 1185 | 1085 | 1100 | 1485 | 3670 | 1085 | 1100 | 1485 | 3670 | - - - | - - - | - - - | - - -
5/4/2026 | 4:30:00 AM | 285.93 | 283.08 | 281.64 | 494.34 | 487.26 | 491.74 | 5.0054 | 5.2937 | 5.5718 | 2.7367 | 1.425 | 1.423 | 1.421 | 1.509 | 1.431 | 1.346 | Over-range | 60.01 | 1141 | 1325 | 1541 | 4006 | - - - | - - - | - - - | - - - | 1141 | 1325 | 1541 | 4006 | 846 | 672 | -6 | 1512 | - - - | - - - | - - - | - - - | 846 | 672 | -6 | 1512 | 1430 | 1495 | 1569 | 4494 | # # # | # # # | # # # | # # # | 0.798 | 0.886 | 0.982 | 0.891 | # # # | # # # | # # # | - - - | 0.803 | 0.891 | 0.999 | 0.9 | - - - | 0.377 | 1.7 | 1.6 | 1.6 | 1.53 | 1.58 | 1.6 | 10.47 | 10.4 | 18.71 | 0 | - - - | - - - | - - - | - - - | 1430 | 1495 | 1569 | 4494 | Over-range | 862 | 690 | 296 | 2036 | 165 | 156 | 291 | 1362 | 1142 | 1326 | 1538 | 4006 | 1142 | 1326 | 1538 | 4006 | - - - | - - - | - - - | - - -
5/4/2026 | 4:45:00 AM | 285.6 | 282.79 | 281.45 | 493.73 | 486.94 | 491.28 | 4.9927 | 5.2634 | 5.5645 | 2.7384 | 1.425 | 1.423 | 1.421 | 1.507 | 1.427 | 1.345 | Over-range | 60 | 1139 | 1320 | 1539 | 3998 | - - - | - - - | - - - | - - - | 1139 | 1320 | 1539 | 3998 | 841 | 669 | -7 | 1503 | - - - | - - - | - - - | - - - | 841 | 669 | -7 | 1503 | 1426 | 1488 | 1566 | 4480 | # # # | # # # | # # # | # # # | 0.799 | 0.887 | 0.983 | 0.892 | # # # | # # # | # # # | - - - | 0.804 | 0.893 | 1 | 0.902 | - - - | 0.376 | 1.7 | 1.59 | 1.57 | 1.52 | 1.57 | 1.59 | 10.43 | 10.18 | 18.5 | 0 | - - - | - - - | - - - | - - - | 1426 | 1488 | 1566 | 4480 | Over-range | 858 | 686 | 288 | 2020 | 167 | 152 | 288 | 1350 | 1139 | 1322 | 1538 | 3999 | 1139 | 1322 | 1538 | 3999 | - - - | - - - | - - - | - - -
5/4/2026 | 5:00:00 AM | 285.41 | 282.61 | 281.19 | 493.5 | 486.47 | 490.9 | 4.6741 | 4.7027 | 5.4039 | 2.7344 | 1.425 | 1.424 | 1.422 | 1.498 | 1.46 | 1.392 | Over-range | 60 | 1084 | 1112 | 1485 | 3681 | - - - | - - - | - - - | - - - | 1084 | 1112 | 1485 | 3681 | 750 | 667 | 83 | 1500 | - - - | - - - | - - - | - - - | 750 | 667 | 83 | 1500 | 1329 | 1313 | 1519 | 4161 | # # # | # # # | # # # | # # # | 0.815 | 0.847 | 0.978 | 0.885 | # # # | # # # | # # # | - - - | 0.822 | 0.853 | 0.996 | 0.895 | - - - | 0.407 | 1.72 | 1.63 | 1.62 | 1.54 | 1.61 | 1.63 | 11.3 | 11.63 | 18.71 | 0 | - - - | - - - | - - - | - - - | 1329 | 1313 | 1519 | 4161 | Over-range | 768 | 684 | 313 | 1937 | 167 | 151 | 283 | 1219 | 1084 | 1111 | 1488 | 3683 | 1084 | 1111 | 1488 | 3683 | - - - | - - - | - - - | - - -
5/4/2026 | 5:15:00 AM | 285.23 | 282.56 | 281.09 | 493.29 | 486.41 | 490.61 | 4.5935 | 4.5137 | 5.3595 | 2.735 | 1.425 | 1.424 | 1.422 | 1.495 | 1.432 | 1.403 | Over-range | 60 | 1073 | 1073 | 1475 | 3622 | - - - | - - - | - - - | - - - | 1073 | 1073 | 1475 | 3622 | 733 | 666 | 100 | 1499 | - - - | - - - | - - - | - - - | 733 | 666 | 100 | 1499 | 1310 | 1273 | 1506 | 4089 | # # # | # # # | # # # | # # # | 0.819 | 0.843 | 0.979 | 0.886 | # # # | # # # | # # # | - - - | 0.826 | 0.849 | 0.997 | 0.896 | - - - | 0.414 | 1.77 | 1.67 | 1.66 | 1.57 | 1.64 | 1.68 | 11.27 | 11.77 | 18.89 | 0 | - - - | - - - | - - - | - - - | 1310 | 1273 | 1506 | 4089 | Over-range | 751 | 684 | 304 | 1899 | 164 | 153 | 284 | 1165 | 1074 | 1071 | 1478 | 3623 | 1074 | 1071 | 1478 | 3623 | - - - | - - - | - - - | - - -
5/4/2026 | 5:30:00 AM | 284.98 | 282.46 | 280.92 | 492.95 | 486.26 | 490.17 | 4.5732 | 4.4687 | 5.3484 | 2.7369 | 1.426 | 1.425 | 1.424 | 1.492 | 1.424 | 1.406 | Over-range | 60 | 1069 | 1062 | 1472 | 3604 | - - - | - - - | - - - | - - - | 1069 | 1062 | 1472 | 3604 | 728 | 664 | 105 | 1497 | - - - | - - - | - - - | - - - | 728 | 664 | 105 | 1497 | 1303 | 1262 | 1502 | 4068 | # # # | # # # | # # # | # # # | 0.821 | 0.842 | 0.98 | 0.886 | # # # | # # # | # # # | - - - | 0.828 | 0.847 | 0.997 | 0.896 | - - - | 0.415 | 1.8 | 1.71 | 1.74 | 1.62 | 1.69 | 1.74 | 11.24 | 11.7 | 18.75 | 0 | - - - | - - - | - - - | - - - | 1303 | 1262 | 1502 | 4068 | Over-range | 745 | 682 | 301 | 1887 | 160 | 153 | 282 | 1149 | 1073 | 1060 | 1473 | 3606 | 1073 | 1060 | 1473 | 3606 | - - - | - - - | - - - | - - -
5/4/2026 | 5:45:00 AM | 284.6 | 282.08 | 280.53 | 492.35 | 485.52 | 489.52 | 4.6335 | 4.5809 | 5.3688 | 2.7289 | 1.426 | 1.425 | 1.423 | 1.492 | 1.42 | 1.397 | Over-range | 60.01 | 1079 | 1101 | 1477 | 3658 | - - - | - - - | - - - | - - - | 1079 | 1101 | 1477 | 3658 | 741 | 658 | 85 | 1484 | - - - | - - - | - - - | - - - | 741 | 658 | 85 | 1484 | 1319 | 1292 | 1506 | 4117 | # # # | # # # | # # # | # # # | 0.818 | 0.853 | 0.981 | 0.888 | # # # | # # # | # # # | - - - | 0.825 | 0.858 | 0.998 | 0.898 | - - - | 0.406 | 1.87 | 1.77 | 1.8 | 1.68 | 1.76 | 1.81 | 10.97 | 11.46 | 18.64 | 0 | - - - | - - - | - - - | - - - | 1319 | 1292 | 1506 | 4117 | Over-range | 758 | 675 | 294 | 1889 | 157 | 152 | 281 | 1169 | 1083 | 1101 | 1475 | 3659 | 1083 | 1101 | 1475 | 3659 | - - - | - - - | - - - | - - -
5/4/2026 | 6:00:00 AM | 283.93 | 281.45 | 279.89 | 491.21 | 484.46 | 488.36 | 5.0756 | 5.2512 | 5.5655 | 2.7191 | 1.426 | 1.425 | 1.423 | 1.492 | 1.448 | 1.357 | Over-range | 60.01 | 1158 | 1315 | 1528 | 4002 | - - - | - - - | - - - | - - - | 1158 | 1315 | 1528 | 4002 | 835 | 647 | 11 | 1493 | - - - | - - - | - - - | - - - | 835 | 647 | 11 | 1493 | 1438 | 1475 | 1557 | 4470 | # # # | # # # | # # # | # # # | 0.806 | 0.892 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.804 | 0.896 | 0.997 | 0.901 | - - - | 0.373 | 1.87 | 1.75 | 1.78 | 1.67 | 1.74 | 1.8 | 9.89 | 10.17 | 18.23 | 0 | - - - | - - - | - - - | - - - | 1438 | 1475 | 1557 | 4470 | Over-range | 851 | 665 | 299 | 1992 | 164 | 152 | 283 | 1309 | 1170 | 1314 | 1528 | 4012 | 1170 | 1314 | 1528 | 4012 | - - - | - - - | - - - | - - -
5/4/2026 | 6:15:00 AM | 282.82 | 280.37 | 278.72 | 489.28 | 482.54 | 486.4 | 4.6986 | 4.7526 | 5.3929 | 2.7087 | 1.426 | 1.426 | 1.424 | 1.49 | 1.463 | 1.381 | Over-range | 59.98 | 1085 | 1141 | 1473 | 3700 | - - - | - - - | - - - | - - - | 1085 | 1141 | 1473 | 3700 | 741 | 635 | 54 | 1431 | - - - | - - - | - - - | - - - | 741 | 635 | 54 | 1431 | 1325 | 1319 | 1502 | 4146 | # # # | # # # | # # # | # # # | 0.819 | 0.865 | 0.981 | 0.892 | # # # | # # # | # # # | - - - | 0.825 | 0.87 | 0.997 | 0.901 | - - - | 0.387 | 1.94 | 1.86 | 1.86 | 1.73 | 1.82 | 1.88 | 10.63 | 10.97 | 17.94 | 0 | - - - | - - - | - - - | - - - | 1325 | 1319 | 1502 | 4146 | Over-range | 758 | 651 | 291 | 1871 | 159 | 143 | 270 | 1201 | 1086 | 1140 | 1475 | 3701 | 1086 | 1140 | 1475 | 3701 | - - - | - - - | - - - | - - -
5/4/2026 | 6:30:00 AM | 282.11 | 279.56 | 277.93 | 488.01 | 481.05 | 485.16 | 4.5705 | 4.4846 | 5.3165 | 2.6977 | 1.425 | 1.425 | 1.424 | 1.493 | 1.437 | 1.396 | Over-range | 60 | 1067 | 1075 | 1450 | 3592 | - - - | - - - | - - - | - - - | 1067 | 1075 | 1450 | 3592 | 705 | 623 | 76 | 1405 | - - - | - - - | - - - | - - - | 705 | 623 | 76 | 1405 | 1289 | 1251 | 1478 | 4018 | # # # | # # # | # # # | # # # | 0.828 | 0.859 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.834 | 0.865 | 0.999 | 0.904 | - - - | 0.391 | 1.94 | 1.88 | 1.85 | 1.73 | 1.81 | 1.88 | 10.64 | 11.28 | 18.22 | 0 | - - - | - - - | - - - | - - - | 1289 | 1251 | 1478 | 4018 | Over-range | 722 | 639 | 284 | 1800 | 155 | 143 | 270 | 1124 | 1068 | 1073 | 1453 | 3593 | 1068 | 1073 | 1453 | 3593 | - - - | - - - | - - - | - - -
5/4/2026 | 6:45:00 AM | 281.95 | 279.49 | 277.88 | 487.72 | 481.03 | 484.98 | 4.5598 | 4.462 | 5.3115 | 2.6992 | 1.425 | 1.426 | 1.423 | 1.492 | 1.428 | 1.394 | Over-range | 60 | 1066 | 1070 | 1449 | 3585 | - - - | - - - | - - - | - - - | 1066 | 1070 | 1449 | 3585 | 702 | 622 | 78 | 1401 | - - - | - - - | - - - | - - - | 702 | 622 | 78 | 1401 | 1285 | 1246 | 1476 | 4007 | # # # | # # # | # # # | # # # | 0.829 | 0.859 | 0.982 | 0.895 | # # # | # # # | # # # | - - - | 0.835 | 0.863 | 0.999 | 0.904 | - - - | 0.391 | 1.9 | 1.84 | 1.82 | 1.69 | 1.78 | 1.85 | 10.67 | 11 | 17.97 | 0 | - - - | - - - | - - - | - - - | 1285 | 1246 | 1476 | 4007 | Over-range | 719 | 638 | 279 | 1790 | 154 | 139 | 266 | 1113 | 1066 | 1068 | 1452 | 3586 | 1066 | 1068 | 1452 | 3586 | - - - | - - - | - - - | - - -
5/4/2026 | 7:00:00 AM | 282.5 | 280.07 | 278.52 | 488.61 | 482.09 | 486.09 | 4.6002 | 4.5358 | 5.3373 | 2.7029 | 1.425 | 1.426 | 1.423 | 1.491 | 1.43 | 1.389 | Over-range | 60.03 | 1073 | 1094 | 1460 | 3628 | - - - | - - - | - - - | - - - | 1073 | 1094 | 1460 | 3628 | 716 | 628 | 70 | 1414 | - - - | - - - | - - - | - - - | 716 | 628 | 70 | 1414 | 1299 | 1270 | 1487 | 4056 | # # # | # # # | # # # | # # # | 0.826 | 0.862 | 0.982 | 0.895 | # # # | # # # | # # # | - - - | 0.833 | 0.867 | 0.999 | 0.904 | - - - | 0.39 | 1.89 | 1.83 | 1.83 | 1.69 | 1.77 | 1.84 | 10.62 | 10.94 | 18.06 | 0 | - - - | - - - | - - - | - - - | 1299 | 1270 | 1487 | 4056 | Over-range | 732 | 644 | 278 | 1813 | 154 | 141 | 268 | 1134 | 1075 | 1093 | 1461 | 3629 | 1075 | 1093 | 1461 | 3629 | - - - | - - - | - - - | - - -
5/4/2026 | 7:15:00 AM | 281.98 | 279.59 | 278 | 487.79 | 481.17 | 485.18 | 5.0373 | 5.3891 | 5.5634 | 2.6931 | 1.425 | 1.426 | 1.422 | 1.491 | 1.471 | 1.325 | Over-range | 60 | 1143 | 1363 | 1521 | 4027 | - - - | - - - | - - - | - - - | 1143 | 1363 | 1521 | 4027 | 828 | 619 | -50 | 1395 | - - - | - - - | - - - | - - - | 828 | 619 | -50 | 1395 | 1420 | 1505 | 1546 | 4471 | # # # | # # # | # # # | # # # | 0.805 | 0.906 | 0.984 | 0.901 | # # # | # # # | # # # | - - - | 0.81 | 0.911 | 0.999 | 0.909 | - - - | 0.346 | 1.87 | 1.82 | 1.81 | 1.66 | 1.75 | 1.81 | 9.63 | 9.54 | 17.69 | 0 | - - - | - - - | - - - | - - - | 1420 | 1505 | 1546 | 4471 | Over-range | 842 | 636 | 279 | 1942 | 154 | 146 | 272 | 1349 | 1144 | 1365 | 1519 | 4028 | 1144 | 1365 | 1519 | 4028 | - - - | - - - | - - - | - - -
5/4/2026 | 7:30:00 AM | 281.86 | 279.45 | 277.92 | 487.51 | 481.04 | 485.03 | 4.6791 | 4.7303 | 5.378 | 2.6951 | 1.425 | 1.426 | 1.422 | 1.488 | 1.475 | 1.376 | Over-range | 60.02 | 1083 | 1135 | 1465 | 3683 | - - - | - - - | - - - | - - - | 1083 | 1135 | 1465 | 3683 | 728 | 619 | 48 | 1395 | - - - | - - - | - - - | - - - | 728 | 619 | 48 | 1395 | 1315 | 1307 | 1494 | 4115 | # # # | # # # | # # # | # # # | 0.824 | 0.868 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.83 | 0.874 | 0.997 | 0.904 | - - - | 0.379 | 1.9 | 1.84 | 1.81 | 1.69 | 1.77 | 1.83 | 10.51 | 10.83 | 17.75 | 0 | - - - | - - - | - - - | - - - | 1315 | 1307 | 1494 | 4115 | Over-range | 744 | 635 | 288 | 1835 | 155 | 142 | 265 | 1186 | 1084 | 1133 | 1468 | 3684 | 1084 | 1133 | 1468 | 3684 | - - - | - - - | - - - | - - -
5/4/2026 | 7:45:00 AM | 281.9 | 279.51 | 278.03 | 487.59 | 481.21 | 485.13 | 4.542 | 3.986 | 5.3045 | 3.4987 | 1.426 | 1.427 | 1.422 | 1.49 | 1.435 | 1.396 | Over-range | 60.02 | 1064 | 840 | 1447 | 3351 | - - - | - - - | - - - | - - - | 1064 | 840 | 1447 | 3351 | 694 | 688 | 81 | 1463 | - - - | - - - | - - - | - - - | 694 | 688 | 81 | 1463 | 1280 | 1109 | 1475 | 3864 | # # # | # # # | # # # | # # # | 0.831 | 0.758 | 0.981 | 0.867 | # # # | # # # | # # # | - - - | 0.837 | 0.766 | 0.998 | 0.878 | - - - | 0.437 | 1.87 | 1.83 | 1.81 | 1.68 | 1.75 | 1.81 | 10.72 | 14.27 | 18.16 | 0 | - - - | - - - | - - - | - - - | 1280 | 1109 | 1475 | 3864 | Over-range | 711 | 705 | 283 | 1912 | 154 | 154 | 268 | 1229 | 1063 | 842 | 1446 | 3351 | 1063 | 842 | 1446 | 3351 | - - - | - - - | - - - | - - -
5/4/2026 | 8:00:00 AM | 282.03 | 279.53 | 278.11 | 487.7 | 481.23 | 485.4 | 4.5851 | 3.6322 | 5.3187 | 4.1012 | 1.425 | 1.427 | 1.422 | 1.489 | 1.448 | 1.388 | Over-range | 60.04 | 1072 | 668 | 1453 | 3193 | - - - | - - - | - - - | - - - | 1072 | 668 | 1453 | 3193 | 707 | 746 | 68 | 1521 | - - - | - - - | - - - | - - - | 707 | 746 | 68 | 1521 | 1293 | 1015 | 1479 | 3787 | # # # | # # # | # # # | # # # | 0.829 | 0.658 | 0.983 | 0.843 | # # # | # # # | # # # | - - - | 0.835 | 0.668 | 0.999 | 0.854 | - - - | 0.476 | 1.86 | 1.79 | 1.79 | 1.66 | 1.73 | 1.79 | 10.61 | 16.48 | 17.99 | 0 | - - - | - - - | - - - | - - - | 1293 | 1015 | 1479 | 3787 | Over-range | 723 | 764 | 275 | 2037 | 153 | 166 | 266 | 1355 | 1072 | 669 | 1452 | 3193 | 1072 | 669 | 1452 | 3193 | - - - | - - - | - - - | - - -
5/4/2026 | 8:15:00 AM | 281.56 | 278.93 | 277.55 | 486.78 | 480.2 | 484.53 | 4.7171 | 3.8227 | 5.3802 | 4.0987 | 1.425 | 1.427 | 1.422 | 1.491 | 1.431 | 1.369 | Over-range | 60.03 | 1093 | 751 | 1469 | 3313 | - - - | - - - | - - - | - - - | 1093 | 751 | 1469 | 3313 | 739 | 736 | 27 | 1503 | - - - | - - - | - - - | - - - | 739 | 736 | 27 | 1503 | 1328 | 1066 | 1493 | 3887 | # # # | # # # | # # # | # # # | 0.823 | 0.704 | 0.984 | 0.852 | # # # | # # # | # # # | - - - | 0.829 | 0.714 | 1 | 0.863 | - - - | 0.454 | 1.84 | 1.81 | 1.8 | 1.65 | 1.75 | 1.8 | 10.19 | 16.04 | 17.82 | 0 | - - - | - - - | - - - | - - - | 1328 | 1066 | 1493 | 3887 | Over-range | 755 | 756 | 268 | 2034 | 153 | 172 | 266 | 1371 | 1094 | 750 | 1470 | 3314 | 1094 | 750 | 1470 | 3314 | - - - | - - - | - - - | - - -
5/4/2026 | 8:30:00 AM | 281.19 | 278.43 | 277.26 | 485.96 | 479.48 | 484.07 | 5.195 | 4.6188 | 5.6405 | 4.0924 | 1.426 | 1.428 | 1.422 | 1.498 | 1.436 | 1.301 | Over-range | 60.03 | 1169 | 1040 | 1536 | 3745 | - - - | - - - | - - - | - - - | 1169 | 1040 | 1536 | 3745 | 861 | 726 | -102 | 1484 | - - - | - - - | - - - | - - - | 861 | 726 | -102 | 1484 | 1460 | 1283 | 1564 | 4307 | # # # | # # # | # # # | # # # | 0.801 | 0.811 | 0.983 | 0.87 | # # # | # # # | # # # | - - - | 0.806 | 0.819 | 0.997 | 0.879 | - - - | 0.396 | 1.87 | 1.83 | 1.83 | 1.68 | 1.78 | 1.83 | 9.23 | 14.04 | 17.26 | 0 | - - - | - - - | - - - | - - - | 1460 | 1283 | 1564 | 4307 | Over-range | 874 | 748 | 291 | 2126 | 152 | 182 | 269 | 1521 | 1172 | 1040 | 1535 | 3746 | 1172 | 1040 | 1535 | 3746 | - - - | - - - | - - - | - - -
5/4/2026 | 8:45:00 AM | 280.52 | 277.47 | 276.44 | 484.55 | 477.8 | 482.91 | 5.4513 | 4.8942 | 5.7404 | 4.0837 | 1.426 | 1.428 | 1.422 | 1.496 | 1.454 | 1.3 | Over-range | 60.02 | 1218 | 1137 | 1557 | 3911 | - - - | - - - | - - - | - - - | 1218 | 1137 | 1557 | 3911 | 906 | 713 | -126 | 1491 | - - - | - - - | - - - | - - - | 906 | 713 | -126 | 1491 | 1526 | 1355 | 1587 | 4467 | # # # | # # # | # # # | # # # | 0.798 | 0.839 | 0.981 | 0.875 | # # # | # # # | # # # | - - - | 0.795 | 0.832 | 0.977 | 0.871 | - - - | 0.381 | 1.83 | 1.87 | 1.83 | 1.67 | 1.8 | 1.82 | 8.91 | 13.21 | 16.88 | 0 | - - - | - - - | - - - | - - - | 1526 | 1355 | 1587 | 4467 | Over-range | 919 | 735 | 306 | 2159 | 153 | 177 | 265 | 1555 | 1234 | 1151 | 1582 | 3967 | 1234 | 1151 | 1582 | 3967 | - - - | - - - | - - - | - - -
5/4/2026 | 9:00:00 AM | 280.31 | 277.18 | 276.26 | 484.06 | 477.43 | 482.62 | 4.8284 | 4.0163 | 5.4282 | 4.0973 | 1.426 | 1.428 | 1.422 | 1.492 | 1.43 | 1.347 | Over-range | 60.01 | 1108 | 812 | 1474 | 3394 | - - - | - - - | - - - | - - - | 1108 | 812 | 1474 | 3394 | 755 | 714 | -12 | 1456 | - - - | - - - | - - - | - - - | 755 | 714 | -12 | 1456 | 1350 | 1105 | 1499 | 3955 | # # # | # # # | # # # | # # # | 0.821 | 0.734 | 0.983 | 0.858 | # # # | # # # | # # # | - - - | 0.827 | 0.742 | 0.998 | 0.868 | - - - | 0.429 | 1.87 | 1.87 | 1.8 | 1.66 | 1.79 | 1.82 | 9.9 | 15.22 | 17.26 | 0 | - - - | - - - | - - - | - - - | 1350 | 1105 | 1499 | 3955 | Over-range | 770 | 734 | 273 | 2025 | 152 | 170 | 258 | 1407 | 1110 | 810 | 1476 | 3396 | 1110 | 810 | 1476 | 3396 | - - - | - - - | - - - | - - -
5/4/2026 | 9:15:00 AM | 280.02 | 276.84 | 275.87 | 483.57 | 476.73 | 482.01 | 4.4677 | 3.4388 | 5.2393 | 4.1004 | 1.426 | 1.428 | 1.423 | 1.489 | 1.448 | 1.395 | Over-range | 60 | 1051 | 595 | 1419 | 3065 | - - - | - - - | - - - | - - - | 1051 | 595 | 1419 | 3065 | 658 | 714 | 80 | 1452 | - - - | - - - | - - - | - - - | 658 | 714 | 80 | 1452 | 1250 | 949 | 1445 | 3644 | # # # | # # # | # # # | # # # | 0.841 | 0.627 | 0.982 | 0.841 | # # # | # # # | # # # | - - - | 0.847 | 0.636 | 0.997 | 0.852 | - - - | 0.474 | 1.8 | 1.82 | 1.78 | 1.62 | 1.75 | 1.77 | 10.66 | 17.06 | 17.69 | 0 | - - - | - - - | - - - | - - - | 1250 | 949 | 1445 | 3644 | Over-range | 675 | 732 | 273 | 1968 | 150 | 164 | 256 | 1328 | 1051 | 594 | 1421 | 3066 | 1051 | 594 | 1421 | 3066 | - - - | - - - | - - - | - - -
5/4/2026 | 9:30:00 AM | 279.73 | 276.48 | 275.56 | 483.05 | 476.1 | 481.52 | 4.7364 | 3.8232 | 5.3523 | 4.0941 | 1.427 | 1.429 | 1.424 | 1.49 | 1.434 | 1.357 | Over-range | 60.02 | 1096 | 763 | 1452 | 3310 | - - - | - - - | - - - | - - - | 1096 | 763 | 1452 | 3310 | 728 | 707 | 1 | 1436 | - - - | - - - | - - - | - - - | 728 | 707 | 1 | 1436 | 1324 | 1055 | 1475 | 3854 | # # # | # # # | # # # | # # # | 0.827 | 0.723 | 0.984 | 0.859 | # # # | # # # | # # # | - - - | 0.833 | 0.732 | 0.999 | 0.869 | - - - | 0.434 | 1.81 | 1.79 | 1.75 | 1.62 | 1.73 | 1.75 | 9.99 | 15.41 | 17.37 | 0 | - - - | - - - | - - - | - - - | 1324 | 1055 | 1475 | 3854 | Over-range | 744 | 726 | 259 | 1973 | 151 | 163 | 256 | 1352 | 1096 | 762 | 1453 | 3311 | 1096 | 762 | 1453 | 3311 | - - - | - - - | - - - | - - -
5/4/2026 | 9:45:00 AM | 280.11 | 276.96 | 275.96 | 483.74 | 476.99 | 482.1 | 4.8043 | 3.9263 | 5.4124 | 4.1122 | 1.426 | 1.428 | 1.424 | 1.491 | 1.425 | 1.346 | Over-range | 60.01 | 1107 | 802 | 1471 | 3380 | - - - | - - - | - - - | - - - | 1107 | 802 | 1471 | 3380 | 750 | 714 | -11 | 1452 | - - - | - - - | - - - | - - - | 750 | 714 | -11 | 1452 | 1346 | 1087 | 1494 | 3926 | # # # | # # # | # # # | # # # | 0.823 | 0.738 | 0.985 | 0.861 | # # # | # # # | # # # | - - - | 0.828 | 0.747 | 1 | 0.871 | - - - | 0.43 | 1.81 | 1.83 | 1.78 | 1.64 | 1.75 | 1.77 | 9.88 | 15.37 | 17.4 | 0 | - - - | - - - | - - - | - - - | 1346 | 1087 | 1494 | 3926 | Over-range | 765 | 733 | 260 | 1998 | 149 | 166 | 260 | 1372 | 1108 | 802 | 1469 | 3380 | 1108 | 802 | 1469 | 3380 | - - - | - - - | - - - | - - -
5/4/2026 | 10:00:00 AM | 281.29 | 278.09 | 277.12 | 485.75 | 478.93 | 484.17 | 5.4372 | 5.0349 | 5.7852 | 4.1152 | 1.427 | 1.429 | 1.425 | 1.499 | 1.455 | 1.295 | Over-range | 60.01 | 1208 | 1177 | 1570 | 3956 | - - - | - - - | - - - | - - - | 1208 | 1177 | 1570 | 3956 | 923 | 724 | -168 | 1477 | - - - | - - - | - - - | - - - | 923 | 724 | -168 | 1477 | 1528 | 1396 | 1603 | 4527 | # # # | # # # | # # # | # # # | 0.791 | 0.843 | 0.98 | 0.874 | # # # | # # # | # # # | - - - | 0.796 | 0.85 | 0.994 | 0.882 | - - - | 0.374 | 1.78 | 1.81 | 1.77 | 1.62 | 1.72 | 1.74 | 8.9 | 12.96 | 16.89 | 0 | - - - | - - - | - - - | - - - | 1528 | 1396 | 1603 | 4527 | Over-range | 935 | 747 | 321 | 2201 | 152 | 184 | 269 | 1630 | 1213 | 1175 | 1569 | 3957 | 1213 | 1175 | 1569 | 3957 | - - - | - - - | - - - | - - -
5/4/2026 | 10:15:00 AM | 280.83 | 277.51 | 276.58 | 484.89 | 477.89 | 483.34 | 5.6138 | 5.3442 | 5.8731 | 4.1066 | 1.426 | 1.429 | 1.425 | 1.501 | 1.474 | 1.299 | Over-range | 60.02 | 1237 | 1285 | 1586 | 4108 | - - - | - - - | - - - | - - - | 1237 | 1285 | 1586 | 4108 | 965 | 714 | -222 | 1456 | - - - | - - - | - - - | - - - | 965 | 714 | -222 | 1456 | 1576 | 1482 | 1624 | 4682 | # # # | # # # | # # # | # # # | 0.785 | 0.867 | 0.977 | 0.877 | # # # | # # # | # # # | - - - | 0.789 | 0.874 | 0.99 | 0.885 | - - - | 0.355 | 1.79 | 1.8 | 1.81 | 1.62 | 1.75 | 1.76 | 8.57 | 12.03 | 16.53 | 0 | - - - | - - - | - - - | - - - | 1576 | 1482 | 1624 | 4682 | Over-range | 977 | 737 | 348 | 2246 | 152 | 180 | 266 | 1709 | 1239 | 1286 | 1583 | 4108 | 1239 | 1286 | 1583 | 4108 | - - - | - - - | - - - | - - -
5/4/2026 | 10:30:00 AM | 280.75 | 277.43 | 276.44 | 484.74 | 477.72 | 483.12 | 5.3157 | 4.7973 | 5.6962 | 4.114 | 1.426 | 1.429 | 1.425 | 1.497 | 1.449 | 1.283 | Over-range | 60.01 | 1190 | 1107 | 1545 | 3842 | - - - | - - - | - - - | - - - | 1190 | 1107 | 1545 | 3842 | 888 | 716 | -143 | 1460 | - - - | - - - | - - - | - - - | 888 | 716 | -143 | 1460 | 1492 | 1330 | 1575 | 4397 | # # # | # # # | # # # | # # # | 0.797 | 0.832 | 0.982 | 0.874 | # # # | # # # | # # # | - - - | 0.802 | 0.839 | 0.995 | 0.882 | - - - | 0.38 | 1.82 | 1.83 | 1.82 | 1.65 | 1.78 | 1.79 | 9.05 | 13.09 | 16.86 | 0 | - - - | - - - | - - - | - - - | 1492 | 1330 | 1575 | 4397 | Over-range | 901 | 738 | 301 | 2139 | 151 | 177 | 264 | 1563 | 1193 | 1106 | 1544 | 3843 | 1193 | 1106 | 1544 | 3843 | - - - | - - - | - - - | - - -
5/4/2026 | 10:45:00 AM | 280.78 | 277.36 | 276.44 | 484.72 | 477.59 | 483.2 | 4.9123 | 4.1008 | 5.4605 | 4.1181 | 1.426 | 1.429 | 1.425 | 1.491 | 1.429 | 1.33 | Over-range | 60.01 | 1126 | 861 | 1486 | 3473 | - - - | - - - | - - - | - - - | 1126 | 861 | 1486 | 3473 | 782 | 719 | -36 | 1464 | - - - | - - - | - - - | - - - | 782 | 719 | -36 | 1464 | 1379 | 1136 | 1509 | 4024 | # # # | # # # | # # # | # # # | 0.816 | 0.759 | 0.985 | 0.863 | # # # | # # # | # # # | - - - | 0.822 | 0.767 | 0.999 | 0.872 | - - - | 0.422 | 1.81 | 1.85 | 1.8 | 1.63 | 1.77 | 1.78 | 9.79 | 14.59 | 17.26 | 0 | - - - | - - - | - - - | - - - | 1379 | 1136 | 1509 | 4024 | Over-range | 796 | 738 | 265 | 2032 | 148 | 168 | 260 | 1408 | 1129 | 861 | 1484 | 3474 | 1129 | 861 | 1484 | 3474 | - - - | - - - | - - - | - - -
5/4/2026 | 11:00:00 AM | 280.84 | 277.58 | 276.58 | 484.98 | 477.96 | 483.31 | 5.2688 | 4.5701 | 5.6251 | 4.1173 | 1.427 | 1.429 | 1.426 | 1.492 | 1.437 | 1.318 | Over-range | 60.02 | 1189 | 1019 | 1527 | 3735 | - - - | - - - | - - - | - - - | 1189 | 1019 | 1527 | 3735 | 860 | 720 | -81 | 1498 | - - - | - - - | - - - | - - - | 860 | 720 | -81 | 1498 | 1476 | 1263 | 1555 | 4294 | # # # | # # # | # # # | # # # | 0.806 | 0.807 | 0.982 | 0.87 | # # # | # # # | # # # | - - - | 0.803 | 0.808 | 0.987 | 0.871 | - - - | 0.401 | 1.87 | 1.82 | 1.87 | 1.67 | 1.8 | 1.82 | 9.22 | 13.85 | 17.16 | 0 | - - - | - - - | - - - | - - - | 1476 | 1263 | 1555 | 4294 | Over-range | 873 | 741 | 295 | 2118 | 151 | 175 | 266 | 1490 | 1203 | 1033 | 1547 | 3784 | 1203 | 1033 | 1547 | 3784 | - - - | - - - | - - - | - - -
5/4/2026 | 11:15:00 AM | 280.76 | 277.46 | 276.58 | 484.7 | 477.93 | 483.27 | 5.3223 | 4.8217 | 5.7169 | 4.123 | 1.428 | 1.43 | 1.427 | 1.497 | 1.447 | 1.289 | Over-range | 60.01 | 1190 | 1109 | 1551 | 3850 | - - - | - - - | - - - | - - - | 1190 | 1109 | 1551 | 3850 | 889 | 718 | -144 | 1462 | - - - | - - - | - - - | - - - | 889 | 718 | -144 | 1462 | 1493 | 1335 | 1581 | 4409 | # # # | # # # | # # # | # # # | 0.797 | 0.831 | 0.981 | 0.873 | # # # | # # # | # # # | - - - | 0.802 | 0.838 | 0.996 | 0.882 | - - - | 0.38 | 1.84 | 1.86 | 1.82 | 1.67 | 1.79 | 1.81 | 9.07 | 13.16 | 16.82 | 0 | - - - | - - - | - - - | - - - | 1493 | 1335 | 1581 | 4409 | Over-range | 902 | 740 | 304 | 2148 | 151 | 178 | 264 | 1572 | 1194 | 1108 | 1550 | 3851 | 1194 | 1108 | 1550 | 3851 | - - - | - - - | - - - | - - -
5/4/2026 | 11:30:00 AM | 280.44 | 277.19 | 276.22 | 484.23 | 477.38 | 482.66 | 4.5163 | 3.5313 | 5.2527 | 4.1267 | 1.427 | 1.43 | 1.426 | 1.488 | 1.452 | 1.388 | Over-range | 60.01 | 1059 | 611 | 1423 | 3092 | - - - | - - - | - - - | - - - | 1059 | 611 | 1423 | 3092 | 671 | 721 | 71 | 1463 | - - - | - - - | - - - | - - - | 671 | 721 | 71 | 1463 | 1263 | 971 | 1450 | 3684 | # # # | # # # | # # # | # # # | 0.838 | 0.629 | 0.981 | 0.839 | # # # | # # # | # # # | - - - | 0.845 | 0.638 | 0.997 | 0.85 | - - - | 0.473 | 1.84 | 1.85 | 1.8 | 1.66 | 1.77 | 1.8 | 10.78 | 16.83 | 17.8 | 0 | - - - | - - - | - - - | - - - | 1263 | 971 | 1450 | 3684 | Over-range | 687 | 739 | 281 | 1997 | 147 | 161 | 258 | 1359 | 1062 | 611 | 1421 | 3093 | 1062 | 611 | 1421 | 3093 | - - - | - - - | - - - | - - -
5/4/2026 | 11:45:00 AM | 280.29 | 277.02 | 276.08 | 483.95 | 477.09 | 482.41 | 4.8657 | 4.0356 | 5.449 | 4.1244 | 1.428 | 1.43 | 1.426 | 1.493 | 1.432 | 1.335 | Over-range | 60 | 1117 | 833 | 1480 | 3430 | - - - | - - - | - - - | - - - | 1117 | 833 | 1480 | 3430 | 766 | 716 | -26 | 1455 | - - - | - - - | - - - | - - - | 766 | 716 | -26 | 1455 | 1363 | 1114 | 1504 | 3981 | # # # | # # # | # # # | # # # | 0.82 | 0.748 | 0.984 | 0.862 | # # # | # # # | # # # | - - - | 0.825 | 0.756 | 0.999 | 0.871 | - - - | 0.424 | 1.83 | 1.87 | 1.83 | 1.67 | 1.79 | 1.81 | 9.89 | 15.19 | 17.42 | 0 | - - - | - - - | - - - | - - - | 1363 | 1114 | 1504 | 3981 | Over-range | 781 | 736 | 267 | 2020 | 148 | 170 | 261 | 1400 | 1120 | 833 | 1478 | 3431 | 1120 | 833 | 1478 | 3431 | - - - | - - - | - - - | - - -
5/4/2026 | 12:00:00 PM | 280.17 | 277.03 | 276.03 | 483.82 | 477.11 | 482.24 | 5.0051 | 4.2652 | 5.5119 | 4.1195 | 1.428 | 1.43 | 1.427 | 1.493 | 1.425 | 1.316 | Over-range | 60 | 1139 | 921 | 1496 | 3556 | - - - | - - - | - - - | - - - | 1139 | 921 | 1496 | 3556 | 803 | 716 | -66 | 1451 | - - - | - - - | - - - | - - - | 803 | 716 | -66 | 1451 | 1402 | 1180 | 1521 | 4103 | # # # | # # # | # # # | # # # | 0.813 | 0.78 | 0.984 | 0.867 | # # # | # # # | # # # | - - - | 0.818 | 0.789 | 0.999 | 0.876 | - - - | 0.408 | 1.84 | 1.85 | 1.82 | 1.67 | 1.78 | 1.81 | 9.6 | 14.61 | 17.43 | 0 | - - - | - - - | - - - | - - - | 1402 | 1180 | 1521 | 4103 | Over-range | 817 | 736 | 275 | 2046 | 151 | 172 | 264 | 1442 | 1141 | 921 | 1494 | 3557 | 1141 | 921 | 1494 | 3557 | - - - | - - - | - - - | - - -
5/4/2026 | 12:15:00 PM | 279.67 | 276.66 | 275.65 | 483.03 | 476.55 | 481.44 | 5.5027 | 5.1256 | 5.8401 | 4.1368 | 1.428 | 1.428 | 1.426 | 1.531 | 1.46 | 1.351 | Over-range | 59.99 | 1221 | 1208 | 1572 | 4001 | - - - | - - - | - - - | - - - | 1221 | 1208 | 1572 | 4001 | 920 | 713 | -191 | 1441 | - - - | - - - | - - - | - - - | 920 | 713 | -191 | 1441 | 1538 | 1416 | 1610 | 4564 | # # # | # # # | # # # | # # # | 0.794 | 0.853 | 0.977 | 0.877 | # # # | # # # | # # # | - - - | 0.799 | 0.861 | 0.992 | 0.886 | - - - | 0.36 | 1.69 | 1.68 | 1.62 | 1.5 | 1.58 | 1.62 | 8.87 | 12.55 | 16.61 | 0 | - - - | - - - | - - - | - - - | 1538 | 1416 | 1610 | 4564 | Over-range | 936 | 737 | 344 | 2195 | 171 | 184 | 284 | 1655 | 1221 | 1210 | 1570 | 4001 | 1221 | 1210 | 1570 | 4001 | - - - | - - - | - - - | - - -
5/4/2026 | 12:30:00 PM | 279.63 | 276.63 | 275.65 | 482.98 | 476.5 | 481.42 | 4.8793 | 4.127 | 5.4575 | 4.1369 | 1.429 | 1.43 | 1.428 | 1.553 | 1.48 | 1.491 | Over-range | 59.99 | 1117 | 815 | 1468 | 3400 | - - - | - - - | - - - | - - - | 1117 | 815 | 1468 | 3400 | 750 | 719 | -20 | 1447 | - - - | - - - | - - - | - - - | 750 | 719 | -20 | 1447 | 1357 | 1124 | 1502 | 3984 | # # # | # # # | # # # | # # # | 0.823 | 0.725 | 0.977 | 0.854 | # # # | # # # | # # # | - - - | 0.829 | 0.735 | 0.996 | 0.865 | - - - | 0.426 | 1.61 | 1.56 | 1.53 | 1.4 | 1.46 | 1.52 | 10.12 | 14.96 | 17.4 | 0 | - - - | - - - | - - - | - - - | 1357 | 1124 | 1502 | 3984 | Over-range | 769 | 741 | 318 | 2065 | 171 | 179 | 290 | 1472 | 1116 | 817 | 1467 | 3401 | 1116 | 817 | 1467 | 3401 | - - - | - - - | - - - | - - -
5/4/2026 | 12:45:00 PM | 278.96 | 275.91 | 274.93 | 481.77 | 475.25 | 480.22 | 4.8667 | 3.9272 | 5.4166 | 4.1404 | 1.428 | 1.428 | 1.426 | 1.553 | 1.487 | 1.505 | Over-range | 59.98 | 1119 | 778 | 1457 | 3354 | - - - | - - - | - - - | - - - | 1119 | 778 | 1457 | 3354 | 738 | 710 | 8 | 1456 | - - - | - - - | - - - | - - - | 738 | 710 | 8 | 1456 | 1352 | 1075 | 1488 | 3915 | # # # | # # # | # # # | # # # | 0.828 | 0.723 | 0.979 | 0.857 | # # # | # # # | # # # | - - - | 0.826 | 0.728 | 0.985 | 0.86 | - - - | 0.434 | 1.58 | 1.54 | 1.5 | 1.38 | 1.45 | 1.49 | 9.86 | 15.4 | 17.43 | 0 | - - - | - - - | - - - | - - - | 1352 | 1075 | 1488 | 3915 | Over-range | 757 | 733 | 302 | 2018 | 170 | 180 | 289 | 1392 | 1128 | 785 | 1471 | 3384 | 1128 | 785 | 1471 | 3384 | - - - | - - - | - - - | - - -
5/4/2026 | 1:00:00 PM | 279.2 | 276.27 | 275.31 | 482.23 | 476.01 | 480.71 | 4.4567 | 3.4328 | 5.2156 | 4.1467 | 1.428 | 1.428 | 1.426 | 1.562 | 1.514 | 1.544 | Over-range | 59.98 | 1048 | 577 | 1403 | 3027 | - - - | - - - | - - - | - - - | 1048 | 577 | 1403 | 3027 | 646 | 716 | 77 | 1439 | - - - | - - - | - - - | - - - | 646 | 716 | 77 | 1439 | 1243 | 944 | 1436 | 3623 | # # # | # # # | # # # | # # # | 0.843 | 0.61 | 0.977 | 0.836 | # # # | # # # | # # # | - - - | 0.851 | 0.621 | 0.997 | 0.849 | - - - | 0.475 | 1.6 | 1.55 | 1.52 | 1.4 | 1.46 | 1.51 | 10.72 | 16.67 | 17.81 | 0 | - - - | - - - | - - - | - - - | 1243 | 944 | 1436 | 3623 | Over-range | 667 | 738 | 302 | 1985 | 167 | 177 | 285 | 1367 | 1047 | 576 | 1405 | 3029 | 1047 | 576 | 1405 | 3029 | - - - | - - - | - - - | - - -
5/4/2026 | 1:15:00 PM | 279.21 | 276.24 | 275.23 | 482.28 | 475.84 | 480.66 | 4.6404 | 3.7532 | 5.3301 | 4.1463 | 1.428 | 1.428 | 1.426 | 1.558 | 1.501 | 1.51 | Over-range | 59.98 | 1075 | 682 | 1433 | 3189 | - - - | - - - | - - - | - - - | 1075 | 682 | 1433 | 3189 | 692 | 714 | 33 | 1438 | - - - | - - - | - - - | - - - | 692 | 714 | 33 | 1438 | 1290 | 1022 | 1466 | 3778 | # # # | # # # | # # # | # # # | 0.833 | 0.667 | 0.977 | 0.844 | # # # | # # # | # # # | - - - | 0.841 | 0.677 | 0.997 | 0.857 | - - - | 0.451 | 1.58 | 1.53 | 1.51 | 1.38 | 1.44 | 1.5 | 10.37 | 15.98 | 17.52 | 0 | - - - | - - - | - - - | - - - | 1290 | 1022 | 1466 | 3778 | Over-range | 712 | 737 | 309 | 2018 | 166 | 183 | 286 | 1414 | 1078 | 680 | 1434 | 3192 | 1078 | 680 | 1434 | 3192 | - - - | - - - | - - - | - - -
5/4/2026 | 1:30:00 PM | 278.94 | 275.95 | 274.97 | 481.75 | 475.35 | 480.24 | 5.0252 | 4.3381 | 5.5203 | 4.1332 | 1.428 | 1.428 | 1.426 | 1.551 | 1.47 | 1.451 | Over-range | 59.98 | 1138 | 926 | 1485 | 3549 | - - - | - - - | - - - | - - - | 1138 | 926 | 1485 | 3549 | 795 | 708 | -77 | 1426 | - - - | - - - | - - - | - - - | 795 | 708 | -77 | 1426 | 1399 | 1188 | 1517 | 4104 | # # # | # # # | # # # | # # # | 0.813 | 0.78 | 0.979 | 0.865 | # # # | # # # | # # # | - - - | 0.82 | 0.789 | 0.997 | 0.876 | - - - | 0.402 | 1.57 | 1.55 | 1.51 | 1.38 | 1.44 | 1.49 | 9.49 | 14.21 | 17.23 | 0 | - - - | - - - | - - - | - - - | 1399 | 1188 | 1517 | 4104 | Over-range | 813 | 732 | 312 | 2059 | 167 | 186 | 290 | 1484 | 1140 | 925 | 1486 | 3551 | 1140 | 925 | 1486 | 3551 | - - - | - - - | - - - | - - -
5/4/2026 | 1:45:00 PM | 278.98 | 275.98 | 275 | 481.8 | 475.43 | 480.29 | 5.1194 | 4.4598 | 5.5879 | 4.1434 | 1.429 | 1.429 | 1.427 | 1.546 | 1.456 | 1.434 | Over-range | 59.98 | 1155 | 989 | 1505 | 3650 | - - - | - - - | - - - | - - - | 1155 | 989 | 1505 | 3650 | 824 | 708 | -104 | 1427 | - - - | - - - | - - - | - - - | 824 | 708 | -104 | 1427 | 1428 | 1231 | 1537 | 4196 | # # # | # # # | # # # | # # # | 0.809 | 0.804 | 0.98 | 0.87 | # # # | # # # | # # # | - - - | 0.815 | 0.813 | 0.997 | 0.881 | - - - | 0.391 | 1.59 | 1.57 | 1.53 | 1.4 | 1.47 | 1.51 | 9.25 | 13.67 | 16.99 | 0 | - - - | - - - | - - - | - - - | 1428 | 1231 | 1537 | 4196 | Over-range | 840 | 732 | 308 | 2069 | 164 | 185 | 289 | 1499 | 1158 | 990 | 1503 | 3651 | 1158 | 990 | 1503 | 3651 | - - - | - - - | - - - | - - -
5/4/2026 | 2:00:00 PM | 278.97 | 276.01 | 274.97 | 481.85 | 475.41 | 480.23 | 4.9321 | 4.1527 | 5.4729 | 4.1398 | 1.429 | 1.429 | 1.427 | 1.55 | 1.474 | 1.472 | Over-range | 59.99 | 1125 | 875 | 1475 | 3475 | - - - | - - - | - - - | - - - | 1125 | 875 | 1475 | 3475 | 773 | 711 | -55 | 1428 | - - - | - - - | - - - | - - - | 773 | 711 | -55 | 1428 | 1375 | 1143 | 1505 | 4023 | # # # | # # # | # # # | # # # | 0.818 | 0.765 | 0.98 | 0.864 | # # # | # # # | # # # | - - - | 0.824 | 0.775 | 0.999 | 0.875 | - - - | 0.411 | 1.58 | 1.58 | 1.52 | 1.4 | 1.46 | 1.51 | 9.63 | 14.41 | 17.33 | 0 | - - - | - - - | - - - | - - - | 1375 | 1143 | 1505 | 4023 | Over-range | 791 | 733 | 297 | 2027 | 166 | 179 | 289 | 1439 | 1125 | 877 | 1473 | 3475 | 1125 | 877 | 1473 | 3475 | - - - | - - - | - - - | - - -
5/4/2026 | 2:15:00 PM | 278.6 | 275.5 | 274.56 | 481.08 | 474.54 | 479.64 | 5.683 | 5.3677 | 5.892 | 4.1256 | 1.429 | 1.43 | 1.428 | 1.54 | 1.464 | 1.393 | Over-range | 59.98 | 1248 | 1286 | 1574 | 4108 | - - - | - - - | - - - | - - - | 1248 | 1286 | 1574 | 4108 | 955 | 699 | -220 | 1432 | - - - | - - - | - - - | - - - | 955 | 699 | -220 | 1432 | 1581 | 1477 | 1617 | 4675 | # # # | # # # | # # # | # # # | 0.79 | 0.871 | 0.973 | 0.879 | # # # | # # # | # # # | - - - | 0.787 | 0.871 | 0.978 | 0.88 | - - - | 0.349 | 1.61 | 1.58 | 1.56 | 1.42 | 1.5 | 1.54 | 8.5 | 11.93 | 16.45 | 0 | - - - | - - - | - - - | - - - | 1581 | 1477 | 1617 | 4675 | Over-range | 970 | 725 | 372 | 2232 | 168 | 190 | 292 | 1707 | 1262 | 1303 | 1601 | 4166 | 1262 | 1303 | 1601 | 4166 | - - - | - - - | - - - | - - -
5/4/2026 | 2:30:00 PM | 278.88 | 275.86 | 274.9 | 481.62 | 475.19 | 480.15 | 5.291 | 4.7972 | 5.6969 | 4.1354 | 1.43 | 1.43 | 1.428 | 1.545 | 1.46 | 1.419 | Over-range | 59.98 | 1180 | 1089 | 1529 | 3798 | - - - | - - - | - - - | - - - | 1180 | 1089 | 1529 | 3798 | 865 | 708 | -149 | 1423 | - - - | - - - | - - - | - - - | 865 | 708 | -149 | 1423 | 1473 | 1316 | 1565 | 4355 | # # # | # # # | # # # | # # # | 0.801 | 0.828 | 0.977 | 0.872 | # # # | # # # | # # # | - - - | 0.806 | 0.836 | 0.994 | 0.882 | - - - | 0.375 | 1.62 | 1.62 | 1.57 | 1.44 | 1.5 | 1.55 | 9.02 | 12.99 | 16.74 | 0 | - - - | - - - | - - - | - - - | 1473 | 1316 | 1565 | 4355 | Over-range | 882 | 731 | 334 | 2129 | 170 | 183 | 289 | 1581 | 1180 | 1091 | 1528 | 3799 | 1180 | 1091 | 1528 | 3799 | - - - | - - - | - - - | - - -
5/4/2026 | 2:45:00 PM | 279.14 | 276.12 | 275.14 | 482.09 | 475.65 | 480.56 | 5.1047 | 4.457 | 5.5826 | 4.1394 | 1.43 | 1.43 | 1.428 | 1.548 | 1.463 | 1.446 | Over-range | 59.98 | 1151 | 978 | 1504 | 3633 | - - - | - - - | - - - | - - - | 1151 | 978 | 1504 | 3633 | 819 | 712 | -98 | 1431 | - - - | - - - | - - - | - - - | 819 | 712 | -98 | 1431 | 1424 | 1226 | 1536 | 4185 | # # # | # # # | # # # | # # # | 0.809 | 0.798 | 0.979 | 0.868 | # # # | # # # | # # # | - - - | 0.815 | 0.808 | 0.997 | 0.879 | - - - | 0.394 | 1.65 | 1.62 | 1.58 | 1.45 | 1.52 | 1.58 | 9.35 | 13.84 | 17.11 | 0 | - - - | - - - | - - - | - - - | 1424 | 1226 | 1536 | 4185 | Over-range | 837 | 735 | 312 | 2077 | 170 | 183 | 290 | 1504 | 1151 | 980 | 1502 | 3633 | 1151 | 980 | 1502 | 3633 | - - - | - - - | - - - | - - -
5/4/2026 | 3:00:00 PM | 279.12 | 276.12 | 275.11 | 482.07 | 475.59 | 480.53 | 5.5588 | 5.2661 | 5.8442 | 4.129 | 1.43 | 1.431 | 1.428 | 1.542 | 1.456 | 1.386 | Over-range | 59.98 | 1223 | 1255 | 1565 | 4042 | - - - | - - - | - - - | - - - | 1223 | 1255 | 1565 | 4042 | 940 | 708 | -220 | 1426 | - - - | - - - | - - - | - - - | 940 | 708 | -220 | 1426 | 1551 | 1454 | 1608 | 4613 | # # # | # # # | # # # | # # # | 0.788 | 0.863 | 0.973 | 0.876 | # # # | # # # | # # # | - - - | 0.794 | 0.871 | 0.99 | 0.886 | - - - | 0.353 | 1.63 | 1.6 | 1.57 | 1.45 | 1.51 | 1.56 | 8.59 | 12.06 | 16.63 | 0 | - - - | - - - | - - - | - - - | 1551 | 1454 | 1608 | 4613 | Over-range | 955 | 734 | 368 | 2222 | 170 | 192 | 294 | 1704 | 1226 | 1254 | 1564 | 4044 | 1226 | 1254 | 1564 | 4044 | - - - | - - - | - - - | - - -
5/4/2026 | 3:15:00 PM | 279.04 | 276.09 | 275.03 | 481.99 | 475.5 | 480.36 | 5.1826 | 4.6636 | 5.6352 | 4.1392 | 1.429 | 1.43 | 1.427 | 1.55 | 1.466 | 1.438 | Over-range | 59.99 | 1159 | 1010 | 1510 | 3679 | - - - | - - - | - - - | - - - | 1159 | 1010 | 1510 | 3679 | 833 | 709 | -113 | 1427 | - - - | - - - | - - - | - - - | 833 | 709 | -113 | 1427 | 1439 | 1268 | 1548 | 4255 | # # # | # # # | # # # | # # # | 0.805 | 0.797 | 0.976 | 0.865 | # # # | # # # | # # # | - - - | 0.812 | 0.805 | 0.993 | 0.876 | - - - | 0.388 | 1.65 | 1.61 | 1.56 | 1.44 | 1.51 | 1.56 | 9.36 | 13.52 | 16.88 | 0 | - - - | - - - | - - - | - - - | 1439 | 1268 | 1548 | 4255 | Over-range | 851 | 733 | 340 | 2129 | 169 | 185 | 290 | 1577 | 1162 | 1009 | 1511 | 3682 | 1162 | 1009 | 1511 | 3682 | - - - | - - - | - - - | - - -
5/4/2026 | 3:30:00 PM | 278.66 | 275.69 | 274.62 | 481.29 | 474.81 | 479.69 | 4.6216 | 3.6649 | 5.3133 | 4.1465 | 1.429 | 1.43 | 1.428 | 1.561 | 1.498 | 1.521 | Over-range | 59.97 | 1073 | 681 | 1429 | 3183 | - - - | - - - | - - - | - - - | 1073 | 681 | 1429 | 3183 | 688 | 709 | 28 | 1424 | - - - | - - - | - - - | - - - | 688 | 709 | 28 | 1424 | 1286 | 1006 | 1459 | 3751 | # # # | # # # | # # # | # # # | 0.835 | 0.677 | 0.979 | 0.849 | # # # | # # # | # # # | - - - | 0.842 | 0.689 | 0.999 | 0.861 | - - - | 0.448 | 1.63 | 1.59 | 1.57 | 1.43 | 1.5 | 1.55 | 10.32 | 16.02 | 17.61 | 0 | - - - | - - - | - - - | - - - | 1286 | 1006 | 1459 | 3751 | Over-range | 708 | 731 | 295 | 1980 | 167 | 176 | 286 | 1375 | 1073 | 683 | 1428 | 3183 | 1073 | 683 | 1428 | 3183 | - - - | - - - | - - - | - - -
5/4/2026 | 3:45:00 PM | 278.83 | 275.82 | 274.75 | 481.6 | 474.98 | 479.95 | 4.677 | 3.6906 | 5.3297 | 4.1441 | 1.429 | 1.43 | 1.428 | 1.558 | 1.501 | 1.528 | Over-range | 59.99 | 1087 | 668 | 1428 | 3182 | - - - | - - - | - - - | - - - | 1087 | 668 | 1428 | 3182 | 689 | 710 | 51 | 1451 | - - - | - - - | - - - | - - - | 689 | 710 | 51 | 1451 | 1299 | 1006 | 1463 | 3768 | # # # | # # # | # # # | # # # | 0.837 | 0.664 | 0.976 | 0.844 | # # # | # # # | # # # | - - - | 0.843 | 0.674 | 0.995 | 0.857 | - - - | 0.456 | 1.62 | 1.6 | 1.55 | 1.42 | 1.49 | 1.54 | 10.28 | 15.89 | 17.48 | 0 | - - - | - - - | - - - | - - - | 1299 | 1006 | 1463 | 3768 | Over-range | 709 | 731 | 316 | 2011 | 165 | 175 | 286 | 1389 | 1088 | 669 | 1426 | 3183 | 1088 | 669 | 1426 | 3183 | - - - | - - - | - - - | - - -
5/4/2026 | 4:00:00 PM | 278.78 | 275.68 | 274.67 | 481.45 | 474.74 | 479.87 | 4.6653 | 3.7899 | 5.328 | 4.1363 | 1.43 | 1.431 | 1.428 | 1.56 | 1.498 | 1.513 | Over-range | 59.98 | 1078 | 699 | 1429 | 3205 | - - - | - - - | - - - | - - - | 1078 | 699 | 1429 | 3205 | 696 | 707 | 20 | 1423 | - - - | - - - | - - - | - - - | 696 | 707 | 20 | 1423 | 1295 | 1029 | 1462 | 3786 | # # # | # # # | # # # | # # # | 0.832 | 0.679 | 0.977 | 0.847 | # # # | # # # | # # # | - - - | 0.84 | 0.689 | 0.997 | 0.859 | - - - | 0.444 | 1.67 | 1.61 | 1.58 | 1.45 | 1.52 | 1.58 | 10.3 | 15.77 | 17.5 | 0 | - - - | - - - | - - - | - - - | 1295 | 1029 | 1462 | 3786 | Over-range | 716 | 730 | 308 | 2007 | 167 | 180 | 285 | 1414 | 1079 | 698 | 1430 | 3207 | 1079 | 698 | 1430 | 3207 | - - - | - - - | - - - | - - -
5/4/2026 | 4:15:00 PM | 278.49 | 275.46 | 274.44 | 480.94 | 474.42 | 479.43 | 4.7477 | 3.9177 | 5.3697 | 4.1338 | 1.43 | 1.431 | 1.428 | 1.559 | 1.494 | 1.506 | Over-range | 59.98 | 1090 | 751 | 1439 | 3280 | - - - | - - - | - - - | - - - | 1090 | 751 | 1439 | 3280 | 715 | 704 | -4 | 1414 | - - - | - - - | - - - | - - - | 715 | 704 | -4 | 1414 | 1316 | 1062 | 1472 | 3850 | # # # | # # # | # # # | # # # | 0.828 | 0.707 | 0.978 | 0.852 | # # # | # # # | # # # | - - - | 0.835 | 0.717 | 0.997 | 0.864 | - - - | 0.431 | 1.63 | 1.59 | 1.58 | 1.44 | 1.51 | 1.57 | 10.09 | 15.22 | 17.41 | 0 | - - - | - - - | - - - | - - - | 1316 | 1062 | 1472 | 3850 | Over-range | 735 | 726 | 308 | 2009 | 170 | 178 | 285 | 1424 | 1090 | 750 | 1442 | 3282 | 1090 | 750 | 1442 | 3282 | - - - | - - - | - - - | - - -
5/4/2026 | 4:30:00 PM | 278.43 | 275.46 | 274.4 | 480.89 | 474.41 | 479.34 | 4.668 | 3.7566 | 5.3335 | 4.1389 | 1.43 | 1.431 | 1.428 | 1.56 | 1.5 | 1.515 | Over-range | 59.99 | 1079 | 708 | 1432 | 3220 | - - - | - - - | - - - | - - - | 1079 | 708 | 1432 | 3220 | 696 | 705 | 14 | 1415 | - - - | - - - | - - - | - - - | 696 | 705 | 14 | 1415 | 1296 | 1025 | 1463 | 3784 | # # # | # # # | # # # | # # # | 0.833 | 0.691 | 0.979 | 0.851 | # # # | # # # | # # # | - - - | 0.84 | 0.702 | 0.998 | 0.863 | - - - | 0.44 | 1.65 | 1.62 | 1.58 | 1.45 | 1.52 | 1.57 | 10.22 | 15.61 | 17.41 | 0 | - - - | - - - | - - - | - - - | 1296 | 1025 | 1463 | 3784 | Over-range | 717 | 726 | 297 | 1984 | 168 | 175 | 284 | 1389 | 1079 | 709 | 1432 | 3220 | 1079 | 709 | 1432 | 3220 | - - - | - - - | - - - | - - -
5/4/2026 | 4:45:00 PM | 280.53 | 277.45 | 276.45 | 484.46 | 477.82 | 482.97 | 5.469 | 5.0992 | 5.8024 | 4.136 | 1.43 | 1.431 | 1.428 | 1.543 | 1.451 | 1.401 | Over-range | 59.98 | 1210 | 1196 | 1565 | 3971 | - - - | - - - | - - - | - - - | 1210 | 1196 | 1565 | 3971 | 924 | 726 | -184 | 1466 | - - - | - - - | - - - | - - - | 924 | 726 | -184 | 1466 | 1534 | 1413 | 1604 | 4550 | # # # | # # # | # # # | # # # | 0.789 | 0.846 | 0.976 | 0.873 | # # # | # # # | # # # | - - - | 0.794 | 0.854 | 0.992 | 0.882 | - - - | 0.369 | 1.66 | 1.61 | 1.59 | 1.45 | 1.52 | 1.57 | 8.84 | 12.51 | 16.82 | 0 | - - - | - - - | - - - | - - - | 1534 | 1413 | 1604 | 4550 | Over-range | 942 | 751 | 352 | 2222 | 180 | 189 | 297 | 1669 | 1210 | 1196 | 1565 | 3972 | 1210 | 1196 | 1565 | 3972 | - - - | - - - | - - - | - - -
5/4/2026 | 5:00:00 PM | 281.48 | 278.69 | 277.56 | 486.35 | 479.99 | 484.64 | 5.1101 | 4.3594 | 5.5694 | 4.1487 | 1.43 | 1.431 | 1.428 | 1.547 | 1.47 | 1.473 | Over-range | 59.98 | 1160 | 937 | 1513 | 3610 | - - - | - - - | - - - | - - - | 1160 | 937 | 1513 | 3610 | 827 | 744 | -45 | 1526 | - - - | - - - | - - - | - - - | 827 | 744 | -45 | 1526 | 1436 | 1213 | 1546 | 4195 | # # # | # # # | # # # | # # # | 0.808 | 0.773 | 0.979 | 0.861 | # # # | # # # | # # # | - - - | 0.806 | 0.776 | 0.985 | 0.863 | - - - | 0.423 | 1.69 | 1.63 | 1.61 | 1.48 | 1.53 | 1.59 | 9.58 | 14.31 | 17.62 | 0 | - - - | - - - | - - - | - - - | 1436 | 1213 | 1546 | 4195 | Over-range | 847 | 768 | 314 | 2135 | 179 | 189 | 301 | 1490 | 1169 | 944 | 1529 | 3642 | 1169 | 944 | 1529 | 3642 | - - - | - - - | - - - | - - -
5/4/2026 | 5:15:00 PM | 282.1 | 279.37 | 278.24 | 487.45 | 481.31 | 485.64 | 5.6559 | 5.439 | 5.9307 | 4.1465 | 1.43 | 1.431 | 1.43 | 1.537 | 1.447 | 1.38 | Over-range | 60 | 1242 | 1306 | 1606 | 4154 | - - - | - - - | - - - | - - - | 1242 | 1306 | 1606 | 4154 | 985 | 747 | -217 | 1513 | - - - | - - - | - - - | - - - | 985 | 747 | -217 | 1513 | 1595 | 1518 | 1650 | 4763 | # # # | # # # | # # # | # # # | 0.778 | 0.86 | 0.974 | 0.872 | # # # | # # # | # # # | - - - | 0.784 | 0.868 | 0.991 | 0.882 | - - - | 0.364 | 1.65 | 1.58 | 1.57 | 1.45 | 1.49 | 1.54 | 8.71 | 12.24 | 16.91 | 0 | - - - | - - - | - - - | - - - | 1595 | 1518 | 1650 | 4763 | Over-range | 1001 | 773 | 377 | 2331 | 182 | 201 | 306 | 1773 | 1244 | 1304 | 1609 | 4156 | 1244 | 1304 | 1609 | 4156 | - - - | - - - | - - - | - - -
5/4/2026 | 5:30:00 PM | 281.79 | 278.86 | 277.81 | 486.81 | 480.38 | 485.07 | 5.4221 | 5.028 | 5.7794 | 4.1418 | 1.43 | 1.431 | 1.43 | 1.542 | 1.452 | 1.413 | Over-range | 59.98 | 1204 | 1162 | 1567 | 3933 | - - - | - - - | - - - | - - - | 1204 | 1162 | 1567 | 3933 | 920 | 743 | -158 | 1504 | - - - | - - - | - - - | - - - | 920 | 743 | -158 | 1504 | 1526 | 1396 | 1605 | 4527 | # # # | # # # | # # # | # # # | 0.789 | 0.833 | 0.976 | 0.869 | # # # | # # # | # # # | - - - | 0.794 | 0.841 | 0.994 | 0.879 | - - - | 0.383 | 1.6 | 1.58 | 1.5 | 1.41 | 1.46 | 1.5 | 9.06 | 12.9 | 17.15 | 0 | - - - | - - - | - - - | - - - | 1526 | 1396 | 1605 | 4527 | Over-range | 938 | 768 | 347 | 2241 | 181 | 194 | 302 | 1660 | 1204 | 1162 | 1569 | 3935 | 1204 | 1162 | 1569 | 3935 | - - - | - - - | - - - | - - -
5/4/2026 | 5:45:00 PM | 281.84 | 278.97 | 277.84 | 486.93 | 480.51 | 485.11 | 5.0054 | 4.2876 | 5.5356 | 4.1474 | 1.43 | 1.432 | 1.43 | 1.548 | 1.474 | 1.469 | Over-range | 59.97 | 1139 | 914 | 1508 | 3560 | - - - | - - - | - - - | - - - | 1139 | 914 | 1508 | 3560 | 814 | 747 | -48 | 1512 | - - - | - - - | - - - | - - - | 814 | 747 | -48 | 1512 | 1411 | 1196 | 1538 | 4145 | # # # | # # # | # # # | # # # | 0.807 | 0.764 | 0.98 | 0.859 | # # # | # # # | # # # | - - - | 0.814 | 0.774 | 0.999 | 0.871 | - - - | 0.425 | 1.61 | 1.55 | 1.52 | 1.42 | 1.47 | 1.51 | 9.76 | 14.46 | 17.66 | 0 | - - - | - - - | - - - | - - - | 1411 | 1196 | 1538 | 4145 | Over-range | 833 | 771 | 304 | 2122 | 177 | 190 | 300 | 1488 | 1139 | 913 | 1510 | 3562 | 1139 | 913 | 1510 | 3562 | - - - | - - - | - - - | - - -
5/4/2026 | 6:00:00 PM | 282.15 | 279.3 | 278.19 | 487.46 | 481.13 | 485.7 | 5.5317 | 5.2174 | 5.853 | 4.1458 | 1.43 | 1.43 | 1.429 | 1.54 | 1.446 | 1.397 | Over-range | 59.99 | 1222 | 1231 | 1588 | 4040 | - - - | - - - | - - - | - - - | 1222 | 1231 | 1588 | 4040 | 952 | 748 | -185 | 1513 | - - - | - - - | - - - | - - - | 952 | 748 | -185 | 1513 | 1560 | 1455 | 1628 | 4643 | # # # | # # # | # # # | # # # | 0.783 | 0.846 | 0.975 | 0.87 | # # # | # # # | # # # | - - - | 0.788 | 0.854 | 0.993 | 0.88 | - - - | 0.375 | 1.56 | 1.5 | 1.47 | 1.37 | 1.41 | 1.45 | 8.88 | 12.63 | 17.12 | 0 | - - - | - - - | - - - | - - - | 1560 | 1455 | 1628 | 4643 | Over-range | 969 | 773 | 360 | 2287 | 183 | 198 | 306 | 1713 | 1222 | 1230 | 1590 | 4042 | 1222 | 1230 | 1590 | 4042 | - - - | - - - | - - - | - - -
5/4/2026 | 6:15:00 PM | 283.07 | 280.27 | 279.04 | 489.15 | 482.69 | 487.19 | 5.4906 | 5.0288 | 5.7994 | 4.1559 | 1.43 | 1.429 | 1.429 | 1.542 | 1.45 | 1.415 | Over-range | 60 | 1223 | 1165 | 1580 | 3969 | - - - | - - - | - - - | - - - | 1223 | 1165 | 1580 | 3969 | 938 | 759 | -135 | 1561 | - - - | - - - | - - - | - - - | 938 | 759 | -135 | 1561 | 1552 | 1407 | 1618 | 4576 | # # # | # # # | # # # | # # # | 0.788 | 0.828 | 0.977 | 0.867 | # # # | # # # | # # # | - - - | 0.787 | 0.83 | 0.986 | 0.87 | - - - | 0.393 | 1.48 | 1.41 | 1.32 | 1.29 | 1.29 | 1.34 | 9.19 | 13.26 | 17.51 | 0 | - - - | - - - | - - - | - - - | 1552 | 1407 | 1618 | 4576 | Over-range | 955 | 786 | 346 | 2279 | 177 | 200 | 309 | 1655 | 1239 | 1182 | 1607 | 4027 | 1239 | 1182 | 1607 | 4027 | - - - | - - - | - - - | - - -
5/4/2026 | 6:30:00 PM | 283.27 | 280.56 | 279.29 | 489.58 | 483.18 | 487.55 | 4.5133 | 3.5933 | 5.3009 | 4.1681 | 1.43 | 1.428 | 1.429 | 1.563 | 1.525 | 1.546 | Over-range | 59.97 | 1058 | 597 | 1443 | 3099 | - - - | - - - | - - - | - - - | 1058 | 597 | 1443 | 3099 | 691 | 773 | 102 | 1567 | - - - | - - - | - - - | - - - | 691 | 773 | 102 | 1567 | 1277 | 1004 | 1480 | 3761 | # # # | # # # | # # # | # # # | 0.829 | 0.594 | 0.975 | 0.824 | # # # | # # # | # # # | - - - | 0.838 | 0.605 | 0.997 | 0.838 | - - - | 0.506 | 1.44 | 1.37 | 1.29 | 1.27 | 1.26 | 1.31 | 11.17 | 17.22 | 18.56 | 0 | - - - | - - - | - - - | - - - | 1277 | 1004 | 1480 | 3761 | Over-range | 713 | 797 | 327 | 2127 | 173 | 195 | 304 | 1439 | 1062 | 596 | 1445 | 3102 | 1062 | 596 | 1445 | 3102 | - - - | - - - | - - - | - - -
5/4/2026 | 6:45:00 PM | 283.01 | 280.2 | 279 | 489.05 | 482.64 | 487.06 | 4.9353 | 4.1954 | 5.5101 | 4.1626 | 1.43 | 1.429 | 1.429 | 1.552 | 1.49 | 1.479 | Over-range | 59.97 | 1128 | 864 | 1506 | 3497 | - - - | - - - | - - - | - - - | 1128 | 864 | 1506 | 3497 | 804 | 766 | -16 | 1553 | - - - | - - - | - - - | - - - | 804 | 766 | -16 | 1553 | 1396 | 1173 | 1537 | 4106 | # # # | # # # | # # # | # # # | 0.808 | 0.736 | 0.979 | 0.852 | # # # | # # # | # # # | - - - | 0.815 | 0.747 | 0.999 | 0.864 | - - - | 0.444 | 1.46 | 1.37 | 1.31 | 1.27 | 1.26 | 1.32 | 10.07 | 15.26 | 18.12 | 0 | - - - | - - - | - - - | - - - | 1396 | 1173 | 1537 | 4106 | Over-range | 822 | 791 | 310 | 2152 | 172 | 198 | 307 | 1489 | 1131 | 863 | 1505 | 3500 | 1131 | 863 | 1505 | 3500 | - - - | - - - | - - - | - - -
5/4/2026 | 7:00:00 PM | 283.2 | 280.5 | 279.16 | 489.49 | 483.1 | 487.28 | 5.0123 | 4.3249 | 5.5574 | 4.1672 | 1.43 | 1.428 | 1.429 | 1.553 | 1.481 | 1.468 | Over-range | 59.98 | 1141 | 913 | 1519 | 3573 | - - - | - - - | - - - | - - - | 1141 | 913 | 1519 | 3573 | 825 | 768 | -38 | 1555 | - - - | - - - | - - - | - - - | 825 | 768 | -38 | 1555 | 1419 | 1211 | 1551 | 4181 | # # # | # # # | # # # | # # # | 0.804 | 0.753 | 0.979 | 0.854 | # # # | # # # | # # # | - - - | 0.811 | 0.764 | 0.999 | 0.867 | - - - | 0.435 | 1.41 | 1.29 | 1.2 | 1.21 | 1.17 | 1.22 | 9.91 | 15.05 | 18.1 | 0 | - - - | - - - | - - - | - - - | 1419 | 1211 | 1551 | 4181 | Over-range | 844 | 794 | 313 | 2172 | 177 | 202 | 309 | 1517 | 1143 | 911 | 1522 | 3576 | 1143 | 911 | 1522 | 3576 | - - - | - - - | - - - | - - -
5/4/2026 | 7:15:00 PM | 283.69 | 281.13 | 279.8 | 490.46 | 484.17 | 488.27 | 5.5636 | 5.2821 | 5.8852 | 4.1599 | 1.43 | 1.427 | 1.429 | 1.546 | 1.44 | 1.397 | Over-range | 59.99 | 1229 | 1248 | 1606 | 4083 | - - - | - - - | - - - | - - - | 1229 | 1248 | 1606 | 4083 | 973 | 776 | -180 | 1567 | - - - | - - - | - - - | - - - | 973 | 776 | -180 | 1567 | 1578 | 1484 | 1647 | 4709 | # # # | # # # | # # # | # # # | 0.779 | 0.841 | 0.975 | 0.867 | # # # | # # # | # # # | - - - | 0.784 | 0.849 | 0.994 | 0.877 | - - - | 0.384 | 1.4 | 1.31 | 1.2 | 1.23 | 1.18 | 1.24 | 9 | 12.98 | 17.52 | 0 | - - - | - - - | - - - | - - - | 1578 | 1484 | 1647 | 4709 | Over-range | 990 | 803 | 363 | 2347 | 186 | 206 | 314 | 1746 | 1228 | 1249 | 1607 | 4084 | 1228 | 1249 | 1607 | 4084 | - - - | - - - | - - - | - - -
5/4/2026 | 7:30:00 PM | 283.88 | 281.41 | 280.01 | 490.9 | 484.62 | 488.59 | 5.5971 | 5.2301 | 5.8775 | 4.1632 | 1.43 | 1.428 | 1.429 | 1.544 | 1.442 | 1.406 | Over-range | 59.97 | 1239 | 1229 | 1606 | 4074 | - - - | - - - | - - - | - - - | 1239 | 1229 | 1606 | 4074 | 974 | 780 | -153 | 1599 | - - - | - - - | - - - | - - - | 974 | 780 | -153 | 1599 | 1587 | 1471 | 1646 | 4704 | # # # | # # # | # # # | # # # | 0.781 | 0.836 | 0.976 | 0.866 | # # # | # # # | # # # | - - - | 0.779 | 0.838 | 0.984 | 0.869 | - - - | 0.392 | 1.42 | 1.31 | 1.21 | 1.25 | 1.18 | 1.24 | 9.13 | 13.24 | 17.72 | 0 | - - - | - - - | - - - | - - - | 1587 | 1471 | 1646 | 4704 | Over-range | 992 | 807 | 360 | 2350 | 185 | 206 | 316 | 1718 | 1251 | 1237 | 1634 | 4122 | 1251 | 1237 | 1634 | 4122 | - - - | - - - | - - - | - - -
5/4/2026 | 7:45:00 PM | 284.16 | 281.73 | 280.21 | 491.41 | 485.14 | 488.95 | 5.1237 | 4.9851 | 5.6314 | 3.5855 | 1.43 | 1.427 | 1.428 | 1.552 | 1.455 | 1.465 | Over-range | 59.98 | 1158 | 1173 | 1544 | 3875 | - - - | - - - | - - - | - - - | 1158 | 1173 | 1544 | 3875 | 861 | 726 | -56 | 1530 | - - - | - - - | - - - | - - - | 861 | 726 | -56 | 1530 | 1454 | 1399 | 1578 | 4431 | # # # | # # # | # # # | # # # | 0.796 | 0.838 | 0.979 | 0.875 | # # # | # # # | # # # | - - - | 0.802 | 0.846 | 0.998 | 0.885 | - - - | 0.395 | 1.42 | 1.3 | 1.2 | 1.24 | 1.17 | 1.23 | 9.93 | 12.07 | 18.19 | 0 | - - - | - - - | - - - | - - - | 1454 | 1399 | 1578 | 4431 | Over-range | 880 | 749 | 324 | 2143 | 182 | 182 | 313 | 1499 | 1158 | 1175 | 1543 | 3876 | 1158 | 1175 | 1543 | 3876 | - - - | - - - | - - - | - - -
5/4/2026 | 8:00:00 PM | 284.64 | 282.28 | 280.79 | 492.3 | 486.13 | 489.85 | 4.8659 | 5.014 | 5.4951 | 2.7878 | 1.431 | 1.428 | 1.428 | 1.557 | 1.453 | 1.506 | Over-range | 59.98 | 1118 | 1235 | 1511 | 3863 | - - - | - - - | - - - | - - - | 1118 | 1235 | 1511 | 3863 | 798 | 671 | 18 | 1487 | - - - | - - - | - - - | - - - | 798 | 671 | 18 | 1487 | 1385 | 1415 | 1543 | 4343 | # # # | # # # | # # # | # # # | 0.807 | 0.873 | 0.979 | 0.889 | # # # | # # # | # # # | - - - | 0.814 | 0.879 | 1 | 0.901 | - - - | 0.385 | 1.43 | 1.32 | 1.2 | 1.26 | 1.18 | 1.25 | 10.53 | 10.25 | 18.69 | 0 | - - - | - - - | - - - | - - - | 1385 | 1415 | 1543 | 4343 | Over-range | 818 | 691 | 315 | 1985 | 178 | 164 | 314 | 1314 | 1119 | 1238 | 1508 | 3864 | 1119 | 1238 | 1508 | 3864 | - - - | - - - | - - - | - - -
5/4/2026 | 8:15:00 PM | 284.97 | 282.63 | 281.12 | 492.91 | 486.7 | 490.39 | 5.3031 | 5.8458 | 5.7386 | 2.7997 | 1.43 | 1.427 | 1.428 | 1.554 | 1.45 | 1.44 | Over-range | 59.97 | 1187 | 1495 | 1578 | 4260 | - - - | - - - | - - - | - - - | 1187 | 1495 | 1578 | 4260 | 916 | 675 | -93 | 1497 | - - - | - - - | - - - | - - - | 916 | 675 | -93 | 1497 | 1511 | 1650 | 1613 | 4774 | # # # | # # # | # # # | # # # | 0.786 | 0.906 | 0.978 | 0.892 | # # # | # # # | # # # | - - - | 0.792 | 0.911 | 0.998 | 0.902 | - - - | 0.351 | 1.41 | 1.28 | 1.18 | 1.24 | 1.16 | 1.23 | 9.73 | 9.31 | 18.37 | 0 | - - - | - - - | - - - | - - - | 1511 | 1650 | 1613 | 4774 | Over-range | 934 | 697 | 336 | 2155 | 181 | 173 | 321 | 1548 | 1188 | 1498 | 1575 | 4261 | 1188 | 1498 | 1575 | 4261 | - - - | - - - | - - - | - - -
5/4/2026 | 8:30:00 PM | 284.82 | 282.41 | 280.8 | 492.61 | 486.21 | 490 | 5.3256 | 5.8818 | 5.7457 | 2.8038 | 1.43 | 1.427 | 1.428 | 1.555 | 1.455 | 1.434 | Over-range | 59.98 | 1192 | 1510 | 1578 | 4280 | - - - | - - - | - - - | - - - | 1192 | 1510 | 1578 | 4280 | 920 | 671 | -105 | 1486 | - - - | - - - | - - - | - - - | 920 | 671 | -105 | 1486 | 1517 | 1661 | 1613 | 4791 | # # # | # # # | # # # | # # # | 0.786 | 0.909 | 0.978 | 0.893 | # # # | # # # | # # # | - - - | 0.792 | 0.914 | 0.997 | 0.903 | - - - | 0.347 | 1.42 | 1.28 | 1.19 | 1.23 | 1.16 | 1.22 | 9.66 | 9.16 | 18.2 | 0 | - - - | - - - | - - - | - - - | 1517 | 1661 | 1613 | 4791 | Over-range | 938 | 692 | 335 | 2154 | 182 | 171 | 318 | 1560 | 1192 | 1513 | 1576 | 4281 | 1192 | 1513 | 1576 | 4281 | - - - | - - - | - - - | - - -
5/4/2026 | 8:45:00 PM | 284.85 | 282.41 | 280.75 | 492.64 | 486.17 | 489.99 | 5.3702 | 5.8463 | 5.7465 | 2.8083 | 1.431 | 1.427 | 1.428 | 1.556 | 1.458 | 1.444 | Over-range | 59.98 | 1204 | 1498 | 1577 | 4280 | - - - | - - - | - - - | - - - | 1204 | 1498 | 1577 | 4280 | 922 | 672 | -84 | 1509 | - - - | - - - | - - - | - - - | 922 | 672 | -84 | 1509 | 1528 | 1651 | 1613 | 4793 | # # # | # # # | # # # | # # # | 0.788 | 0.907 | 0.978 | 0.893 | # # # | # # # | # # # | - - - | 0.786 | 0.905 | 0.988 | 0.894 | - - - | 0.353 | 1.43 | 1.28 | 1.19 | 1.23 | 1.17 | 1.22 | 9.63 | 9.3 | 18.41 | 0 | - - - | - - - | - - - | - - - | 1528 | 1651 | 1613 | 4793 | Over-range | 941 | 694 | 338 | 2157 | 184 | 172 | 321 | 1537 | 1216 | 1511 | 1587 | 4315 | 1216 | 1511 | 1587 | 4315 | - - - | - - - | - - - | - - -
5/4/2026 | 9:00:00 PM | 284.96 | 282.53 | 280.82 | 492.91 | 486.3 | 490.1 | 4.9256 | 5.1532 | 5.5325 | 2.8142 | 1.431 | 1.427 | 1.428 | 1.564 | 1.487 | 1.5 | Over-range | 59.98 | 1123 | 1244 | 1514 | 3882 | - - - | - - - | - - - | - - - | 1123 | 1244 | 1514 | 3882 | 808 | 677 | 12 | 1497 | - - - | - - - | - - - | - - - | 808 | 677 | 12 | 1497 | 1397 | 1435 | 1552 | 4385 | # # # | # # # | # # # | # # # | 0.804 | 0.867 | 0.975 | 0.885 | # # # | # # # | # # # | - - - | 0.811 | 0.874 | 0.997 | 0.897 | - - - | 0.386 | 1.44 | 1.29 | 1.2 | 1.23 | 1.17 | 1.23 | 10.76 | 10.73 | 18.68 | 0 | - - - | - - - | - - - | - - - | 1397 | 1435 | 1552 | 4385 | Over-range | 829 | 698 | 341 | 2037 | 183 | 168 | 317 | 1373 | 1123 | 1247 | 1513 | 3883 | 1123 | 1247 | 1513 | 3883 | - - - | - - - | - - - | - - -
5/4/2026 | 9:15:00 PM | 285.46 | 282.93 | 281.37 | 493.66 | 487.09 | 491.07 | 4.7792 | 4.8304 | 5.456 | 2.8234 | 1.431 | 1.427 | 1.427 | 1.566 | 1.482 | 1.516 | Over-range | 59.99 | 1103 | 1161 | 1499 | 3763 | - - - | - - - | - - - | - - - | 1103 | 1161 | 1499 | 3763 | 779 | 684 | 53 | 1516 | - - - | - - - | - - - | - - - | 779 | 684 | 53 | 1516 | 1362 | 1360 | 1535 | 4257 | # # # | # # # | # # # | # # # | 0.81 | 0.853 | 0.977 | 0.884 | # # # | # # # | # # # | - - - | 0.817 | 0.86 | 0.998 | 0.896 | - - - | 0.403 | 1.45 | 1.3 | 1.22 | 1.25 | 1.19 | 1.25 | 11 | 11.09 | 18.95 | 0 | - - - | - - - | - - - | - - - | 1362 | 1360 | 1535 | 4257 | Over-range | 799 | 705 | 329 | 1992 | 179 | 171 | 318 | 1289 | 1106 | 1161 | 1497 | 3764 | 1106 | 1161 | 1497 | 3764 | - - - | - - - | - - - | - - -
5/4/2026 | 9:30:00 PM | 285.9 | 283.41 | 281.8 | 494.43 | 487.91 | 491.81 | 4.8919 | 5.0237 | 5.5144 | 2.828 | 1.431 | 1.427 | 1.428 | 1.561 | 1.461 | 1.5 | Over-range | 59.99 | 1123 | 1233 | 1520 | 3876 | - - - | - - - | - - - | - - - | 1123 | 1233 | 1520 | 3876 | 814 | 690 | 25 | 1529 | - - - | - - - | - - - | - - - | 814 | 690 | 25 | 1529 | 1398 | 1423 | 1554 | 4376 | # # # | # # # | # # # | # # # | 0.803 | 0.866 | 0.978 | 0.886 | # # # | # # # | # # # | - - - | 0.81 | 0.873 | 1 | 0.897 | - - - | 0.395 | 1.46 | 1.32 | 1.22 | 1.27 | 1.2 | 1.26 | 10.8 | 10.67 | 18.92 | 0 | - - - | - - - | - - - | - - - | 1398 | 1423 | 1554 | 4376 | Over-range | 834 | 711 | 322 | 2031 | 181 | 172 | 320 | 1337 | 1125 | 1234 | 1518 | 3877 | 1125 | 1234 | 1518 | 3877 | - - - | - - - | - - - | - - -
5/4/2026 | 9:45:00 PM | 285.11 | 282.63 | 281.09 | 493.06 | 486.61 | 490.53 | 5.3734 | 5.9784 | 5.7622 | 2.8026 | 1.431 | 1.426 | 1.427 | 1.558 | 1.458 | 1.432 | Over-range | 59.99 | 1199 | 1532 | 1582 | 4313 | - - - | - - - | - - - | - - - | 1199 | 1532 | 1582 | 4313 | 933 | 676 | -113 | 1496 | - - - | - - - | - - - | - - - | 933 | 676 | -113 | 1496 | 1531 | 1685 | 1619 | 4835 | # # # | # # # | # # # | # # # | 0.783 | 0.909 | 0.977 | 0.892 | # # # | # # # | # # # | - - - | 0.789 | 0.914 | 0.996 | 0.902 | - - - | 0.347 | 1.44 | 1.3 | 1.2 | 1.24 | 1.18 | 1.25 | 9.68 | 9.2 | 18.25 | 0 | - - - | - - - | - - - | - - - | 1531 | 1685 | 1619 | 4835 | Over-range | 952 | 698 | 347 | 2185 | 187 | 170 | 321 | 1590 | 1198 | 1534 | 1581 | 4313 | 1198 | 1534 | 1581 | 4313 | - - - | - - - | - - - | - - -
5/4/2026 | 10:00:00 PM | 284.21 | 281.82 | 280.22 | 491.6 | 485.18 | 488.95 | 5.0349 | 5.3684 | 5.5882 | 2.8059 | 1.43 | 1.426 | 1.426 | 1.563 | 1.482 | 1.48 | Over-range | 59.99 | 1141 | 1314 | 1527 | 3982 | - - - | - - - | - - - | - - - | 1141 | 1314 | 1527 | 3982 | 831 | 665 | -24 | 1472 | - - - | - - - | - - - | - - - | 831 | 665 | -24 | 1472 | 1424 | 1490 | 1564 | 4479 | # # # | # # # | # # # | # # # | 0.801 | 0.882 | 0.976 | 0.889 | # # # | # # # | # # # | - - - | 0.808 | 0.888 | 0.996 | 0.9 | - - - | 0.37 | 1.42 | 1.29 | 1.18 | 1.24 | 1.17 | 1.23 | 10.37 | 10.03 | 18.25 | 0 | - - - | - - - | - - - | - - - | 1424 | 1490 | 1564 | 4479 | Over-range | 851 | 685 | 339 | 2049 | 179 | 165 | 312 | 1418 | 1141 | 1317 | 1525 | 3983 | 1141 | 1317 | 1525 | 3983 | - - - | - - - | - - - | - - -
5/4/2026 | 10:15:00 PM | 283.7 | 281.29 | 279.74 | 490.7 | 484.33 | 488.08 | 4.6786 | 4.5823 | 5.3884 | 2.7806 | 1.429 | 1.427 | 1.425 | 1.506 | 1.442 | 1.403 | Over-range | 59.99 | 1090 | 1093 | 1477 | 3660 | - - - | - - - | - - - | - - - | 1090 | 1093 | 1477 | 3660 | 733 | 656 | 76 | 1465 | - - - | - - - | - - - | - - - | 733 | 656 | 76 | 1465 | 1324 | 1285 | 1507 | 4116 | # # # | # # # | # # # | # # # | 0.823 | 0.851 | 0.98 | 0.889 | # # # | # # # | # # # | - - - | 0.821 | 0.848 | 0.982 | 0.888 | - - - | 0.4 | 1.61 | 1.46 | 1.4 | 1.43 | 1.4 | 1.44 | 11.02 | 11.24 | 18.72 | 0 | - - - | - - - | - - - | - - - | 1324 | 1285 | 1507 | 4116 | Over-range | 751 | 672 | 299 | 1882 | 165 | 146 | 284 | 1179 | 1099 | 1103 | 1492 | 3695 | 1099 | 1103 | 1492 | 3695 | - - - | - - - | - - - | - - -
5/4/2026 | 10:30:00 PM | 283.18 | 280.59 | 279.04 | 489.72 | 482.95 | 487.1 | 4.8229 | 4.8673 | 5.4496 | 2.7649 | 1.429 | 1.428 | 1.425 | 1.501 | 1.432 | 1.368 | Over-range | 59.98 | 1114 | 1193 | 1494 | 3800 | - - - | - - - | - - - | - - - | 1114 | 1193 | 1494 | 3800 | 770 | 645 | 26 | 1441 | - - - | - - - | - - - | - - - | 770 | 645 | 26 | 1441 | 1364 | 1364 | 1520 | 4248 | # # # | # # # | # # # | # # # | 0.817 | 0.875 | 0.983 | 0.895 | # # # | # # # | # # # | - - - | 0.823 | 0.879 | 0.999 | 0.904 | - - - | 0.379 | 1.62 | 1.51 | 1.45 | 1.47 | 1.44 | 1.48 | 10.55 | 10.33 | 18.28 | 0 | - - - | - - - | - - - | - - - | 1364 | 1364 | 1520 | 4248 | Over-range | 787 | 660 | 282 | 1897 | 162 | 141 | 277 | 1232 | 1113 | 1194 | 1494 | 3801 | 1113 | 1194 | 1494 | 3801 | - - - | - - - | - - - | - - -
5/4/2026 | 10:45:00 PM | 283.73 | 281.17 | 279.56 | 490.72 | 483.92 | 488 | 4.8222 | 4.9218 | 5.4485 | 2.7634 | 1.429 | 1.427 | 1.425 | 1.503 | 1.429 | 1.364 | Over-range | 59.98 | 1112 | 1211 | 1497 | 3820 | - - - | - - - | - - - | - - - | 1112 | 1211 | 1497 | 3820 | 781 | 652 | 15 | 1447 | - - - | - - - | - - - | - - - | 781 | 652 | 15 | 1447 | 1368 | 1383 | 1523 | 4275 | # # # | # # # | # # # | # # # | 0.813 | 0.875 | 0.983 | 0.894 | # # # | # # # | # # # | - - - | 0.819 | 0.88 | 1 | 0.903 | - - - | 0.379 | 1.64 | 1.51 | 1.47 | 1.48 | 1.45 | 1.49 | 10.6 | 10.38 | 18.58 | 0 | - - - | - - - | - - - | - - - | 1368 | 1383 | 1523 | 4275 | Over-range | 797 | 668 | 282 | 1918 | 159 | 148 | 281 | 1259 | 1114 | 1211 | 1495 | 3820 | 1114 | 1211 | 1495 | 3820 | - - - | - - - | - - - | - - -
5/4/2026 | 11:00:00 PM | 284.19 | 281.64 | 280.03 | 491.48 | 484.79 | 488.8 | 5.411 | 5.9732 | 5.7633 | 2.7725 | 1.43 | 1.428 | 1.425 | 1.513 | 1.466 | 1.296 | Over-range | 60 | 1209 | 1539 | 1584 | 4332 | - - - | - - - | - - - | - - - | 1209 | 1539 | 1584 | 4332 | 934 | 652 | -110 | 1475 | - - - | - - - | - - - | - - - | 934 | 652 | -110 | 1475 | 1537 | 1680 | 1614 | 4830 | # # # | # # # | # # # | # # # | 0.787 | 0.916 | 0.981 | 0.897 | # # # | # # # | # # # | - - - | 0.792 | 0.92 | 0.997 | 0.905 | - - - | 0.34 | 1.67 | 1.54 | 1.47 | 1.5 | 1.47 | 1.5 | 9.49 | 9.14 | 17.9 | 0 | - - - | - - - | - - - | - - - | 1537 | 1680 | 1614 | 4830 | Over-range | 948 | 672 | 310 | 2137 | 166 | 159 | 286 | 1545 | 1212 | 1536 | 1585 | 4333 | 1212 | 1536 | 1585 | 4333 | - - - | - - - | - - - | - - -
5/4/2026 | 11:15:00 PM | 284.35 | 281.58 | 280.01 | 491.61 | 484.57 | 489.02 | 5.3631 | 5.8697 | 5.7243 | 2.765 | 1.43 | 1.429 | 1.426 | 1.512 | 1.465 | 1.303 | Over-range | 59.97 | 1202 | 1508 | 1574 | 4284 | - - - | - - - | - - - | - - - | 1202 | 1508 | 1574 | 4284 | 922 | 654 | -95 | 1480 | - - - | - - - | - - - | - - - | 922 | 654 | -95 | 1480 | 1525 | 1651 | 1603 | 4779 | # # # | # # # | # # # | # # # | 0.789 | 0.913 | 0.982 | 0.897 | # # # | # # # | # # # | - - - | 0.794 | 0.917 | 0.998 | 0.905 | - - - | 0.346 | 1.69 | 1.58 | 1.48 | 1.51 | 1.5 | 1.53 | 9.61 | 9.21 | 17.93 | 0 | - - - | - - - | - - - | - - - | 1525 | 1651 | 1603 | 4779 | Over-range | 937 | 672 | 302 | 2117 | 170 | 154 | 284 | 1512 | 1203 | 1506 | 1576 | 4285 | 1203 | 1506 | 1576 | 4285 | - - - | - - - | - - - | - - -
5/4/2026 | 11:30:00 PM | 284.83 | 281.91 | 280.47 | 492.31 | 485.19 | 489.9 | 4.8651 | 4.8992 | 5.4406 | 2.7659 | 1.43 | 1.428 | 1.425 | 1.505 | 1.428 | 1.377 | Over-range | 60 | 1124 | 1200 | 1499 | 3822 | - - - | - - - | - - - | - - - | 1124 | 1200 | 1499 | 3822 | 793 | 662 | 41 | 1495 | - - - | - - - | - - - | - - - | 793 | 662 | 41 | 1495 | 1385 | 1379 | 1526 | 4290 | # # # | # # # | # # # | # # # | 0.811 | 0.87 | 0.982 | 0.891 | # # # | # # # | # # # | - - - | 0.817 | 0.875 | 0.999 | 0.9 | - - - | 0.391 | 1.69 | 1.56 | 1.48 | 1.51 | 1.5 | 1.53 | 10.71 | 10.64 | 18.56 | 0 | - - - | - - - | - - - | - - - | 1385 | 1379 | 1526 | 4290 | Over-range | 810 | 678 | 287 | 1948 | 166 | 146 | 282 | 1247 | 1123 | 1201 | 1498 | 3822 | 1123 | 1201 | 1498 | 3822 | - - - | - - - | - - - | - - -
5/4/2026 | 11:45:00 PM | 285.04 | 282.14 | 280.61 | 492.72 | 485.56 | 490.13 | 4.9042 | 4.9627 | 5.4787 | 2.7797 | 1.43 | 1.428 | 1.425 | 1.506 | 1.427 | 1.372 | Over-range | 59.99 | 1130 | 1222 | 1511 | 3863 | - - - | - - - | - - - | - - - | 1130 | 1222 | 1511 | 3863 | 807 | 665 | 34 | 1506 | - - - | - - - | - - - | - - - | 807 | 665 | 34 | 1506 | 1398 | 1400 | 1537 | 4335 | # # # | # # # | # # # | # # # | 0.809 | 0.873 | 0.983 | 0.891 | # # # | # # # | # # # | - - - | 0.815 | 0.878 | 1 | 0.9 | - - - | 0.39 | 1.71 | 1.59 | 1.51 | 1.54 | 1.53 | 1.55 | 10.62 | 10.66 | 18.54 | 0 | - - - | - - - | - - - | - - - | 1398 | 1400 | 1537 | 4335 | Over-range | 822 | 682 | 286 | 1967 | 161 | 153 | 283 | 1265 | 1133 | 1223 | 1508 | 3863 | 1133 | 1223 | 1508 | 3863 | - - - | - - - | - - - | - - -
5/5/2026 | 12:00:00 AM | 285.22 | 282.4 | 280.84 | 493.12 | 485.98 | 490.46 | 5.4193 | 5.9617 | 5.7429 | 2.7715 | 1.429 | 1.428 | 1.424 | 1.515 | 1.461 | 1.3 | Over-range | 59.99 | 1212 | 1536 | 1582 | 4330 | - - - | - - - | - - - | - - - | 1212 | 1536 | 1582 | 4330 | 943 | 663 | -101 | 1504 | - - - | - - - | - - - | - - - | 943 | 663 | -101 | 1504 | 1545 | 1681 | 1613 | 4839 | # # # | # # # | # # # | # # # | 0.785 | 0.913 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.79 | 0.918 | 0.997 | 0.903 | - - - | 0.347 | 1.68 | 1.58 | 1.49 | 1.52 | 1.51 | 1.53 | 9.64 | 9.32 | 18.21 | 0 | - - - | - - - | - - - | - - - | 1545 | 1681 | 1613 | 4839 | Over-range | 958 | 683 | 311 | 2159 | 163 | 163 | 290 | 1547 | 1216 | 1535 | 1580 | 4331 | 1216 | 1535 | 1580 | 4331 | - - - | - - - | - - - | - - -
5/5/2026 | 12:15:00 AM | 285.25 | 282.36 | 280.79 | 493.17 | 485.85 | 490.45 | 5.1666 | 5.4969 | 5.6214 | 2.777 | 1.428 | 1.426 | 1.423 | 1.511 | 1.459 | 1.337 | Over-range | 59.98 | 1170 | 1372 | 1547 | 4089 | - - - | - - - | - - - | - - - | 1170 | 1372 | 1547 | 4089 | 873 | 667 | -28 | 1511 | - - - | - - - | - - - | - - - | 873 | 667 | -28 | 1511 | 1470 | 1539 | 1577 | 4586 | # # # | # # # | # # # | # # # | 0.796 | 0.892 | 0.981 | 0.892 | # # # | # # # | # # # | - - - | 0.801 | 0.896 | 0.997 | 0.9 | - - - | 0.37 | 1.68 | 1.55 | 1.49 | 1.52 | 1.5 | 1.52 | 10.27 | 10.05 | 18.27 | 0 | - - - | - - - | - - - | - - - | 1470 | 1539 | 1577 | 4586 | Over-range | 889 | 685 | 305 | 2074 | 168 | 154 | 286 | 1416 | 1170 | 1373 | 1546 | 4089 | 1170 | 1373 | 1546 | 4089 | - - - | - - - | - - - | - - -
5/5/2026 | 12:30:00 AM | 285.4 | 282.52 | 280.85 | 493.46 | 486.11 | 490.54 | 4.6677 | 4.3667 | 5.3398 | 2.7848 | 1.428 | 1.426 | 1.423 | 1.498 | 1.455 | 1.429 | Over-range | 59.98 | 1096 | 1015 | 1462 | 3573 | - - - | - - - | - - - | - - - | 1096 | 1015 | 1462 | 3573 | 729 | 675 | 150 | 1554 | - - - | - - - | - - - | - - - | 729 | 675 | 150 | 1554 | 1328 | 1230 | 1499 | 4057 | # # # | # # # | # # # | # # # | 0.826 | 0.825 | 0.975 | 0.881 | # # # | # # # | # # # | - - - | 0.824 | 0.824 | 0.98 | 0.881 | - - - | 0.435 | 1.67 | 1.56 | 1.47 | 1.5 | 1.49 | 1.51 | 11.49 | 12.02 | 18.94 | 0 | - - - | - - - | - - - | - - - | 1328 | 1230 | 1499 | 4057 | Over-range | 748 | 691 | 328 | 1920 | 166 | 149 | 284 | 1121 | 1107 | 1023 | 1475 | 3605 | 1107 | 1023 | 1475 | 3605 | - - - | - - - | - - - | - - -
5/5/2026 | 12:45:00 AM | 285.69 | 282.67 | 281.07 | 493.83 | 486.36 | 491.06 | 4.8124 | 4.7881 | 5.4294 | 2.7835 | 1.428 | 1.426 | 1.423 | 1.508 | 1.429 | 1.387 | Over-range | 59.99 | 1115 | 1162 | 1497 | 3774 | - - - | - - - | - - - | - - - | 1115 | 1162 | 1497 | 3774 | 786 | 674 | 66 | 1525 | - - - | - - - | - - - | - - - | 786 | 674 | 66 | 1525 | 1374 | 1352 | 1526 | 4253 | # # # | # # # | # # # | # # # | 0.812 | 0.859 | 0.981 | 0.888 | # # # | # # # | # # # | - - - | 0.818 | 0.864 | 0.999 | 0.897 | - - - | 0.404 | 1.68 | 1.57 | 1.47 | 1.51 | 1.49 | 1.51 | 11.02 | 11.06 | 18.81 | 0 | - - - | - - - | - - - | - - - | 1374 | 1352 | 1526 | 4253 | Over-range | 803 | 691 | 294 | 1959 | 162 | 154 | 285 | 1228 | 1119 | 1161 | 1495 | 3775 | 1119 | 1161 | 1495 | 3775 | - - - | - - - | - - - | - - -
5/5/2026 | 1:00:00 AM | 286.05 | 283.16 | 281.55 | 494.57 | 487.24 | 491.74 | 4.8086 | 4.7805 | 5.4367 | 2.7857 | 1.428 | 1.425 | 1.422 | 1.508 | 1.422 | 1.389 | Over-range | 59.99 | 1115 | 1160 | 1502 | 3776 | - - - | - - - | - - - | - - - | 1115 | 1160 | 1502 | 3776 | 789 | 680 | 72 | 1541 | - - - | - - - | - - - | - - - | 789 | 680 | 72 | 1541 | 1375 | 1354 | 1531 | 4260 | # # # | # # # | # # # | # # # | 0.81 | 0.857 | 0.981 | 0.886 | # # # | # # # | # # # | - - - | 0.817 | 0.862 | 0.999 | 0.896 | - - - | 0.408 | 1.7 | 1.56 | 1.48 | 1.52 | 1.5 | 1.52 | 11.11 | 11.16 | 18.88 | 0 | - - - | - - - | - - - | - - - | 1375 | 1354 | 1531 | 4260 | Over-range | 806 | 698 | 296 | 1971 | 163 | 155 | 287 | 1229 | 1117 | 1160 | 1499 | 3776 | 1117 | 1160 | 1499 | 3776 | - - - | - - - | - - - | - - -
5/5/2026 | 1:15:00 AM | 285.33 | 282.36 | 280.91 | 493.15 | 486.02 | 490.64 | 5.0463 | 5.2475 | 5.5376 | 2.7676 | 1.427 | 1.424 | 1.421 | 1.513 | 1.431 | 1.354 | Over-range | 59.98 | 1152 | 1307 | 1527 | 3987 | - - - | - - - | - - - | - - - | 1152 | 1307 | 1527 | 3987 | 845 | 669 | 0 | 1513 | - - - | - - - | - - - | - - - | 845 | 669 | 0 | 1513 | 1439 | 1477 | 1555 | 4471 | # # # | # # # | # # # | # # # | 0.801 | 0.885 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.806 | 0.89 | 0.999 | 0.901 | - - - | 0.38 | 1.67 | 1.55 | 1.44 | 1.5 | 1.48 | 1.49 | 10.42 | 10.27 | 18.72 | 0 | - - - | - - - | - - - | - - - | 1439 | 1477 | 1555 | 4471 | Over-range | 861 | 686 | 294 | 2024 | 167 | 151 | 288 | 1342 | 1152 | 1309 | 1525 | 3986 | 1152 | 1309 | 1525 | 3986 | - - - | - - - | - - - | - - -
5/5/2026 | 1:30:00 AM | 285.44 | 282.47 | 280.95 | 493.4 | 486.13 | 490.74 | 5.3666 | 5.8626 | 5.7285 | 2.7722 | 1.427 | 1.424 | 1.422 | 1.517 | 1.448 | 1.306 | Over-range | 59.98 | 1204 | 1505 | 1581 | 4289 | - - - | - - - | - - - | - - - | 1204 | 1505 | 1581 | 4289 | 931 | 667 | -85 | 1512 | - - - | - - - | - - - | - - - | 931 | 667 | -85 | 1512 | 1531 | 1654 | 1609 | 4794 | # # # | # # # | # # # | # # # | 0.786 | 0.91 | 0.982 | 0.895 | # # # | # # # | # # # | - - - | 0.791 | 0.914 | 0.999 | 0.903 | - - - | 0.353 | 1.68 | 1.56 | 1.44 | 1.51 | 1.49 | 1.5 | 9.78 | 9.27 | 18.09 | 0 | - - - | - - - | - - - | - - - | 1531 | 1654 | 1609 | 4794 | Over-range | 946 | 685 | 302 | 2142 | 166 | 157 | 288 | 1515 | 1206 | 1505 | 1579 | 4290 | 1206 | 1505 | 1579 | 4290 | - - - | - - - | - - - | - - -
5/5/2026 | 1:45:00 AM | 285.92 | 283.05 | 281.58 | 494.29 | 487.2 | 491.69 | 4.9842 | 5.1865 | 5.5629 | 2.7791 | 1.427 | 1.424 | 1.422 | 1.508 | 1.452 | 1.363 | Over-range | 59.99 | 1140 | 1265 | 1534 | 3939 | - - - | - - - | - - - | - - - | 1140 | 1265 | 1534 | 3939 | 830 | 682 | 26 | 1537 | - - - | - - - | - - - | - - - | 830 | 682 | 26 | 1537 | 1421 | 1453 | 1565 | 4439 | # # # | # # # | # # # | # # # | 0.802 | 0.871 | 0.98 | 0.887 | # # # | # # # | # # # | - - - | 0.808 | 0.876 | 0.997 | 0.896 | - - - | 0.39 | 1.7 | 1.55 | 1.49 | 1.52 | 1.51 | 1.52 | 10.81 | 10.72 | 18.56 | 0 | - - - | - - - | - - - | - - - | 1421 | 1453 | 1565 | 4439 | Over-range | 847 | 701 | 310 | 2045 | 168 | 162 | 289 | 1343 | 1142 | 1263 | 1535 | 3940 | 1142 | 1263 | 1535 | 3940 | - - - | - - - | - - - | - - -
5/5/2026 | 2:00:00 AM | 286.39 | 283.68 | 282.16 | 495.21 | 488.36 | 492.52 | 4.615 | 4.4369 | 5.3604 | 2.7906 | 1.427 | 1.424 | 1.421 | 1.504 | 1.45 | 1.416 | Over-range | 60.01 | 1082 | 1037 | 1478 | 3597 | - - - | - - - | - - - | - - - | 1082 | 1037 | 1478 | 3597 | 739 | 689 | 131 | 1559 | - - - | - - - | - - - | - - - | 739 | 689 | 131 | 1559 | 1321 | 1256 | 1512 | 4089 | # # # | # # # | # # # | # # # | 0.819 | 0.826 | 0.977 | 0.879 | # # # | # # # | # # # | - - - | 0.826 | 0.831 | 0.995 | 0.89 | - - - | 0.433 | 1.69 | 1.56 | 1.47 | 1.52 | 1.5 | 1.51 | 11.71 | 12.22 | 19.29 | 0 | - - - | - - - | - - - | - - - | 1321 | 1256 | 1512 | 4089 | Over-range | 758 | 706 | 321 | 1946 | 166 | 158 | 290 | 1163 | 1084 | 1035 | 1478 | 3598 | 1084 | 1035 | 1478 | 3598 | - - - | - - - | - - - | - - -
5/5/2026 | 2:15:00 AM | 286.29 | 283.69 | 282.21 | 495.07 | 488.49 | 492.45 | 4.7945 | 4.7631 | 5.4469 | 2.7898 | 1.427 | 1.423 | 1.422 | 1.507 | 1.428 | 1.391 | Over-range | 59.99 | 1111 | 1149 | 1506 | 3767 | - - - | - - - | - - - | - - - | 1111 | 1149 | 1506 | 3767 | 788 | 689 | 83 | 1560 | - - - | - - - | - - - | - - - | 788 | 689 | 83 | 1560 | 1372 | 1350 | 1537 | 4259 | # # # | # # # | # # # | # # # | 0.81 | 0.851 | 0.98 | 0.884 | # # # | # # # | # # # | - - - | 0.816 | 0.857 | 0.998 | 0.894 | - - - | 0.414 | 1.69 | 1.57 | 1.48 | 1.52 | 1.5 | 1.51 | 11.2 | 11.44 | 19.15 | 0 | - - - | - - - | - - - | - - - | 1372 | 1350 | 1537 | 4259 | Over-range | 805 | 707 | 305 | 1988 | 165 | 158 | 292 | 1231 | 1114 | 1149 | 1504 | 3767 | 1114 | 1149 | 1504 | 3767 | - - - | - - - | - - - | - - -
5/5/2026 | 2:30:00 AM | 286.22 | 283.59 | 282.18 | 494.9 | 488.39 | 492.39 | 4.8689 | 4.9061 | 5.4822 | 2.7821 | 1.426 | 1.423 | 1.422 | 1.509 | 1.42 | 1.381 | Over-range | 59.99 | 1124 | 1197 | 1517 | 3838 | - - - | - - - | - - - | - - - | 1124 | 1197 | 1517 | 3838 | 806 | 689 | 62 | 1556 | - - - | - - - | - - - | - - - | 806 | 689 | 62 | 1556 | 1393 | 1390 | 1547 | 4330 | # # # | # # # | # # # | # # # | 0.807 | 0.861 | 0.981 | 0.886 | # # # | # # # | # # # | - - - | 0.812 | 0.866 | 0.999 | 0.896 | - - - | 0.406 | 1.69 | 1.57 | 1.49 | 1.53 | 1.51 | 1.53 | 10.98 | 11.19 | 19.11 | 0 | - - - | - - - | - - - | - - - | 1393 | 1390 | 1547 | 4330 | Over-range | 824 | 706 | 301 | 2005 | 169 | 155 | 293 | 1264 | 1123 | 1198 | 1515 | 3837 | 1123 | 1198 | 1515 | 3837 | - - - | - - - | - - - | - - -
5/5/2026 | 2:45:00 AM | 286.36 | 283.8 | 282.31 | 495.22 | 488.71 | 492.58 | 5.3889 | 5.7189 | 5.7189 | 2.7792 | 1.428 | 1.424 | 1.422 | 1.512 | 1.438 | 1.33 | Over-range | 59.98 | 1215 | 1459 | 1584 | 4258 | - - - | - - - | - - - | - - - | 1215 | 1459 | 1584 | 4258 | 931 | 687 | -27 | 1590 | - - - | - - - | - - - | - - - | 931 | 687 | -27 | 1590 | 1540 | 1621 | 1614 | 4776 | # # # | # # # | # # # | # # # | 0.789 | 0.9 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.786 | 0.897 | 0.988 | 0.892 | - - - | 0.373 | 1.69 | 1.55 | 1.5 | 1.53 | 1.5 | 1.53 | 10.08 | 9.98 | 18.73 | 0 | - - - | - - - | - - - | - - - | 1540 | 1621 | 1614 | 4776 | Over-range | 946 | 706 | 309 | 2162 | 168 | 162 | 298 | 1460 | 1231 | 1482 | 1607 | 4321 | 1231 | 1482 | 1607 | 4321 | - - - | - - - | - - - | - - -
5/5/2026 | 3:00:00 AM | 286.49 | 283.98 | 282.58 | 495.44 | 489.15 | 492.93 | 5.1815 | 5.4957 | 5.647 | 2.7853 | 1.427 | 1.423 | 1.421 | 1.514 | 1.43 | 1.337 | Over-range | 59.99 | 1173 | 1389 | 1567 | 4130 | - - - | - - - | - - - | - - - | 1173 | 1389 | 1567 | 4130 | 893 | 690 | -17 | 1565 | - - - | - - - | - - - | - - - | 893 | 690 | -17 | 1565 | 1484 | 1560 | 1596 | 4640 | # # # | # # # | # # # | # # # | 0.791 | 0.89 | 0.982 | 0.89 | # # # | # # # | # # # | - - - | 0.796 | 0.896 | 0.999 | 0.899 | - - - | 0.379 | 1.7 | 1.55 | 1.46 | 1.52 | 1.49 | 1.52 | 10.36 | 10.27 | 18.83 | 0 | - - - | - - - | - - - | - - - | 1484 | 1560 | 1596 | 4640 | Over-range | 909 | 709 | 299 | 2115 | 167 | 166 | 297 | 1422 | 1176 | 1389 | 1565 | 4130 | 1176 | 1389 | 1565 | 4130 | - - - | - - - | - - - | - - -
5/5/2026 | 3:15:00 AM | 286.48 | 284.04 | 282.58 | 495.52 | 489.2 | 492.88 | 5.0391 | 5.2815 | 5.5832 | 2.7855 | 1.427 | 1.423 | 1.422 | 1.508 | 1.468 | 1.362 | Over-range | 59.98 | 1145 | 1283 | 1542 | 3971 | - - - | - - - | - - - | - - - | 1145 | 1283 | 1542 | 3971 | 848 | 693 | 29 | 1570 | - - - | - - - | - - - | - - - | 848 | 693 | 29 | 1570 | 1437 | 1478 | 1576 | 4491 | # # # | # # # | # # # | # # # | 0.797 | 0.869 | 0.978 | 0.884 | # # # | # # # | # # # | - - - | 0.803 | 0.874 | 0.996 | 0.894 | - - - | 0.395 | 1.72 | 1.57 | 1.49 | 1.53 | 1.5 | 1.54 | 10.92 | 11.17 | 18.91 | 0 | - - - | - - - | - - - | - - - | 1437 | 1478 | 1576 | 4491 | Over-range | 865 | 712 | 324 | 2094 | 168 | 166 | 295 | 1377 | 1148 | 1282 | 1542 | 3972 | 1148 | 1282 | 1542 | 3972 | - - - | - - - | - - - | - - -
5/5/2026 | 3:30:00 AM | 286.6 | 284.15 | 282.76 | 495.65 | 489.49 | 493.17 | 4.6598 | 4.5252 | 5.3934 | 2.7854 | 1.427 | 1.424 | 1.422 | 1.505 | 1.441 | 1.414 | Over-range | 59.99 | 1089 | 1066 | 1491 | 3645 | - - - | - - - | - - - | - - - | 1089 | 1066 | 1491 | 3645 | 753 | 698 | 125 | 1576 | - - - | - - - | - - - | - - - | 753 | 698 | 125 | 1576 | 1335 | 1284 | 1525 | 4145 | # # # | # # # | # # # | # # # | 0.815 | 0.83 | 0.977 | 0.88 | # # # | # # # | # # # | - - - | 0.822 | 0.837 | 0.996 | 0.89 | - - - | 0.432 | 1.71 | 1.57 | 1.49 | 1.53 | 1.51 | 1.54 | 11.62 | 12.22 | 19.48 | 0 | - - - | - - - | - - - | - - - | 1335 | 1284 | 1525 | 4145 | Over-range | 773 | 715 | 322 | 1972 | 172 | 158 | 295 | 1184 | 1088 | 1066 | 1492 | 3646 | 1088 | 1066 | 1492 | 3646 | - - - | - - - | - - - | - - -
5/5/2026 | 3:45:00 AM | 286.69 | 284.3 | 282.81 | 495.9 | 489.69 | 493.24 | 4.7357 | 4.6632 | 5.429 | 2.7864 | 1.427 | 1.423 | 1.422 | 1.506 | 1.431 | 1.402 | Over-range | 59.99 | 1101 | 1114 | 1503 | 3718 | - - - | - - - | - - - | - - - | 1101 | 1114 | 1503 | 3718 | 775 | 699 | 105 | 1579 | - - - | - - - | - - - | - - - | 775 | 699 | 105 | 1579 | 1357 | 1325 | 1535 | 4218 | # # # | # # # | # # # | # # # | 0.811 | 0.841 | 0.979 | 0.881 | # # # | # # # | # # # | - - - | 0.818 | 0.847 | 0.997 | 0.892 | - - - | 0.425 | 1.71 | 1.55 | 1.49 | 1.53 | 1.49 | 1.53 | 11.46 | 11.92 | 19.43 | 0 | - - - | - - - | - - - | - - - | 1357 | 1325 | 1535 | 4218 | Over-range | 794 | 717 | 315 | 1992 | 173 | 158 | 296 | 1214 | 1100 | 1114 | 1503 | 3718 | 1100 | 1114 | 1503 | 3718 | - - - | - - - | - - - | - - -
5/5/2026 | 4:00:00 AM | 286.61 | 284.22 | 282.83 | 495.76 | 489.62 | 493.2 | 4.7366 | 4.6586 | 5.4257 | 2.7864 | 1.427 | 1.423 | 1.422 | 1.505 | 1.429 | 1.403 | Over-range | 60 | 1102 | 1114 | 1502 | 3718 | - - - | - - - | - - - | - - - | 1102 | 1114 | 1502 | 3718 | 776 | 697 | 105 | 1577 | - - - | - - - | - - - | - - - | 776 | 697 | 105 | 1577 | 1358 | 1324 | 1535 | 4216 | # # # | # # # | # # # | # # # | 0.811 | 0.842 | 0.979 | 0.882 | # # # | # # # | # # # | - - - | 0.818 | 0.848 | 0.998 | 0.892 | - - - | 0.424 | 1.74 | 1.58 | 1.54 | 1.55 | 1.53 | 1.57 | 11.4 | 11.88 | 19.4 | 0 | - - - | - - - | - - - | - - - | 1358 | 1324 | 1535 | 4216 | Over-range | 793 | 715 | 313 | 1988 | 166 | 160 | 295 | 1209 | 1104 | 1115 | 1500 | 3718 | 1104 | 1115 | 1500 | 3718 | - - - | - - - | - - - | - - -
5/5/2026 | 4:15:00 AM | 286.48 | 284.19 | 282.7 | 495.63 | 489.53 | 492.92 | 4.8805 | 4.9334 | 5.4981 | 2.7865 | 1.426 | 1.423 | 1.421 | 1.508 | 1.429 | 1.383 | Over-range | 59.98 | 1124 | 1201 | 1523 | 3848 | - - - | - - - | - - - | - - - | 1124 | 1201 | 1523 | 3848 | 814 | 695 | 68 | 1577 | - - - | - - - | - - - | - - - | 814 | 695 | 68 | 1577 | 1397 | 1399 | 1554 | 4350 | # # # | # # # | # # # | # # # | 0.804 | 0.859 | 0.98 | 0.884 | # # # | # # # | # # # | - - - | 0.811 | 0.865 | 0.999 | 0.895 | - - - | 0.41 | 1.72 | 1.57 | 1.51 | 1.53 | 1.51 | 1.55 | 11.06 | 11.46 | 19.31 | 0 | - - - | - - - | - - - | - - - | 1397 | 1399 | 1554 | 4350 | Over-range | 830 | 715 | 309 | 2029 | 166 | 165 | 297 | 1276 | 1127 | 1200 | 1522 | 3849 | 1127 | 1200 | 1522 | 3849 | - - - | - - - | - - - | - - -
5/5/2026 | 4:30:00 AM | 286.41 | 284.06 | 282.65 | 495.42 | 489.37 | 492.85 | 5.2008 | 5.5428 | 5.6605 | 2.78 | 1.426 | 1.423 | 1.422 | 1.509 | 1.43 | 1.336 | Over-range | 59.99 | 1176 | 1402 | 1571 | 4148 | - - - | - - - | - - - | - - - | 1176 | 1402 | 1571 | 4148 | 897 | 691 | -21 | 1566 | - - - | - - - | - - - | - - - | 897 | 691 | -21 | 1566 | 1489 | 1572 | 1600 | 4661 | # # # | # # # | # # # | # # # | 0.79 | 0.892 | 0.982 | 0.89 | # # # | # # # | # # # | - - - | 0.795 | 0.896 | 0.999 | 0.899 | - - - | 0.378 | 1.71 | 1.58 | 1.52 | 1.53 | 1.52 | 1.56 | 10.3 | 10.24 | 18.75 | 0 | - - - | - - - | - - - | - - - | 1489 | 1572 | 1600 | 4661 | Over-range | 913 | 710 | 301 | 2124 | 170 | 166 | 297 | 1433 | 1178 | 1399 | 1572 | 4150 | 1178 | 1399 | 1572 | 4150 | - - - | - - - | - - - | - - -
5/5/2026 | 4:45:00 AM | 285.86 | 283.48 | 282.07 | 494.48 | 488.31 | 491.91 | 5.1017 | 5.3509 | 5.5966 | 2.7719 | 1.426 | 1.423 | 1.422 | 1.509 | 1.431 | 1.348 | Over-range | 59.99 | 1160 | 1345 | 1551 | 4056 | - - - | - - - | - - - | - - - | 1160 | 1345 | 1551 | 4056 | 869 | 682 | -1 | 1549 | - - - | - - - | - - - | - - - | 869 | 682 | -1 | 1549 | 1458 | 1517 | 1579 | 4554 | # # # | # # # | # # # | # # # | 0.795 | 0.887 | 0.983 | 0.891 | # # # | # # # | # # # | - - - | 0.802 | 0.892 | 1 | 0.9 | - - - | 0.382 | 1.7 | 1.59 | 1.54 | 1.53 | 1.52 | 1.55 | 10.39 | 10.37 | 18.77 | 0 | - - - | - - - | - - - | - - - | 1458 | 1517 | 1579 | 4554 | Over-range | 884 | 701 | 293 | 2070 | 163 | 163 | 293 | 1374 | 1164 | 1344 | 1549 | 4057 | 1164 | 1344 | 1549 | 4057 | - - - | - - - | - - - | - - -
5/5/2026 | 5:00:00 AM | 285.86 | 283.47 | 282.05 | 494.45 | 488.28 | 491.9 | 4.6352 | 4.5113 | 5.3756 | 2.7747 | 1.426 | 1.424 | 1.423 | 1.499 | 1.469 | 1.415 | Over-range | 59.99 | 1082 | 1045 | 1479 | 3605 | - - - | - - - | - - - | - - - | 1082 | 1045 | 1479 | 3605 | 739 | 686 | 131 | 1556 | - - - | - - - | - - - | - - - | 739 | 686 | 131 | 1556 | 1321 | 1266 | 1515 | 4102 | # # # | # # # | # # # | # # # | 0.819 | 0.826 | 0.976 | 0.879 | # # # | # # # | # # # | - - - | 0.826 | 0.832 | 0.994 | 0.889 | - - - | 0.432 | 1.7 | 1.62 | 1.53 | 1.53 | 1.53 | 1.57 | 11.66 | 12.32 | 19.11 | 0 | - - - | - - - | - - - | - - - | 1321 | 1266 | 1515 | 4102 | Over-range | 758 | 704 | 329 | 1956 | 163 | 156 | 288 | 1179 | 1084 | 1045 | 1477 | 3606 | 1084 | 1045 | 1477 | 3606 | - - - | - - - | - - - | - - -
5/5/2026 | 5:15:00 AM | 285.23 | 282.71 | 281.31 | 493.3 | 486.9 | 490.75 | 4.8284 | 4.7232 | 5.4495 | 2.764 | 1.426 | 1.424 | 1.423 | 1.497 | 1.431 | 1.397 | Over-range | 60.01 | 1122 | 1138 | 1499 | 3759 | - - - | - - - | - - - | - - - | 1122 | 1138 | 1499 | 3759 | 775 | 672 | 98 | 1545 | - - - | - - - | - - - | - - - | 775 | 672 | 98 | 1545 | 1374 | 1332 | 1533 | 4239 | # # # | # # # | # # # | # # # | 0.816 | 0.854 | 0.978 | 0.887 | # # # | # # # | # # # | - - - | 0.814 | 0.853 | 0.984 | 0.887 | - - - | 0.411 | 1.71 | 1.59 | 1.57 | 1.53 | 1.54 | 1.58 | 10.9 | 11.4 | 18.8 | 0 | - - - | - - - | - - - | - - - | 1374 | 1332 | 1533 | 4239 | Over-range | 793 | 689 | 316 | 1959 | 167 | 153 | 288 | 1195 | 1132 | 1144 | 1513 | 3789 | 1132 | 1144 | 1513 | 3789 | - - - | - - - | - - - | - - -
5/5/2026 | 5:30:00 AM | 284.7 | 282.02 | 280.58 | 492.34 | 485.53 | 489.7 | 4.749 | 4.7851 | 5.4295 | 2.7526 | 1.426 | 1.424 | 1.424 | 1.496 | 1.42 | 1.377 | Over-range | 60.01 | 1100 | 1167 | 1496 | 3764 | - - - | - - - | - - - | - - - | 1100 | 1167 | 1496 | 3764 | 769 | 660 | 49 | 1478 | - - - | - - - | - - - | - - - | 769 | 660 | 49 | 1478 | 1352 | 1349 | 1523 | 4225 | # # # | # # # | # # # | # # # | 0.814 | 0.865 | 0.982 | 0.891 | # # # | # # # | # # # | - - - | 0.821 | 0.87 | 0.999 | 0.901 | - - - | 0.393 | 1.7 | 1.59 | 1.55 | 1.53 | 1.55 | 1.57 | 10.84 | 10.85 | 18.56 | 0 | - - - | - - - | - - - | - - - | 1352 | 1349 | 1523 | 4225 | Over-range | 785 | 677 | 286 | 1919 | 160 | 152 | 281 | 1224 | 1104 | 1165 | 1497 | 3765 | 1104 | 1165 | 1497 | 3765 | - - - | - - - | - - - | - - -
5/5/2026 | 5:45:00 AM | 284.54 | 281.73 | 280.36 | 491.93 | 485.06 | 489.41 | 5.1291 | 5.529 | 5.6295 | 2.7446 | 1.426 | 1.425 | 1.424 | 1.502 | 1.449 | 1.324 | Over-range | 60 | 1161 | 1398 | 1550 | 4108 | - - - | - - - | - - - | - - - | 1161 | 1398 | 1550 | 4108 | 867 | 653 | -53 | 1467 | - - - | - - - | - - - | - - - | 867 | 653 | -53 | 1467 | 1458 | 1552 | 1578 | 4588 | # # # | # # # | # # # | # # # | 0.796 | 0.901 | 0.982 | 0.895 | # # # | # # # | # # # | - - - | 0.802 | 0.905 | 0.998 | 0.904 | - - - | 0.357 | 1.71 | 1.64 | 1.56 | 1.53 | 1.56 | 1.59 | 9.96 | 9.81 | 18.15 | 0 | - - - | - - - | - - - | - - - | 1458 | 1552 | 1578 | 4588 | Over-range | 882 | 672 | 296 | 2042 | 158 | 157 | 285 | 1418 | 1164 | 1397 | 1547 | 4109 | 1164 | 1397 | 1547 | 4109 | - - - | - - - | - - - | - - -
5/5/2026 | 6:00:00 AM | 284.32 | 281.78 | 280.39 | 491.72 | 485.28 | 489.17 | 5.3121 | 5.8849 | 5.7394 | 2.742 | 1.426 | 1.425 | 1.423 | 1.503 | 1.461 | 1.296 | Over-range | 60.01 | 1190 | 1515 | 1580 | 4285 | - - - | - - - | - - - | - - - | 1190 | 1515 | 1580 | 4285 | 916 | 652 | -103 | 1464 | - - - | - - - | - - - | - - - | 916 | 652 | -103 | 1464 | 1510 | 1657 | 1609 | 4776 | # # # | # # # | # # # | # # # | 0.788 | 0.914 | 0.982 | 0.897 | # # # | # # # | # # # | - - - | 0.793 | 0.918 | 0.997 | 0.905 | - - - | 0.342 | 1.73 | 1.65 | 1.59 | 1.56 | 1.57 | 1.62 | 9.56 | 9.23 | 17.85 | 0 | - - - | - - - | - - - | - - - | 1510 | 1657 | 1609 | 4776 | Over-range | 930 | 671 | 305 | 2111 | 159 | 159 | 285 | 1519 | 1193 | 1514 | 1578 | 4286 | 1193 | 1514 | 1578 | 4286 | - - - | - - - | - - - | - - -
5/5/2026 | 6:15:00 AM | 283.72 | 281.3 | 279.88 | 490.76 | 484.42 | 488.22 | 4.6464 | 4.637 | 5.3647 | 2.7308 | 1.427 | 1.427 | 1.425 | 1.489 | 1.464 | 1.388 | Over-range | 60 | 1079 | 1095 | 1469 | 3644 | - - - | - - - | - - - | - - - | 1079 | 1095 | 1469 | 3644 | 730 | 652 | 77 | 1459 | - - - | - - - | - - - | - - - | 730 | 652 | 77 | 1459 | 1314 | 1289 | 1500 | 4104 | # # # | # # # | # # # | # # # | 0.821 | 0.85 | 0.979 | 0.888 | # # # | # # # | # # # | - - - | 0.827 | 0.856 | 0.996 | 0.898 | - - - | 0.4 | 1.84 | 1.79 | 1.74 | 1.67 | 1.7 | 1.76 | 11.06 | 11.56 | 18.51 | 0 | - - - | - - - | - - - | - - - | 1314 | 1289 | 1500 | 4104 | Over-range | 748 | 668 | 304 | 1886 | 161 | 145 | 277 | 1190 | 1079 | 1097 | 1468 | 3644 | 1079 | 1097 | 1468 | 3644 | - - - | - - - | - - - | - - -
5/5/2026 | 6:30:00 AM | 283.28 | 280.95 | 279.39 | 490.11 | 483.72 | 487.35 | 4.7051 | 4.7254 | 5.403 | 2.7349 | 1.426 | 1.427 | 1.425 | 1.488 | 1.442 | 1.376 | Over-range | 60 | 1090 | 1143 | 1481 | 3715 | - - - | - - - | - - - | - - - | 1090 | 1143 | 1481 | 3715 | 747 | 643 | 54 | 1445 | - - - | - - - | - - - | - - - | 747 | 643 | 54 | 1445 | 1331 | 1322 | 1509 | 4163 | # # # | # # # | # # # | # # # | 0.819 | 0.865 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.825 | 0.87 | 0.999 | 0.902 | - - - | 0.389 | 1.86 | 1.8 | 1.77 | 1.68 | 1.72 | 1.78 | 10.69 | 11.1 | 18.35 | 0 | - - - | - - - | - - - | - - - | 1331 | 1322 | 1509 | 4163 | Over-range | 764 | 661 | 288 | 1879 | 158 | 150 | 277 | 1198 | 1092 | 1140 | 1483 | 3716 | 1092 | 1140 | 1483 | 3716 | - - - | - - - | - - - | - - -
5/5/2026 | 6:45:00 AM | 283.54 | 281.2 | 279.7 | 490.51 | 484.18 | 487.9 | 4.7219 | 4.7443 | 5.4141 | 2.7357 | 1.426 | 1.427 | 1.424 | 1.487 | 1.429 | 1.371 | Over-range | 60.01 | 1094 | 1157 | 1488 | 3739 | - - - | - - - | - - - | - - - | 1094 | 1157 | 1488 | 3739 | 756 | 647 | 51 | 1453 | - - - | - - - | - - - | - - - | 756 | 647 | 51 | 1453 | 1339 | 1334 | 1514 | 4187 | # # # | # # # | # # # | # # # | 0.817 | 0.867 | 0.983 | 0.893 | # # # | # # # | # # # | - - - | 0.824 | 0.872 | 0.999 | 0.902 | - - - | 0.389 | 1.87 | 1.78 | 1.72 | 1.67 | 1.69 | 1.76 | 10.64 | 10.84 | 18.27 | 0 | - - - | - - - | - - - | - - - | 1339 | 1334 | 1514 | 4187 | Over-range | 772 | 664 | 281 | 1885 | 156 | 150 | 276 | 1200 | 1097 | 1155 | 1488 | 3740 | 1097 | 1155 | 1488 | 3740 | - - - | - - - | - - - | - - -
5/5/2026 | 7:00:00 AM | 283.45 | 281.13 | 279.59 | 490.43 | 483.94 | 487.76 | 5.1387 | 5.5618 | 5.634 | 2.7269 | 1.426 | 1.426 | 1.422 | 1.49 | 1.464 | 1.312 | Over-range | 60.02 | 1160 | 1411 | 1547 | 4119 | - - - | - - - | - - - | - - - | 1160 | 1411 | 1547 | 4119 | 863 | 641 | -61 | 1441 | - - - | - - - | - - - | - - - | 863 | 641 | -61 | 1441 | 1455 | 1559 | 1575 | 4589 | # # # | # # # | # # # | # # # | 0.797 | 0.905 | 0.983 | 0.898 | # # # | # # # | # # # | - - - | 0.803 | 0.91 | 0.999 | 0.906 | - - - | 0.35 | 1.87 | 1.77 | 1.73 | 1.65 | 1.68 | 1.76 | 9.75 | 9.65 | 17.86 | 0 | - - - | - - - | - - - | - - - | 1455 | 1559 | 1575 | 4589 | Over-range | 878 | 659 | 293 | 2023 | 161 | 154 | 280 | 1416 | 1163 | 1408 | 1549 | 4120 | 1163 | 1408 | 1549 | 4120 | - - - | - - - | - - - | - - -
5/5/2026 | 7:15:00 AM | 283.08 | 280.73 | 279.3 | 489.66 | 483.37 | 487.26 | 5.3049 | 5.8867 | 5.7091 | 2.7143 | 1.425 | 1.426 | 1.422 | 1.492 | 1.473 | 1.293 | Over-range | 59.99 | 1186 | 1513 | 1565 | 4264 | - - - | - - - | - - - | - - - | 1186 | 1513 | 1565 | 4264 | 905 | 636 | -109 | 1430 | - - - | - - - | - - - | - - - | 905 | 636 | -109 | 1430 | 1501 | 1649 | 1594 | 4744 | # # # | # # # | # # # | # # # | 0.791 | 0.918 | 0.982 | 0.899 | # # # | # # # | # # # | - - - | 0.796 | 0.922 | 0.997 | 0.907 | - - - | 0.335 | 1.85 | 1.79 | 1.74 | 1.66 | 1.7 | 1.77 | 9.41 | 9.09 | 17.64 | 0 | - - - | - - - | - - - | - - - | 1501 | 1649 | 1594 | 4744 | Over-range | 919 | 654 | 304 | 2079 | 162 | 153 | 279 | 1507 | 1189 | 1511 | 1566 | 4266 | 1189 | 1511 | 1566 | 4266 | - - - | - - - | - - - | - - -
5/5/2026 | 7:30:00 AM | 283.07 | 280.64 | 279.2 | 489.6 | 483.14 | 487.2 | 4.6974 | 4.7497 | 5.4009 | 2.7234 | 1.425 | 1.426 | 1.421 | 1.488 | 1.473 | 1.374 | Over-range | 60.02 | 1087 | 1130 | 1476 | 3693 | - - - | - - - | - - - | - - - | 1087 | 1130 | 1476 | 3693 | 737 | 639 | 56 | 1433 | - - - | - - - | - - - | - - - | 737 | 639 | 56 | 1433 | 1324 | 1314 | 1507 | 4145 | # # # | # # # | # # # | # # # | 0.821 | 0.86 | 0.98 | 0.891 | # # # | # # # | # # # | - - - | 0.826 | 0.865 | 0.996 | 0.9 | - - - | 0.388 | 1.86 | 1.83 | 1.78 | 1.67 | 1.72 | 1.78 | 10.82 | 11.21 | 18.1 | 0 | - - - | - - - | - - - | - - - | 1324 | 1314 | 1507 | 4145 | Over-range | 755 | 655 | 300 | 1880 | 159 | 143 | 272 | 1208 | 1086 | 1132 | 1475 | 3693 | 1086 | 1132 | 1475 | 3693 | - - - | - - - | - - - | - - -
5/5/2026 | 7:45:00 AM | 283.09 | 280.59 | 279.26 | 489.51 | 483.15 | 487.35 | 4.679 | 4.0914 | 5.3851 | 3.647 | 1.425 | 1.426 | 1.421 | 1.488 | 1.434 | 1.375 | Over-range | 60.01 | 1087 | 872 | 1476 | 3435 | - - - | - - - | - - - | - - - | 1087 | 872 | 1476 | 3435 | 737 | 716 | 57 | 1511 | - - - | - - - | - - - | - - - | 737 | 716 | 57 | 1511 | 1323 | 1146 | 1504 | 3973 | # # # | # # # | # # # | # # # | 0.822 | 0.76 | 0.982 | 0.865 | # # # | # # # | # # # | - - - | 0.827 | 0.768 | 0.999 | 0.875 | - - - | 0.44 | 1.87 | 1.8 | 1.77 | 1.67 | 1.72 | 1.78 | 10.69 | 14.52 | 18.3 | 0 | - - - | - - - | - - - | - - - | 1323 | 1146 | 1504 | 3973 | Over-range | 754 | 735 | 286 | 1991 | 160 | 165 | 274 | 1294 | 1086 | 872 | 1477 | 3435 | 1086 | 872 | 1477 | 3435 | - - - | - - - | - - - | - - -
5/5/2026 | 8:00:00 AM | 282.82 | 280.34 | 279.06 | 489.03 | 482.83 | 486.9 | 4.874 | 3.9154 | 5.4317 | 4.1239 | 1.425 | 1.426 | 1.421 | 1.486 | 1.439 | 1.373 | Over-range | 60.01 | 1128 | 772 | 1487 | 3387 | - - - | - - - | - - - | - - - | 1128 | 772 | 1487 | 3387 | 771 | 760 | 52 | 1583 | - - - | - - - | - - - | - - - | 771 | 760 | 52 | 1583 | 1376 | 1098 | 1516 | 3989 | # # # | # # # | # # # | # # # | 0.82 | 0.703 | 0.981 | 0.849 | # # # | # # # | # # # | - - - | 0.817 | 0.707 | 0.984 | 0.851 | - - - | 0.468 | 1.85 | 1.82 | 1.75 | 1.65 | 1.71 | 1.78 | 10.22 | 15.98 | 18.18 | 0 | - - - | - - - | - - - | - - - | 1376 | 1098 | 1516 | 3989 | Over-range | 788 | 780 | 288 | 2107 | 161 | 177 | 275 | 1385 | 1137 | 777 | 1504 | 3417 | 1137 | 777 | 1504 | 3417 | - - - | - - - | - - - | - - -
5/5/2026 | 8:15:00 AM | 282.6 | 279.93 | 278.87 | 488.43 | 482.23 | 486.68 | 4.9856 | 4.2604 | 5.5356 | 4.1205 | 1.426 | 1.428 | 1.422 | 1.492 | 1.426 | 1.329 | Over-range | 60.01 | 1138 | 902 | 1518 | 3557 | - - - | - - - | - - - | - - - | 1138 | 902 | 1518 | 3557 | 815 | 754 | -31 | 1536 | - - - | - - - | - - - | - - - | 815 | 754 | -31 | 1536 | 1408 | 1190 | 1544 | 4142 | # # # | # # # | # # # | # # # | 0.808 | 0.757 | 0.984 | 0.859 | # # # | # # # | # # # | - - - | 0.813 | 0.767 | 0.999 | 0.869 | - - - | 0.432 | 1.85 | 1.82 | 1.74 | 1.64 | 1.71 | 1.76 | 9.86 | 15.19 | 17.88 | 0 | - - - | - - - | - - - | - - - | 1408 | 1190 | 1544 | 4142 | Over-range | 830 | 774 | 279 | 2121 | 157 | 178 | 273 | 1462 | 1137 | 904 | 1516 | 3556 | 1137 | 904 | 1516 | 3556 | - - - | - - - | - - - | - - -
5/5/2026 | 8:30:00 AM | 282.61 | 279.86 | 278.83 | 488.41 | 482.07 | 486.67 | 5.2948 | 4.7883 | 5.711 | 4.1194 | 1.426 | 1.427 | 1.422 | 1.497 | 1.43 | 1.293 | Over-range | 60.01 | 1187 | 1089 | 1563 | 3839 | - - - | - - - | - - - | - - - | 1187 | 1089 | 1563 | 3839 | 895 | 749 | -115 | 1528 | - - - | - - - | - - - | - - - | 895 | 749 | -115 | 1528 | 1495 | 1337 | 1592 | 4424 | # # # | # # # | # # # | # # # | 0.794 | 0.815 | 0.982 | 0.868 | # # # | # # # | # # # | - - - | 0.798 | 0.822 | 0.997 | 0.877 | - - - | 0.398 | 1.8 | 1.76 | 1.68 | 1.59 | 1.65 | 1.7 | 9.32 | 13.72 | 17.35 | 0 | - - - | - - - | - - - | - - - | 1495 | 1337 | 1592 | 4424 | Over-range | 910 | 772 | 301 | 2198 | 162 | 185 | 274 | 1578 | 1188 | 1087 | 1565 | 3841 | 1188 | 1087 | 1565 | 3841 | - - - | - - - | - - - | - - -
5/5/2026 | 8:45:00 AM | 281.88 | 279.15 | 278.09 | 487.11 | 480.87 | 485.39 | 4.9573 | 4.2206 | 5.5018 | 4.1212 | 1.426 | 1.428 | 1.422 | 1.493 | 1.424 | 1.331 | Over-range | 60.01 | 1132 | 882 | 1504 | 3517 | - - - | - - - | - - - | - - - | 1132 | 882 | 1504 | 3517 | 801 | 743 | -30 | 1512 | - - - | - - - | - - - | - - - | 801 | 743 | -30 | 1512 | 1395 | 1174 | 1530 | 4098 | # # # | # # # | # # # | # # # | 0.811 | 0.752 | 0.983 | 0.858 | # # # | # # # | # # # | - - - | 0.817 | 0.76 | 0.999 | 0.868 | - - - | 0.43 | 1.77 | 1.73 | 1.66 | 1.58 | 1.64 | 1.68 | 9.92 | 14.96 | 17.71 | 0 | - - - | - - - | - - - | - - - | 1395 | 1174 | 1530 | 4098 | Over-range | 815 | 763 | 280 | 2100 | 151 | 176 | 269 | 1457 | 1135 | 883 | 1501 | 3518 | 1135 | 883 | 1501 | 3518 | - - - | - - - | - - - | - - -
5/5/2026 | 9:00:00 AM | 281.64 | 278.89 | 277.82 | 486.71 | 480.38 | 484.95 | 4.4707 | 3.4749 | 5.2666 | 4.13 | 1.426 | 1.428 | 1.423 | 1.487 | 1.458 | 1.397 | Over-range | 60 | 1053 | 584 | 1434 | 3072 | - - - | - - - | - - - | - - - | 1053 | 584 | 1434 | 3072 | 671 | 744 | 98 | 1513 | - - - | - - - | - - - | - - - | 671 | 744 | 98 | 1513 | 1258 | 966 | 1463 | 3687 | # # # | # # # | # # # | # # # | 0.837 | 0.605 | 0.981 | 0.833 | # # # | # # # | # # # | - - - | 0.843 | 0.614 | 0.997 | 0.844 | - - - | 0.492 | 1.74 | 1.77 | 1.68 | 1.58 | 1.65 | 1.69 | 10.97 | 17.35 | 18.06 | 0 | - - - | - - - | - - - | - - - | 1258 | 966 | 1463 | 3687 | Over-range | 687 | 763 | 286 | 2036 | 148 | 168 | 264 | 1362 | 1056 | 584 | 1433 | 3073 | 1056 | 584 | 1433 | 3073 | - - - | - - - | - - - | - - -
5/5/2026 | 9:15:00 AM | 281.13 | 278.28 | 277.28 | 485.7 | 479.38 | 484.08 | 4.7754 | 3.902 | 5.3966 | 4.1193 | 1.427 | 1.428 | 1.424 | 1.492 | 1.434 | 1.353 | Over-range | 60 | 1103 | 778 | 1472 | 3353 | - - - | - - - | - - - | - - - | 1103 | 778 | 1472 | 3353 | 749 | 733 | 8 | 1490 | - - - | - - - | - - - | - - - | 749 | 733 | 8 | 1490 | 1342 | 1084 | 1496 | 3923 | # # # | # # # | # # # | # # # | 0.822 | 0.718 | 0.984 | 0.855 | # # # | # # # | # # # | - - - | 0.828 | 0.726 | 1 | 0.865 | - - - | 0.444 | 1.78 | 1.77 | 1.71 | 1.59 | 1.67 | 1.7 | 10.14 | 15.8 | 17.82 | 0 | - - - | - - - | - - - | - - - | 1342 | 1084 | 1496 | 3923 | Over-range | 764 | 754 | 267 | 2035 | 152 | 174 | 266 | 1386 | 1105 | 776 | 1474 | 3355 | 1105 | 776 | 1474 | 3355 | - - - | - - - | - - - | - - -
5/5/2026 | 9:30:00 AM | 281.3 | 278.38 | 277.47 | 485.88 | 479.68 | 484.41 | 4.9465 | 4.1759 | 5.5091 | 4.1307 | 1.427 | 1.429 | 1.424 | 1.493 | 1.421 | 1.326 | Over-range | 60.01 | 1131 | 882 | 1504 | 3517 | - - - | - - - | - - - | - - - | 1131 | 882 | 1504 | 3517 | 794 | 733 | -37 | 1489 | - - - | - - - | - - - | - - - | 794 | 733 | -37 | 1489 | 1391 | 1161 | 1528 | 4081 | # # # | # # # | # # # | # # # | 0.813 | 0.759 | 0.984 | 0.862 | # # # | # # # | # # # | - - - | 0.819 | 0.768 | 0.999 | 0.872 | - - - | 0.423 | 1.8 | 1.8 | 1.76 | 1.63 | 1.72 | 1.74 | 9.8 | 15.13 | 17.56 | 0 | - - - | - - - | - - - | - - - | 1391 | 1161 | 1528 | 4081 | Over-range | 810 | 755 | 271 | 2069 | 157 | 177 | 267 | 1437 | 1132 | 881 | 1506 | 3518 | 1132 | 881 | 1506 | 3518 | - - - | - - - | - - - | - - -
5/5/2026 | 9:45:00 AM | 280.89 | 278.02 | 277.02 | 485.26 | 478.96 | 483.64 | 5.5654 | 5.2695 | 5.8572 | 4.1188 | 1.428 | 1.43 | 1.425 | 1.5 | 1.467 | 1.282 | Over-range | 60.01 | 1228 | 1256 | 1586 | 4070 | - - - | - - - | - - - | - - - | 1228 | 1256 | 1586 | 4070 | 953 | 724 | -206 | 1471 | - - - | - - - | - - - | - - - | 953 | 724 | -206 | 1471 | 1563 | 1462 | 1622 | 4647 | # # # | # # # | # # # | # # # | 0.786 | 0.859 | 0.978 | 0.876 | # # # | # # # | # # # | - - - | 0.791 | 0.865 | 0.991 | 0.884 | - - - | 0.361 | 1.83 | 1.85 | 1.77 | 1.66 | 1.75 | 1.78 | 8.71 | 12.44 | 16.74 | 0 | - - - | - - - | - - - | - - - | 1563 | 1462 | 1622 | 4647 | Over-range | 966 | 747 | 341 | 2243 | 157 | 185 | 269 | 1693 | 1231 | 1254 | 1586 | 4071 | 1231 | 1254 | 1586 | 4071 | - - - | - - - | - - - | - - -
5/5/2026 | 10:00:00 AM | 280.59 | 277.74 | 276.8 | 484.72 | 478.53 | 483.23 | 5.2197 | 4.6583 | 5.6571 | 4.1255 | 1.428 | 1.43 | 1.426 | 1.496 | 1.441 | 1.294 | Over-range | 60 | 1172 | 1045 | 1537 | 3754 | - - - | - - - | - - - | - - - | 1172 | 1045 | 1537 | 3754 | 861 | 723 | -114 | 1470 | - - - | - - - | - - - | - - - | 861 | 723 | -114 | 1470 | 1463 | 1287 | 1565 | 4315 | # # # | # # # | # # # | # # # | 0.801 | 0.812 | 0.982 | 0.87 | # # # | # # # | # # # | - - - | 0.807 | 0.82 | 0.996 | 0.879 | - - - | 0.392 | 1.82 | 1.84 | 1.79 | 1.66 | 1.74 | 1.78 | 9.29 | 13.59 | 17.04 | 0 | - - - | - - - | - - - | - - - | 1463 | 1287 | 1565 | 4315 | Over-range | 874 | 745 | 296 | 2126 | 151 | 178 | 265 | 1535 | 1176 | 1044 | 1536 | 3756 | 1176 | 1044 | 1536 | 3756 | - - - | - - - | - - - | - - -
5/5/2026 | 10:15:00 AM | 280.36 | 277.61 | 276.52 | 484.45 | 478.21 | 482.72 | 5.0095 | 4.1129 | 5.4946 | 4.1322 | 1.429 | 1.431 | 1.427 | 1.487 | 1.42 | 1.335 | Over-range | 60.02 | 1148 | 867 | 1494 | 3509 | - - - | - - - | - - - | - - - | 1148 | 867 | 1494 | 3509 | 791 | 723 | -16 | 1497 | - - - | - - - | - - - | - - - | 791 | 723 | -16 | 1497 | 1402 | 1142 | 1519 | 4063 | # # # | # # # | # # # | # # # | 0.819 | 0.759 | 0.983 | 0.864 | # # # | # # # | # # # | - - - | 0.816 | 0.761 | 0.984 | 0.863 | - - - | 0.427 | 1.86 | 1.85 | 1.84 | 1.69 | 1.78 | 1.81 | 9.64 | 14.72 | 17.37 | 0 | - - - | - - - | - - - | - - - | 1402 | 1142 | 1519 | 4063 | Over-range | 805 | 743 | 274 | 2049 | 151 | 170 | 264 | 1393 | 1160 | 872 | 1509 | 3542 | 1160 | 872 | 1509 | 3542 | - - - | - - - | - - - | - - -
5/5/2026 | 10:30:00 AM | 280.12 | 277.32 | 276.28 | 483.99 | 477.76 | 482.29 | 5.1649 | 4.5553 | 5.6155 | 4.1255 | 1.427 | 1.429 | 1.426 | 1.496 | 1.436 | 1.295 | Over-range | 60.01 | 1164 | 1015 | 1523 | 3702 | - - - | - - - | - - - | - - - | 1164 | 1015 | 1523 | 3702 | 843 | 720 | -106 | 1455 | - - - | - - - | - - - | - - - | 843 | 720 | -106 | 1455 | 1446 | 1259 | 1551 | 4256 | # # # | # # # | # # # | # # # | 0.805 | 0.807 | 0.982 | 0.87 | # # # | # # # | # # # | - - - | 0.809 | 0.815 | 0.997 | 0.879 | - - - | 0.393 | 1.83 | 1.84 | 1.81 | 1.67 | 1.76 | 1.78 | 9.38 | 13.88 | 17.2 | 0 | - - - | - - - | - - - | - - - | 1446 | 1259 | 1551 | 4256 | Over-range | 857 | 740 | 291 | 2098 | 157 | 172 | 265 | 1509 | 1163 | 1017 | 1522 | 3702 | 1163 | 1017 | 1522 | 3702 | - - - | - - - | - - - | - - -
5/5/2026 | 10:45:00 AM | 279.8 | 276.93 | 275.88 | 483.4 | 477.01 | 481.68 | 5.4748 | 5.1014 | 5.8114 | 4.1208 | 1.428 | 1.43 | 1.426 | 1.5 | 1.472 | 1.263 | Over-range | 60.02 | 1213 | 1207 | 1569 | 3989 | - - - | - - - | - - - | - - - | 1213 | 1207 | 1569 | 3989 | 922 | 711 | -194 | 1439 | - - - | - - - | - - - | - - - | 922 | 711 | -194 | 1439 | 1532 | 1412 | 1603 | 4547 | # # # | # # # | # # # | # # # | 0.792 | 0.855 | 0.979 | 0.877 | # # # | # # # | # # # | - - - | 0.797 | 0.862 | 0.992 | 0.885 | - - - | 0.361 | 1.84 | 1.85 | 1.83 | 1.68 | 1.78 | 1.8 | 8.82 | 12.5 | 16.57 | 0 | - - - | - - - | - - - | - - - | 1532 | 1412 | 1603 | 4547 | Over-range | 936 | 733 | 328 | 2183 | 159 | 177 | 264 | 1642 | 1214 | 1207 | 1569 | 3989 | 1214 | 1207 | 1569 | 3989 | - - - | - - - | - - - | - - -
5/5/2026 | 11:00:00 AM | 279.46 | 276.63 | 275.49 | 482.89 | 476.42 | 481 | 4.9604 | 4.2932 | 5.5058 | 4.1237 | 1.428 | 1.43 | 1.426 | 1.491 | 1.46 | 1.325 | Over-range | 60 | 1125 | 873 | 1484 | 3483 | - - - | - - - | - - - | - - - | 1125 | 873 | 1484 | 3483 | 777 | 711 | -48 | 1439 | - - - | - - - | - - - | - - - | 777 | 711 | -48 | 1439 | 1378 | 1165 | 1514 | 4057 | # # # | # # # | # # # | # # # | 0.817 | 0.75 | 0.98 | 0.858 | # # # | # # # | # # # | - - - | 0.823 | 0.758 | 0.995 | 0.868 | - - - | 0.413 | 1.86 | 1.87 | 1.83 | 1.7 | 1.79 | 1.81 | 9.91 | 14.75 | 17.12 | 0 | - - - | - - - | - - - | - - - | 1378 | 1165 | 1514 | 4057 | Over-range | 792 | 732 | 301 | 2070 | 152 | 170 | 259 | 1486 | 1128 | 872 | 1485 | 3484 | 1128 | 872 | 1485 | 3484 | - - - | - - - | - - - | - - -
5/5/2026 | 11:15:00 AM | 278.91 | 276.2 | 274.98 | 481.96 | 475.71 | 480.08 | 4.8106 | 3.9527 | 5.4353 | 4.1568 | 1.428 | 1.429 | 1.426 | 1.553 | 1.489 | 1.489 | Over-range | 60 | 1110 | 779 | 1463 | 3352 | - - - | - - - | - - - | - - - | 1110 | 779 | 1463 | 3352 | 727 | 713 | -8 | 1431 | - - - | - - - | - - - | - - - | 727 | 713 | -8 | 1431 | 1338 | 1081 | 1494 | 3913 | # # # | # # # | # # # | # # # | 0.829 | 0.721 | 0.979 | 0.857 | # # # | # # # | # # # | - - - | 0.836 | 0.731 | 0.998 | 0.868 | - - - | 0.427 | 1.62 | 1.6 | 1.52 | 1.42 | 1.46 | 1.52 | 10.12 | 15.18 | 17.28 | 0 | - - - | - - - | - - - | - - - | 1338 | 1081 | 1494 | 3913 | Over-range | 747 | 736 | 301 | 2016 | 172 | 181 | 288 | 1419 | 1110 | 778 | 1465 | 3354 | 1110 | 778 | 1465 | 3354 | - - - | - - - | - - - | - - -
5/5/2026 | 11:30:00 AM | 279.13 | 276.49 | 275.25 | 482.46 | 476.15 | 480.48 | 4.5016 | 3.4986 | 5.2587 | 4.1489 | 1.428 | 1.429 | 1.426 | 1.558 | 1.509 | 1.531 | Over-range | 60 | 1056 | 602 | 1415 | 3073 | - - - | - - - | - - - | - - - | 1056 | 602 | 1415 | 3073 | 655 | 717 | 69 | 1441 | - - - | - - - | - - - | - - - | 655 | 717 | 69 | 1441 | 1255 | 963 | 1447 | 3664 | # # # | # # # | # # # | # # # | 0.842 | 0.625 | 0.978 | 0.839 | # # # | # # # | # # # | - - - | 0.849 | 0.636 | 0.997 | 0.852 | - - - | 0.469 | 1.6 | 1.55 | 1.54 | 1.41 | 1.45 | 1.51 | 10.68 | 16.39 | 17.66 | 0 | - - - | - - - | - - - | - - - | 1255 | 963 | 1447 | 3664 | Over-range | 677 | 740 | 302 | 1992 | 167 | 180 | 286 | 1374 | 1057 | 601 | 1417 | 3075 | 1057 | 601 | 1417 | 3075 | - - - | - - - | - - - | - - -
5/5/2026 | 11:45:00 AM | 278.89 | 276.28 | 275.11 | 482.05 | 475.84 | 480.18 | 5.2288 | 4.6617 | 5.6495 | 4.1374 | 1.428 | 1.429 | 1.426 | 1.543 | 1.448 | 1.421 | Over-range | 60 | 1172 | 1057 | 1521 | 3750 | - - - | - - - | - - - | - - - | 1172 | 1057 | 1521 | 3750 | 851 | 711 | -133 | 1427 | - - - | - - - | - - - | - - - | 851 | 711 | -133 | 1427 | 1458 | 1287 | 1554 | 4300 | # # # | # # # | # # # | # # # | 0.804 | 0.821 | 0.979 | 0.872 | # # # | # # # | # # # | - - - | 0.81 | 0.831 | 0.996 | 0.883 | - - - | 0.381 | 1.58 | 1.57 | 1.49 | 1.4 | 1.43 | 1.49 | 9.07 | 13.2 | 16.99 | 0 | - - - | - - - | - - - | - - - | 1458 | 1287 | 1554 | 4300 | Over-range | 868 | 734 | 321 | 2104 | 168 | 185 | 291 | 1546 | 1173 | 1059 | 1519 | 3750 | 1173 | 1059 | 1519 | 3750 | - - - | - - - | - - - | - - -
5/5/2026 | 12:00:00 PM | 278.61 | 276.09 | 274.84 | 481.62 | 475.55 | 479.63 | 5.0444 | 4.2067 | 5.5239 | 4.1503 | 1.428 | 1.429 | 1.426 | 1.544 | 1.466 | 1.464 | Over-range | 60.01 | 1148 | 898 | 1488 | 3534 | - - - | - - - | - - - | - - - | 1148 | 898 | 1488 | 3534 | 788 | 709 | -45 | 1450 | - - - | - - - | - - - | - - - | 788 | 709 | -45 | 1450 | 1403 | 1160 | 1518 | 4080 | # # # | # # # | # # # | # # # | 0.819 | 0.774 | 0.98 | 0.866 | # # # | # # # | # # # | - - - | 0.817 | 0.777 | 0.983 | 0.867 | - - - | 0.41 | 1.56 | 1.54 | 1.47 | 1.38 | 1.41 | 1.46 | 9.37 | 14.14 | 17.1 | 0 | - - - | - - - | - - - | - - - | 1403 | 1160 | 1518 | 4080 | Over-range | 805 | 732 | 301 | 2039 | 165 | 182 | 288 | 1429 | 1161 | 904 | 1503 | 3568 | 1161 | 904 | 1503 | 3568 | - - - | - - - | - - - | - - -
5/5/2026 | 12:15:00 PM | 278.53 | 275.95 | 274.74 | 481.45 | 475.28 | 479.5 | 5.3224 | 4.8433 | 5.7004 | 4.1339 | 1.428 | 1.429 | 1.426 | 1.542 | 1.45 | 1.405 | Over-range | 59.99 | 1185 | 1113 | 1529 | 3827 | - - - | - - - | - - - | - - - | 1185 | 1113 | 1529 | 3827 | 873 | 705 | -160 | 1416 | - - - | - - - | - - - | - - - | 873 | 705 | -160 | 1416 | 1481 | 1333 | 1566 | 4380 | # # # | # # # | # # # | # # # | 0.8 | 0.835 | 0.977 | 0.874 | # # # | # # # | # # # | - - - | 0.806 | 0.844 | 0.994 | 0.884 | - - - | 0.37 | 1.58 | 1.54 | 1.51 | 1.4 | 1.43 | 1.49 | 8.88 | 12.92 | 16.83 | 0 | - - - | - - - | - - - | - - - | 1481 | 1333 | 1566 | 4380 | Over-range | 889 | 730 | 336 | 2130 | 169 | 190 | 291 | 1590 | 1188 | 1111 | 1531 | 3830 | 1188 | 1111 | 1531 | 3830 | - - - | - - - | - - - | - - -
5/5/2026 | 12:30:00 PM | 278.72 | 276.14 | 274.94 | 481.77 | 475.59 | 479.87 | 5.7531 | 5.6366 | 5.9959 | 4.1317 | 1.429 | 1.43 | 1.428 | 1.537 | 1.467 | 1.377 | Over-range | 60 | 1253 | 1373 | 1599 | 4225 | - - - | - - - | - - - | - - - | 1253 | 1373 | 1599 | 4225 | 984 | 706 | -273 | 1416 | - - - | - - - | - - - | - - - | 984 | 706 | -273 | 1416 | 1603 | 1556 | 1648 | 4807 | # # # | # # # | # # # | # # # | 0.781 | 0.883 | 0.97 | 0.879 | # # # | # # # | # # # | - - - | 0.786 | 0.889 | 0.985 | 0.887 | - - - | 0.335 | 1.64 | 1.61 | 1.55 | 1.45 | 1.48 | 1.55 | 8.26 | 11.4 | 16.1 | 0 | - - - | - - - | - - - | - - - | 1603 | 1556 | 1648 | 4807 | Over-range | 1000 | 731 | 401 | 2294 | 178 | 190 | 291 | 1804 | 1253 | 1372 | 1600 | 4226 | 1253 | 1372 | 1600 | 4226 | - - - | - - - | - - - | - - -
5/5/2026 | 12:45:00 PM | 280.25 | 277.68 | 276.45 | 484.43 | 478.3 | 482.43 | 5.4134 | 5.001 | 5.781 | 4.1465 | 1.429 | 1.43 | 1.428 | 1.539 | 1.442 | 1.394 | Over-range | 60.02 | 1202 | 1167 | 1561 | 3930 | - - - | - - - | - - - | - - - | 1202 | 1167 | 1561 | 3930 | 908 | 727 | -171 | 1463 | - - - | - - - | - - - | - - - | 908 | 727 | -171 | 1463 | 1517 | 1388 | 1598 | 4503 | # # # | # # # | # # # | # # # | 0.793 | 0.84 | 0.977 | 0.873 | # # # | # # # | # # # | - - - | 0.798 | 0.849 | 0.994 | 0.883 | - - - | 0.372 | 1.66 | 1.61 | 1.57 | 1.45 | 1.48 | 1.54 | 8.87 | 12.79 | 16.84 | 0 | - - - | - - - | - - - | - - - | 1517 | 1388 | 1598 | 4503 | Over-range | 925 | 752 | 343 | 2199 | 177 | 193 | 297 | 1642 | 1204 | 1165 | 1564 | 3932 | 1204 | 1165 | 1564 | 3932 | - - - | - - - | - - - | - - -
5/5/2026 | 1:00:00 PM | 279.8 | 277.02 | 275.86 | 483.49 | 477.09 | 481.66 | 5.0368 | 4.4417 | 5.5584 | 4.1442 | 1.429 | 1.43 | 1.428 | 1.548 | 1.469 | 1.456 | Over-range | 60.01 | 1136 | 915 | 1494 | 3545 | - - - | - - - | - - - | - - - | 1136 | 915 | 1494 | 3545 | 796 | 721 | -66 | 1450 | - - - | - - - | - - - | - - - | 796 | 721 | -66 | 1450 | 1400 | 1207 | 1531 | 4139 | # # # | # # # | # # # | # # # | 0.812 | 0.758 | 0.976 | 0.857 | # # # | # # # | # # # | - - - | 0.818 | 0.767 | 0.993 | 0.868 | - - - | 0.409 | 1.63 | 1.61 | 1.6 | 1.45 | 1.52 | 1.56 | 9.71 | 14.35 | 17.11 | 0 | - - - | - - - | - - - | - - - | 1400 | 1207 | 1531 | 4139 | Over-range | 815 | 744 | 336 | 2123 | 174 | 184 | 290 | 1549 | 1136 | 915 | 1495 | 3547 | 1136 | 915 | 1495 | 3547 | - - - | - - - | - - - | - - -
5/5/2026 | 1:15:00 PM | 280.13 | 277.41 | 276.15 | 484.17 | 477.66 | 482.16 | 4.8925 | 4.0314 | 5.4534 | 4.1479 | 1.429 | 1.43 | 1.428 | 1.549 | 1.488 | 1.496 | Over-range | 60.02 | 1124 | 802 | 1471 | 3397 | - - - | - - - | - - - | - - - | 1124 | 802 | 1471 | 3397 | 756 | 727 | 2 | 1484 | - - - | - - - | - - - | - - - | 756 | 727 | 2 | 1484 | 1366 | 1107 | 1505 | 3978 | # # # | # # # | # # # | # # # | 0.822 | 0.725 | 0.977 | 0.854 | # # # | # # # | # # # | - - - | 0.821 | 0.73 | 0.988 | 0.859 | - - - | 0.437 | 1.63 | 1.6 | 1.57 | 1.44 | 1.5 | 1.54 | 9.9 | 15.26 | 17.57 | 0 | - - - | - - - | - - - | - - - | 1366 | 1107 | 1505 | 3978 | Over-range | 776 | 750 | 316 | 2068 | 174 | 185 | 293 | 1435 | 1132 | 807 | 1483 | 3422 | 1132 | 807 | 1483 | 3422 | - - - | - - - | - - - | - - -
5/5/2026 | 1:30:00 PM | 280.16 | 277.41 | 276.12 | 484.23 | 477.61 | 482.14 | 4.5072 | 3.5273 | 5.2645 | 4.1515 | 1.429 | 1.43 | 1.428 | 1.556 | 1.513 | 1.538 | Over-range | 60 | 1056 | 605 | 1420 | 3082 | - - - | - - - | - - - | - - - | 1056 | 605 | 1420 | 3082 | 666 | 730 | 72 | 1469 | - - - | - - - | - - - | - - - | 666 | 730 | 72 | 1469 | 1261 | 974 | 1453 | 3688 | # # # | # # # | # # # | # # # | 0.838 | 0.621 | 0.978 | 0.836 | # # # | # # # | # # # | - - - | 0.846 | 0.633 | 0.998 | 0.849 | - - - | 0.476 | 1.63 | 1.59 | 1.52 | 1.42 | 1.47 | 1.52 | 10.72 | 16.48 | 17.83 | 0 | - - - | - - - | - - - | - - - | 1261 | 974 | 1453 | 3688 | Over-range | 687 | 751 | 306 | 2020 | 168 | 176 | 289 | 1387 | 1057 | 607 | 1419 | 3082 | 1057 | 607 | 1419 | 3082 | - - - | - - - | - - - | - - -
5/5/2026 | 1:45:00 PM | 280.28 | 277.5 | 276.29 | 484.34 | 477.9 | 482.4 | 5.2992 | 4.7871 | 5.7017 | 4.1465 | 1.429 | 1.43 | 1.428 | 1.542 | 1.447 | 1.413 | Over-range | 60.01 | 1185 | 1096 | 1541 | 3821 | - - - | - - - | - - - | - - - | 1185 | 1096 | 1541 | 3821 | 879 | 725 | -141 | 1462 | - - - | - - - | - - - | - - - | 879 | 725 | -141 | 1462 | 1485 | 1328 | 1575 | 4388 | # # # | # # # | # # # | # # # | 0.798 | 0.825 | 0.978 | 0.871 | # # # | # # # | # # # | - - - | 0.804 | 0.834 | 0.995 | 0.881 | - - - | 0.383 | 1.62 | 1.58 | 1.54 | 1.43 | 1.47 | 1.52 | 9.04 | 13.17 | 17.02 | 0 | - - - | - - - | - - - | - - - | 1485 | 1328 | 1575 | 4388 | Over-range | 895 | 749 | 329 | 2158 | 169 | 190 | 295 | 1587 | 1187 | 1097 | 1538 | 3822 | 1187 | 1097 | 1538 | 3822 | - - - | - - - | - - - | - - -
5/5/2026 | 2:00:00 PM | 280.44 | 277.77 | 276.52 | 484.73 | 478.31 | 482.72 | 5.003 | 4.2825 | 5.5305 | 4.1471 | 1.43 | 1.43 | 1.428 | 1.545 | 1.469 | 1.456 | Over-range | 60.01 | 1137 | 916 | 1499 | 3552 | - - - | - - - | - - - | - - - | 1137 | 916 | 1499 | 3552 | 803 | 730 | -60 | 1473 | - - - | - - - | - - - | - - - | 803 | 730 | -60 | 1473 | 1402 | 1188 | 1529 | 4119 | # # # | # # # | # # # | # # # | 0.811 | 0.771 | 0.98 | 0.862 | # # # | # # # | # # # | - - - | 0.817 | 0.781 | 0.999 | 0.874 | - - - | 0.415 | 1.63 | 1.6 | 1.55 | 1.44 | 1.48 | 1.53 | 9.61 | 14.29 | 17.38 | 0 | - - - | - - - | - - - | - - - | 1402 | 1188 | 1529 | 4119 | Over-range | 821 | 754 | 303 | 2086 | 169 | 188 | 294 | 1477 | 1140 | 915 | 1499 | 3554 | 1140 | 915 | 1499 | 3554 | - - - | - - - | - - - | - - -
5/5/2026 | 2:15:00 PM | 280.43 | 277.67 | 276.48 | 484.66 | 478.15 | 482.73 | 5.307 | 4.8208 | 5.7079 | 4.1414 | 1.43 | 1.43 | 1.428 | 1.542 | 1.453 | 1.414 | Over-range | 60.02 | 1185 | 1099 | 1542 | 3826 | - - - | - - - | - - - | - - - | 1185 | 1099 | 1542 | 3826 | 881 | 726 | -141 | 1465 | - - - | - - - | - - - | - - - | 881 | 726 | -141 | 1465 | 1487 | 1334 | 1578 | 4398 | # # # | # # # | # # # | # # # | 0.797 | 0.824 | 0.977 | 0.87 | # # # | # # # | # # # | - - - | 0.803 | 0.832 | 0.995 | 0.881 | - - - | 0.383 | 1.63 | 1.59 | 1.54 | 1.43 | 1.47 | 1.53 | 9.07 | 13.26 | 17.06 | 0 | - - - | - - - | - - - | - - - | 1487 | 1334 | 1578 | 4398 | Over-range | 898 | 752 | 333 | 2170 | 172 | 195 | 297 | 1599 | 1189 | 1097 | 1543 | 3828 | 1189 | 1097 | 1543 | 3828 | - - - | - - - | - - - | - - -
5/5/2026 | 2:30:00 PM | 280.34 | 277.61 | 276.4 | 484.46 | 478.1 | 482.55 | 5.9006 | 5.7551 | 6.07 | 4.1372 | 1.429 | 1.431 | 1.428 | 1.536 | 1.464 | 1.384 | Over-range | 60.01 | 1291 | 1410 | 1629 | 4330 | - - - | - - - | - - - | - - - | 1291 | 1410 | 1629 | 4330 | 1015 | 723 | -256 | 1480 | - - - | - - - | - - - | - - - | 1015 | 723 | -256 | 1480 | 1653 | 1597 | 1678 | 4927 | # # # | # # # | # # # | # # # | 0.781 | 0.883 | 0.971 | 0.879 | # # # | # # # | # # # | - - - | 0.779 | 0.882 | 0.976 | 0.879 | - - - | 0.342 | 1.65 | 1.58 | 1.53 | 1.42 | 1.46 | 1.52 | 8.42 | 11.52 | 16.23 | 0 | - - - | - - - | - - - | - - - | 1653 | 1597 | 1678 | 4927 | Over-range | 1032 | 749 | 401 | 2352 | 182 | 196 | 299 | 1823 | 1304 | 1417 | 1658 | 4380 | 1304 | 1417 | 1658 | 4380 | - - - | - - - | - - - | - - -
5/5/2026 | 2:45:00 PM | 280.23 | 277.61 | 276.34 | 484.37 | 478.07 | 482.38 | 5.6894 | 5.4753 | 5.9718 | 4.1379 | 1.43 | 1.431 | 1.428 | 1.541 | 1.454 | 1.383 | Over-range | 60.01 | 1253 | 1318 | 1606 | 4176 | - - - | - - - | - - - | - - - | 1253 | 1318 | 1606 | 4176 | 968 | 725 | -231 | 1461 | - - - | - - - | - - - | - - - | 968 | 725 | -231 | 1461 | 1594 | 1517 | 1650 | 4761 | # # # | # # # | # # # | # # # | 0.786 | 0.869 | 0.973 | 0.877 | # # # | # # # | # # # | - - - | 0.792 | 0.876 | 0.99 | 0.887 | - - - | 0.35 | 1.61 | 1.57 | 1.55 | 1.43 | 1.46 | 1.51 | 8.65 | 11.87 | 16.39 | 0 | - - - | - - - | - - - | - - - | 1594 | 1517 | 1650 | 4761 | Over-range | 985 | 750 | 379 | 2286 | 181 | 195 | 298 | 1757 | 1254 | 1318 | 1606 | 4178 | 1254 | 1318 | 1606 | 4178 | - - - | - - - | - - - | - - -
5/5/2026 | 3:00:00 PM | 279.98 | 277.27 | 276.07 | 483.88 | 477.49 | 481.97 | 5.473 | 5.0913 | 5.8227 | 4.1371 | 1.429 | 1.431 | 1.428 | 1.542 | 1.448 | 1.394 | Over-range | 60 | 1215 | 1195 | 1569 | 3979 | - - - | - - - | - - - | - - - | 1215 | 1195 | 1569 | 3979 | 915 | 721 | -182 | 1454 | - - - | - - - | - - - | - - - | 915 | 721 | -182 | 1454 | 1532 | 1410 | 1607 | 4549 | # # # | # # # | # # # | # # # | 0.793 | 0.848 | 0.976 | 0.875 | # # # | # # # | # # # | - - - | 0.799 | 0.855 | 0.993 | 0.885 | - - - | 0.365 | 1.61 | 1.59 | 1.54 | 1.43 | 1.47 | 1.52 | 8.88 | 12.48 | 16.65 | 0 | - - - | - - - | - - - | - - - | 1532 | 1410 | 1607 | 4549 | Over-range | 933 | 746 | 349 | 2205 | 179 | 192 | 296 | 1657 | 1216 | 1193 | 1571 | 3981 | 1216 | 1193 | 1571 | 3981 | - - - | - - - | - - - | - - -
5/5/2026 | 3:15:00 PM | 280.06 | 277.48 | 276.17 | 484.12 | 477.83 | 482.06 | 4.9229 | 4.148 | 5.4832 | 4.1478 | 1.43 | 1.432 | 1.429 | 1.549 | 1.475 | 1.47 | Over-range | 60.03 | 1124 | 869 | 1484 | 3477 | - - - | - - - | - - - | - - - | 1124 | 869 | 1484 | 3477 | 779 | 726 | -43 | 1461 | - - - | - - - | - - - | - - - | 779 | 726 | -43 | 1461 | 1378 | 1149 | 1514 | 4041 | # # # | # # # | # # # | # # # | 0.816 | 0.756 | 0.98 | 0.861 | # # # | # # # | # # # | - - - | 0.823 | 0.766 | 0.999 | 0.872 | - - - | 0.42 | 1.67 | 1.62 | 1.53 | 1.45 | 1.48 | 1.54 | 9.73 | 14.63 | 17.44 | 0 | - - - | - - - | - - - | - - - | 1378 | 1149 | 1514 | 4041 | Over-range | 797 | 749 | 299 | 2058 | 167 | 186 | 293 | 1449 | 1128 | 869 | 1483 | 3479 | 1128 | 869 | 1483 | 3479 | - - - | - - - | - - - | - - -
5/5/2026 | 3:30:00 PM | 280.04 | 277.47 | 276.22 | 484.06 | 477.9 | 482.09 | 5.6902 | 5.413 | 5.9266 | 4.1367 | 1.43 | 1.431 | 1.429 | 1.537 | 1.456 | 1.388 | Over-range | 60 | 1249 | 1298 | 1593 | 4140 | - - - | - - - | - - - | - - - | 1249 | 1298 | 1593 | 4140 | 968 | 725 | -214 | 1478 | - - - | - - - | - - - | - - - | 968 | 725 | -214 | 1478 | 1591 | 1500 | 1637 | 4728 | # # # | # # # | # # # | # # # | 0.785 | 0.865 | 0.973 | 0.876 | # # # | # # # | # # # | - - - | 0.783 | 0.866 | 0.981 | 0.877 | - - - | 0.357 | 1.64 | 1.61 | 1.53 | 1.44 | 1.47 | 1.52 | 8.58 | 12.15 | 16.7 | 0 | - - - | - - - | - - - | - - - | 1591 | 1500 | 1637 | 4728 | Over-range | 985 | 750 | 374 | 2282 | 178 | 193 | 298 | 1735 | 1261 | 1307 | 1619 | 4186 | 1261 | 1307 | 1619 | 4186 | - - - | - - - | - - - | - - -
5/5/2026 | 3:45:00 PM | 280.14 | 277.5 | 276.25 | 484.21 | 477.84 | 482.25 | 5.4449 | 5.082 | 5.7953 | 4.138 | 1.431 | 1.432 | 1.429 | 1.54 | 1.453 | 1.4 | Over-range | 59.99 | 1205 | 1181 | 1560 | 3946 | - - - | - - - | - - - | - - - | 1205 | 1181 | 1560 | 3946 | 915 | 724 | -178 | 1461 | - - - | - - - | - - - | - - - | 915 | 724 | -178 | 1461 | 1523 | 1404 | 1600 | 4527 | # # # | # # # | # # # | # # # | 0.791 | 0.841 | 0.975 | 0.872 | # # # | # # # | # # # | - - - | 0.797 | 0.849 | 0.992 | 0.882 | - - - | 0.37 | 1.68 | 1.63 | 1.56 | 1.47 | 1.51 | 1.57 | 8.86 | 12.64 | 16.82 | 0 | - - - | - - - | - - - | - - - | 1523 | 1404 | 1600 | 4527 | Over-range | 931 | 750 | 354 | 2217 | 171 | 195 | 297 | 1667 | 1209 | 1179 | 1561 | 3949 | 1209 | 1179 | 1561 | 3949 | - - - | - - - | - - - | - - -
5/5/2026 | 4:00:00 PM | 279.71 | 277.06 | 275.79 | 483.5 | 477.04 | 481.5 | 4.5182 | 3.5414 | 5.2683 | 4.145 | 1.43 | 1.432 | 1.429 | 1.56 | 1.51 | 1.534 | Over-range | 60.01 | 1057 | 616 | 1420 | 3094 | - - - | - - - | - - - | - - - | 1057 | 616 | 1420 | 3094 | 666 | 724 | 66 | 1456 | - - - | - - - | - - - | - - - | 666 | 724 | 66 | 1456 | 1262 | 977 | 1453 | 3691 | # # # | # # # | # # # | # # # | 0.838 | 0.631 | 0.978 | 0.838 | # # # | # # # | # # # | - - - | 0.846 | 0.641 | 0.998 | 0.851 | - - - | 0.471 | 1.66 | 1.62 | 1.56 | 1.46 | 1.51 | 1.56 | 10.63 | 16.41 | 17.73 | 0 | - - - | - - - | - - - | - - - | 1262 | 977 | 1453 | 3691 | Over-range | 688 | 746 | 303 | 2009 | 170 | 181 | 288 | 1383 | 1058 | 615 | 1423 | 3096 | 1058 | 615 | 1423 | 3096 | - - - | - - - | - - - | - - -
5/5/2026 | 4:15:00 PM | 279.78 | 277.14 | 275.92 | 483.55 | 477.3 | 481.64 | 4.6985 | 3.8614 | 5.3671 | 4.1502 | 1.431 | 1.432 | 1.429 | 1.556 | 1.495 | 1.514 | Over-range | 60.01 | 1084 | 715 | 1445 | 3245 | - - - | - - - | - - - | - - - | 1084 | 715 | 1445 | 3245 | 711 | 725 | 21 | 1457 | - - - | - - - | - - - | - - - | 711 | 725 | 21 | 1457 | 1309 | 1054 | 1479 | 3842 | # # # | # # # | # # # | # # # | 0.828 | 0.679 | 0.977 | 0.845 | # # # | # # # | # # # | - - - | 0.836 | 0.689 | 0.997 | 0.857 | - - - | 0.449 | 1.66 | 1.62 | 1.57 | 1.47 | 1.5 | 1.56 | 10.35 | 15.77 | 17.64 | 0 | - - - | - - - | - - - | - - - | 1309 | 1054 | 1479 | 3842 | Over-range | 731 | 747 | 314 | 2048 | 168 | 179 | 290 | 1439 | 1085 | 717 | 1444 | 3246 | 1085 | 717 | 1444 | 3246 | - - - | - - - | - - - | - - -
5/5/2026 | 4:30:00 PM | 279.53 | 276.98 | 275.58 | 483.31 | 476.78 | 481.13 | 4.7334 | 3.9175 | 5.3826 | 4.1446 | 1.431 | 1.433 | 1.43 | 1.554 | 1.492 | 1.507 | Over-range | 60.01 | 1089 | 737 | 1448 | 3274 | - - - | - - - | - - - | - - - | 1089 | 737 | 1448 | 3274 | 719 | 722 | 11 | 1451 | - - - | - - - | - - - | - - - | 719 | 722 | 11 | 1451 | 1317 | 1068 | 1482 | 3867 | # # # | # # # | # # # | # # # | 0.827 | 0.69 | 0.977 | 0.847 | # # # | # # # | # # # | - - - | 0.834 | 0.701 | 0.997 | 0.859 | - - - | 0.443 | 1.69 | 1.65 | 1.59 | 1.49 | 1.52 | 1.59 | 10.25 | 15.58 | 17.54 | 0 | - - - | - - - | - - - | - - - | 1317 | 1068 | 1482 | 3867 | Over-range | 739 | 744 | 314 | 2048 | 168 | 180 | 289 | 1444 | 1090 | 739 | 1446 | 3275 | 1090 | 739 | 1446 | 3275 | - - - | - - - | - - - | - - -
5/5/2026 | 4:45:00 PM | 279.2 | 276.48 | 275.13 | 482.6 | 475.9 | 480.49 | 4.9581 | 4.1552 | 5.4842 | 4.1374 | 1.43 | 1.433 | 1.43 | 1.55 | 1.483 | 1.486 | Over-range | 60 | 1132 | 850 | 1474 | 3455 | - - - | - - - | - - - | - - - | 1132 | 850 | 1474 | 3455 | 768 | 715 | -27 | 1455 | - - - | - - - | - - - | - - - | 768 | 715 | -27 | 1455 | 1380 | 1135 | 1508 | 4022 | # # # | # # # | # # # | # # # | 0.82 | 0.749 | 0.977 | 0.859 | # # # | # # # | # # # | - - - | 0.819 | 0.753 | 0.987 | 0.863 | - - - | 0.421 | 1.67 | 1.66 | 1.6 | 1.48 | 1.53 | 1.58 | 9.68 | 14.7 | 17.27 | 0 | - - - | - - - | - - - | - - - | 1380 | 1135 | 1508 | 4022 | Over-range | 788 | 737 | 317 | 2057 | 172 | 179 | 290 | 1447 | 1140 | 856 | 1483 | 3479 | 1140 | 856 | 1483 | 3479 | - - - | - - - | - - - | - - -
5/5/2026 | 5:00:00 PM | 279.19 | 276.27 | 275.03 | 482.4 | 475.57 | 480.47 | 5.2761 | 4.7513 | 5.6785 | 4.1329 | 1.431 | 1.433 | 1.431 | 1.542 | 1.454 | 1.416 | Over-range | 60.01 | 1179 | 1084 | 1527 | 3790 | - - - | - - - | - - - | - - - | 1179 | 1084 | 1527 | 3790 | 865 | 710 | -145 | 1428 | - - - | - - - | - - - | - - - | 865 | 710 | -145 | 1428 | 1472 | 1310 | 1561 | 4344 | # # # | # # # | # # # | # # # | 0.801 | 0.828 | 0.978 | 0.873 | # # # | # # # | # # # | - - - | 0.807 | 0.836 | 0.995 | 0.883 | - - - | 0.377 | 1.69 | 1.68 | 1.63 | 1.5 | 1.57 | 1.61 | 9.01 | 12.96 | 16.77 | 0 | - - - | - - - | - - - | - - - | 1472 | 1310 | 1561 | 4344 | Over-range | 882 | 733 | 328 | 2123 | 169 | 184 | 290 | 1569 | 1181 | 1086 | 1525 | 3791 | 1181 | 1086 | 1525 | 3791 | - - - | - - - | - - - | - - -
5/5/2026 | 5:15:00 PM | 280.51 | 277.72 | 276.4 | 484.76 | 478.13 | 482.72 | 5.0863 | 4.4295 | 5.5772 | 4.1466 | 1.431 | 1.433 | 1.431 | 1.547 | 1.465 | 1.45 | Over-range | 60.02 | 1151 | 965 | 1509 | 3625 | - - - | - - - | - - - | - - - | 1151 | 965 | 1509 | 3625 | 824 | 728 | -83 | 1468 | - - - | - - - | - - - | - - - | 824 | 728 | -83 | 1468 | 1426 | 1226 | 1541 | 4193 | # # # | # # # | # # # | # # # | 0.807 | 0.787 | 0.979 | 0.865 | # # # | # # # | # # # | - - - | 0.814 | 0.797 | 0.998 | 0.876 | - - - | 0.405 | 1.7 | 1.64 | 1.59 | 1.5 | 1.54 | 1.6 | 9.49 | 14.1 | 17.34 | 0 | - - - | - - - | - - - | - - - | 1426 | 1226 | 1541 | 4193 | Over-range | 841 | 752 | 312 | 2107 | 172 | 189 | 295 | 1510 | 1153 | 965 | 1509 | 3626 | 1153 | 965 | 1509 | 3626 | - - - | - - - | - - - | - - -
5/5/2026 | 5:30:00 PM | 280.48 | 277.6 | 276.37 | 484.65 | 477.96 | 482.69 | 5.7618 | 5.6411 | 5.9933 | 4.1384 | 1.432 | 1.434 | 1.432 | 1.538 | 1.467 | 1.381 | Over-range | 60.01 | 1257 | 1373 | 1607 | 4237 | - - - | - - - | - - - | - - - | 1257 | 1373 | 1607 | 4237 | 1000 | 723 | -263 | 1460 | - - - | - - - | - - - | - - - | 1000 | 723 | -263 | 1460 | 1616 | 1565 | 1656 | 4837 | # # # | # # # | # # # | # # # | 0.778 | 0.877 | 0.97 | 0.876 | # # # | # # # | # # # | - - - | 0.783 | 0.884 | 0.986 | 0.885 | - - - | 0.344 | 1.66 | 1.6 | 1.6 | 1.48 | 1.52 | 1.58 | 8.39 | 11.61 | 16.41 | 0 | - - - | - - - | - - - | - - - | 1616 | 1565 | 1656 | 4837 | Over-range | 1015 | 750 | 400 | 2332 | 172 | 197 | 299 | 1818 | 1260 | 1374 | 1604 | 4238 | 1260 | 1374 | 1604 | 4238 | - - - | - - - | - - - | - - -
5/5/2026 | 5:45:00 PM | 281.15 | 278.32 | 277.02 | 485.89 | 479.15 | 483.78 | 5.5816 | 5.2136 | 5.8529 | 4.1442 | 1.432 | 1.434 | 1.433 | 1.539 | 1.457 | 1.407 | Over-range | 60 | 1234 | 1227 | 1580 | 4041 | - - - | - - - | - - - | - - - | 1234 | 1227 | 1580 | 4041 | 948 | 734 | -178 | 1503 | - - - | - - - | - - - | - - - | 948 | 734 | -178 | 1503 | 1567 | 1445 | 1621 | 4633 | # # # | # # # | # # # | # # # | 0.788 | 0.849 | 0.975 | 0.872 | # # # | # # # | # # # | - - - | 0.786 | 0.843 | 0.973 | 0.869 | - - - | 0.372 | 1.66 | 1.62 | 1.57 | 1.48 | 1.52 | 1.58 | 8.86 | 12.66 | 16.97 | 0 | - - - | - - - | - - - | - - - | 1567 | 1445 | 1621 | 4633 | Over-range | 964 | 760 | 362 | 2266 | 173 | 194 | 301 | 1689 | 1247 | 1244 | 1603 | 4094 | 1247 | 1244 | 1603 | 4094 | - - - | - - - | - - - | - - -
5/5/2026 | 6:00:00 PM | 281.33 | 278.54 | 277.21 | 486.21 | 479.53 | 484.1 | 4.9982 | 4.2652 | 5.53 | 4.1585 | 1.432 | 1.434 | 1.433 | 1.549 | 1.475 | 1.464 | Over-range | 60.01 | 1138 | 910 | 1503 | 3551 | - - - | - - - | - - - | - - - | 1138 | 910 | 1503 | 3551 | 808 | 739 | -53 | 1493 | - - - | - - - | - - - | - - - | 808 | 739 | -53 | 1493 | 1406 | 1188 | 1533 | 4127 | # # # | # # # | # # # | # # # | 0.809 | 0.766 | 0.98 | 0.86 | # # # | # # # | # # # | - - - | 0.816 | 0.776 | 0.999 | 0.872 | - - - | 0.42 | 1.62 | 1.59 | 1.52 | 1.44 | 1.47 | 1.53 | 9.7 | 14.44 | 17.56 | 0 | - - - | - - - | - - - | - - - | 1406 | 1188 | 1533 | 4127 | Over-range | 826 | 763 | 303 | 2103 | 171 | 191 | 298 | 1482 | 1141 | 909 | 1503 | 3553 | 1141 | 909 | 1503 | 3553 | - - - | - - - | - - - | - - -
5/5/2026 | 6:15:00 PM | 282.16 | 279.4 | 278.13 | 487.69 | 481.09 | 485.6 | 5.5754 | 5.3005 | 5.8805 | 4.1563 | 1.432 | 1.432 | 1.432 | 1.544 | 1.459 | 1.395 | Over-range | 60.01 | 1230 | 1255 | 1593 | 4077 | - - - | - - - | - - - | - - - | 1230 | 1255 | 1593 | 4077 | 963 | 747 | -199 | 1510 | - - - | - - - | - - - | - - - | 963 | 747 | -199 | 1510 | 1572 | 1476 | 1635 | 4683 | # # # | # # # | # # # | # # # | 0.782 | 0.85 | 0.974 | 0.871 | # # # | # # # | # # # | - - - | 0.788 | 0.858 | 0.991 | 0.881 | - - - | 0.37 | 1.53 | 1.48 | 1.4 | 1.36 | 1.35 | 1.41 | 8.84 | 12.64 | 17.13 | 0 | - - - | - - - | - - - | - - - | 1572 | 1476 | 1635 | 4683 | Over-range | 979 | 774 | 370 | 2304 | 174 | 204 | 307 | 1739 | 1234 | 1254 | 1591 | 4079 | 1234 | 1254 | 1591 | 4079 | - - - | - - - | - - - | - - -
5/5/2026 | 6:30:00 PM | 282.18 | 279.44 | 278.06 | 487.77 | 481.06 | 485.52 | 5.6728 | 5.4671 | 5.9379 | 4.1549 | 1.432 | 1.431 | 1.432 | 1.543 | 1.454 | 1.384 | Over-range | 60 | 1245 | 1316 | 1606 | 4167 | - - - | - - - | - - - | - - - | 1245 | 1316 | 1606 | 4167 | 990 | 747 | -225 | 1511 | - - - | - - - | - - - | - - - | 990 | 747 | -225 | 1511 | 1601 | 1527 | 1651 | 4778 | # # # | # # # | # # # | # # # | 0.778 | 0.862 | 0.973 | 0.872 | # # # | # # # | # # # | - - - | 0.784 | 0.87 | 0.99 | 0.882 | - - - | 0.363 | 1.52 | 1.45 | 1.37 | 1.35 | 1.33 | 1.39 | 8.68 | 12.22 | 16.96 | 0 | - - - | - - - | - - - | - - - | 1601 | 1527 | 1651 | 4778 | Over-range | 1005 | 774 | 382 | 2338 | 173 | 204 | 307 | 1784 | 1249 | 1317 | 1604 | 4169 | 1249 | 1317 | 1604 | 4169 | - - - | - - - | - - - | - - -
5/5/2026 | 6:45:00 PM | 282.39 | 279.66 | 278.26 | 488.13 | 481.43 | 485.87 | 5.5203 | 5.0867 | 5.8186 | 4.1567 | 1.432 | 1.431 | 1.431 | 1.543 | 1.445 | 1.408 | Over-range | 59.99 | 1227 | 1190 | 1581 | 3998 | - - - | - - - | - - - | - - - | 1227 | 1190 | 1581 | 3998 | 942 | 752 | -153 | 1541 | - - - | - - - | - - - | - - - | 942 | 752 | -153 | 1541 | 1558 | 1422 | 1619 | 4599 | # # # | # # # | # # # | # # # | 0.788 | 0.837 | 0.976 | 0.869 | # # # | # # # | # # # | - - - | 0.786 | 0.839 | 0.986 | 0.872 | - - - | 0.385 | 1.5 | 1.42 | 1.36 | 1.33 | 1.32 | 1.37 | 9.05 | 13.1 | 17.38 | 0 | - - - | - - - | - - - | - - - | 1558 | 1422 | 1619 | 4599 | Over-range | 959 | 779 | 351 | 2273 | 175 | 200 | 308 | 1668 | 1242 | 1206 | 1605 | 4053 | 1242 | 1206 | 1605 | 4053 | - - - | - - - | - - - | - - -
5/5/2026 | 7:00:00 PM | 282.74 | 280.04 | 278.59 | 488.77 | 482.05 | 486.46 | 4.758 | 3.9875 | 5.4187 | 4.17 | 1.432 | 1.43 | 1.43 | 1.561 | 1.504 | 1.511 | Over-range | 60 | 1096 | 741 | 1472 | 3309 | - - - | - - - | - - - | - - - | 1096 | 741 | 1472 | 3309 | 747 | 762 | 30 | 1539 | - - - | - - - | - - - | - - - | 747 | 762 | 30 | 1539 | 1339 | 1101 | 1508 | 3949 | # # # | # # # | # # # | # # # | 0.818 | 0.673 | 0.976 | 0.838 | # # # | # # # | # # # | - - - | 0.826 | 0.683 | 0.997 | 0.851 | - - - | 0.465 | 1.47 | 1.4 | 1.29 | 1.3 | 1.27 | 1.33 | 10.63 | 16.09 | 18.15 | 0 | - - - | - - - | - - - | - - - | 1339 | 1101 | 1508 | 3949 | Over-range | 768 | 787 | 328 | 2146 | 174 | 196 | 302 | 1494 | 1099 | 739 | 1474 | 3312 | 1099 | 739 | 1474 | 3312 | - - - | - - - | - - - | - - -
5/5/2026 | 7:15:00 PM | 282.61 | 280.04 | 278.48 | 488.75 | 481.95 | 486.17 | 4.8495 | 4.0706 | 5.4643 | 4.169 | 1.432 | 1.43 | 1.431 | 1.557 | 1.5 | 1.495 | Over-range | 60 | 1114 | 812 | 1489 | 3415 | - - - | - - - | - - - | - - - | 1114 | 812 | 1489 | 3415 | 776 | 762 | 0 | 1537 | - - - | - - - | - - - | - - - | 776 | 762 | 0 | 1537 | 1369 | 1135 | 1521 | 4026 | # # # | # # # | # # # | # # # | 0.814 | 0.715 | 0.979 | 0.848 | # # # | # # # | # # # | - - - | 0.821 | 0.726 | 0.999 | 0.861 | - - - | 0.45 | 1.46 | 1.37 | 1.27 | 1.29 | 1.24 | 1.3 | 10.27 | 15.55 | 18.12 | 0 | - - - | - - - | - - - | - - - | 1369 | 1135 | 1521 | 4026 | Over-range | 795 | 787 | 310 | 2130 | 175 | 196 | 304 | 1474 | 1117 | 811 | 1490 | 3418 | 1117 | 811 | 1490 | 3418 | - - - | - - - | - - - | - - -
5/5/2026 | 7:30:00 PM | 283 | 280.5 | 278.91 | 489.5 | 482.73 | 486.87 | 4.9807 | 4.2678 | 5.5345 | 4.1676 | 1.431 | 1.429 | 1.43 | 1.554 | 1.486 | 1.485 | Over-range | 60 | 1136 | 894 | 1512 | 3543 | - - - | - - - | - - - | - - - | 1136 | 894 | 1512 | 3543 | 814 | 769 | -34 | 1549 | - - - | - - - | - - - | - - - | 814 | 769 | -34 | 1549 | 1409 | 1196 | 1544 | 4149 | # # # | # # # | # # # | # # # | 0.806 | 0.748 | 0.98 | 0.854 | # # # | # # # | # # # | - - - | 0.813 | 0.759 | 0.999 | 0.866 | - - - | 0.437 | 1.46 | 1.35 | 1.23 | 1.27 | 1.21 | 1.27 | 10.01 | 15.05 | 18.15 | 0 | - - - | - - - | - - - | - - - | 1409 | 1196 | 1544 | 4149 | Over-range | 834 | 793 | 310 | 2159 | 178 | 194 | 307 | 1504 | 1136 | 897 | 1510 | 3543 | 1136 | 897 | 1510 | 3543 | - - - | - - - | - - - | - - -
5/5/2026 | 7:45:00 PM | 283.18 | 280.8 | 279.14 | 489.86 | 483.31 | 487.14 | 5.6062 | 5.7473 | 5.911 | 3.8149 | 1.432 | 1.43 | 1.43 | 1.545 | 1.457 | 1.395 | Over-range | 59.99 | 1235 | 1396 | 1607 | 4238 | - - - | - - - | - - - | - - - | 1235 | 1396 | 1607 | 4238 | 979 | 732 | -198 | 1512 | - - - | - - - | - - - | - - - | 979 | 732 | -198 | 1512 | 1587 | 1598 | 1650 | 4834 | # # # | # # # | # # # | # # # | 0.778 | 0.874 | 0.974 | 0.877 | # # # | # # # | # # # | - - - | 0.783 | 0.88 | 0.992 | 0.886 | - - - | 0.357 | 1.45 | 1.34 | 1.23 | 1.28 | 1.21 | 1.28 | 8.91 | 11.45 | 17.34 | 0 | - - - | - - - | - - - | - - - | 1587 | 1598 | 1650 | 4834 | Over-range | 996 | 757 | 372 | 2322 | 186 | 192 | 312 | 1760 | 1234 | 1396 | 1608 | 4239 | 1234 | 1396 | 1608 | 4239 | - - - | - - - | - - - | - - -
5/5/2026 | 8:00:00 PM | 283.64 | 281.28 | 279.58 | 490.73 | 484.07 | 487.91 | 5.7258 | 6.6152 | 5.9544 | 2.7222 | 1.431 | 1.429 | 1.43 | 1.548 | 1.475 | 1.394 | Over-range | 60 | 1262 | 1738 | 1622 | 4622 | - - - | - - - | - - - | - - - | 1262 | 1738 | 1622 | 4622 | 1001 | 643 | -199 | 1444 | - - - | - - - | - - - | - - - | 1001 | 643 | -199 | 1444 | 1622 | 1860 | 1665 | 5146 | # # # | # # # | # # # | # # # | 0.778 | 0.934 | 0.975 | 0.898 | # # # | # # # | # # # | - - - | 0.774 | 0.929 | 0.983 | 0.897 | - - - | 0.312 | 1.43 | 1.32 | 1.2 | 1.26 | 1.18 | 1.25 | 10.68 | 9.52 | 18.36 | 0 | - - - | - - - | - - - | - - - | 1622 | 1860 | 1665 | 5146 | Over-range | 1019 | 662 | 372 | 2264 | 155 | 130 | 306 | 1740 | 1275 | 1761 | 1648 | 4685 | 1275 | 1761 | 1648 | 4685 | - - - | - - - | - - - | - - -
5/5/2026 | 8:15:00 PM | 284.01 | 281.62 | 279.9 | 491.33 | 484.65 | 488.5 | 5.4611 | 6.1734 | 5.8246 | 2.7907 | 1.431 | 1.429 | 1.43 | 1.55 | 1.468 | 1.404 | Over-range | 60 | 1213 | 1600 | 1592 | 4405 | - - - | - - - | - - - | - - - | 1213 | 1600 | 1592 | 4405 | 949 | 657 | -153 | 1452 | - - - | - - - | - - - | - - - | 949 | 657 | -153 | 1452 | 1551 | 1738 | 1630 | 4919 | # # # | # # # | # # # | # # # | 0.782 | 0.921 | 0.977 | 0.895 | # # # | # # # | # # # | - - - | 0.788 | 0.925 | 0.996 | 0.905 | - - - | 0.33 | 1.41 | 1.3 | 1.21 | 1.25 | 1.17 | 1.24 | 9.28 | 8.61 | 17.71 | 0 | - - - | - - - | - - - | - - - | 1551 | 1738 | 1630 | 4919 | Over-range | 967 | 679 | 350 | 2190 | 183 | 171 | 314 | 1639 | 1215 | 1598 | 1595 | 4407 | 1215 | 1598 | 1595 | 4407 | - - - | - - - | - - - | - - -
5/5/2026 | 8:30:00 PM | 283.3 | 280.95 | 279.1 | 490.2 | 483.4 | 487.13 | 4.9296 | 5.1907 | 5.5227 | 2.7955 | 1.43 | 1.428 | 1.429 | 1.561 | 1.486 | 1.484 | Over-range | 60 | 1123 | 1258 | 1503 | 3883 | - - - | - - - | - - - | - - - | 1123 | 1258 | 1503 | 3883 | 797 | 651 | -9 | 1437 | - - - | - - - | - - - | - - - | 797 | 651 | -9 | 1437 | 1390 | 1434 | 1540 | 4364 | # # # | # # # | # # # | # # # | 0.808 | 0.877 | 0.976 | 0.89 | # # # | # # # | # # # | - - - | 0.815 | 0.883 | 0.995 | 0.901 | - - - | 0.37 | 1.42 | 1.29 | 1.16 | 1.23 | 1.15 | 1.22 | 10.39 | 10.08 | 18.09 | 0 | - - - | - - - | - - - | - - - | 1390 | 1434 | 1540 | 4364 | Over-range | 817 | 671 | 333 | 1988 | 177 | 164 | 305 | 1365 | 1126 | 1256 | 1504 | 3886 | 1126 | 1256 | 1504 | 3886 | - - - | - - - | - - - | - - -
5/5/2026 | 8:45:00 PM | 283.24 | 280.8 | 279.02 | 489.98 | 483.2 | 487.03 | 4.8093 | 4.9181 | 5.453 | 2.7985 | 1.431 | 1.428 | 1.429 | 1.564 | 1.47 | 1.498 | Over-range | 60 | 1107 | 1195 | 1488 | 3790 | - - - | - - - | - - - | - - - | 1107 | 1195 | 1488 | 3790 | 770 | 650 | 16 | 1436 | - - - | - - - | - - - | - - - | 770 | 650 | 16 | 1436 | 1360 | 1373 | 1521 | 4253 | # # # | # # # | # # # | # # # | 0.814 | 0.871 | 0.978 | 0.891 | # # # | # # # | # # # | - - - | 0.822 | 0.876 | 0.999 | 0.902 | - - - | 0.379 | 1.43 | 1.28 | 1.18 | 1.24 | 1.15 | 1.23 | 10.45 | 10.22 | 18.33 | 0 | - - - | - - - | - - - | - - - | 1360 | 1373 | 1521 | 4253 | Over-range | 789 | 670 | 315 | 1931 | 175 | 164 | 306 | 1287 | 1110 | 1193 | 1490 | 3793 | 1110 | 1193 | 1490 | 3793 | - - - | - - - | - - - | - - -
5/5/2026 | 9:00:00 PM | 283.63 | 281.2 | 279.37 | 490.73 | 483.8 | 487.65 | 4.5695 | 4.3577 | 5.3257 | 2.8041 | 1.431 | 1.429 | 1.429 | 1.568 | 1.505 | 1.55 | Over-range | 60.01 | 1073 | 1010 | 1448 | 3531 | - - - | - - - | - - - | - - - | 1073 | 1010 | 1448 | 3531 | 698 | 656 | 115 | 1469 | - - - | - - - | - - - | - - - | 698 | 656 | 115 | 1469 | 1293 | 1219 | 1487 | 3999 | # # # | # # # | # # # | # # # | 0.83 | 0.829 | 0.973 | 0.883 | # # # | # # # | # # # | - - - | 0.831 | 0.83 | 0.979 | 0.886 | - - - | 0.416 | 1.44 | 1.32 | 1.19 | 1.26 | 1.18 | 1.25 | 11.18 | 11.4 | 18.53 | 0 | - - - | - - - | - - - | - - - | 1293 | 1219 | 1487 | 3999 | Over-range | 720 | 676 | 336 | 1877 | 176 | 163 | 305 | 1162 | 1085 | 1013 | 1465 | 3563 | 1085 | 1013 | 1465 | 3563 | - - - | - - - | - - - | - - -
5/5/2026 | 9:15:00 PM | 283.75 | 281.4 | 279.54 | 490.98 | 484.2 | 487.86 | 4.7593 | 4.8541 | 5.4359 | 2.7995 | 1.43 | 1.428 | 1.428 | 1.565 | 1.496 | 1.519 | Over-range | 60 | 1096 | 1151 | 1481 | 3729 | - - - | - - - | - - - | - - - | 1096 | 1151 | 1481 | 3729 | 755 | 659 | 41 | 1456 | - - - | - - - | - - - | - - - | 755 | 659 | 41 | 1456 | 1344 | 1345 | 1518 | 4207 | # # # | # # # | # # # | # # # | 0.816 | 0.856 | 0.975 | 0.886 | # # # | # # # | # # # | - - - | 0.823 | 0.863 | 0.997 | 0.898 | - - - | 0.39 | 1.42 | 1.3 | 1.18 | 1.25 | 1.16 | 1.23 | 10.85 | 10.78 | 18.47 | 0 | - - - | - - - | - - - | - - - | 1344 | 1345 | 1518 | 4207 | Over-range | 776 | 679 | 333 | 1947 | 175 | 163 | 308 | 1285 | 1098 | 1153 | 1479 | 3730 | 1098 | 1153 | 1479 | 3730 | - - - | - - - | - - - | - - -
5/5/2026 | 9:30:00 PM | 284.08 | 281.69 | 279.93 | 491.44 | 484.83 | 488.52 | 4.7385 | 4.8102 | 5.4315 | 2.8078 | 1.431 | 1.429 | 1.428 | 1.566 | 1.501 | 1.515 | Over-range | 60.01 | 1093 | 1136 | 1481 | 3711 | - - - | - - - | - - - | - - - | 1093 | 1136 | 1481 | 3711 | 753 | 662 | 51 | 1466 | - - - | - - - | - - - | - - - | 753 | 662 | 51 | 1466 | 1340 | 1334 | 1519 | 4193 | # # # | # # # | # # # | # # # | 0.816 | 0.852 | 0.975 | 0.885 | # # # | # # # | # # # | - - - | 0.824 | 0.859 | 0.996 | 0.897 | - - - | 0.395 | 1.44 | 1.29 | 1.19 | 1.25 | 1.16 | 1.22 | 10.96 | 10.94 | 18.54 | 0 | - - - | - - - | - - - | - - - | 1340 | 1334 | 1519 | 4193 | Over-range | 773 | 683 | 335 | 1950 | 175 | 167 | 309 | 1279 | 1097 | 1135 | 1481 | 3713 | 1097 | 1135 | 1481 | 3713 | - - - | - - - | - - - | - - -
5/5/2026 | 9:45:00 PM | 284.46 | 282.12 | 280.37 | 492.19 | 485.57 | 489.2 | 4.8577 | 5.0072 | 5.4909 | 2.8084 | 1.43 | 1.427 | 1.427 | 1.563 | 1.476 | 1.505 | Over-range | 60.01 | 1115 | 1216 | 1504 | 3834 | - - - | - - - | - - - | - - - | 1115 | 1216 | 1504 | 3834 | 790 | 669 | 19 | 1478 | - - - | - - - | - - - | - - - | 790 | 669 | 19 | 1478 | 1378 | 1401 | 1539 | 4318 | # # # | # # # | # # # | # # # | 0.809 | 0.868 | 0.977 | 0.888 | # # # | # # # | # # # | - - - | 0.816 | 0.874 | 0.998 | 0.899 | - - - | 0.385 | 1.45 | 1.29 | 1.18 | 1.24 | 1.16 | 1.22 | 10.65 | 10.51 | 18.61 | 0 | - - - | - - - | - - - | - - - | 1378 | 1401 | 1539 | 4318 | Over-range | 810 | 689 | 326 | 1986 | 180 | 166 | 313 | 1321 | 1116 | 1216 | 1503 | 3836 | 1116 | 1216 | 1503 | 3836 | - - - | - - - | - - - | - - -
5/5/2026 | 10:00:00 PM | 284.6 | 282.24 | 280.52 | 492.37 | 485.82 | 489.49 | 5.3861 | 5.908 | 5.7606 | 2.8079 | 1.431 | 1.428 | 1.428 | 1.555 | 1.47 | 1.434 | Over-range | 60.01 | 1205 | 1508 | 1578 | 4291 | - - - | - - - | - - - | - - - | 1205 | 1508 | 1578 | 4291 | 922 | 667 | -93 | 1494 | - - - | - - - | - - - | - - - | 922 | 667 | -93 | 1494 | 1529 | 1660 | 1615 | 4805 | # # # | # # # | # # # | # # # | 0.788 | 0.908 | 0.977 | 0.893 | # # # | # # # | # # # | - - - | 0.787 | 0.906 | 0.988 | 0.895 | - - - | 0.348 | 1.45 | 1.29 | 1.2 | 1.26 | 1.17 | 1.24 | 9.72 | 9.29 | 18.07 | 0 | - - - | - - - | - - - | - - - | 1529 | 1660 | 1615 | 4805 | Over-range | 940 | 689 | 344 | 2161 | 183 | 171 | 317 | 1555 | 1217 | 1517 | 1591 | 4325 | 1217 | 1517 | 1591 | 4325 | - - - | - - - | - - - | - - -
5/5/2026 | 10:15:00 PM | 284.58 | 282.15 | 280.36 | 492.32 | 485.53 | 489.33 | 4.5687 | 4.4499 | 5.3441 | 2.8197 | 1.431 | 1.428 | 1.429 | 1.572 | 1.504 | 1.552 | Over-range | 60.01 | 1069 | 1036 | 1460 | 3565 | - - - | - - - | - - - | - - - | 1069 | 1036 | 1460 | 3565 | 713 | 672 | 96 | 1481 | - - - | - - - | - - - | - - - | 713 | 672 | 96 | 1481 | 1298 | 1249 | 1498 | 4045 | # # # | # # # | # # # | # # # | 0.823 | 0.83 | 0.975 | 0.881 | # # # | # # # | # # # | - - - | 0.831 | 0.837 | 0.997 | 0.894 | - - - | 0.416 | 1.48 | 1.32 | 1.22 | 1.28 | 1.21 | 1.28 | 11.42 | 11.61 | 18.82 | 0 | - - - | - - - | - - - | - - - | 1298 | 1249 | 1498 | 4045 | Over-range | 736 | 691 | 332 | 1909 | 182 | 163 | 310 | 1203 | 1068 | 1037 | 1461 | 3566 | 1068 | 1037 | 1461 | 3566 | - - - | - - - | - - - | - - -
5/5/2026 | 10:30:00 PM | 284.68 | 282.2 | 280.43 | 492.45 | 485.58 | 489.54 | 5.2864 | 5.8012 | 5.7188 | 2.8146 | 1.43 | 1.428 | 1.428 | 1.558 | 1.459 | 1.439 | Over-range | 60 | 1186 | 1483 | 1568 | 4237 | - - - | - - - | - - - | - - - | 1186 | 1483 | 1568 | 4237 | 908 | 667 | -98 | 1476 | - - - | - - - | - - - | - - - | 908 | 667 | -98 | 1476 | 1504 | 1635 | 1604 | 4743 | # # # | # # # | # # # | # # # | 0.788 | 0.907 | 0.978 | 0.893 | # # # | # # # | # # # | - - - | 0.794 | 0.912 | 0.997 | 0.903 | - - - | 0.348 | 1.46 | 1.31 | 1.22 | 1.27 | 1.19 | 1.26 | 9.75 | 9.24 | 18.12 | 0 | - - - | - - - | - - - | - - - | 1504 | 1635 | 1604 | 4743 | Over-range | 926 | 689 | 333 | 2132 | 179 | 173 | 316 | 1537 | 1188 | 1484 | 1566 | 4238 | 1188 | 1484 | 1566 | 4238 | - - - | - - - | - - - | - - -
5/5/2026 | 10:45:00 PM | 284.71 | 282.05 | 280.37 | 492.38 | 485.34 | 489.56 | 4.9554 | 5.1611 | 5.5317 | 2.8139 | 1.431 | 1.428 | 1.429 | 1.563 | 1.457 | 1.484 | Over-range | 60.01 | 1133 | 1280 | 1519 | 3931 | - - - | - - - | - - - | - - - | 1133 | 1280 | 1519 | 3931 | 821 | 667 | -9 | 1477 | - - - | - - - | - - - | - - - | 821 | 667 | -9 | 1477 | 1410 | 1454 | 1551 | 4415 | # # # | # # # | # # # | # # # | 0.803 | 0.88 | 0.979 | 0.89 | # # # | # # # | # # # | - - - | 0.81 | 0.886 | 1 | 0.901 | - - - | 0.376 | 1.45 | 1.31 | 1.23 | 1.27 | 1.2 | 1.26 | 10.43 | 10.04 | 18.42 | 0 | - - - | - - - | - - - | - - - | 1410 | 1454 | 1551 | 4415 | Over-range | 840 | 688 | 315 | 2009 | 179 | 170 | 312 | 1360 | 1136 | 1278 | 1520 | 3934 | 1136 | 1278 | 1520 | 3934 | - - - | - - - | - - - | - - -
5/5/2026 | 11:00:00 PM | 285.34 | 282.69 | 280.98 | 493.48 | 486.41 | 490.62 | 5.4127 | 6.0427 | 5.7929 | 2.8153 | 1.431 | 1.428 | 1.428 | 1.557 | 1.465 | 1.42 | Over-range | 60.01 | 1206 | 1557 | 1590 | 4353 | - - - | - - - | - - - | - - - | 1206 | 1557 | 1590 | 4353 | 946 | 673 | -125 | 1493 | - - - | - - - | - - - | - - - | 946 | 673 | -125 | 1493 | 1544 | 1706 | 1627 | 4877 | # # # | # # # | # # # | # # # | 0.781 | 0.913 | 0.977 | 0.893 | # # # | # # # | # # # | - - - | 0.788 | 0.917 | 0.997 | 0.902 | - - - | 0.343 | 1.45 | 1.34 | 1.23 | 1.28 | 1.21 | 1.27 | 9.61 | 9.12 | 18.1 | 0 | - - - | - - - | - - - | - - - | 1544 | 1706 | 1627 | 4877 | Over-range | 963 | 696 | 346 | 2199 | 183 | 178 | 320 | 1614 | 1210 | 1555 | 1591 | 4356 | 1210 | 1555 | 1591 | 4356 | - - - | - - - | - - - | - - -
5/5/2026 | 11:15:00 PM | 285.19 | 282.41 | 280.81 | 493.05 | 486.03 | 490.4 | 5.5759 | 6.2435 | 5.8613 | 2.8131 | 1.431 | 1.428 | 1.429 | 1.554 | 1.47 | 1.411 | Over-range | 60 | 1238 | 1622 | 1607 | 4467 | - - - | - - - | - - - | - - - | 1238 | 1622 | 1607 | 4467 | 978 | 669 | -140 | 1505 | - - - | - - - | - - - | - - - | 978 | 669 | -140 | 1505 | 1589 | 1763 | 1646 | 4998 | # # # | # # # | # # # | # # # | 0.779 | 0.92 | 0.976 | 0.894 | # # # | # # # | # # # | - - - | 0.778 | 0.917 | 0.986 | 0.895 | - - - | 0.337 | 1.46 | 1.34 | 1.24 | 1.28 | 1.22 | 1.28 | 9.42 | 8.9 | 17.92 | 0 | - - - | - - - | - - - | - - - | 1589 | 1763 | 1646 | 4998 | Over-range | 996 | 692 | 356 | 2242 | 182 | 175 | 319 | 1657 | 1252 | 1632 | 1633 | 4516 | 1252 | 1632 | 1633 | 4516 | - - - | - - - | - - - | - - -
5/5/2026 | 11:30:00 PM | 285.48 | 282.5 | 280.91 | 493.48 | 486.03 | 490.8 | 5.107 | 5.4847 | 5.6185 | 2.7997 | 1.431 | 1.429 | 1.427 | 1.524 | 1.47 | 1.393 | Over-range | 60 | 1155 | 1357 | 1543 | 4055 | - - - | - - - | - - - | - - - | 1155 | 1357 | 1543 | 4055 | 861 | 670 | -39 | 1492 | - - - | - - - | - - - | - - - | 861 | 670 | -39 | 1492 | 1452 | 1530 | 1577 | 4559 | # # # | # # # | # # # | # # # | 0.795 | 0.887 | 0.978 | 0.889 | # # # | # # # | # # # | - - - | 0.801 | 0.893 | 0.996 | 0.899 | - - - | 0.368 | 1.58 | 1.47 | 1.38 | 1.4 | 1.38 | 1.42 | 10.42 | 10.16 | 18.25 | 0 | - - - | - - - | - - - | - - - | 1452 | 1530 | 1577 | 4559 | Over-range | 878 | 690 | 326 | 2082 | 171 | 165 | 298 | 1445 | 1158 | 1357 | 1542 | 4057 | 1158 | 1357 | 1542 | 4057 | - - - | - - - | - - - | - - -
5/5/2026 | 11:45:00 PM | 285.4 | 282.42 | 280.82 | 493.35 | 485.88 | 490.64 | 4.704 | 4.6994 | 5.4078 | 2.7905 | 1.431 | 1.431 | 1.427 | 1.499 | 1.45 | 1.386 | Over-range | 60.01 | 1092 | 1122 | 1488 | 3702 | - - - | - - - | - - - | - - - | 1092 | 1122 | 1488 | 3702 | 758 | 669 | 63 | 1489 | - - - | - - - | - - - | - - - | 758 | 669 | 63 | 1489 | 1340 | 1318 | 1518 | 4177 | # # # | # # # | # # # | # # # | 0.815 | 0.851 | 0.98 | 0.886 | # # # | # # # | # # # | - - - | 0.822 | 0.856 | 0.998 | 0.896 | - - - | 0.402 | 1.69 | 1.6 | 1.51 | 1.54 | 1.53 | 1.55 | 11.26 | 11.55 | 18.83 | 0 | - - - | - - - | - - - | - - - | 1340 | 1318 | 1518 | 4177 | Over-range | 775 | 687 | 301 | 1933 | 164 | 156 | 285 | 1229 | 1095 | 1120 | 1487 | 3702 | 1095 | 1120 | 1487 | 3702 | - - - | - - - | - - - | - - -
5/6/2026 | 12:00:00 AM | 285.26 | 282.29 | 280.69 | 493.09 | 485.71 | 490.4 | 4.6199 | 4.5635 | 5.3717 | 2.7941 | 1.431 | 1.431 | 1.426 | 1.495 | 1.467 | 1.396 | Over-range | 60.02 | 1077 | 1063 | 1474 | 3614 | - - - | - - - | - - - | - - - | 1077 | 1063 | 1474 | 3614 | 731 | 667 | 87 | 1485 | - - - | - - - | - - - | - - - | 731 | 667 | 87 | 1485 | 1313 | 1271 | 1507 | 4091 | # # # | # # # | # # # | # # # | 0.82 | 0.836 | 0.978 | 0.883 | # # # | # # # | # # # | - - - | 0.827 | 0.842 | 0.995 | 0.893 | - - - | 0.411 | 1.69 | 1.58 | 1.53 | 1.53 | 1.52 | 1.55 | 11.64 | 11.88 | 18.68 | 0 | - - - | - - - | - - - | - - - | 1313 | 1271 | 1507 | 4091 | Over-range | 750 | 685 | 313 | 1916 | 165 | 154 | 281 | 1203 | 1079 | 1061 | 1474 | 3615 | 1079 | 1061 | 1474 | 3615 | - - - | - - - | - - - | - - -
5/6/2026 | 12:15:00 AM | 285.25 | 282.18 | 280.54 | 493.06 | 485.38 | 490.28 | 4.7704 | 4.8542 | 5.443 | 2.7868 | 1.43 | 1.429 | 1.425 | 1.5 | 1.469 | 1.378 | Over-range | 59.98 | 1100 | 1153 | 1493 | 3747 | - - - | - - - | - - - | - - - | 1100 | 1153 | 1493 | 3747 | 771 | 667 | 48 | 1486 | - - - | - - - | - - - | - - - | 771 | 667 | 48 | 1486 | 1355 | 1350 | 1526 | 4230 | # # # | # # # | # # # | # # # | 0.812 | 0.855 | 0.979 | 0.886 | # # # | # # # | # # # | - - - | 0.819 | 0.86 | 0.996 | 0.896 | - - - | 0.397 | 1.7 | 1.57 | 1.52 | 1.53 | 1.52 | 1.54 | 11.29 | 11.46 | 18.7 | 0 | - - - | - - - | - - - | - - - | 1355 | 1350 | 1526 | 4230 | Over-range | 789 | 685 | 312 | 1962 | 167 | 157 | 284 | 1273 | 1102 | 1151 | 1494 | 3748 | 1102 | 1151 | 1494 | 3748 | - - - | - - - | - - - | - - -
5/6/2026 | 12:30:00 AM | 285.53 | 282.39 | 280.87 | 493.44 | 485.87 | 490.82 | 5.1431 | 5.4574 | 5.6298 | 2.7862 | 1.43 | 1.429 | 1.424 | 1.504 | 1.455 | 1.346 | Over-range | 60 | 1167 | 1349 | 1545 | 4061 | - - - | - - - | - - - | - - - | 1167 | 1349 | 1545 | 4061 | 861 | 668 | -22 | 1506 | - - - | - - - | - - - | - - - | 861 | 668 | -22 | 1506 | 1462 | 1519 | 1580 | 4561 | # # # | # # # | # # # | # # # | 0.798 | 0.888 | 0.978 | 0.89 | # # # | # # # | # # # | - - - | 0.797 | 0.886 | 0.986 | 0.892 | - - - | 0.371 | 1.69 | 1.59 | 1.5 | 1.53 | 1.52 | 1.54 | 10.44 | 10.37 | 18.4 | 0 | - - - | - - - | - - - | - - - | 1462 | 1519 | 1580 | 4561 | Over-range | 879 | 686 | 326 | 2075 | 174 | 154 | 289 | 1410 | 1175 | 1357 | 1555 | 4088 | 1175 | 1357 | 1555 | 4088 | - - - | - - - | - - - | - - -
5/6/2026 | 12:45:00 AM | 285.94 | 282.92 | 281.32 | 494.26 | 486.79 | 491.5 | 5.2839 | 5.7848 | 5.7204 | 2.7918 | 1.43 | 1.429 | 1.425 | 1.51 | 1.456 | 1.3 | Over-range | 60.01 | 1188 | 1482 | 1580 | 4250 | - - - | - - - | - - - | - - - | 1188 | 1482 | 1580 | 4250 | 917 | 674 | -90 | 1500 | - - - | - - - | - - - | - - - | 917 | 674 | -90 | 1500 | 1511 | 1636 | 1609 | 4756 | # # # | # # # | # # # | # # # | 0.786 | 0.906 | 0.982 | 0.893 | # # # | # # # | # # # | - - - | 0.792 | 0.91 | 0.998 | 0.902 | - - - | 0.353 | 1.71 | 1.62 | 1.52 | 1.55 | 1.54 | 1.56 | 10.11 | 9.68 | 18.32 | 0 | - - - | - - - | - - - | - - - | 1511 | 1636 | 1609 | 4756 | Over-range | 934 | 693 | 306 | 2136 | 174 | 162 | 292 | 1521 | 1189 | 1480 | 1581 | 4250 | 1189 | 1480 | 1581 | 4250 | - - - | - - - | - - - | - - -
5/6/2026 | 1:00:00 AM | 285.84 | 282.78 | 281.14 | 494.05 | 486.5 | 491.27 | 4.5239 | 4.3599 | 5.3261 | 2.8005 | 1.431 | 1.429 | 1.425 | 1.497 | 1.467 | 1.415 | Over-range | 60 | 1063 | 1006 | 1464 | 3533 | - - - | - - - | - - - | - - - | 1063 | 1006 | 1464 | 3533 | 713 | 678 | 116 | 1507 | - - - | - - - | - - - | - - - | 713 | 678 | 116 | 1507 | 1291 | 1226 | 1497 | 4015 | # # # | # # # | # # # | # # # | 0.824 | 0.821 | 0.978 | 0.88 | # # # | # # # | # # # | - - - | 0.831 | 0.827 | 0.995 | 0.89 | - - - | 0.427 | 1.71 | 1.59 | 1.53 | 1.55 | 1.53 | 1.56 | 12 | 12.36 | 19.02 | 0 | - - - | - - - | - - - | - - - | 1291 | 1226 | 1497 | 4015 | Over-range | 732 | 695 | 314 | 1905 | 165 | 153 | 284 | 1164 | 1065 | 1007 | 1461 | 3533 | 1065 | 1007 | 1461 | 3533 | - - - | - - - | - - - | - - -
5/6/2026 | 1:15:00 AM | 285.62 | 282.62 | 281.14 | 493.66 | 486.39 | 491.12 | 4.7402 | 4.7975 | 5.439 | 2.7942 | 1.431 | 1.43 | 1.426 | 1.502 | 1.471 | 1.388 | Over-range | 59.98 | 1095 | 1131 | 1494 | 3721 | - - - | - - - | - - - | - - - | 1095 | 1131 | 1494 | 3721 | 766 | 676 | 62 | 1504 | - - - | - - - | - - - | - - - | 766 | 676 | 62 | 1504 | 1348 | 1336 | 1528 | 4211 | # # # | # # # | # # # | # # # | 0.813 | 0.847 | 0.978 | 0.884 | # # # | # # # | # # # | - - - | 0.82 | 0.853 | 0.996 | 0.894 | - - - | 0.404 | 1.7 | 1.62 | 1.51 | 1.56 | 1.53 | 1.56 | 11.5 | 11.79 | 18.92 | 0 | - - - | - - - | - - - | - - - | 1348 | 1336 | 1528 | 4211 | Over-range | 784 | 694 | 317 | 1970 | 166 | 158 | 287 | 1264 | 1098 | 1131 | 1493 | 3721 | 1098 | 1131 | 1493 | 3721 | - - - | - - - | - - - | - - -
5/6/2026 | 1:30:00 AM | 285.67 | 282.58 | 281.14 | 493.69 | 486.31 | 491.18 | 5.0707 | 5.4055 | 5.6077 | 2.7872 | 1.43 | 1.429 | 1.425 | 1.507 | 1.455 | 1.336 | Over-range | 60.01 | 1152 | 1346 | 1546 | 4043 | - - - | - - - | - - - | - - - | 1152 | 1346 | 1546 | 4043 | 855 | 672 | -33 | 1492 | - - - | - - - | - - - | - - - | 855 | 672 | -33 | 1492 | 1445 | 1516 | 1576 | 4537 | # # # | # # # | # # # | # # # | 0.797 | 0.888 | 0.981 | 0.891 | # # # | # # # | # # # | - - - | 0.803 | 0.892 | 0.998 | 0.9 | - - - | 0.369 | 1.72 | 1.6 | 1.51 | 1.55 | 1.53 | 1.55 | 10.57 | 10.43 | 18.56 | 0 | - - - | - - - | - - - | - - - | 1445 | 1516 | 1576 | 4537 | Over-range | 872 | 690 | 307 | 2058 | 173 | 157 | 290 | 1411 | 1151 | 1345 | 1547 | 4043 | 1151 | 1345 | 1547 | 4043 | - - - | - - - | - - - | - - -
5/6/2026 | 1:45:00 AM | 285.94 | 282.75 | 281.35 | 494.03 | 486.65 | 491.61 | 5.3093 | 5.749 | 5.74 | 2.7918 | 1.43 | 1.429 | 1.425 | 1.507 | 1.453 | 1.313 | Over-range | 60.01 | 1197 | 1466 | 1584 | 4247 | - - - | - - - | - - - | - - - | 1197 | 1466 | 1584 | 4247 | 913 | 676 | -70 | 1518 | - - - | - - - | - - - | - - - | 913 | 676 | -70 | 1518 | 1516 | 1623 | 1615 | 4753 | # # # | # # # | # # # | # # # | 0.79 | 0.903 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.787 | 0.9 | 0.986 | 0.892 | - - - | 0.357 | 1.73 | 1.63 | 1.55 | 1.57 | 1.55 | 1.58 | 10.15 | 9.76 | 18.42 | 0 | - - - | - - - | - - - | - - - | 1516 | 1623 | 1615 | 4753 | Over-range | 929 | 695 | 311 | 2134 | 172 | 164 | 294 | 1495 | 1213 | 1474 | 1599 | 4287 | 1213 | 1474 | 1599 | 4287 | - - - | - - - | - - - | - - -
5/6/2026 | 2:00:00 AM | 285.96 | 282.81 | 281.37 | 494.17 | 486.67 | 491.64 | 5.0507 | 5.3429 | 5.5918 | 2.7941 | 1.43 | 1.43 | 1.426 | 1.506 | 1.441 | 1.339 | Over-range | 60.01 | 1150 | 1335 | 1544 | 4029 | - - - | - - - | - - - | - - - | 1150 | 1335 | 1544 | 4029 | 855 | 674 | -26 | 1501 | - - - | - - - | - - - | - - - | 855 | 674 | -26 | 1501 | 1443 | 1506 | 1573 | 4522 | # # # | # # # | # # # | # # # | 0.797 | 0.887 | 0.982 | 0.891 | # # # | # # # | # # # | - - - | 0.803 | 0.891 | 0.999 | 0.9 | - - - | 0.373 | 1.75 | 1.63 | 1.57 | 1.58 | 1.57 | 1.6 | 10.66 | 10.44 | 18.59 | 0 | - - - | - - - | - - - | - - - | 1443 | 1506 | 1573 | 4522 | Over-range | 871 | 693 | 298 | 2051 | 170 | 161 | 291 | 1395 | 1152 | 1332 | 1546 | 4030 | 1152 | 1332 | 1546 | 4030 | - - - | - - - | - - - | - - -
5/6/2026 | 2:15:00 AM | 285.98 | 282.85 | 281.35 | 494.24 | 486.66 | 491.63 | 5.5865 | 6.3757 | 5.8951 | 2.7868 | 1.431 | 1.43 | 1.427 | 1.51 | 1.468 | 1.281 | Over-range | 60 | 1236 | 1665 | 1623 | 4524 | - - - | - - - | - - - | - - - | 1236 | 1665 | 1623 | 4524 | 997 | 671 | -170 | 1497 | - - - | - - - | - - - | - - - | 997 | 671 | -170 | 1497 | 1597 | 1803 | 1659 | 5059 | # # # | # # # | # # # | # # # | 0.774 | 0.924 | 0.979 | 0.894 | # # # | # # # | # # # | - - - | 0.779 | 0.927 | 0.994 | 0.902 | - - - | 0.331 | 1.78 | 1.69 | 1.6 | 1.62 | 1.62 | 1.64 | 9.61 | 9.01 | 17.9 | 0 | - - - | - - - | - - - | - - - | 1597 | 1803 | 1659 | 5059 | Over-range | 1012 | 691 | 340 | 2264 | 175 | 166 | 294 | 1699 | 1238 | 1662 | 1624 | 4525 | 1238 | 1662 | 1624 | 4525 | - - - | - - - | - - - | - - -
5/6/2026 | 2:30:00 AM | 286.09 | 282.89 | 281.46 | 494.28 | 486.84 | 491.86 | 5.5107 | 6.2259 | 5.8541 | 2.788 | 1.431 | 1.43 | 1.427 | 1.509 | 1.465 | 1.284 | Over-range | 60 | 1224 | 1619 | 1614 | 4458 | - - - | - - - | - - - | - - - | 1224 | 1619 | 1614 | 4458 | 978 | 672 | -149 | 1500 | - - - | - - - | - - - | - - - | 978 | 672 | -149 | 1500 | 1577 | 1761 | 1648 | 4985 | # # # | # # # | # # # | # # # | 0.777 | 0.919 | 0.98 | 0.894 | # # # | # # # | # # # | - - - | 0.782 | 0.923 | 0.996 | 0.902 | - - - | 0.336 | 1.76 | 1.68 | 1.61 | 1.61 | 1.61 | 1.63 | 9.79 | 9.21 | 18.08 | 0 | - - - | - - - | - - - | - - - | 1577 | 1761 | 1648 | 4985 | Over-range | 993 | 693 | 331 | 2232 | 175 | 166 | 295 | 1653 | 1227 | 1617 | 1615 | 4458 | 1227 | 1617 | 1615 | 4458 | - - - | - - - | - - - | - - -
5/6/2026 | 2:45:00 AM | 286.14 | 282.93 | 281.47 | 494.41 | 486.87 | 491.88 | 5.3656 | 5.8223 | 5.7396 | 2.7888 | 1.431 | 1.43 | 1.427 | 1.504 | 1.451 | 1.32 | Over-range | 60.01 | 1206 | 1490 | 1585 | 4281 | - - - | - - - | - - - | - - - | 1206 | 1490 | 1585 | 4281 | 928 | 673 | -77 | 1523 | - - - | - - - | - - - | - - - | 928 | 673 | -77 | 1523 | 1532 | 1644 | 1615 | 4791 | # # # | # # # | # # # | # # # | 0.787 | 0.907 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.785 | 0.895 | 0.976 | 0.887 | - - - | 0.356 | 1.81 | 1.7 | 1.65 | 1.64 | 1.66 | 1.67 | 10.32 | 9.86 | 18.39 | 0 | - - - | - - - | - - - | - - - | 1532 | 1644 | 1615 | 4791 | Over-range | 944 | 693 | 312 | 2151 | 173 | 163 | 294 | 1515 | 1219 | 1510 | 1614 | 4343 | 1219 | 1510 | 1614 | 4343 | - - - | - - - | - - - | - - -
5/6/2026 | 3:00:00 AM | 286.18 | 282.92 | 281.53 | 494.44 | 486.88 | 492.02 | 5.3999 | 6.004 | 5.7827 | 2.7884 | 1.431 | 1.431 | 1.427 | 1.507 | 1.458 | 1.307 | Over-range | 60.01 | 1207 | 1551 | 1596 | 4355 | - - - | - - - | - - - | - - - | 1207 | 1551 | 1596 | 4355 | 949 | 672 | -119 | 1501 | - - - | - - - | - - - | - - - | 949 | 672 | -119 | 1501 | 1545 | 1698 | 1628 | 4872 | # # # | # # # | # # # | # # # | 0.781 | 0.913 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.787 | 0.917 | 0.997 | 0.902 | - - - | 0.345 | 1.81 | 1.74 | 1.67 | 1.64 | 1.68 | 1.69 | 10.09 | 9.53 | 18.31 | 0 | - - - | - - - | - - - | - - - | 1545 | 1698 | 1628 | 4872 | Over-range | 965 | 692 | 319 | 2184 | 171 | 165 | 295 | 1587 | 1210 | 1551 | 1593 | 4354 | 1210 | 1551 | 1593 | 4354 | - - - | - - - | - - - | - - -
5/6/2026 | 3:15:00 AM | 285.82 | 282.59 | 281.16 | 493.82 | 486.3 | 491.36 | 5.3102 | 5.8321 | 5.7337 | 2.7899 | 1.431 | 1.43 | 1.428 | 1.506 | 1.454 | 1.324 | Over-range | 60 | 1193 | 1497 | 1582 | 4271 | - - - | - - - | - - - | - - - | 1193 | 1497 | 1582 | 4271 | 922 | 669 | -99 | 1491 | - - - | - - - | - - - | - - - | 922 | 669 | -99 | 1491 | 1518 | 1648 | 1612 | 4777 | # # # | # # # | # # # | # # # | 0.786 | 0.909 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.791 | 0.913 | 0.998 | 0.903 | - - - | 0.349 | 1.81 | 1.72 | 1.66 | 1.65 | 1.68 | 1.69 | 10.25 | 9.75 | 18.45 | 0 | - - - | - - - | - - - | - - - | 1518 | 1648 | 1612 | 4777 | Over-range | 938 | 688 | 312 | 2140 | 174 | 161 | 295 | 1534 | 1193 | 1498 | 1579 | 4270 | 1193 | 1498 | 1579 | 4270 | - - - | - - - | - - - | - - -
5/6/2026 | 3:30:00 AM | 286.15 | 282.95 | 281.52 | 494.39 | 486.96 | 491.94 | 5.2765 | 5.7595 | 5.719 | 2.7969 | 1.431 | 1.431 | 1.428 | 1.503 | 1.451 | 1.331 | Over-range | 60.01 | 1187 | 1474 | 1580 | 4242 | - - - | - - - | - - - | - - - | 1187 | 1474 | 1580 | 4242 | 917 | 673 | -85 | 1504 | - - - | - - - | - - - | - - - | 917 | 673 | -85 | 1504 | 1510 | 1629 | 1610 | 4749 | # # # | # # # | # # # | # # # | 0.787 | 0.905 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.792 | 0.91 | 0.999 | 0.902 | - - - | 0.355 | 1.82 | 1.76 | 1.72 | 1.67 | 1.71 | 1.72 | 10.39 | 9.94 | 18.61 | 0 | - - - | - - - | - - - | - - - | 1510 | 1629 | 1610 | 4749 | Over-range | 933 | 694 | 310 | 2136 | 171 | 168 | 298 | 1517 | 1191 | 1472 | 1579 | 4242 | 1191 | 1472 | 1579 | 4242 | - - - | - - - | - - - | - - -
5/6/2026 | 3:45:00 AM | 286.28 | 283.09 | 281.72 | 494.61 | 487.24 | 492.27 | 5.3226 | 5.8478 | 5.7415 | 2.7934 | 1.431 | 1.431 | 1.429 | 1.503 | 1.455 | 1.335 | Over-range | 60 | 1195 | 1502 | 1587 | 4284 | - - - | - - - | - - - | - - - | 1195 | 1502 | 1587 | 4284 | 929 | 675 | -96 | 1508 | - - - | - - - | - - - | - - - | 929 | 675 | -96 | 1508 | 1524 | 1655 | 1617 | 4797 | # # # | # # # | # # # | # # # | 0.784 | 0.908 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.789 | 0.912 | 0.998 | 0.902 | - - - | 0.352 | 1.84 | 1.77 | 1.72 | 1.68 | 1.72 | 1.73 | 10.34 | 9.9 | 18.59 | 0 | - - - | - - - | - - - | - - - | 1524 | 1655 | 1617 | 4797 | Over-range | 946 | 695 | 314 | 2159 | 176 | 166 | 299 | 1545 | 1196 | 1501 | 1586 | 4283 | 1196 | 1501 | 1586 | 4283 | - - - | - - - | - - - | - - -
5/6/2026 | 4:00:00 AM | 286.27 | 283.13 | 281.7 | 494.65 | 487.27 | 492.22 | 5.363 | 5.9298 | 5.7669 | 2.7912 | 1.431 | 1.43 | 1.429 | 1.503 | 1.454 | 1.336 | Over-range | 60.01 | 1201 | 1528 | 1593 | 4322 | - - - | - - - | - - - | - - - | 1201 | 1528 | 1593 | 4322 | 939 | 677 | -107 | 1507 | - - - | - - - | - - - | - - - | 939 | 677 | -107 | 1507 | 1535 | 1679 | 1625 | 4838 | # # # | # # # | # # # | # # # | 0.782 | 0.91 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.787 | 0.914 | 0.998 | 0.902 | - - - | 0.349 | 1.85 | 1.77 | 1.72 | 1.68 | 1.73 | 1.74 | 10.26 | 9.79 | 18.52 | 0 | - - - | - - - | - - - | - - - | 1535 | 1679 | 1625 | 4838 | Over-range | 956 | 696 | 318 | 2175 | 181 | 162 | 299 | 1568 | 1200 | 1528 | 1593 | 4321 | 1200 | 1528 | 1593 | 4321 | - - - | - - - | - - - | - - -
5/6/2026 | 4:15:00 AM | 286.05 | 282.95 | 281.54 | 494.24 | 487.07 | 491.86 | 5.2117 | 5.5596 | 5.663 | 2.7944 | 1.431 | 1.432 | 1.43 | 1.496 | 1.482 | 1.369 | Over-range | 60 | 1176 | 1375 | 1558 | 4109 | - - - | - - - | - - - | - - - | 1176 | 1375 | 1558 | 4109 | 880 | 675 | -24 | 1530 | - - - | - - - | - - - | - - - | 880 | 675 | -24 | 1530 | 1481 | 1550 | 1593 | 4624 | # # # | # # # | # # # | # # # | 0.794 | 0.887 | 0.978 | 0.889 | # # # | # # # | # # # | - - - | 0.791 | 0.884 | 0.983 | 0.888 | - - - | 0.372 | 1.91 | 1.83 | 1.82 | 1.73 | 1.8 | 1.82 | 10.92 | 10.83 | 18.65 | 0 | - - - | - - - | - - - | - - - | 1481 | 1550 | 1593 | 4624 | Over-range | 898 | 694 | 331 | 2117 | 174 | 161 | 295 | 1451 | 1192 | 1386 | 1569 | 4148 | 1192 | 1386 | 1569 | 4148 | - - - | - - - | - - - | - - -
5/6/2026 | 4:30:00 AM | 285.84 | 282.74 | 281.3 | 493.95 | 486.61 | 491.47 | 4.6823 | 4.6393 | 5.4029 | 2.7931 | 1.431 | 1.431 | 1.43 | 1.496 | 1.443 | 1.395 | Over-range | 60.01 | 1090 | 1106 | 1488 | 3683 | - - - | - - - | - - - | - - - | 1090 | 1106 | 1488 | 3683 | 754 | 676 | 76 | 1506 | - - - | - - - | - - - | - - - | 754 | 676 | 76 | 1506 | 1337 | 1307 | 1520 | 4164 | # # # | # # # | # # # | # # # | 0.815 | 0.846 | 0.979 | 0.885 | # # # | # # # | # # # | - - - | 0.822 | 0.852 | 0.998 | 0.895 | - - - | 0.409 | 1.88 | 1.83 | 1.81 | 1.72 | 1.79 | 1.81 | 11.78 | 12.15 | 19.26 | 0 | - - - | - - - | - - - | - - - | 1337 | 1307 | 1520 | 4164 | Over-range | 775 | 694 | 308 | 1942 | 176 | 158 | 293 | 1224 | 1089 | 1105 | 1489 | 3683 | 1089 | 1105 | 1489 | 3683 | - - - | - - - | - - - | - - -
5/6/2026 | 4:45:00 AM | 285.91 | 282.82 | 281.44 | 494.05 | 486.81 | 491.67 | 5.0352 | 5.2956 | 5.5796 | 2.7896 | 1.431 | 1.431 | 1.431 | 1.497 | 1.439 | 1.35 | Over-range | 60.01 | 1148 | 1326 | 1542 | 4016 | - - - | - - - | - - - | - - - | 1148 | 1326 | 1542 | 4016 | 850 | 673 | -20 | 1502 | - - - | - - - | - - - | - - - | 850 | 673 | -20 | 1502 | 1439 | 1496 | 1570 | 4506 | # # # | # # # | # # # | # # # | 0.798 | 0.886 | 0.982 | 0.891 | # # # | # # # | # # # | - - - | 0.804 | 0.892 | 1 | 0.901 | - - - | 0.374 | 1.91 | 1.82 | 1.83 | 1.74 | 1.81 | 1.83 | 10.92 | 10.72 | 18.83 | 0 | - - - | - - - | - - - | - - - | 1439 | 1496 | 1570 | 4506 | Over-range | 868 | 692 | 298 | 2043 | 178 | 158 | 295 | 1384 | 1147 | 1327 | 1542 | 4015 | 1147 | 1327 | 1542 | 4015 | - - - | - - - | - - - | - - -
5/6/2026 | 5:00:00 AM | 285.72 | 282.66 | 281.26 | 493.7 | 486.58 | 491.34 | 5.5419 | 6.284 | 5.8696 | 2.7863 | 1.432 | 1.432 | 1.431 | 1.499 | 1.467 | 1.356 | Over-range | 60.01 | 1228 | 1633 | 1615 | 4476 | - - - | - - - | - - - | - - - | 1228 | 1633 | 1615 | 4476 | 981 | 666 | -155 | 1492 | - - - | - - - | - - - | - - - | 981 | 666 | -155 | 1492 | 1582 | 1772 | 1650 | 5005 | # # # | # # # | # # # | # # # | 0.776 | 0.921 | 0.979 | 0.894 | # # # | # # # | # # # | - - - | 0.781 | 0.925 | 0.995 | 0.902 | - - - | 0.333 | 1.94 | 1.85 | 1.86 | 1.76 | 1.84 | 1.86 | 9.9 | 9.32 | 18.13 | 0 | - - - | - - - | - - - | - - - | 1582 | 1772 | 1650 | 5005 | Over-range | 997 | 687 | 340 | 2239 | 176 | 165 | 298 | 1667 | 1229 | 1634 | 1612 | 4475 | 1229 | 1634 | 1612 | 4475 | - - - | - - - | - - - | - - -
5/6/2026 | 5:15:00 AM | 285.69 | 282.63 | 281.17 | 493.7 | 486.42 | 491.22 | 5.6813 | 6.5542 | 5.9483 | 2.7802 | 1.432 | 1.432 | 1.432 | 1.498 | 1.472 | 1.366 | Over-range | 60.01 | 1251 | 1720 | 1634 | 4605 | - - - | - - - | - - - | - - - | 1251 | 1720 | 1634 | 4605 | 1018 | 665 | -193 | 1489 | - - - | - - - | - - - | - - - | 1018 | 665 | -193 | 1489 | 1623 | 1852 | 1672 | 5147 | # # # | # # # | # # # | # # # | 0.771 | 0.929 | 0.977 | 0.895 | # # # | # # # | # # # | - - - | 0.776 | 0.933 | 0.993 | 0.902 | - - - | 0.323 | 1.94 | 1.87 | 1.87 | 1.76 | 1.84 | 1.87 | 9.63 | 8.93 | 17.87 | 0 | - - - | - - - | - - - | - - - | 1623 | 1852 | 1672 | 5147 | Over-range | 1034 | 685 | 356 | 2299 | 180 | 164 | 297 | 1751 | 1251 | 1721 | 1632 | 4604 | 1251 | 1721 | 1632 | 4604 | - - - | - - - | - - - | - - -
5/6/2026 | 5:30:00 AM | 285.39 | 282.29 | 280.96 | 493.11 | 485.93 | 490.83 | 5.4019 | 5.895 | 5.7533 | 2.7766 | 1.432 | 1.433 | 1.432 | 1.494 | 1.458 | 1.35 | Over-range | 60.01 | 1210 | 1511 | 1584 | 4305 | - - - | - - - | - - - | - - - | 1210 | 1511 | 1584 | 4305 | 931 | 663 | -87 | 1506 | - - - | - - - | - - - | - - - | 931 | 663 | -87 | 1506 | 1538 | 1659 | 1616 | 4813 | # # # | # # # | # # # | # # # | 0.787 | 0.911 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.785 | 0.907 | 0.988 | 0.895 | - - - | 0.35 | 1.94 | 1.89 | 1.9 | 1.77 | 1.86 | 1.89 | 10.23 | 9.8 | 18.26 | 0 | - - - | - - - | - - - | - - - | 1538 | 1659 | 1616 | 4813 | Over-range | 948 | 682 | 317 | 2150 | 176 | 160 | 294 | 1529 | 1223 | 1519 | 1596 | 4338 | 1223 | 1519 | 1596 | 4338 | - - - | - - - | - - - | - - -
5/6/2026 | 5:45:00 AM | 285.19 | 282.22 | 280.81 | 492.87 | 485.81 | 490.47 | 4.9277 | 5.0908 | 5.5202 | 2.7853 | 1.433 | 1.433 | 1.433 | 1.491 | 1.432 | 1.357 | Over-range | 60 | 1129 | 1261 | 1522 | 3912 | - - - | - - - | - - - | - - - | 1129 | 1261 | 1522 | 3912 | 818 | 666 | 7 | 1491 | - - - | - - - | - - - | - - - | 818 | 666 | 7 | 1491 | 1405 | 1435 | 1550 | 4390 | # # # | # # # | # # # | # # # | 0.804 | 0.878 | 0.982 | 0.891 | # # # | # # # | # # # | - - - | 0.81 | 0.884 | 1 | 0.901 | - - - | 0.381 | 1.99 | 1.92 | 1.96 | 1.82 | 1.91 | 1.94 | 11.06 | 10.95 | 18.73 | 0 | - - - | - - - | - - - | - - - | 1405 | 1435 | 1550 | 4390 | Over-range | 836 | 685 | 293 | 1992 | 170 | 158 | 291 | 1320 | 1131 | 1262 | 1519 | 3911 | 1131 | 1262 | 1519 | 3911 | - - - | - - - | - - - | - - -
5/6/2026 | 6:00:00 AM | 284.72 | 281.78 | 280.4 | 492.07 | 485.08 | 489.71 | 5.5692 | 6.3466 | 5.8802 | 2.7728 | 1.433 | 1.434 | 1.433 | 1.494 | 1.477 | 1.348 | Over-range | 60.01 | 1231 | 1654 | 1613 | 4498 | - - - | - - - | - - - | - - - | 1231 | 1654 | 1613 | 4498 | 982 | 654 | -169 | 1466 | - - - | - - - | - - - | - - - | 982 | 654 | -169 | 1466 | 1585 | 1786 | 1649 | 5020 | # # # | # # # | # # # | # # # | 0.777 | 0.926 | 0.978 | 0.896 | # # # | # # # | # # # | - - - | 0.782 | 0.93 | 0.994 | 0.904 | - - - | 0.326 | 2.06 | 2.03 | 2.02 | 1.88 | 1.99 | 2.03 | 9.64 | 9.17 | 17.85 | 0 | - - - | - - - | - - - | - - - | 1585 | 1786 | 1649 | 5020 | Over-range | 998 | 673 | 341 | 2228 | 176 | 162 | 293 | 1677 | 1232 | 1654 | 1611 | 4497 | 1232 | 1654 | 1611 | 4497 | - - - | - - - | - - - | - - -
5/6/2026 | 6:15:00 AM | 284.06 | 281.24 | 279.72 | 491.07 | 484.04 | 488.48 | 5.5601 | 6.3392 | 5.872 | 2.762 | 1.434 | 1.436 | 1.435 | 1.488 | 1.483 | 1.339 | Over-range | 59.99 | 1228 | 1651 | 1607 | 4486 | - - - | - - - | - - - | - - - | 1228 | 1651 | 1607 | 4486 | 977 | 647 | -169 | 1454 | - - - | - - - | - - - | - - - | 977 | 647 | -169 | 1454 | 1579 | 1781 | 1642 | 5003 | # # # | # # # | # # # | # # # | 0.778 | 0.927 | 0.979 | 0.897 | # # # | # # # | # # # | - - - | 0.783 | 0.931 | 0.994 | 0.905 | - - - | 0.324 | 2.19 | 2.16 | 2.23 | 2.02 | 2.15 | 2.2 | 9.58 | 9.15 | 17.65 | 0 | - - - | - - - | - - - | - - - | 1579 | 1781 | 1642 | 5003 | Over-range | 993 | 667 | 337 | 2213 | 174 | 163 | 290 | 1667 | 1231 | 1647 | 1609 | 4487 | 1231 | 1647 | 1609 | 4487 | - - - | - - - | - - - | - - -
5/6/2026 | 6:30:00 AM | 284.16 | 281.34 | 279.81 | 491.26 | 484.21 | 488.65 | 4.7053 | 4.7167 | 5.4038 | 2.7723 | 1.435 | 1.438 | 1.436 | 1.484 | 1.481 | 1.382 | Over-range | 59.99 | 1088 | 1115 | 1478 | 3681 | - - - | - - - | - - - | - - - | 1088 | 1115 | 1478 | 3681 | 749 | 655 | 67 | 1471 | - - - | - - - | - - - | - - - | 749 | 655 | 67 | 1471 | 1332 | 1310 | 1511 | 4153 | # # # | # # # | # # # | # # # | 0.816 | 0.851 | 0.978 | 0.886 | # # # | # # # | # # # | - - - | 0.824 | 0.857 | 0.996 | 0.896 | - - - | 0.4 | 2.23 | 2.22 | 2.28 | 2.07 | 2.19 | 2.24 | 11.56 | 12.2 | 18.65 | 0 | - - - | - - - | - - - | - - - | 1332 | 1310 | 1511 | 4153 | Over-range | 768 | 674 | 310 | 1921 | 168 | 158 | 283 | 1229 | 1090 | 1112 | 1479 | 3681 | 1090 | 1112 | 1479 | 3681 | - - - | - - - | - - - | - - -
5/6/2026 | 6:45:00 AM | 284.12 | 281.4 | 279.92 | 491.18 | 484.43 | 488.71 | 4.7761 | 4.7245 | 5.4238 | 2.7758 | 1.435 | 1.437 | 1.435 | 1.484 | 1.483 | 1.391 | Over-range | 60 | 1104 | 1117 | 1483 | 3704 | - - - | - - - | - - - | - - - | 1104 | 1117 | 1483 | 3704 | 752 | 654 | 81 | 1487 | - - - | - - - | - - - | - - - | 752 | 654 | 81 | 1487 | 1348 | 1311 | 1517 | 4177 | # # # | # # # | # # # | # # # | 0.819 | 0.852 | 0.978 | 0.887 | # # # | # # # | # # # | - - - | 0.815 | 0.85 | 0.984 | 0.887 | - - - | 0.402 | 2.2 | 2.17 | 2.19 | 2.01 | 2.11 | 2.18 | 11.48 | 12.2 | 18.73 | 0 | - - - | - - - | - - - | - - - | 1348 | 1311 | 1517 | 4177 | Over-range | 773 | 673 | 318 | 1928 | 174 | 157 | 286 | 1218 | 1118 | 1133 | 1510 | 3762 | 1118 | 1133 | 1510 | 3762 | - - - | - - - | - - - | - - -
5/6/2026 | 7:00:00 AM | 284.09 | 281.38 | 279.81 | 491.24 | 484.21 | 488.61 | 4.7819 | 4.8518 | 5.442 | 2.7695 | 1.435 | 1.438 | 1.434 | 1.485 | 1.448 | 1.373 | Over-range | 60.02 | 1102 | 1171 | 1492 | 3765 | - - - | - - - | - - - | - - - | 1102 | 1171 | 1492 | 3765 | 768 | 652 | 39 | 1460 | - - - | - - - | - - - | - - - | 768 | 652 | 39 | 1460 | 1355 | 1353 | 1522 | 4230 | # # # | # # # | # # # | # # # | 0.814 | 0.866 | 0.98 | 0.89 | # # # | # # # | # # # | - - - | 0.82 | 0.871 | 0.998 | 0.9 | - - - | 0.388 | 2.2 | 2.13 | 2.16 | 1.98 | 2.07 | 2.15 | 11.28 | 11.58 | 18.62 | 0 | - - - | - - - | - - - | - - - | 1355 | 1353 | 1522 | 4230 | Over-range | 787 | 671 | 301 | 1927 | 172 | 156 | 284 | 1252 | 1103 | 1168 | 1494 | 3765 | 1103 | 1168 | 1494 | 3765 | - - - | - - - | - - - | - - -
5/6/2026 | 7:15:00 AM | 284.06 | 281.37 | 279.81 | 491.16 | 484.23 | 488.59 | 4.503 | 4.3178 | 5.3064 | 2.7727 | 1.434 | 1.438 | 1.434 | 1.481 | 1.472 | 1.397 | Over-range | 59.99 | 1057 | 999 | 1451 | 3507 | - - - | - - - | - - - | - - - | 1057 | 999 | 1451 | 3507 | 696 | 657 | 117 | 1470 | - - - | - - - | - - - | - - - | 696 | 657 | 117 | 1470 | 1277 | 1209 | 1484 | 3971 | # # # | # # # | # # # | # # # | 0.827 | 0.827 | 0.978 | 0.883 | # # # | # # # | # # # | - - - | 0.835 | 0.833 | 0.996 | 0.894 | - - - | 0.419 | 2.19 | 2.15 | 2.16 | 1.99 | 2.08 | 2.16 | 12.04 | 12.73 | 18.84 | 0 | - - - | - - - | - - - | - - - | 1277 | 1209 | 1484 | 3971 | Over-range | 717 | 675 | 311 | 1860 | 170 | 155 | 281 | 1138 | 1058 | 997 | 1453 | 3508 | 1058 | 997 | 1453 | 3508 | - - - | - - - | - - - | - - -
5/6/2026 | 7:30:00 AM | 283.7 | 281.04 | 279.46 | 490.5 | 483.73 | 487.97 | 5.3774 | 5.9835 | 5.7657 | 2.764 | 1.434 | 1.437 | 1.434 | 1.485 | 1.483 | 1.336 | Over-range | 60.01 | 1199 | 1544 | 1580 | 4323 | - - - | - - - | - - - | - - - | 1199 | 1544 | 1580 | 4323 | 926 | 643 | -126 | 1442 | - - - | - - - | - - - | - - - | 926 | 643 | -126 | 1442 | 1525 | 1680 | 1611 | 4817 | # # # | # # # | # # # | # # # | 0.786 | 0.919 | 0.981 | 0.898 | # # # | # # # | # # # | - - - | 0.792 | 0.923 | 0.997 | 0.906 | - - - | 0.334 | 2.19 | 2.15 | 2.2 | 2 | 2.1 | 2.17 | 9.89 | 9.51 | 17.83 | 0 | - - - | - - - | - - - | - - - | 1525 | 1680 | 1611 | 4817 | Over-range | 942 | 663 | 315 | 2124 | 175 | 159 | 287 | 1558 | 1201 | 1541 | 1582 | 4323 | 1201 | 1541 | 1582 | 4323 | - - - | - - - | - - - | - - -
5/6/2026 | 7:45:00 AM | 283.26 | 280.5 | 279.06 | 489.65 | 482.83 | 487.32 | 5.0447 | 5.3421 | 5.5529 | 2.7533 | 1.434 | 1.437 | 1.433 | 1.482 | 1.462 | 1.341 | Over-range | 60 | 1145 | 1338 | 1522 | 4005 | - - - | - - - | - - - | - - - | 1145 | 1338 | 1522 | 4005 | 835 | 640 | -40 | 1433 | - - - | - - - | - - - | - - - | 835 | 640 | -40 | 1433 | 1427 | 1493 | 1549 | 4469 | # # # | # # # | # # # | # # # | 0.802 | 0.897 | 0.982 | 0.896 | # # # | # # # | # # # | - - - | 0.808 | 0.901 | 0.999 | 0.905 | - - - | 0.358 | 2.16 | 2.16 | 2.17 | 1.98 | 2.09 | 2.15 | 10.51 | 10.28 | 18.17 | 0 | - - - | - - - | - - - | - - - | 1427 | 1493 | 1549 | 4469 | Over-range | 851 | 658 | 291 | 1983 | 167 | 153 | 281 | 1367 | 1147 | 1338 | 1520 | 4005 | 1147 | 1338 | 1520 | 4005 | - - - | - - - | - - - | - - -
5/6/2026 | 8:00:00 AM | 282.59 | 279.88 | 278.46 | 488.45 | 481.81 | 486.25 | 5.1284 | 5.5193 | 5.6203 | 2.7538 | 1.434 | 1.437 | 1.433 | 1.485 | 1.471 | 1.34 | Over-range | 60 | 1158 | 1393 | 1536 | 4088 | - - - | - - - | - - - | - - - | 1158 | 1393 | 1536 | 4088 | 852 | 631 | -69 | 1412 | - - - | - - - | - - - | - - - | 852 | 631 | -69 | 1412 | 1448 | 1539 | 1565 | 4551 | # # # | # # # | # # # | # # # | 0.8 | 0.906 | 0.982 | 0.898 | # # # | # # # | # # # | - - - | 0.806 | 0.91 | 0.998 | 0.907 | - - - | 0.345 | 2.1 | 2.08 | 2.11 | 1.93 | 2.02 | 2.08 | 10.24 | 9.99 | 17.96 | 0 | - - - | - - - | - - - | - - - | 1448 | 1539 | 1565 | 4551 | Over-range | 868 | 649 | 296 | 2000 | 166 | 154 | 281 | 1412 | 1161 | 1392 | 1535 | 4087 | 1161 | 1392 | 1535 | 4087 | - - - | - - - | - - - | - - -
5/6/2026 | 8:15:00 AM | 282.19 | 279.43 | 278.08 | 487.66 | 481.11 | 485.59 | 5.7568 | 6.6381 | 5.9607 | 2.7095 | 1.435 | 1.438 | 1.434 | 1.486 | 1.499 | 1.37 | Over-range | 60.01 | 1266 | 1743 | 1619 | 4628 | - - - | - - - | - - - | - - - | 1266 | 1743 | 1619 | 4628 | 998 | 616 | -210 | 1403 | - - - | - - - | - - - | - - - | 998 | 616 | -210 | 1403 | 1623 | 1854 | 1657 | 5134 | # # # | # # # | # # # | # # # | 0.78 | 0.94 | 0.977 | 0.901 | # # # | # # # | # # # | - - - | 0.776 | 0.935 | 0.98 | 0.899 | - - - | 0.303 | 2.15 | 2.12 | 2.14 | 1.95 | 2.07 | 2.13 | 10.24 | 9.33 | 17.64 | 0 | - - - | - - - | - - - | - - - | 1623 | 1854 | 1657 | 5134 | Over-range | 1015 | 634 | 353 | 2223 | 154 | 130 | 274 | 1720 | 1278 | 1765 | 1646 | 4689 | 1278 | 1765 | 1646 | 4689 | - - - | - - - | - - - | - - -
5/6/2026 | 8:30:00 AM | 282.01 | 279.2 | 277.89 | 487.34 | 480.69 | 485.32 | 5.6991 | 6.6503 | 5.942 | 2.7342 | 1.435 | 1.438 | 1.435 | 1.486 | 1.496 | 1.378 | Over-range | 60.01 | 1249 | 1743 | 1611 | 4603 | - - - | - - - | - - - | - - - | 1249 | 1743 | 1611 | 4603 | 997 | 616 | -229 | 1383 | - - - | - - - | - - - | - - - | 997 | 616 | -229 | 1383 | 1607 | 1856 | 1651 | 5114 | # # # | # # # | # # # | # # # | 0.777 | 0.939 | 0.975 | 0.9 | # # # | # # # | # # # | - - - | 0.782 | 0.943 | 0.99 | 0.907 | - - - | 0.301 | 2.16 | 2.13 | 2.15 | 1.96 | 2.08 | 2.15 | 9.14 | 8.33 | 17.08 | 0 | - - - | - - - | - - - | - - - | 1607 | 1856 | 1651 | 5114 | Over-range | 1011 | 636 | 364 | 2229 | 166 | 158 | 281 | 1747 | 1253 | 1740 | 1610 | 4603 | 1253 | 1740 | 1610 | 4603 | - - - | - - - | - - - | - - -
5/6/2026 | 8:45:00 AM | 282.06 | 279.25 | 277.85 | 487.49 | 480.64 | 485.32 | 5.4784 | 6.2073 | 5.8189 | 2.7436 | 1.434 | 1.438 | 1.435 | 1.483 | 1.488 | 1.357 | Over-range | 60.01 | 1215 | 1612 | 1583 | 4410 | - - - | - - - | - - - | - - - | 1215 | 1612 | 1583 | 4410 | 941 | 618 | -171 | 1387 | - - - | - - - | - - - | - - - | 941 | 618 | -171 | 1387 | 1545 | 1733 | 1617 | 4895 | # # # | # # # | # # # | # # # | 0.786 | 0.93 | 0.979 | 0.901 | # # # | # # # | # # # | - - - | 0.792 | 0.933 | 0.994 | 0.908 | - - - | 0.315 | 2.13 | 2.11 | 2.13 | 1.95 | 2.06 | 2.12 | 9.48 | 8.75 | 17.26 | 0 | - - - | - - - | - - - | - - - | 1545 | 1733 | 1617 | 4895 | Over-range | 955 | 638 | 327 | 2125 | 165 | 156 | 279 | 1610 | 1219 | 1608 | 1582 | 4410 | 1219 | 1608 | 1582 | 4410 | - - - | - - - | - - - | - - -
5/6/2026 | 9:00:00 AM | 281.7 | 278.79 | 277.44 | 486.74 | 479.91 | 484.68 | 5.4029 | 6.0641 | 5.754 | 2.7318 | 1.434 | 1.438 | 1.435 | 1.482 | 1.486 | 1.35 | Over-range | 60.01 | 1202 | 1567 | 1564 | 4334 | - - - | - - - | - - - | - - - | 1202 | 1567 | 1564 | 4334 | 918 | 614 | -156 | 1375 | - - - | - - - | - - - | - - - | 918 | 614 | -156 | 1375 | 1522 | 1690 | 1596 | 4808 | # # # | # # # | # # # | # # # | 0.79 | 0.927 | 0.98 | 0.901 | # # # | # # # | # # # | - - - | 0.795 | 0.931 | 0.995 | 0.909 | - - - | 0.317 | 2.15 | 2.14 | 2.19 | 1.98 | 2.11 | 2.15 | 9.59 | 8.88 | 17.34 | 0 | - - - | - - - | - - - | - - - | 1522 | 1690 | 1596 | 4808 | Over-range | 933 | 632 | 319 | 2083 | 168 | 152 | 277 | 1564 | 1205 | 1564 | 1565 | 4334 | 1205 | 1564 | 1565 | 4334 | - - - | - - - | - - - | - - -
5/6/2026 | 9:15:00 AM | 280.97 | 277.96 | 276.69 | 485.38 | 478.49 | 483.44 | 5.4177 | 5.3253 | 5.772 | 3.7815 | 1.434 | 1.438 | 1.436 | 1.481 | 1.459 | 1.351 | Over-range | 60.01 | 1204 | 1283 | 1565 | 4053 | - - - | - - - | - - - | - - - | 1204 | 1283 | 1565 | 4053 | 917 | 689 | -164 | 1440 | - - - | - - - | - - - | - - - | 917 | 689 | -164 | 1440 | 1522 | 1473 | 1597 | 4592 | # # # | # # # | # # # | # # # | 0.791 | 0.871 | 0.98 | 0.882 | # # # | # # # | # # # | - - - | 0.796 | 0.877 | 0.994 | 0.89 | - - - | 0.355 | 2.17 | 2.17 | 2.21 | 1.99 | 2.14 | 2.18 | 9.48 | 11.61 | 17.1 | 0 | - - - | - - - | - - - | - - - | 1522 | 1473 | 1597 | 4592 | Over-range | 931 | 710 | 319 | 2156 | 162 | 172 | 273 | 1604 | 1208 | 1281 | 1563 | 4053 | 1208 | 1281 | 1563 | 4053 | - - - | - - - | - - - | - - -
5/6/2026 | 9:30:00 AM | 280.67 | 277.54 | 276.41 | 484.76 | 477.81 | 483.02 | 5.3856 | 4.795 | 5.7021 | 4.135 | 1.435 | 1.439 | 1.436 | 1.478 | 1.435 | 1.35 | Over-range | 60 | 1205 | 1102 | 1545 | 3851 | - - - | - - - | - - - | - - - | 1205 | 1102 | 1545 | 3851 | 894 | 722 | -126 | 1488 | - - - | - - - | - - - | - - - | 894 | 722 | -126 | 1488 | 1510 | 1329 | 1576 | 4415 | # # # | # # # | # # # | # # # | 0.798 | 0.829 | 0.98 | 0.872 | # # # | # # # | # # # | - - - | 0.796 | 0.829 | 0.983 | 0.872 | - - - | 0.386 | 2.17 | 2.19 | 2.23 | 2 | 2.16 | 2.2 | 9.54 | 13.06 | 17.26 | 0 | - - - | - - - | - - - | - - - | 1510 | 1329 | 1576 | 4415 | Over-range | 909 | 742 | 311 | 2158 | 167 | 173 | 272 | 1558 | 1216 | 1108 | 1558 | 3883 | 1216 | 1108 | 1558 | 3883 | - - - | - - - | - - - | - - -
5/6/2026 | 9:45:00 AM | 279.87 | 276.72 | 275.51 | 483.37 | 476.34 | 481.52 | 4.8038 | 4.1298 | 5.1808 | 3.9433 | 1.434 | 1.438 | 1.436 | 1.492 | 1.427 | 1.354 | Over-range | 60.01 | 1078 | 876 | 1389 | 3343 | - - - | - - - | - - - | - - - | 1078 | 876 | 1389 | 3343 | 777 | 715 | -60 | 1431 | - - - | - - - | - - - | - - - | 777 | 715 | -60 | 1431 | 1341 | 1143 | 1416 | 3899 | # # # | # # # | # # # | # # # | 0.804 | 0.767 | 0.981 | 0.858 | # # # | # # # | # # # | - - - | 0.81 | 0.776 | 0.999 | 0.868 | - - - | 0.428 | 2.09 | 2.1 | 2.16 | 1.92 | 2.08 | 2.11 | 10.4 | 14.39 | 18.3 | 0 | - - - | - - - | - - - | - - - | 1341 | 1143 | 1416 | 3899 | Over-range | 794 | 733 | 269 | 2002 | 160 | 165 | 261 | 1399 | 1078 | 878 | 1387 | 3342 | 1078 | 878 | 1387 | 3342 | - - - | - - - | - - - | - - -
5/6/2026 | 10:00:00 AM | 279.68 | 276.65 | 275.21 | 483.08 | 476.09 | 481.09 | 5.5798 | 5.2475 | 5.887 | 4.1876 | 1.437 | 1.441 | 1.438 | 1.534 | 1.472 | 1.472 | Over-range | 60.02 | 1233 | 1238 | 1575 | 4046 | - - - | - - - | - - - | - - - | 1233 | 1238 | 1575 | 4046 | 935 | 719 | -210 | 1442 | - - - | - - - | - - - | - - - | 935 | 719 | -210 | 1442 | 1559 | 1446 | 1620 | 4625 | # # # | # # # | # # # | # # # | 0.791 | 0.856 | 0.973 | 0.875 | # # # | # # # | # # # | - - - | 0.797 | 0.863 | 0.991 | 0.885 | - - - | 0.356 | 2.01 | 1.98 | 2.03 | 1.82 | 1.93 | 2 | 9.45 | 12.29 | 16.91 | 0 | - - - | - - - | - - - | - - - | 1559 | 1446 | 1620 | 4625 | Over-range | 953 | 744 | 375 | 2239 | 187 | 192 | 306 | 1712 | 1236 | 1235 | 1576 | 4047 | 1236 | 1235 | 1576 | 4047 | - - - | - - - | - - - | - - -
5/6/2026 | 10:15:00 AM | 279.99 | 276.87 | 275.61 | 483.56 | 476.55 | 481.76 | 5.484 | 5.1058 | 5.8117 | 4.1631 | 1.434 | 1.438 | 1.433 | 1.532 | 1.469 | 1.482 | Over-range | 60.02 | 1213 | 1196 | 1559 | 3968 | - - - | - - - | - - - | - - - | 1213 | 1196 | 1559 | 3968 | 922 | 719 | -191 | 1450 | - - - | - - - | - - - | - - - | 922 | 719 | -191 | 1450 | 1535 | 1411 | 1601 | 4546 | # # # | # # # | # # # | # # # | 0.79 | 0.848 | 0.974 | 0.873 | # # # | # # # | # # # | - - - | 0.797 | 0.856 | 0.992 | 0.883 | - - - | 0.365 | 1.97 | 1.96 | 2.03 | 1.79 | 1.93 | 1.97 | 9.55 | 12.6 | 17.33 | 0 | - - - | - - - | - - - | - - - | 1535 | 1411 | 1601 | 4546 | Over-range | 940 | 745 | 365 | 2219 | 184 | 194 | 308 | 1679 | 1216 | 1194 | 1560 | 3970 | 1216 | 1194 | 1560 | 3970 | - - - | - - - | - - - | - - -
5/6/2026 | 10:30:00 AM | 280.97 | 277.94 | 276.73 | 485.3 | 478.5 | 483.55 | 5.2806 | 4.7356 | 5.6884 | 4.1614 | 1.432 | 1.436 | 1.431 | 1.535 | 1.455 | 1.463 | Over-range | 60.01 | 1182 | 1074 | 1538 | 3794 | - - - | - - - | - - - | - - - | 1182 | 1074 | 1538 | 3794 | 878 | 735 | -127 | 1485 | - - - | - - - | - - - | - - - | 878 | 735 | -127 | 1485 | 1484 | 1316 | 1574 | 4374 | # # # | # # # | # # # | # # # | 0.797 | 0.816 | 0.977 | 0.868 | # # # | # # # | # # # | - - - | 0.803 | 0.825 | 0.996 | 0.879 | - - - | 0.391 | 1.94 | 1.92 | 1.95 | 1.75 | 1.87 | 1.91 | 9.87 | 13.56 | 17.81 | 0 | - - - | - - - | - - - | - - - | 1484 | 1316 | 1574 | 4374 | Over-range | 896 | 760 | 336 | 2176 | 181 | 193 | 311 | 1590 | 1184 | 1075 | 1535 | 3794 | 1184 | 1075 | 1535 | 3794 | - - - | - - - | - - - | - - -
5/6/2026 | 10:45:00 AM | 282.14 | 279.1 | 278.01 | 487.24 | 480.69 | 485.67 | 5.3776 | 4.7947 | 5.7245 | 4.1692 | 1.433 | 1.436 | 1.432 | 1.534 | 1.452 | 1.455 | Over-range | 60.01 | 1205 | 1091 | 1554 | 3850 | - - - | - - - | - - - | - - - | 1205 | 1091 | 1554 | 3850 | 900 | 750 | -110 | 1539 | - - - | - - - | - - - | - - - | 900 | 750 | -110 | 1539 | 1516 | 1338 | 1591 | 4445 | # # # | # # # | # # # | # # # | 0.795 | 0.815 | 0.977 | 0.866 | # # # | # # # | # # # | - - - | 0.793 | 0.817 | 0.988 | 0.87 | - - - | 0.4 | 1.95 | 1.92 | 1.92 | 1.76 | 1.84 | 1.91 | 9.79 | 13.67 | 17.89 | 0 | - - - | - - - | - - - | - - - | 1516 | 1338 | 1591 | 4445 | Over-range | 920 | 775 | 341 | 2223 | 189 | 195 | 315 | 1599 | 1214 | 1099 | 1564 | 3878 | 1214 | 1099 | 1564 | 3878 | - - - | - - - | - - - | - - -
5/6/2026 | 11:00:00 AM | 282.07 | 279.11 | 277.95 | 487.25 | 480.59 | 485.55 | 5.3142 | 4.801 | 5.7145 | 4.1636 | 1.433 | 1.435 | 1.432 | 1.537 | 1.452 | 1.443 | Over-range | 60.01 | 1188 | 1093 | 1552 | 3833 | - - - | - - - | - - - | - - - | 1188 | 1093 | 1552 | 3833 | 894 | 750 | -127 | 1516 | - - - | - - - | - - - | - - - | 894 | 750 | -127 | 1516 | 1499 | 1340 | 1588 | 4427 | # # # | # # # | # # # | # # # | 0.793 | 0.816 | 0.977 | 0.866 | # # # | # # # | # # # | - - - | 0.799 | 0.824 | 0.997 | 0.877 | - - - | 0.395 | 1.96 | 1.9 | 1.89 | 1.74 | 1.83 | 1.89 | 9.84 | 13.61 | 17.86 | 0 | - - - | - - - | - - - | - - - | 1499 | 1340 | 1588 | 4427 | Over-range | 914 | 775 | 338 | 2215 | 190 | 197 | 313 | 1616 | 1188 | 1092 | 1554 | 3834 | 1188 | 1092 | 1554 | 3834 | - - - | - - - | - - - | - - -
5/6/2026 | 11:15:00 AM | 282.57 | 279.61 | 278.42 | 488.13 | 481.45 | 486.35 | 5.3024 | 4.7807 | 5.7068 | 4.1656 | 1.433 | 1.435 | 1.432 | 1.536 | 1.452 | 1.44 | Over-range | 60.02 | 1187 | 1084 | 1553 | 3824 | - - - | - - - | - - - | - - - | 1187 | 1084 | 1553 | 3824 | 895 | 756 | -119 | 1530 | - - - | - - - | - - - | - - - | 895 | 756 | -119 | 1530 | 1498 | 1337 | 1589 | 4424 | # # # | # # # | # # # | # # # | 0.792 | 0.811 | 0.977 | 0.865 | # # # | # # # | # # # | - - - | 0.799 | 0.82 | 0.997 | 0.876 | - - - | 0.4 | 1.94 | 1.9 | 1.88 | 1.73 | 1.81 | 1.88 | 9.85 | 13.71 | 17.95 | 0 | - - - | - - - | - - - | - - - | 1498 | 1337 | 1589 | 4424 | Over-range | 914 | 782 | 337 | 2224 | 187 | 198 | 314 | 1613 | 1188 | 1084 | 1553 | 3825 | 1188 | 1084 | 1553 | 3825 | - - - | - - - | - - - | - - -
5/6/2026 | 11:30:00 AM | 282.31 | 279.38 | 278.18 | 487.66 | 481.12 | 485.89 | 5.3043 | 4.7836 | 5.7107 | 4.1671 | 1.433 | 1.435 | 1.432 | 1.537 | 1.451 | 1.44 | Over-range | 60.01 | 1187 | 1086 | 1552 | 3826 | - - - | - - - | - - - | - - - | 1187 | 1086 | 1552 | 3826 | 893 | 754 | -122 | 1524 | - - - | - - - | - - - | - - - | 893 | 754 | -122 | 1524 | 1497 | 1336 | 1589 | 4422 | # # # | # # # | # # # | # # # | 0.793 | 0.813 | 0.977 | 0.865 | # # # | # # # | # # # | - - - | 0.799 | 0.822 | 0.997 | 0.876 | - - - | 0.399 | 1.93 | 1.89 | 1.89 | 1.72 | 1.8 | 1.87 | 9.85 | 13.68 | 17.9 | 0 | - - - | - - - | - - - | - - - | 1497 | 1336 | 1589 | 4422 | Over-range | 913 | 779 | 337 | 2219 | 187 | 195 | 314 | 1612 | 1186 | 1087 | 1551 | 3825 | 1186 | 1087 | 1551 | 3825 | - - - | - - - | - - - | - - -
5/6/2026 | 11:45:00 AM | 281.67 | 278.77 | 277.55 | 486.62 | 480.02 | 484.79 | 5.3481 | 4.8635 | 5.7335 | 4.1655 | 1.433 | 1.436 | 1.433 | 1.536 | 1.45 | 1.435 | Over-range | 59.99 | 1193 | 1114 | 1554 | 3862 | - - - | - - - | - - - | - - - | 1193 | 1114 | 1554 | 3862 | 901 | 747 | -139 | 1507 | - - - | - - - | - - - | - - - | 901 | 747 | -139 | 1507 | 1506 | 1356 | 1591 | 4454 | # # # | # # # | # # # | # # # | 0.792 | 0.822 | 0.977 | 0.867 | # # # | # # # | # # # | - - - | 0.798 | 0.831 | 0.996 | 0.878 | - - - | 0.39 | 1.93 | 1.89 | 1.89 | 1.73 | 1.81 | 1.88 | 9.7 | 13.4 | 17.72 | 0 | - - - | - - - | - - - | - - - | 1506 | 1356 | 1591 | 4454 | Over-range | 920 | 772 | 342 | 2219 | 188 | 194 | 311 | 1628 | 1192 | 1115 | 1554 | 3861 | 1192 | 1115 | 1554 | 3861 | - - - | - - - | - - - | - - -
5/6/2026 | 12:00:00 PM | 281.18 | 278.27 | 277.14 | 485.73 | 479.19 | 484.07 | 5.4383 | 4.9184 | 5.7597 | 4.1614 | 1.434 | 1.437 | 1.433 | 1.534 | 1.452 | 1.435 | Over-range | 59.99 | 1212 | 1134 | 1558 | 3904 | - - - | - - - | - - - | - - - | 1212 | 1134 | 1558 | 3904 | 911 | 741 | -136 | 1514 | - - - | - - - | - - - | - - - | 911 | 741 | -136 | 1514 | 1528 | 1369 | 1596 | 4492 | # # # | # # # | # # # | # # # | 0.793 | 0.829 | 0.976 | 0.869 | # # # | # # # | # # # | - - - | 0.792 | 0.831 | 0.984 | 0.872 | - - - | 0.388 | 1.97 | 1.9 | 1.93 | 1.75 | 1.84 | 1.91 | 9.6 | 13.3 | 17.62 | 0 | - - - | - - - | - - - | - - - | 1528 | 1369 | 1596 | 4492 | Over-range | 930 | 766 | 345 | 2222 | 185 | 192 | 310 | 1622 | 1223 | 1150 | 1587 | 3959 | 1223 | 1150 | 1587 | 3959 | - - - | - - - | - - - | - - -
5/6/2026 | 12:15:00 PM | 281.09 | 278.27 | 277.08 | 485.64 | 479.19 | 483.89 | 4.6176 | 3.7386 | 5.3323 | 4.1674 | 1.434 | 1.437 | 1.434 | 1.554 | 1.524 | 1.539 | Over-range | 60 | 1072 | 655 | 1439 | 3167 | - - - | - - - | - - - | - - - | 1072 | 655 | 1439 | 3167 | 697 | 743 | 57 | 1497 | - - - | - - - | - - - | - - - | 697 | 743 | 57 | 1497 | 1293 | 1026 | 1476 | 3795 | # # # | # # # | # # # | # # # | 0.83 | 0.639 | 0.975 | 0.835 | # # # | # # # | # # # | - - - | 0.838 | 0.651 | 0.996 | 0.849 | - - - | 0.473 | 1.94 | 1.9 | 1.89 | 1.74 | 1.81 | 1.89 | 11.32 | 16.74 | 18.45 | 0 | - - - | - - - | - - - | - - - | 1293 | 1026 | 1476 | 3795 | Over-range | 720 | 767 | 329 | 2084 | 181 | 187 | 305 | 1449 | 1072 | 657 | 1438 | 3167 | 1072 | 657 | 1438 | 3167 | - - - | - - - | - - - | - - -
5/6/2026 | 12:30:00 PM | 280.59 | 277.8 | 276.58 | 484.77 | 478.4 | 483.01 | 4.7053 | 3.8521 | 5.3703 | 4.1696 | 1.435 | 1.438 | 1.435 | 1.553 | 1.507 | 1.52 | Over-range | 60.01 | 1087 | 712 | 1448 | 3247 | - - - | - - - | - - - | - - - | 1087 | 712 | 1448 | 3247 | 717 | 735 | 27 | 1479 | - - - | - - - | - - - | - - - | 717 | 735 | 27 | 1479 | 1315 | 1058 | 1484 | 3858 | # # # | # # # | # # # | # # # | 0.826 | 0.673 | 0.976 | 0.842 | # # # | # # # | # # # | - - - | 0.834 | 0.685 | 0.997 | 0.855 | - - - | 0.455 | 1.97 | 1.93 | 1.95 | 1.78 | 1.86 | 1.93 | 11.06 | 16.28 | 18.31 | 0 | - - - | - - - | - - - | - - - | 1315 | 1058 | 1484 | 3858 | Over-range | 740 | 759 | 323 | 2075 | 180 | 188 | 303 | 1455 | 1087 | 713 | 1448 | 3247 | 1087 | 713 | 1448 | 3247 | - - - | - - - | - - - | - - -
5/6/2026 | 12:45:00 PM | 280.8 | 278.13 | 276.84 | 485.29 | 478.92 | 483.38 | 4.7248 | 3.9042 | 5.3837 | 4.1706 | 1.436 | 1.439 | 1.436 | 1.553 | 1.511 | 1.521 | Over-range | 60 | 1088 | 721 | 1452 | 3262 | - - - | - - - | - - - | - - - | 1088 | 721 | 1452 | 3262 | 723 | 740 | 26 | 1489 | - - - | - - - | - - - | - - - | 723 | 740 | 26 | 1489 | 1321 | 1069 | 1489 | 3879 | # # # | # # # | # # # | # # # | 0.824 | 0.674 | 0.975 | 0.841 | # # # | # # # | # # # | - - - | 0.832 | 0.685 | 0.997 | 0.854 | - - - | 0.456 | 2 | 1.96 | 1.97 | 1.81 | 1.88 | 1.95 | 11.06 | 16.17 | 18.35 | 0 | - - - | - - - | - - - | - - - | 1321 | 1069 | 1489 | 3879 | Over-range | 746 | 764 | 328 | 2092 | 183 | 192 | 305 | 1468 | 1089 | 720 | 1455 | 3263 | 1089 | 720 | 1455 | 3263 | - - - | - - - | - - - | - - -
5/6/2026 | 1:00:00 PM | 280.76 | 278.17 | 276.81 | 485.28 | 478.95 | 483.28 | 4.8162 | 3.9145 | 5.4131 | 4.1748 | 1.437 | 1.441 | 1.438 | 1.55 | 1.504 | 1.513 | Over-range | 60 | 1109 | 748 | 1461 | 3319 | - - - | - - - | - - - | - - - | 1109 | 748 | 1461 | 3319 | 741 | 739 | 28 | 1509 | - - - | - - - | - - - | - - - | 741 | 739 | 28 | 1509 | 1347 | 1079 | 1497 | 3924 | # # # | # # # | # # # | # # # | 0.824 | 0.693 | 0.976 | 0.846 | # # # | # # # | # # # | - - - | 0.823 | 0.698 | 0.987 | 0.851 | - - - | 0.455 | 2.06 | 2 | 2 | 1.86 | 1.92 | 2.01 | 10.84 | 16.1 | 18.41 | 0 | - - - | - - - | - - - | - - - | 1347 | 1079 | 1497 | 3924 | Over-range | 763 | 764 | 326 | 2090 | 182 | 194 | 308 | 1441 | 1122 | 751 | 1475 | 3348 | 1122 | 751 | 1475 | 3348 | - - - | - - - | - - - | - - -
5/6/2026 | 1:15:00 PM | 280.36 | 277.66 | 276.37 | 484.44 | 478.15 | 482.6 | 5.5528 | 5.239 | 5.86 | 4.1665 | 1.437 | 1.441 | 1.438 | 1.534 | 1.464 | 1.444 | Over-range | 60.01 | 1223 | 1242 | 1576 | 4041 | - - - | - - - | - - - | - - - | 1223 | 1242 | 1576 | 4041 | 944 | 727 | -207 | 1464 | - - - | - - - | - - - | - - - | 944 | 727 | -207 | 1464 | 1556 | 1453 | 1619 | 4629 | # # # | # # # | # # # | # # # | 0.786 | 0.855 | 0.973 | 0.873 | # # # | # # # | # # # | - - - | 0.793 | 0.862 | 0.991 | 0.883 | - - - | 0.362 | 2.04 | 1.99 | 2 | 1.85 | 1.91 | 2 | 9.29 | 12.53 | 17.26 | 0 | - - - | - - - | - - - | - - - | 1556 | 1453 | 1619 | 4629 | Over-range | 962 | 754 | 373 | 2259 | 184 | 199 | 309 | 1720 | 1227 | 1239 | 1577 | 4043 | 1227 | 1239 | 1577 | 4043 | - - - | - - - | - - - | - - -
5/6/2026 | 1:30:00 PM | 279.9 | 277.28 | 275.91 | 483.77 | 477.41 | 481.76 | 4.9281 | 4.2475 | 5.4946 | 4.1702 | 1.437 | 1.442 | 1.439 | 1.549 | 1.492 | 1.503 | Over-range | 59.99 | 1118 | 843 | 1475 | 3437 | - - - | - - - | - - - | - - - | 1118 | 843 | 1475 | 3437 | 769 | 728 | -34 | 1462 | - - - | - - - | - - - | - - - | 769 | 728 | -34 | 1462 | 1371 | 1156 | 1514 | 4041 | # # # | # # # | # # # | # # # | 0.816 | 0.73 | 0.975 | 0.851 | # # # | # # # | # # # | - - - | 0.823 | 0.739 | 0.995 | 0.863 | - - - | 0.425 | 2.07 | 2.01 | 2.01 | 1.87 | 1.93 | 2.02 | 10.68 | 15.23 | 18.08 | 0 | - - - | - - - | - - - | - - - | 1371 | 1156 | 1514 | 4041 | Over-range | 791 | 753 | 338 | 2114 | 181 | 192 | 305 | 1526 | 1120 | 841 | 1477 | 3439 | 1120 | 841 | 1477 | 3439 | - - - | - - - | - - - | - - -
5/6/2026 | 1:45:00 PM | 279.45 | 276.83 | 275.52 | 482.96 | 476.67 | 481.07 | 4.769 | 3.9852 | 5.4043 | 4.166 | 1.437 | 1.442 | 1.438 | 1.552 | 1.507 | 1.526 | Over-range | 60 | 1093 | 750 | 1450 | 3293 | - - - | - - - | - - - | - - - | 1093 | 750 | 1450 | 3293 | 724 | 724 | 2 | 1449 | - - - | - - - | - - - | - - - | 724 | 724 | 2 | 1449 | 1325 | 1080 | 1487 | 3893 | # # # | # # # | # # # | # # # | 0.825 | 0.694 | 0.975 | 0.846 | # # # | # # # | # # # | - - - | 0.833 | 0.705 | 0.996 | 0.859 | - - - | 0.44 | 2.07 | 2.02 | 2.01 | 1.87 | 1.94 | 2.02 | 10.91 | 15.8 | 18.16 | 0 | - - - | - - - | - - - | - - - | 1325 | 1080 | 1487 | 3893 | Over-range | 747 | 747 | 329 | 2068 | 181 | 187 | 301 | 1472 | 1093 | 749 | 1452 | 3294 | 1093 | 749 | 1452 | 3294 | - - - | - - - | - - - | - - -
5/6/2026 | 2:00:00 PM | 279.55 | 276.97 | 275.68 | 483.12 | 476.97 | 481.29 | 4.5556 | 3.5052 | 5.2733 | 4.1733 | 1.438 | 1.442 | 1.439 | 1.557 | 1.521 | 1.554 | Over-range | 60 | 1067 | 594 | 1416 | 3076 | - - - | - - - | - - - | - - - | 1067 | 594 | 1416 | 3076 | 663 | 728 | 85 | 1476 | - - - | - - - | - - - | - - - | 663 | 728 | 85 | 1476 | 1270 | 966 | 1453 | 3689 | # # # | # # # | # # # | # # # | 0.84 | 0.615 | 0.974 | 0.834 | # # # | # # # | # # # | - - - | 0.841 | 0.621 | 0.981 | 0.839 | - - - | 0.48 | 2.07 | 2.01 | 2.02 | 1.87 | 1.93 | 2.02 | 11.43 | 16.88 | 18.48 | 0 | - - - | - - - | - - - | - - - | 1270 | 966 | 1453 | 3689 | Over-range | 687 | 750 | 325 | 2031 | 180 | 183 | 302 | 1392 | 1076 | 598 | 1431 | 3105 | 1076 | 598 | 1431 | 3105 | - - - | - - - | - - - | - - -
5/6/2026 | 2:15:00 PM | 279.48 | 276.96 | 275.65 | 483.03 | 476.99 | 481.16 | 5.7879 | 5.6939 | 6.0214 | 4.1654 | 1.438 | 1.442 | 1.439 | 1.532 | 1.483 | 1.48 | Over-range | 60.01 | 1257 | 1381 | 1606 | 4244 | - - - | - - - | - - - | - - - | 1257 | 1381 | 1606 | 4244 | 998 | 720 | -273 | 1444 | - - - | - - - | - - - | - - - | 998 | 720 | -273 | 1444 | 1616 | 1572 | 1659 | 4847 | # # # | # # # | # # # | # # # | 0.778 | 0.879 | 0.968 | 0.875 | # # # | # # # | # # # | - - - | 0.783 | 0.886 | 0.985 | 0.885 | - - - | 0.34 | 2.11 | 2.04 | 2.05 | 1.9 | 1.97 | 2.05 | 8.98 | 11.84 | 16.95 | 0 | - - - | - - - | - - - | - - - | 1616 | 1572 | 1659 | 4847 | Over-range | 1015 | 746 | 417 | 2342 | 184 | 197 | 309 | 1842 | 1258 | 1382 | 1603 | 4243 | 1258 | 1382 | 1603 | 4243 | - - - | - - - | - - - | - - -
5/6/2026 | 2:30:00 PM | 279.76 | 277.28 | 275.94 | 483.55 | 477.51 | 481.69 | 5.6226 | 5.3708 | 5.9088 | 4.1687 | 1.438 | 1.443 | 1.44 | 1.532 | 1.467 | 1.476 | Over-range | 60.01 | 1232 | 1285 | 1584 | 4101 | - - - | - - - | - - - | - - - | 1232 | 1285 | 1584 | 4101 | 960 | 726 | -228 | 1456 | - - - | - - - | - - - | - - - | 960 | 726 | -228 | 1456 | 1573 | 1489 | 1630 | 4692 | # # # | # # # | # # # | # # # | 0.784 | 0.863 | 0.971 | 0.874 | # # # | # # # | # # # | - - - | 0.79 | 0.871 | 0.99 | 0.884 | - - - | 0.355 | 2.15 | 2.11 | 2.11 | 1.96 | 2.03 | 2.12 | 9.25 | 12.29 | 17.34 | 0 | - - - | - - - | - - - | - - - | 1573 | 1489 | 1630 | 4692 | Over-range | 977 | 752 | 387 | 2280 | 184 | 196 | 311 | 1754 | 1234 | 1285 | 1582 | 4101 | 1234 | 1285 | 1582 | 4101 | - - - | - - - | - - - | - - -
5/6/2026 | 2:45:00 PM | 279.61 | 277.16 | 275.81 | 483.34 | 477.29 | 481.41 | 5.5348 | 5.207 | 5.8522 | 4.1719 | 1.438 | 1.444 | 1.44 | 1.532 | 1.46 | 1.484 | Over-range | 60.01 | 1218 | 1232 | 1570 | 4021 | - - - | - - - | - - - | - - - | 1218 | 1232 | 1570 | 4021 | 937 | 724 | -206 | 1454 | - - - | - - - | - - - | - - - | 937 | 724 | -206 | 1454 | 1548 | 1443 | 1614 | 4605 | # # # | # # # | # # # | # # # | 0.787 | 0.854 | 0.973 | 0.873 | # # # | # # # | # # # | - - - | 0.794 | 0.862 | 0.992 | 0.884 | - - - | 0.362 | 2.19 | 2.15 | 2.17 | 2 | 2.09 | 2.17 | 9.41 | 12.59 | 17.53 | 0 | - - - | - - - | - - - | - - - | 1548 | 1443 | 1614 | 4605 | Over-range | 955 | 751 | 375 | 2245 | 182 | 198 | 312 | 1710 | 1222 | 1230 | 1570 | 4022 | 1222 | 1230 | 1570 | 4022 | - - - | - - - | - - - | - - -
5/6/2026 | 3:00:00 PM | 279.69 | 277.36 | 275.97 | 483.55 | 477.72 | 481.55 | 5.1918 | 4.5122 | 5.6248 | 4.1799 | 1.439 | 1.444 | 1.441 | 1.538 | 1.462 | 1.489 | Over-range | 60.01 | 1169 | 990 | 1515 | 3674 | - - - | - - - | - - - | - - - | 1169 | 990 | 1515 | 3674 | 838 | 728 | -85 | 1481 | - - - | - - - | - - - | - - - | 838 | 728 | -85 | 1481 | 1450 | 1247 | 1552 | 4249 | # # # | # # # | # # # | # # # | 0.806 | 0.794 | 0.976 | 0.865 | # # # | # # # | # # # | - - - | 0.806 | 0.797 | 0.986 | 0.869 | - - - | 0.403 | 2.21 | 2.16 | 2.18 | 2.01 | 2.09 | 2.18 | 10.05 | 14.12 | 18.09 | 0 | - - - | - - - | - - - | - - - | 1450 | 1247 | 1552 | 4249 | Over-range | 858 | 753 | 336 | 2133 | 179 | 193 | 311 | 1531 | 1182 | 995 | 1526 | 3703 | 1182 | 995 | 1526 | 3703 | - - - | - - - | - - - | - - -
5/6/2026 | 3:15:00 PM | 279.62 | 277.33 | 275.96 | 483.45 | 477.65 | 481.51 | 5.5172 | 5.1955 | 5.8454 | 4.1752 | 1.439 | 1.444 | 1.441 | 1.535 | 1.468 | 1.492 | Over-range | 60.01 | 1214 | 1216 | 1567 | 3997 | - - - | - - - | - - - | - - - | 1214 | 1216 | 1567 | 3997 | 930 | 726 | -198 | 1457 | - - - | - - - | - - - | - - - | 930 | 726 | -198 | 1457 | 1541 | 1433 | 1612 | 4586 | # # # | # # # | # # # | # # # | 0.788 | 0.849 | 0.972 | 0.872 | # # # | # # # | # # # | - - - | 0.794 | 0.856 | 0.991 | 0.882 | - - - | 0.365 | 2.23 | 2.2 | 2.19 | 2.03 | 2.1 | 2.2 | 9.54 | 12.86 | 17.69 | 0 | - - - | - - - | - - - | - - - | 1541 | 1433 | 1612 | 4586 | Over-range | 948 | 752 | 377 | 2247 | 182 | 197 | 313 | 1708 | 1216 | 1216 | 1565 | 3997 | 1216 | 1216 | 1565 | 3997 | - - - | - - - | - - - | - - -
5/6/2026 | 3:30:00 PM | 279.35 | 277.14 | 275.72 | 483.07 | 477.3 | 481.03 | 5.8737 | 5.8467 | 6.0821 | 4.1728 | 1.439 | 1.444 | 1.441 | 1.529 | 1.485 | 1.508 | Over-range | 60.01 | 1269 | 1435 | 1620 | 4324 | - - - | - - - | - - - | - - - | 1269 | 1435 | 1620 | 4324 | 1024 | 723 | -294 | 1452 | - - - | - - - | - - - | - - - | 1024 | 723 | -294 | 1452 | 1641 | 1620 | 1677 | 4937 | # # # | # # # | # # # | # # # | 0.774 | 0.886 | 0.966 | 0.876 | # # # | # # # | # # # | - - - | 0.78 | 0.892 | 0.984 | 0.885 | - - - | 0.336 | 2.29 | 2.19 | 2.23 | 2.07 | 2.14 | 2.24 | 8.97 | 11.58 | 17.14 | 0 | - - - | - - - | - - - | - - - | 1641 | 1620 | 1677 | 4937 | Over-range | 1040 | 751 | 432 | 2383 | 183 | 203 | 316 | 1889 | 1273 | 1433 | 1618 | 4324 | 1273 | 1433 | 1618 | 4324 | - - - | - - - | - - - | - - -
5/6/2026 | 3:45:00 PM | 279.12 | 276.95 | 275.6 | 482.68 | 477.1 | 480.71 | 5.6476 | 5.4236 | 5.9294 | 4.1743 | 1.439 | 1.444 | 1.441 | 1.532 | 1.472 | 1.501 | Over-range | 60 | 1233 | 1300 | 1585 | 4119 | - - - | - - - | - - - | - - - | 1233 | 1300 | 1585 | 4119 | 964 | 721 | -236 | 1447 | - - - | - - - | - - - | - - - | 964 | 721 | -236 | 1447 | 1576 | 1500 | 1634 | 4710 | # # # | # # # | # # # | # # # | 0.783 | 0.866 | 0.97 | 0.874 | # # # | # # # | # # # | - - - | 0.789 | 0.873 | 0.989 | 0.885 | - - - | 0.351 | 2.26 | 2.23 | 2.24 | 2.08 | 2.14 | 2.24 | 9.34 | 12.25 | 17.49 | 0 | - - - | - - - | - - - | - - - | 1576 | 1500 | 1634 | 4710 | Over-range | 981 | 748 | 395 | 2285 | 181 | 200 | 314 | 1767 | 1238 | 1298 | 1584 | 4119 | 1238 | 1298 | 1584 | 4119 | - - - | - - - | - - - | - - -
5/6/2026 | 4:00:00 PM | 279.39 | 277.19 | 275.78 | 483.09 | 477.48 | 481.11 | 5.5974 | 5.2467 | 5.8735 | 4.1777 | 1.44 | 1.444 | 1.441 | 1.532 | 1.47 | 1.5 | Over-range | 60 | 1230 | 1236 | 1574 | 4040 | - - - | - - - | - - - | - - - | 1230 | 1236 | 1574 | 4040 | 942 | 725 | -194 | 1472 | - - - | - - - | - - - | - - - | 942 | 725 | -194 | 1472 | 1561 | 1450 | 1619 | 4631 | # # # | # # # | # # # | # # # | 0.788 | 0.852 | 0.972 | 0.872 | # # # | # # # | # # # | - - - | 0.787 | 0.853 | 0.98 | 0.875 | - - - | 0.365 | 2.27 | 2.19 | 2.22 | 2.06 | 2.12 | 2.23 | 9.53 | 12.75 | 17.69 | 0 | - - - | - - - | - - - | - - - | 1561 | 1450 | 1619 | 4631 | Over-range | 960 | 751 | 380 | 2261 | 180 | 197 | 314 | 1713 | 1244 | 1251 | 1599 | 4095 | 1244 | 1251 | 1599 | 4095 | - - - | - - - | - - - | - - -
5/6/2026 | 4:15:00 PM | 279.59 | 277.48 | 275.99 | 483.58 | 477.89 | 481.43 | 4.5401 | 3.5726 | 5.2867 | 4.1887 | 1.44 | 1.444 | 1.441 | 1.561 | 1.525 | 1.544 | Over-range | 60.01 | 1058 | 618 | 1422 | 3098 | - - - | - - - | - - - | - - - | 1058 | 618 | 1422 | 3098 | 672 | 733 | 64 | 1470 | - - - | - - - | - - - | - - - | 672 | 733 | 64 | 1470 | 1267 | 987 | 1459 | 3713 | # # # | # # # | # # # | # # # | 0.835 | 0.626 | 0.975 | 0.835 | # # # | # # # | # # # | - - - | 0.844 | 0.637 | 0.997 | 0.849 | - - - | 0.474 | 2.26 | 2.19 | 2.23 | 2.06 | 2.12 | 2.23 | 11.73 | 17.01 | 19.03 | 0 | - - - | - - - | - - - | - - - | 1267 | 987 | 1459 | 3713 | Over-range | 696 | 758 | 323 | 2041 | 180 | 190 | 309 | 1415 | 1061 | 616 | 1422 | 3100 | 1061 | 616 | 1422 | 3100 | - - - | - - - | - - - | - - -
5/6/2026 | 4:30:00 PM | 279.71 | 277.53 | 276.06 | 483.71 | 477.98 | 481.62 | 4.7235 | 3.9096 | 5.3887 | 4.1865 | 1.439 | 1.444 | 1.441 | 1.555 | 1.513 | 1.536 | Over-range | 60 | 1085 | 720 | 1448 | 3253 | - - - | - - - | - - - | - - - | 1085 | 720 | 1448 | 3253 | 717 | 733 | 20 | 1470 | - - - | - - - | - - - | - - - | 717 | 733 | 20 | 1470 | 1315 | 1067 | 1486 | 3867 | # # # | # # # | # # # | # # # | 0.825 | 0.675 | 0.974 | 0.841 | # # # | # # # | # # # | - - - | 0.834 | 0.685 | 0.996 | 0.855 | - - - | 0.452 | 2.23 | 2.19 | 2.19 | 2.04 | 2.1 | 2.2 | 11.34 | 16.3 | 18.77 | 0 | - - - | - - - | - - - | - - - | 1315 | 1067 | 1486 | 3867 | Over-range | 740 | 758 | 334 | 2084 | 182 | 193 | 309 | 1475 | 1087 | 718 | 1449 | 3254 | 1087 | 718 | 1449 | 3254 | - - - | - - - | - - - | - - -
5/6/2026 | 4:45:00 PM | 280.12 | 277.87 | 276.38 | 484.37 | 478.52 | 482.26 | 5.3745 | 4.8772 | 5.7351 | 4.1763 | 1.44 | 1.444 | 1.441 | 1.538 | 1.48 | 1.498 | Over-range | 60.01 | 1195 | 1090 | 1542 | 3826 | - - - | - - - | - - - | - - - | 1195 | 1090 | 1542 | 3826 | 882 | 734 | -126 | 1490 | - - - | - - - | - - - | - - - | 882 | 734 | -126 | 1490 | 1498 | 1339 | 1583 | 4421 | # # # | # # # | # # # | # # # | 0.797 | 0.814 | 0.974 | 0.866 | # # # | # # # | # # # | - - - | 0.796 | 0.815 | 0.984 | 0.869 | - - - | 0.389 | 2.25 | 2.16 | 2.17 | 2.03 | 2.08 | 2.2 | 9.98 | 13.93 | 18.08 | 0 | - - - | - - - | - - - | - - - | 1498 | 1339 | 1583 | 4421 | Over-range | 903 | 759 | 358 | 2211 | 189 | 194 | 313 | 1628 | 1205 | 1098 | 1569 | 3871 | 1205 | 1098 | 1569 | 3871 | - - - | - - - | - - - | - - -
5/6/2026 | 5:00:00 PM | 280.19 | 277.94 | 276.37 | 484.54 | 478.56 | 482.29 | 5.1696 | 4.6545 | 5.6395 | 4.1781 | 1.44 | 1.444 | 1.441 | 1.544 | 1.484 | 1.508 | Over-range | 60 | 1155 | 990 | 1515 | 3659 | - - - | - - - | - - - | - - - | 1155 | 990 | 1515 | 3659 | 836 | 735 | -94 | 1475 | - - - | - - - | - - - | - - - | 836 | 735 | -94 | 1475 | 1440 | 1273 | 1556 | 4270 | # # # | # # # | # # # | # # # | 0.802 | 0.777 | 0.973 | 0.857 | # # # | # # # | # # # | - - - | 0.809 | 0.787 | 0.993 | 0.869 | - - - | 0.403 | 2.24 | 2.18 | 2.17 | 2.03 | 2.08 | 2.2 | 10.4 | 14.29 | 18.14 | 0 | - - - | - - - | - - - | - - - | 1440 | 1273 | 1556 | 4270 | Over-range | 857 | 760 | 358 | 2188 | 187 | 195 | 311 | 1614 | 1156 | 988 | 1517 | 3660 | 1156 | 988 | 1517 | 3660 | - - - | - - - | - - - | - - -
5/6/2026 | 5:15:00 PM | 280.6 | 278.3 | 276.78 | 485.22 | 479.18 | 483 | 4.7954 | 3.9826 | 5.4237 | 4.1866 | 1.44 | 1.444 | 1.442 | 1.555 | 1.503 | 1.529 | Over-range | 60.02 | 1100 | 771 | 1464 | 3336 | - - - | - - - | - - - | - - - | 1100 | 771 | 1464 | 3336 | 744 | 742 | 1 | 1487 | - - - | - - - | - - - | - - - | 744 | 742 | 1 | 1487 | 1342 | 1097 | 1500 | 3940 | # # # | # # # | # # # | # # # | 0.82 | 0.703 | 0.976 | 0.847 | # # # | # # # | # # # | - - - | 0.828 | 0.714 | 0.998 | 0.861 | - - - | 0.446 | 2.19 | 2.11 | 2.14 | 1.99 | 2.04 | 2.16 | 11.12 | 16.18 | 18.85 | 0 | - - - | - - - | - - - | - - - | 1342 | 1097 | 1500 | 3940 | Over-range | 767 | 767 | 326 | 2092 | 187 | 193 | 313 | 1470 | 1100 | 770 | 1466 | 3335 | 1100 | 770 | 1466 | 3335 | - - - | - - - | - - - | - - -
5/6/2026 | 5:30:00 PM | 280.43 | 278.19 | 276.68 | 484.95 | 479.07 | 482.75 | 5.5275 | 5.1929 | 5.8471 | 4.1827 | 1.44 | 1.444 | 1.442 | 1.534 | 1.466 | 1.499 | Over-range | 60.01 | 1217 | 1225 | 1573 | 4016 | - - - | - - - | - - - | - - - | 1217 | 1225 | 1573 | 4016 | 939 | 736 | -197 | 1477 | - - - | - - - | - - - | - - - | 939 | 736 | -197 | 1477 | 1550 | 1443 | 1618 | 4611 | # # # | # # # | # # # | # # # | 0.786 | 0.849 | 0.973 | 0.871 | # # # | # # # | # # # | - - - | 0.792 | 0.856 | 0.992 | 0.882 | - - - | 0.368 | 2.2 | 2.13 | 2.19 | 2.02 | 2.08 | 2.19 | 9.7 | 12.86 | 17.94 | 0 | - - - | - - - | - - - | - - - | 1550 | 1443 | 1618 | 4611 | Over-range | 959 | 762 | 376 | 2266 | 193 | 199 | 318 | 1718 | 1218 | 1223 | 1575 | 4016 | 1218 | 1223 | 1575 | 4016 | - - - | - - - | - - - | - - -
5/6/2026 | 5:45:00 PM | 280.51 | 278.32 | 276.74 | 485.12 | 479.28 | 482.82 | 4.7548 | 3.8718 | 5.3901 | 4.202 | 1.441 | 1.444 | 1.443 | 1.556 | 1.526 | 1.555 | Over-range | 60.01 | 1095 | 700 | 1450 | 3245 | - - - | - - - | - - - | - - - | 1095 | 700 | 1450 | 3245 | 719 | 743 | 45 | 1506 | - - - | - - - | - - - | - - - | 719 | 743 | 45 | 1506 | 1325 | 1060 | 1490 | 3874 | # # # | # # # | # # # | # # # | 0.826 | 0.661 | 0.973 | 0.838 | # # # | # # # | # # # | - - - | 0.825 | 0.667 | 0.985 | 0.843 | - - - | 0.464 | 2.25 | 2.15 | 2.2 | 2.05 | 2.1 | 2.22 | 11.65 | 16.61 | 19.04 | 0 | - - - | - - - | - - - | - - - | 1325 | 1060 | 1490 | 3874 | Over-range | 744 | 768 | 341 | 2108 | 188 | 192 | 315 | 1471 | 1104 | 714 | 1476 | 3295 | 1104 | 714 | 1476 | 3295 | - - - | - - - | - - - | - - -
5/6/2026 | 6:00:00 PM | 280.63 | 278.39 | 276.89 | 485.29 | 479.42 | 483.1 | 4.7846 | 4.0117 | 5.4259 | 4.2026 | 1.441 | 1.444 | 1.443 | 1.555 | 1.518 | 1.549 | Over-range | 60.01 | 1096 | 750 | 1461 | 3306 | - - - | - - - | - - - | - - - | 1096 | 750 | 1461 | 3306 | 738 | 745 | 10 | 1493 | - - - | - - - | - - - | - - - | 738 | 745 | 10 | 1493 | 1336 | 1097 | 1501 | 3933 | # # # | # # # | # # # | # # # | 0.82 | 0.683 | 0.973 | 0.841 | # # # | # # # | # # # | - - - | 0.829 | 0.695 | 0.996 | 0.855 | - - - | 0.452 | 2.2 | 2.12 | 2.17 | 2.02 | 2.07 | 2.19 | 11.5 | 16.31 | 19.06 | 0 | - - - | - - - | - - - | - - - | 1336 | 1097 | 1501 | 3933 | Over-range | 761 | 769 | 342 | 2121 | 186 | 192 | 316 | 1504 | 1096 | 751 | 1459 | 3305 | 1096 | 751 | 1459 | 3305 | - - - | - - - | - - - | - - -
5/6/2026 | 6:15:00 PM | 281.67 | 279.66 | 278.07 | 487.29 | 481.67 | 484.92 | 5.144 | 5.0487 | 5.6451 | 3.857 | 1.44 | 1.441 | 1.441 | 1.549 | 1.508 | 1.54 | Over-range | 60.01 | 1154 | 1090 | 1525 | 3769 | - - - | - - - | - - - | - - - | 1154 | 1090 | 1525 | 3769 | 839 | 723 | -76 | 1486 | - - - | - - - | - - - | - - - | 839 | 723 | -76 | 1486 | 1441 | 1360 | 1567 | 4368 | # # # | # # # | # # # | # # # | 0.801 | 0.802 | 0.973 | 0.863 | # # # | # # # | # # # | - - - | 0.807 | 0.811 | 0.995 | 0.875 | - - - | 0.394 | 2.13 | 1.98 | 2.02 | 1.92 | 1.93 | 2.05 | 10.82 | 13.95 | 18.94 | 0 | - - - | - - - | - - - | - - - | 1441 | 1360 | 1567 | 4368 | Over-range | 861 | 748 | 362 | 2194 | 190 | 190 | 325 | 1607 | 1153 | 1092 | 1522 | 3767 | 1153 | 1092 | 1522 | 3767 | - - - | - - - | - - - | - - -
5/6/2026 | 6:30:00 PM | 281.65 | 279.64 | 278.03 | 487.25 | 481.66 | 484.83 | 5.6664 | 6.5057 | 5.9303 | 2.7937 | 1.44 | 1.441 | 1.441 | 1.538 | 1.495 | 1.512 | Over-range | 60 | 1246 | 1696 | 1602 | 4544 | - - - | - - - | - - - | - - - | 1246 | 1696 | 1602 | 4544 | 977 | 632 | -199 | 1409 | - - - | - - - | - - - | - - - | 977 | 632 | -199 | 1409 | 1595 | 1819 | 1649 | 5062 | # # # | # # # | # # # | # # # | 0.781 | 0.933 | 0.972 | 0.898 | # # # | # # # | # # # | - - - | 0.78 | 0.93 | 0.984 | 0.9 | - - - | 0.31 | 2.08 | 1.96 | 1.96 | 1.89 | 1.89 | 2.01 | 9.65 | 9.02 | 18.25 | 0 | - - - | - - - | - - - | - - - | 1595 | 1819 | 1649 | 5062 | Over-range | 996 | 656 | 389 | 2231 | 188 | 175 | 327 | 1726 | 1258 | 1708 | 1612 | 4577 | 1258 | 1708 | 1612 | 4577 | - - - | - - - | - - - | - - -
5/6/2026 | 6:45:00 PM | 281.76 | 279.87 | 278.2 | 487.53 | 482.07 | 485.01 | 5.0874 | 5.5023 | 5.618 | 2.8231 | 1.44 | 1.44 | 1.441 | 1.553 | 1.523 | 1.533 | Over-range | 59.99 | 1143 | 1344 | 1518 | 4005 | - - - | - - - | - - - | - - - | 1143 | 1344 | 1518 | 4005 | 826 | 640 | -58 | 1408 | - - - | - - - | - - - | - - - | 826 | 640 | -58 | 1408 | 1425 | 1511 | 1561 | 4496 | # # # | # # # | # # # | # # # | 0.802 | 0.89 | 0.973 | 0.891 | # # # | # # # | # # # | - - - | 0.811 | 0.896 | 0.995 | 0.903 | - - - | 0.351 | 2.03 | 1.91 | 1.94 | 1.86 | 1.84 | 1.97 | 10.92 | 11.03 | 18.93 | 0 | - - - | - - - | - - - | - - - | 1425 | 1511 | 1561 | 4496 | Over-range | 848 | 665 | 363 | 2040 | 185 | 181 | 324 | 1466 | 1147 | 1342 | 1518 | 4006 | 1147 | 1342 | 1518 | 4006 | - - - | - - - | - - - | - - -
5/6/2026 | 7:00:00 PM | 281.86 | 280.05 | 278.34 | 487.83 | 482.35 | 485.18 | 4.8903 | 5.0807 | 5.5035 | 2.8302 | 1.439 | 1.439 | 1.44 | 1.561 | 1.481 | 1.526 | Over-range | 60 | 1116 | 1237 | 1493 | 3845 | - - - | - - - | - - - | - - - | 1116 | 1237 | 1493 | 3845 | 781 | 644 | -11 | 1413 | - - - | - - - | - - - | - - - | 781 | 644 | -11 | 1413 | 1375 | 1409 | 1531 | 4315 | # # # | # # # | # # # | # # # | 0.812 | 0.877 | 0.975 | 0.891 | # # # | # # # | # # # | - - - | 0.82 | 0.884 | 0.998 | 0.904 | - - - | 0.367 | 1.95 | 1.81 | 1.83 | 1.77 | 1.74 | 1.87 | 11.08 | 11.28 | 19.25 | 0 | - - - | - - - | - - - | - - - | 1375 | 1409 | 1531 | 4315 | Over-range | 802 | 668 | 338 | 1957 | 183 | 179 | 324 | 1348 | 1119 | 1234 | 1493 | 3846 | 1119 | 1234 | 1493 | 3846 | - - - | - - - | - - - | - - -
5/6/2026 | 7:15:00 PM | 282.28 | 280.47 | 278.79 | 488.5 | 483.09 | 485.98 | 5.446 | 6.1392 | 5.8199 | 2.8253 | 1.44 | 1.439 | 1.44 | 1.545 | 1.487 | 1.508 | Over-range | 60 | 1206 | 1585 | 1580 | 4372 | - - - | - - - | - - - | - - - | 1206 | 1585 | 1580 | 4372 | 933 | 644 | -160 | 1416 | - - - | - - - | - - - | - - - | 933 | 644 | -160 | 1416 | 1537 | 1721 | 1622 | 4881 | # # # | # # # | # # # | # # # | 0.785 | 0.921 | 0.974 | 0.896 | # # # | # # # | # # # | - - - | 0.792 | 0.926 | 0.994 | 0.906 | - - - | 0.324 | 1.97 | 1.85 | 1.84 | 1.8 | 1.77 | 1.9 | 9.97 | 9.54 | 18.61 | 0 | - - - | - - - | - - - | - - - | 1537 | 1721 | 1622 | 4881 | Over-range | 952 | 670 | 368 | 2170 | 190 | 182 | 330 | 1643 | 1210 | 1582 | 1581 | 4373 | 1210 | 1582 | 1581 | 4373 | - - - | - - - | - - - | - - -
5/6/2026 | 7:30:00 PM | 282.48 | 280.74 | 279.02 | 488.9 | 483.61 | 486.29 | 5.6815 | 6.5094 | 5.9449 | 2.8101 | 1.439 | 1.439 | 1.441 | 1.539 | 1.493 | 1.54 | Over-range | 60 | 1249 | 1699 | 1612 | 4560 | - - - | - - - | - - - | - - - | 1249 | 1699 | 1612 | 4560 | 985 | 646 | -194 | 1436 | - - - | - - - | - - - | - - - | 985 | 646 | -194 | 1436 | 1603 | 1827 | 1659 | 5089 | # # # | # # # | # # # | # # # | 0.779 | 0.93 | 0.972 | 0.896 | # # # | # # # | # # # | - - - | 0.777 | 0.927 | 0.981 | 0.897 | - - - | 0.315 | 2.03 | 1.88 | 1.9 | 1.84 | 1.81 | 1.94 | 10.28 | 9.6 | 18.83 | 0 | - - - | - - - | - - - | - - - | 1603 | 1827 | 1659 | 5089 | Over-range | 1005 | 670 | 391 | 2258 | 187 | 170 | 334 | 1740 | 1260 | 1722 | 1640 | 4622 | 1260 | 1722 | 1640 | 4622 | - - - | - - - | - - - | - - -
5/6/2026 | 7:45:00 PM | 282.43 | 280.66 | 278.96 | 488.81 | 483.41 | 486.24 | 5.4951 | 6.2364 | 5.8522 | 2.8212 | 1.439 | 1.439 | 1.44 | 1.542 | 1.486 | 1.532 | Over-range | 59.99 | 1215 | 1615 | 1589 | 4418 | - - - | - - - | - - - | - - - | 1215 | 1615 | 1589 | 4418 | 946 | 647 | -170 | 1422 | - - - | - - - | - - - | - - - | 946 | 647 | -170 | 1422 | 1552 | 1749 | 1632 | 4933 | # # # | # # # | # # # | # # # | 0.783 | 0.923 | 0.973 | 0.896 | # # # | # # # | # # # | - - - | 0.789 | 0.928 | 0.994 | 0.906 | - - - | 0.322 | 2 | 1.87 | 1.87 | 1.82 | 1.79 | 1.92 | 10.04 | 9.46 | 18.71 | 0 | - - - | - - - | - - - | - - - | 1552 | 1749 | 1632 | 4933 | Over-range | 965 | 672 | 376 | 2195 | 194 | 179 | 333 | 1671 | 1214 | 1617 | 1587 | 4417 | 1214 | 1617 | 1587 | 4417 | - - - | - - - | - - - | - - -
5/6/2026 | 8:00:00 PM | 282.51 | 280.62 | 279 | 488.86 | 483.38 | 486.36 | 5.2264 | 5.7009 | 5.6901 | 2.8272 | 1.439 | 1.439 | 1.44 | 1.549 | 1.473 | 1.52 | Over-range | 60 | 1173 | 1451 | 1549 | 4173 | - - - | - - - | - - - | - - - | 1173 | 1451 | 1549 | 4173 | 877 | 648 | -99 | 1425 | - - - | - - - | - - - | - - - | 877 | 648 | -99 | 1425 | 1476 | 1600 | 1588 | 4664 | # # # | # # # | # # # | # # # | 0.794 | 0.907 | 0.976 | 0.895 | # # # | # # # | # # # | - - - | 0.802 | 0.913 | 0.998 | 0.906 | - - - | 0.342 | 1.96 | 1.83 | 1.86 | 1.79 | 1.77 | 1.89 | 10.5 | 10.15 | 19.05 | 0 | - - - | - - - | - - - | - - - | 1476 | 1600 | 1588 | 4664 | Over-range | 897 | 673 | 346 | 2082 | 191 | 181 | 332 | 1518 | 1175 | 1448 | 1551 | 4174 | 1175 | 1448 | 1551 | 4174 | - - - | - - - | - - - | - - -
5/6/2026 | 8:15:00 PM | 282.6 | 280.74 | 278.97 | 489.11 | 483.44 | 486.37 | 5.375 | 5.9847 | 5.7777 | 2.8344 | 1.439 | 1.439 | 1.44 | 1.545 | 1.482 | 1.52 | Over-range | 59.99 | 1196 | 1539 | 1571 | 4305 | - - - | - - - | - - - | - - - | 1196 | 1539 | 1571 | 4305 | 917 | 649 | -137 | 1428 | - - - | - - - | - - - | - - - | 917 | 649 | -137 | 1428 | 1519 | 1680 | 1612 | 4811 | # # # | # # # | # # # | # # # | 0.787 | 0.916 | 0.975 | 0.895 | # # # | # # # | # # # | - - - | 0.795 | 0.921 | 0.996 | 0.906 | - - - | 0.332 | 1.96 | 1.83 | 1.86 | 1.79 | 1.77 | 1.89 | 10.21 | 9.8 | 18.87 | 0 | - - - | - - - | - - - | - - - | 1519 | 1680 | 1612 | 4811 | Over-range | 937 | 674 | 360 | 2146 | 191 | 184 | 333 | 1602 | 1199 | 1535 | 1572 | 4306 | 1199 | 1535 | 1572 | 4306 | - - - | - - - | - - - | - - -
5/6/2026 | 8:30:00 PM | 282.64 | 280.74 | 279 | 489.1 | 483.48 | 486.44 | 5.2313 | 5.6162 | 5.6748 | 2.8342 | 1.439 | 1.439 | 1.44 | 1.549 | 1.49 | 1.531 | Over-range | 59.99 | 1176 | 1409 | 1542 | 4128 | - - - | - - - | - - - | - - - | 1176 | 1409 | 1542 | 4128 | 865 | 651 | -67 | 1448 | - - - | - - - | - - - | - - - | 865 | 651 | -67 | 1448 | 1474 | 1567 | 1582 | 4623 | # # # | # # # | # # # | # # # | 0.798 | 0.9 | 0.975 | 0.893 | # # # | # # # | # # # | - - - | 0.797 | 0.898 | 0.989 | 0.896 | - - - | 0.351 | 1.96 | 1.83 | 1.88 | 1.78 | 1.77 | 1.89 | 10.71 | 10.59 | 19.16 | 0 | - - - | - - - | - - - | - - - | 1474 | 1567 | 1582 | 4623 | Over-range | 887 | 675 | 353 | 2080 | 190 | 178 | 331 | 1487 | 1187 | 1421 | 1552 | 4160 | 1187 | 1421 | 1552 | 4160 | - - - | - - - | - - - | - - -
5/6/2026 | 8:45:00 PM | 283.07 | 281.21 | 279.47 | 489.91 | 484.31 | 487.18 | 4.596 | 4.4986 | 5.3595 | 2.843 | 1.439 | 1.439 | 1.44 | 1.567 | 1.51 | 1.558 | Over-range | 59.99 | 1070 | 1051 | 1457 | 3578 | - - - | - - - | - - - | - - - | 1070 | 1051 | 1457 | 3578 | 711 | 662 | 81 | 1455 | - - - | - - - | - - - | - - - | 711 | 662 | 81 | 1455 | 1299 | 1259 | 1497 | 4056 | # # # | # # # | # # # | # # # | 0.824 | 0.835 | 0.973 | 0.882 | # # # | # # # | # # # | - - - | 0.834 | 0.844 | 0.997 | 0.897 | - - - | 0.406 | 1.98 | 1.85 | 1.86 | 1.78 | 1.77 | 1.9 | 12.16 | 12.8 | 19.96 | 0 | - - - | - - - | - - - | - - - | 1299 | 1259 | 1497 | 4056 | Over-range | 736 | 687 | 346 | 1908 | 190 | 182 | 330 | 1233 | 1072 | 1050 | 1457 | 3578 | 1072 | 1050 | 1457 | 3578 | - - - | - - - | - - - | - - -
5/6/2026 | 9:00:00 PM | 281.97 | 280.09 | 278.26 | 488.03 | 482.28 | 485.17 | 4.6921 | 4.7215 | 5.3979 | 2.8264 | 1.437 | 1.438 | 1.439 | 1.563 | 1.515 | 1.554 | Over-range | 60 | 1082 | 1108 | 1460 | 3649 | - - - | - - - | - - - | - - - | 1082 | 1108 | 1460 | 3649 | 725 | 644 | 47 | 1416 | - - - | - - - | - - - | - - - | 725 | 644 | 47 | 1416 | 1317 | 1301 | 1501 | 4119 | # # # | # # # | # # # | # # # | 0.822 | 0.851 | 0.973 | 0.886 | # # # | # # # | # # # | - - - | 0.83 | 0.859 | 0.996 | 0.899 | - - - | 0.388 | 1.91 | 1.78 | 1.83 | 1.73 | 1.73 | 1.85 | 11.77 | 12.18 | 19.54 | 0 | - - - | - - - | - - - | - - - | 1317 | 1301 | 1501 | 4119 | Over-range | 749 | 669 | 348 | 1908 | 185 | 179 | 324 | 1272 | 1085 | 1105 | 1460 | 3651 | 1085 | 1105 | 1460 | 3651 | - - - | - - - | - - - | - - -
5/6/2026 | 9:15:00 PM | 282.06 | 280.24 | 278.42 | 488.17 | 482.64 | 485.33 | 5.243 | 5.7531 | 5.7042 | 2.8299 | 1.437 | 1.437 | 1.438 | 1.548 | 1.478 | 1.525 | Over-range | 59.98 | 1173 | 1453 | 1547 | 4173 | - - - | - - - | - - - | - - - | 1173 | 1453 | 1547 | 4173 | 876 | 644 | -102 | 1418 | - - - | - - - | - - - | - - - | 876 | 644 | -102 | 1418 | 1476 | 1603 | 1587 | 4666 | # # # | # # # | # # # | # # # | 0.794 | 0.907 | 0.975 | 0.894 | # # # | # # # | # # # | - - - | 0.802 | 0.913 | 0.996 | 0.905 | - - - | 0.34 | 1.89 | 1.8 | 1.82 | 1.73 | 1.73 | 1.83 | 10.44 | 10.13 | 19 | 0 | - - - | - - - | - - - | - - - | 1476 | 1603 | 1587 | 4666 | Over-range | 896 | 670 | 356 | 2088 | 186 | 182 | 330 | 1528 | 1176 | 1452 | 1545 | 4173 | 1176 | 1452 | 1545 | 4173 | - - - | - - - | - - - | - - -
5/6/2026 | 9:30:00 PM | 282.02 | 280.33 | 278.42 | 488.25 | 482.7 | 485.29 | 5.5909 | 6.3179 | 5.8868 | 2.8254 | 1.437 | 1.437 | 1.438 | 1.54 | 1.482 | 1.53 | Over-range | 60.01 | 1235 | 1641 | 1594 | 4470 | - - - | - - - | - - - | - - - | 1235 | 1641 | 1594 | 4470 | 959 | 642 | -171 | 1429 | - - - | - - - | - - - | - - - | 959 | 642 | -171 | 1429 | 1575 | 1771 | 1639 | 4985 | # # # | # # # | # # # | # # # | 0.784 | 0.926 | 0.973 | 0.897 | # # # | # # # | # # # | - - - | 0.782 | 0.924 | 0.982 | 0.898 | - - - | 0.32 | 1.9 | 1.79 | 1.82 | 1.74 | 1.73 | 1.84 | 9.83 | 9.21 | 18.57 | 0 | - - - | - - - | - - - | - - - | 1575 | 1771 | 1639 | 4985 | Over-range | 978 | 667 | 380 | 2207 | 187 | 178 | 332 | 1679 | 1247 | 1664 | 1619 | 4530 | 1247 | 1664 | 1619 | 4530 | - - - | - - - | - - - | - - -
5/6/2026 | 9:45:00 PM | 282.08 | 280.31 | 278.42 | 488.31 | 482.64 | 485.34 | 5.414 | 6.0709 | 5.7995 | 2.8273 | 1.436 | 1.437 | 1.438 | 1.543 | 1.474 | 1.517 | Over-range | 60.01 | 1202 | 1565 | 1573 | 4340 | - - - | - - - | - - - | - - - | 1202 | 1565 | 1573 | 4340 | 923 | 642 | -152 | 1412 | - - - | - - - | - - - | - - - | 923 | 642 | -152 | 1412 | 1527 | 1701 | 1615 | 4843 | # # # | # # # | # # # | # # # | 0.787 | 0.92 | 0.974 | 0.896 | # # # | # # # | # # # | - - - | 0.794 | 0.925 | 0.995 | 0.906 | - - - | 0.325 | 1.91 | 1.78 | 1.81 | 1.73 | 1.72 | 1.84 | 9.96 | 9.39 | 18.6 | 0 | - - - | - - - | - - - | - - - | 1527 | 1701 | 1615 | 4843 | Over-range | 941 | 667 | 364 | 2148 | 184 | 180 | 330 | 1619 | 1205 | 1565 | 1570 | 4341 | 1205 | 1565 | 1570 | 4341 | - - - | - - - | - - - | - - -
5/6/2026 | 10:00:00 PM | 282.49 | 280.75 | 278.79 | 489.07 | 483.39 | 485.96 | 5.3754 | 5.9883 | 5.7807 | 2.8371 | 1.436 | 1.437 | 1.438 | 1.543 | 1.472 | 1.529 | Over-range | 60.02 | 1196 | 1541 | 1571 | 4308 | - - - | - - - | - - - | - - - | 1196 | 1541 | 1571 | 4308 | 916 | 648 | -138 | 1425 | - - - | - - - | - - - | - - - | 916 | 648 | -138 | 1425 | 1518 | 1681 | 1612 | 4811 | # # # | # # # | # # # | # # # | 0.788 | 0.916 | 0.975 | 0.895 | # # # | # # # | # # # | - - - | 0.795 | 0.922 | 0.996 | 0.906 | - - - | 0.331 | 1.94 | 1.79 | 1.83 | 1.76 | 1.73 | 1.86 | 10.15 | 9.59 | 18.85 | 0 | - - - | - - - | - - - | - - - | 1518 | 1681 | 1612 | 4811 | Over-range | 935 | 673 | 361 | 2143 | 187 | 181 | 333 | 1601 | 1199 | 1541 | 1568 | 4308 | 1199 | 1541 | 1568 | 4308 | - - - | - - - | - - - | - - -
5/6/2026 | 10:15:00 PM | 281.79 | 280.02 | 278.05 | 487.85 | 482.05 | 484.77 | 4.8678 | 5.0604 | 5.5097 | 2.8364 | 1.436 | 1.436 | 1.437 | 1.558 | 1.509 | 1.563 | Over-range | 60 | 1110 | 1216 | 1490 | 3816 | - - - | - - - | - - - | - - - | 1110 | 1216 | 1490 | 3816 | 770 | 647 | -1 | 1415 | - - - | - - - | - - - | - - - | 770 | 647 | -1 | 1415 | 1366 | 1397 | 1531 | 4293 | # # # | # # # | # # # | # # # | 0.813 | 0.871 | 0.973 | 0.889 | # # # | # # # | # # # | - - - | 0.821 | 0.878 | 0.997 | 0.902 | - - - | 0.371 | 1.99 | 1.84 | 1.89 | 1.8 | 1.79 | 1.92 | 11.54 | 11.61 | 19.56 | 0 | - - - | - - - | - - - | - - - | 1366 | 1397 | 1531 | 4293 | Over-range | 793 | 671 | 351 | 1965 | 188 | 177 | 330 | 1357 | 1111 | 1217 | 1487 | 3816 | 1111 | 1217 | 1487 | 3816 | - - - | - - - | - - - | - - -
5/6/2026 | 10:30:00 PM | 281.74 | 279.8 | 277.87 | 487.71 | 481.57 | 484.62 | 4.8351 | 4.9732 | 5.47 | 2.8181 | 1.435 | 1.436 | 1.436 | 1.561 | 1.477 | 1.526 | Over-range | 60 | 1108 | 1207 | 1482 | 3796 | - - - | - - - | - - - | - - - | 1108 | 1207 | 1482 | 3796 | 764 | 639 | 1 | 1404 | - - - | - - - | - - - | - - - | 764 | 639 | 1 | 1404 | 1359 | 1380 | 1519 | 4258 | # # # | # # # | # # # | # # # | 0.815 | 0.875 | 0.976 | 0.892 | # # # | # # # | # # # | - - - | 0.823 | 0.881 | 0.999 | 0.904 | - - - | 0.37 | 1.85 | 1.73 | 1.72 | 1.67 | 1.64 | 1.77 | 11.09 | 11.13 | 19.21 | 0 | - - - | - - - | - - - | - - - | 1359 | 1380 | 1519 | 4258 | Over-range | 786 | 662 | 334 | 1928 | 184 | 174 | 322 | 1315 | 1110 | 1205 | 1483 | 3798 | 1110 | 1205 | 1483 | 3798 | - - - | - - - | - - - | - - -
5/6/2026 | 10:45:00 PM | 282.6 | 280.58 | 278.69 | 489.16 | 482.9 | 486.09 | 5.2117 | 5.575 | 5.6541 | 2.7996 | 1.434 | 1.435 | 1.434 | 1.548 | 1.461 | 1.48 | Over-range | 60.01 | 1177 | 1415 | 1540 | 4132 | - - - | - - - | - - - | - - - | 1177 | 1415 | 1540 | 4132 | 862 | 645 | -67 | 1439 | - - - | - - - | - - - | - - - | 862 | 645 | -67 | 1439 | 1471 | 1564 | 1576 | 4611 | # # # | # # # | # # # | # # # | 0.8 | 0.905 | 0.977 | 0.896 | # # # | # # # | # # # | - - - | 0.799 | 0.903 | 0.984 | 0.897 | - - - | 0.348 | 1.68 | 1.56 | 1.53 | 1.51 | 1.46 | 1.56 | 10.08 | 9.55 | 18.42 | 0 | - - - | - - - | - - - | - - - | 1471 | 1564 | 1576 | 4611 | Over-range | 882 | 667 | 334 | 2047 | 188 | 167 | 321 | 1452 | 1187 | 1426 | 1555 | 4168 | 1187 | 1426 | 1555 | 4168 | - - - | - - - | - - - | - - -
5/6/2026 | 11:00:00 PM | 282.93 | 280.78 | 278.92 | 489.61 | 483.27 | 486.59 | 4.664 | 4.6647 | 5.3883 | 2.8058 | 1.433 | 1.433 | 1.431 | 1.565 | 1.508 | 1.54 | Over-range | 60.01 | 1082 | 1097 | 1463 | 3641 | - - - | - - - | - - - | - - - | 1082 | 1097 | 1463 | 3641 | 723 | 652 | 59 | 1433 | - - - | - - - | - - - | - - - | 723 | 652 | 59 | 1433 | 1315 | 1293 | 1502 | 4110 | # # # | # # # | # # # | # # # | 0.823 | 0.848 | 0.974 | 0.886 | # # # | # # # | # # # | - - - | 0.831 | 0.855 | 0.996 | 0.898 | - - - | 0.394 | 1.66 | 1.54 | 1.5 | 1.49 | 1.44 | 1.53 | 11.47 | 11.67 | 19.06 | 0 | - - - | - - - | - - - | - - - | 1315 | 1293 | 1502 | 4110 | Over-range | 746 | 673 | 340 | 1906 | 184 | 168 | 318 | 1250 | 1081 | 1098 | 1462 | 3641 | 1081 | 1098 | 1462 | 3641 | - - - | - - - | - - - | - - -
5/6/2026 | 11:15:00 PM | 283.03 | 280.63 | 278.78 | 489.66 | 482.84 | 486.64 | 5.1488 | 5.5812 | 5.6374 | 2.795 | 1.432 | 1.433 | 1.43 | 1.555 | 1.481 | 1.488 | Over-range | 59.99 | 1161 | 1398 | 1532 | 4091 | - - - | - - - | - - - | - - - | 1161 | 1398 | 1532 | 4091 | 854 | 646 | -71 | 1427 | - - - | - - - | - - - | - - - | 854 | 646 | -71 | 1427 | 1453 | 1553 | 1571 | 4577 | # # # | # # # | # # # | # # # | 0.799 | 0.9 | 0.976 | 0.894 | # # # | # # # | # # # | - - - | 0.805 | 0.906 | 0.997 | 0.905 | - - - | 0.349 | 1.66 | 1.57 | 1.5 | 1.5 | 1.46 | 1.54 | 10.25 | 9.96 | 18.59 | 0 | - - - | - - - | - - - | - - - | 1453 | 1553 | 1571 | 4577 | Over-range | 874 | 668 | 344 | 2052 | 184 | 171 | 321 | 1468 | 1161 | 1400 | 1531 | 4091 | 1161 | 1400 | 1531 | 4091 | - - - | - - - | - - - | - - -
5/6/2026 | 11:30:00 PM | 283.58 | 281.23 | 279.33 | 490.64 | 483.86 | 487.58 | 5.2716 | 5.7907 | 5.7075 | 2.7994 | 1.432 | 1.433 | 1.43 | 1.55 | 1.474 | 1.456 | Over-range | 60 | 1183 | 1482 | 1557 | 4222 | - - - | - - - | - - - | - - - | 1183 | 1482 | 1557 | 4222 | 895 | 651 | -103 | 1442 | - - - | - - - | - - - | - - - | 895 | 651 | -103 | 1442 | 1495 | 1628 | 1594 | 4717 | # # # | # # # | # # # | # # # | 0.791 | 0.91 | 0.977 | 0.895 | # # # | # # # | # # # | - - - | 0.799 | 0.915 | 0.997 | 0.906 | - - - | 0.341 | 1.69 | 1.56 | 1.52 | 1.51 | 1.48 | 1.56 | 10 | 9.47 | 18.44 | 0 | - - - | - - - | - - - | - - - | 1495 | 1628 | 1594 | 4717 | Over-range | 914 | 674 | 341 | 2103 | 185 | 175 | 324 | 1531 | 1186 | 1479 | 1558 | 4224 | 1186 | 1479 | 1558 | 4224 | - - - | - - - | - - - | - - -
5/6/2026 | 11:45:00 PM | 283.63 | 281.32 | 279.4 | 490.73 | 484.09 | 487.62 | 4.4943 | 4.3159 | 5.3028 | 2.8082 | 1.432 | 1.432 | 1.43 | 1.571 | 1.516 | 1.558 | Over-range | 60 | 1056 | 996 | 1441 | 3493 | - - - | - - - | - - - | - - - | 1056 | 996 | 1441 | 3493 | 685 | 658 | 110 | 1453 | - - - | - - - | - - - | - - - | 685 | 658 | 110 | 1453 | 1273 | 1209 | 1481 | 3963 | # # # | # # # | # # # | # # # | 0.83 | 0.824 | 0.973 | 0.881 | # # # | # # # | # # # | - - - | 0.839 | 0.832 | 0.996 | 0.895 | - - - | 0.416 | 1.65 | 1.57 | 1.52 | 1.5 | 1.47 | 1.54 | 11.95 | 12.4 | 19.32 | 0 | - - - | - - - | - - - | - - - | 1273 | 1209 | 1481 | 3963 | Over-range | 710 | 680 | 341 | 1871 | 185 | 172 | 318 | 1177 | 1057 | 994 | 1444 | 3495 | 1057 | 994 | 1444 | 3495 | - - - | - - - | - - - | - - -
5/7/2026 | 12:00:00 AM | 284.09 | 281.81 | 279.82 | 491.63 | 484.81 | 488.37 | 4.9627 | 5.0733 | 5.5243 | 2.8115 | 1.432 | 1.432 | 1.429 | 1.556 | 1.466 | 1.503 | Over-range | 60.01 | 1139 | 1250 | 1508 | 3897 | - - - | - - - | - - - | - - - | 1139 | 1250 | 1508 | 3897 | 807 | 662 | 18 | 1486 | - - - | - - - | - - - | - - - | 807 | 662 | 18 | 1486 | 1408 | 1427 | 1546 | 4380 | # # # | # # # | # # # | # # # | 0.809 | 0.876 | 0.976 | 0.89 | # # # | # # # | # # # | - - - | 0.808 | 0.876 | 0.986 | 0.892 | - - - | 0.382 | 1.68 | 1.56 | 1.53 | 1.51 | 1.48 | 1.56 | 10.76 | 10.84 | 19.08 | 0 | - - - | - - - | - - - | - - - | 1408 | 1427 | 1546 | 4380 | Over-range | 828 | 685 | 337 | 2000 | 185 | 177 | 325 | 1332 | 1154 | 1256 | 1521 | 3931 | 1154 | 1256 | 1521 | 3931 | - - - | - - - | - - - | - - -
5/7/2026 | 12:15:00 AM | 284.4 | 282.01 | 280.16 | 492.05 | 485.27 | 488.97 | 5.2969 | 5.8352 | 5.729 | 2.8099 | 1.431 | 1.432 | 1.429 | 1.553 | 1.471 | 1.46 | Over-range | 59.99 | 1186 | 1487 | 1566 | 4240 | - - - | - - - | - - - | - - - | 1186 | 1487 | 1566 | 4240 | 906 | 664 | -98 | 1471 | - - - | - - - | - - - | - - - | 906 | 664 | -98 | 1471 | 1505 | 1640 | 1605 | 4749 | # # # | # # # | # # # | # # # | 0.788 | 0.907 | 0.976 | 0.893 | # # # | # # # | # # # | - - - | 0.795 | 0.912 | 0.997 | 0.903 | - - - | 0.347 | 1.65 | 1.53 | 1.52 | 1.49 | 1.46 | 1.53 | 10.12 | 9.8 | 18.74 | 0 | - - - | - - - | - - - | - - - | 1505 | 1640 | 1605 | 4749 | Over-range | 925 | 688 | 349 | 2140 | 187 | 180 | 329 | 1551 | 1189 | 1485 | 1566 | 4241 | 1189 | 1485 | 1566 | 4241 | - - - | - - - | - - - | - - -
5/7/2026 | 12:30:00 AM | 284.76 | 282.49 | 280.57 | 492.74 | 486.17 | 489.55 | 5.48 | 6.1847 | 5.8406 | 2.8139 | 1.431 | 1.431 | 1.429 | 1.55 | 1.476 | 1.443 | Over-range | 60.02 | 1217 | 1602 | 1598 | 4417 | - - - | - - - | - - - | - - - | 1217 | 1602 | 1598 | 4417 | 957 | 668 | -145 | 1479 | - - - | - - - | - - - | - - - | 957 | 668 | -145 | 1479 | 1560 | 1746 | 1639 | 4944 | # # # | # # # | # # # | # # # | 0.78 | 0.918 | 0.975 | 0.893 | # # # | # # # | # # # | - - - | 0.786 | 0.923 | 0.996 | 0.903 | - - - | 0.335 | 1.68 | 1.54 | 1.5 | 1.49 | 1.45 | 1.52 | 9.78 | 9.28 | 18.43 | 0 | - - - | - - - | - - - | - - - | 1560 | 1746 | 1639 | 4944 | Over-range | 976 | 692 | 363 | 2222 | 192 | 180 | 330 | 1657 | 1219 | 1599 | 1600 | 4419 | 1219 | 1599 | 1600 | 4419 | - - - | - - - | - - - | - - -
5/7/2026 | 12:45:00 AM | 284.94 | 282.5 | 280.67 | 492.94 | 486.15 | 489.88 | 5.6891 | 6.587 | 5.9618 | 2.8119 | 1.431 | 1.431 | 1.429 | 1.549 | 1.48 | 1.444 | Over-range | 60 | 1250 | 1726 | 1628 | 4604 | - - - | - - - | - - - | - - - | 1250 | 1726 | 1628 | 4604 | 1015 | 667 | -198 | 1483 | - - - | - - - | - - - | - - - | 1015 | 667 | -198 | 1483 | 1621 | 1860 | 1673 | 5154 | # # # | # # # | # # # | # # # | 0.771 | 0.928 | 0.973 | 0.893 | # # # | # # # | # # # | - - - | 0.777 | 0.933 | 0.993 | 0.903 | - - - | 0.322 | 1.64 | 1.54 | 1.51 | 1.48 | 1.45 | 1.52 | 9.45 | 8.76 | 18.2 | 0 | - - - | - - - | - - - | - - - | 1621 | 1860 | 1673 | 5154 | Over-range | 1032 | 692 | 387 | 2316 | 186 | 185 | 332 | 1779 | 1254 | 1725 | 1627 | 4605 | 1254 | 1725 | 1627 | 4605 | - - - | - - - | - - - | - - -
5/7/2026 | 1:00:00 AM | 285.15 | 282.71 | 280.86 | 493.3 | 486.48 | 490.23 | 5.3334 | 5.8898 | 5.749 | 2.8145 | 1.431 | 1.431 | 1.428 | 1.552 | 1.466 | 1.459 | Over-range | 60.01 | 1194 | 1509 | 1576 | 4279 | - - - | - - - | - - - | - - - | 1194 | 1509 | 1576 | 4279 | 922 | 673 | -102 | 1492 | - - - | - - - | - - - | - - - | 922 | 673 | -102 | 1492 | 1520 | 1662 | 1614 | 4797 | # # # | # # # | # # # | # # # | 0.786 | 0.908 | 0.976 | 0.892 | # # # | # # # | # # # | - - - | 0.791 | 0.914 | 0.997 | 0.903 | - - - | 0.349 | 1.66 | 1.54 | 1.5 | 1.49 | 1.46 | 1.53 | 10.14 | 9.69 | 18.79 | 0 | - - - | - - - | - - - | - - - | 1520 | 1662 | 1614 | 4797 | Over-range | 940 | 696 | 349 | 2168 | 187 | 179 | 331 | 1571 | 1195 | 1511 | 1573 | 4279 | 1195 | 1511 | 1573 | 4279 | - - - | - - - | - - - | - - -
5/7/2026 | 1:15:00 AM | 285.06 | 282.57 | 280.84 | 493.04 | 486.38 | 490.16 | 5.4298 | 6.0736 | 5.8085 | 2.8154 | 1.431 | 1.431 | 1.428 | 1.552 | 1.472 | 1.45 | Over-range | 60 | 1210 | 1568 | 1592 | 4369 | - - - | - - - | - - - | - - - | 1210 | 1568 | 1592 | 4369 | 947 | 671 | -128 | 1489 | - - - | - - - | - - - | - - - | 947 | 671 | -128 | 1489 | 1548 | 1715 | 1631 | 4894 | # # # | # # # | # # # | # # # | 0.782 | 0.914 | 0.976 | 0.893 | # # # | # # # | # # # | - - - | 0.788 | 0.92 | 0.997 | 0.903 | - - - | 0.341 | 1.68 | 1.55 | 1.52 | 1.5 | 1.47 | 1.55 | 9.95 | 9.46 | 18.65 | 0 | - - - | - - - | - - - | - - - | 1548 | 1715 | 1631 | 4894 | Over-range | 965 | 695 | 357 | 2205 | 188 | 180 | 332 | 1626 | 1211 | 1570 | 1589 | 4370 | 1211 | 1570 | 1589 | 4370 | - - - | - - - | - - - | - - -
5/7/2026 | 1:30:00 AM | 285.21 | 282.72 | 281 | 493.31 | 486.65 | 490.43 | 5.3915 | 5.8681 | 5.7592 | 2.8125 | 1.431 | 1.431 | 1.429 | 1.543 | 1.467 | 1.45 | Over-range | 60.01 | 1210 | 1506 | 1581 | 4297 | - - - | - - - | - - - | - - - | 1210 | 1506 | 1581 | 4297 | 926 | 673 | -84 | 1514 | - - - | - - - | - - - | - - - | 926 | 673 | -84 | 1514 | 1536 | 1659 | 1618 | 4813 | # # # | # # # | # # # | # # # | 0.788 | 0.908 | 0.977 | 0.893 | # # # | # # # | # # # | - - - | 0.787 | 0.906 | 0.988 | 0.895 | - - - | 0.352 | 1.69 | 1.58 | 1.57 | 1.53 | 1.51 | 1.58 | 10.06 | 9.73 | 18.79 | 0 | - - - | - - - | - - - | - - - | 1536 | 1659 | 1618 | 4813 | Over-range | 946 | 695 | 346 | 2169 | 192 | 175 | 328 | 1548 | 1221 | 1517 | 1592 | 4330 | 1221 | 1517 | 1592 | 4330 | - - - | - - - | - - - | - - -
5/7/2026 | 1:45:00 AM | 285.58 | 282.87 | 281.15 | 493.88 | 486.74 | 490.94 | 5.3148 | 5.8753 | 5.7677 | 2.7888 | 1.432 | 1.431 | 1.43 | 1.503 | 1.453 | 1.315 | Over-range | 60.01 | 1193 | 1511 | 1591 | 4295 | - - - | - - - | - - - | - - - | 1193 | 1511 | 1591 | 4295 | 921 | 672 | -103 | 1489 | - - - | - - - | - - - | - - - | 921 | 672 | -103 | 1489 | 1518 | 1662 | 1622 | 4801 | # # # | # # # | # # # | # # # | 0.786 | 0.909 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.792 | 0.913 | 0.998 | 0.903 | - - - | 0.347 | 1.81 | 1.73 | 1.63 | 1.64 | 1.64 | 1.67 | 10.07 | 9.55 | 18.44 | 0 | - - - | - - - | - - - | - - - | 1518 | 1662 | 1622 | 4801 | Over-range | 938 | 692 | 315 | 2146 | 176 | 164 | 298 | 1546 | 1194 | 1508 | 1593 | 4295 | 1194 | 1508 | 1593 | 4295 | - - - | - - - | - - - | - - -
5/7/2026 | 2:00:00 AM | 285.69 | 283.01 | 281.29 | 494.07 | 487 | 491.15 | 5.3152 | 5.8431 | 5.7403 | 2.7919 | 1.433 | 1.431 | 1.431 | 1.499 | 1.452 | 1.342 | Over-range | 60.02 | 1194 | 1504 | 1584 | 4281 | - - - | - - - | - - - | - - - | 1194 | 1504 | 1584 | 4281 | 921 | 669 | -99 | 1491 | - - - | - - - | - - - | - - - | 921 | 669 | -99 | 1491 | 1518 | 1654 | 1615 | 4787 | # # # | # # # | # # # | # # # | 0.786 | 0.909 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.792 | 0.913 | 0.998 | 0.903 | - - - | 0.348 | 1.86 | 1.77 | 1.72 | 1.69 | 1.71 | 1.75 | 10.14 | 9.65 | 18.52 | 0 | - - - | - - - | - - - | - - - | 1518 | 1654 | 1615 | 4787 | Over-range | 939 | 688 | 314 | 2141 | 179 | 160 | 298 | 1537 | 1194 | 1502 | 1585 | 4281 | 1194 | 1502 | 1585 | 4281 | - - - | - - - | - - - | - - -
5/7/2026 | 2:15:00 AM | 285.6 | 282.94 | 281.2 | 493.91 | 486.92 | 490.95 | 5.3208 | 5.8481 | 5.7447 | 2.7955 | 1.433 | 1.431 | 1.432 | 1.498 | 1.451 | 1.352 | Over-range | 60 | 1195 | 1505 | 1584 | 4284 | - - - | - - - | - - - | - - - | 1195 | 1505 | 1584 | 4284 | 923 | 670 | -99 | 1492 | - - - | - - - | - - - | - - - | 923 | 670 | -99 | 1492 | 1520 | 1655 | 1615 | 4790 | # # # | # # # | # # # | # # # | 0.786 | 0.909 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.791 | 0.914 | 0.998 | 0.903 | - - - | 0.348 | 1.89 | 1.79 | 1.75 | 1.71 | 1.74 | 1.78 | 10.2 | 9.66 | 18.59 | 0 | - - - | - - - | - - - | - - - | 1520 | 1655 | 1615 | 4790 | Over-range | 939 | 688 | 315 | 2143 | 177 | 159 | 299 | 1538 | 1194 | 1507 | 1582 | 4283 | 1194 | 1507 | 1582 | 4283 | - - - | - - - | - - - | - - -
5/7/2026 | 2:30:00 AM | 285.63 | 282.99 | 281.35 | 493.97 | 487.1 | 491.11 | 5.3306 | 5.822 | 5.7327 | 2.7944 | 1.434 | 1.432 | 1.432 | 1.496 | 1.452 | 1.354 | Over-range | 60.01 | 1197 | 1496 | 1582 | 4276 | - - - | - - - | - - - | - - - | 1197 | 1496 | 1582 | 4276 | 923 | 671 | -88 | 1504 | - - - | - - - | - - - | - - - | 923 | 671 | -88 | 1504 | 1523 | 1648 | 1613 | 4783 | # # # | # # # | # # # | # # # | 0.787 | 0.908 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.792 | 0.913 | 0.998 | 0.903 | - - - | 0.352 | 1.95 | 1.82 | 1.77 | 1.75 | 1.78 | 1.82 | 10.21 | 9.77 | 18.6 | 0 | - - - | - - - | - - - | - - - | 1523 | 1648 | 1613 | 4783 | Over-range | 940 | 689 | 312 | 2143 | 181 | 160 | 299 | 1526 | 1197 | 1496 | 1583 | 4276 | 1197 | 1496 | 1583 | 4276 | - - - | - - - | - - - | - - -
5/7/2026 | 2:45:00 AM | 285.82 | 283.24 | 281.53 | 494.37 | 487.49 | 491.38 | 5.3586 | 5.8177 | 5.7304 | 2.8008 | 1.434 | 1.432 | 1.432 | 1.496 | 1.448 | 1.359 | Over-range | 60 | 1203 | 1495 | 1583 | 4281 | - - - | - - - | - - - | - - - | 1203 | 1495 | 1583 | 4281 | 930 | 673 | -77 | 1525 | - - - | - - - | - - - | - - - | 930 | 673 | -77 | 1525 | 1532 | 1648 | 1613 | 4793 | # # # | # # # | # # # | # # # | 0.786 | 0.907 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.792 | 0.911 | 0.999 | 0.902 | - - - | 0.356 | 1.95 | 1.82 | 1.81 | 1.76 | 1.78 | 1.82 | 10.24 | 9.81 | 18.66 | 0 | - - - | - - - | - - - | - - - | 1532 | 1648 | 1613 | 4793 | Over-range | 947 | 693 | 311 | 2154 | 180 | 164 | 301 | 1520 | 1206 | 1492 | 1585 | 4282 | 1206 | 1492 | 1585 | 4282 | - - - | - - - | - - - | - - -
5/7/2026 | 3:00:00 AM | 285.9 | 283.32 | 281.63 | 494.46 | 487.7 | 491.55 | 5.3601 | 5.8165 | 5.7336 | 2.8057 | 1.434 | 1.432 | 1.432 | 1.495 | 1.448 | 1.36 | Over-range | 60.01 | 1204 | 1494 | 1584 | 4283 | - - - | - - - | - - - | - - - | 1204 | 1494 | 1584 | 4283 | 931 | 675 | -77 | 1528 | - - - | - - - | - - - | - - - | 931 | 675 | -77 | 1528 | 1532 | 1648 | 1615 | 4795 | # # # | # # # | # # # | # # # | 0.786 | 0.907 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.791 | 0.911 | 0.999 | 0.902 | - - - | 0.357 | 1.92 | 1.82 | 1.82 | 1.76 | 1.79 | 1.83 | 10.26 | 9.85 | 18.71 | 0 | - - - | - - - | - - - | - - - | 1532 | 1648 | 1615 | 4795 | Over-range | 948 | 694 | 311 | 2157 | 181 | 164 | 301 | 1522 | 1205 | 1492 | 1586 | 4283 | 1205 | 1492 | 1586 | 4283 | - - - | - - - | - - - | - - -
5/7/2026 | 3:15:00 AM | 285.87 | 283.36 | 281.6 | 494.51 | 487.7 | 491.47 | 5.4108 | 5.8286 | 5.7233 | 2.785 | 1.434 | 1.432 | 1.432 | 1.492 | 1.444 | 1.383 | Over-range | 60.01 | 1215 | 1498 | 1579 | 4292 | - - - | - - - | - - - | - - - | 1215 | 1498 | 1579 | 4292 | 936 | 676 | -65 | 1546 | - - - | - - - | - - - | - - - | 936 | 676 | -65 | 1546 | 1545 | 1652 | 1612 | 4808 | # # # | # # # | # # # | # # # | 0.787 | 0.907 | 0.98 | 0.893 | # # # | # # # | # # # | - - - | 0.784 | 0.904 | 0.985 | 0.893 | - - - | 0.36 | 1.91 | 1.8 | 1.8 | 1.74 | 1.76 | 1.82 | 10.36 | 9.95 | 19.1 | 0 | - - - | - - - | - - - | - - - | 1545 | 1652 | 1612 | 4808 | Over-range | 954 | 695 | 321 | 2166 | 180 | 162 | 305 | 1512 | 1225 | 1519 | 1605 | 4350 | 1225 | 1519 | 1605 | 4350 | - - - | - - - | - - - | - - -
5/7/2026 | 3:30:00 AM | 285.06 | 282.68 | 280.87 | 493.16 | 486.55 | 490.12 | 5.2944 | 5.8156 | 5.7374 | 2.8013 | 1.436 | 1.434 | 1.431 | 1.484 | 1.438 | 1.465 | Over-range | 60.01 | 1189 | 1493 | 1578 | 4260 | - - - | - - - | - - - | - - - | 1189 | 1493 | 1578 | 4260 | 911 | 667 | -99 | 1479 | - - - | - - - | - - - | - - - | 911 | 667 | -99 | 1479 | 1509 | 1644 | 1611 | 4765 | # # # | # # # | # # # | # # # | 0.788 | 0.908 | 0.979 | 0.894 | # # # | # # # | # # # | - - - | 0.794 | 0.913 | 0.998 | 0.904 | - - - | 0.347 | 1.89 | 1.83 | 1.81 | 1.74 | 1.78 | 1.82 | 10.6 | 10 | 19.14 | 0 | - - - | - - - | - - - | - - - | 1509 | 1644 | 1611 | 4765 | Over-range | 929 | 688 | 327 | 2134 | 184 | 166 | 311 | 1538 | 1188 | 1495 | 1576 | 4259 | 1188 | 1495 | 1576 | 4259 | - - - | - - - | - - - | - - -
5/7/2026 | 3:45:00 AM | 285.29 | 282.96 | 281.3 | 493.51 | 487.28 | 490.66 | 5.2891 | 5.8063 | 5.7467 | 2.8 | 1.434 | 1.433 | 1.431 | 1.48 | 1.437 | 1.525 | Over-range | 60 | 1187 | 1490 | 1582 | 4259 | - - - | - - - | - - - | - - - | 1187 | 1490 | 1582 | 4259 | 912 | 671 | -89 | 1493 | - - - | - - - | - - - | - - - | 912 | 671 | -89 | 1493 | 1509 | 1643 | 1617 | 4768 | # # # | # # # | # # # | # # # | 0.787 | 0.907 | 0.978 | 0.893 | # # # | # # # | # # # | - - - | 0.793 | 0.912 | 0.998 | 0.903 | - - - | 0.351 | 1.96 | 1.9 | 1.95 | 1.81 | 1.89 | 1.92 | 10.91 | 10.42 | 19.65 | 0 | - - - | - - - | - - - | - - - | 1509 | 1643 | 1617 | 4768 | Over-range | 931 | 693 | 334 | 2145 | 189 | 172 | 321 | 1541 | 1186 | 1491 | 1580 | 4257 | 1186 | 1491 | 1580 | 4257 | - - - | - - - | - - - | - - -
5/7/2026 | 4:00:00 AM | 285.53 | 283.2 | 281.53 | 494.01 | 487.6 | 491.06 | 5.3011 | 5.8358 | 5.7535 | 2.7931 | 1.434 | 1.432 | 1.431 | 1.482 | 1.437 | 1.48 | Over-range | 60.02 | 1190 | 1500 | 1586 | 4276 | - - - | - - - | - - - | - - - | 1190 | 1500 | 1586 | 4276 | 916 | 674 | -93 | 1496 | - - - | - - - | - - - | - - - | 916 | 674 | -93 | 1496 | 1514 | 1653 | 1620 | 4786 | # # # | # # # | # # # | # # # | 0.786 | 0.907 | 0.979 | 0.893 | # # # | # # # | # # # | - - - | 0.792 | 0.912 | 0.998 | 0.903 | - - - | 0.35 | 1.9 | 1.82 | 1.82 | 1.73 | 1.79 | 1.82 | 10.64 | 10.13 | 19.31 | 0 | - - - | - - - | - - - | - - - | 1514 | 1653 | 1620 | 4786 | Over-range | 935 | 695 | 330 | 2151 | 187 | 168 | 316 | 1545 | 1189 | 1500 | 1585 | 4275 | 1189 | 1500 | 1585 | 4275 | - - - | - - - | - - - | - - -
5/7/2026 | 4:15:00 AM | 285.51 | 283.07 | 281.52 | 493.86 | 487.46 | 491.08 | 5.3392 | 5.8333 | 5.7395 | 2.7809 | 1.434 | 1.432 | 1.431 | 1.483 | 1.437 | 1.423 | Over-range | 60 | 1199 | 1498 | 1584 | 4281 | - - - | - - - | - - - | - - - | 1199 | 1498 | 1584 | 4281 | 923 | 674 | -80 | 1516 | - - - | - - - | - - - | - - - | 923 | 674 | -80 | 1516 | 1524 | 1651 | 1616 | 4791 | # # # | # # # | # # # | # # # | 0.787 | 0.908 | 0.98 | 0.893 | # # # | # # # | # # # | - - - | 0.792 | 0.912 | 0.999 | 0.903 | - - - | 0.354 | 1.88 | 1.78 | 1.76 | 1.7 | 1.73 | 1.78 | 10.44 | 9.93 | 19.06 | 0 | - - - | - - - | - - - | - - - | 1524 | 1651 | 1616 | 4791 | Over-range | 941 | 694 | 320 | 2151 | 182 | 165 | 309 | 1526 | 1199 | 1501 | 1581 | 4280 | 1199 | 1501 | 1581 | 4280 | - - - | - - - | - - - | - - -
5/7/2026 | 4:30:00 AM | 285.32 | 282.97 | 281.35 | 493.59 | 487.31 | 490.73 | 5.3476 | 5.8332 | 5.74 | 2.782 | 1.434 | 1.432 | 1.431 | 1.483 | 1.438 | 1.418 | Over-range | 60 | 1201 | 1499 | 1583 | 4283 | - - - | - - - | - - - | - - - | 1201 | 1499 | 1583 | 4283 | 923 | 671 | -78 | 1516 | - - - | - - - | - - - | - - - | 923 | 671 | -78 | 1516 | 1526 | 1651 | 1615 | 4791 | # # # | # # # | # # # | # # # | 0.787 | 0.908 | 0.98 | 0.894 | # # # | # # # | # # # | - - - | 0.793 | 0.913 | 0.999 | 0.903 | - - - | 0.354 | 1.86 | 1.76 | 1.76 | 1.69 | 1.72 | 1.77 | 10.35 | 9.87 | 18.96 | 0 | - - - | - - - | - - - | - - - | 1526 | 1651 | 1615 | 4791 | Over-range | 942 | 691 | 318 | 2148 | 184 | 165 | 308 | 1523 | 1201 | 1498 | 1584 | 4283 | 1201 | 1498 | 1584 | 4283 | - - - | - - - | - - - | - - -
5/7/2026 | 4:45:00 AM | 285.21 | 282.83 | 281.25 | 493.39 | 487.03 | 490.58 | 5.3412 | 5.8211 | 5.7313 | 2.7783 | 1.434 | 1.432 | 1.431 | 1.482 | 1.439 | 1.406 | Over-range | 60 | 1200 | 1495 | 1581 | 4275 | - - - | - - - | - - - | - - - | 1200 | 1495 | 1581 | 4275 | 921 | 670 | -78 | 1512 | - - - | - - - | - - - | - - - | 921 | 670 | -78 | 1512 | 1523 | 1646 | 1612 | 4782 | # # # | # # # | # # # | # # # | 0.788 | 0.908 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.793 | 0.913 | 0.999 | 0.903 | - - - | 0.354 | 1.86 | 1.77 | 1.77 | 1.7 | 1.73 | 1.78 | 10.28 | 9.84 | 18.88 | 0 | - - - | - - - | - - - | - - - | 1523 | 1646 | 1612 | 4782 | Over-range | 939 | 690 | 317 | 2141 | 183 | 163 | 306 | 1517 | 1199 | 1496 | 1580 | 4275 | 1199 | 1496 | 1580 | 4275 | - - - | - - - | - - - | - - -
5/7/2026 | 5:00:00 AM | 285.46 | 283.13 | 281.5 | 493.88 | 487.53 | 490.98 | 5.4204 | 5.8188 | 5.7485 | 2.7842 | 1.434 | 1.432 | 1.431 | 1.479 | 1.438 | 1.418 | Over-range | 60.02 | 1220 | 1494 | 1585 | 4299 | - - - | - - - | - - - | - - - | 1220 | 1494 | 1585 | 4299 | 932 | 672 | -54 | 1549 | - - - | - - - | - - - | - - - | 932 | 672 | -54 | 1549 | 1545 | 1647 | 1618 | 4811 | # # # | # # # | # # # | # # # | 0.789 | 0.907 | 0.98 | 0.894 | # # # | # # # | # # # | - - - | 0.788 | 0.904 | 0.979 | 0.892 | - - - | 0.36 | 1.88 | 1.78 | 1.79 | 1.71 | 1.75 | 1.8 | 10.18 | 9.93 | 18.97 | 0 | - - - | - - - | - - - | - - - | 1545 | 1647 | 1618 | 4811 | Over-range | 949 | 693 | 324 | 2159 | 178 | 170 | 310 | 1500 | 1235 | 1502 | 1610 | 4347 | 1235 | 1502 | 1610 | 4347 | - - - | - - - | - - - | - - -
5/7/2026 | 5:15:00 AM | 285.03 | 282.78 | 281.06 | 493.18 | 486.9 | 490.19 | 5.3454 | 5.8273 | 5.7363 | 2.7851 | 1.435 | 1.433 | 1.432 | 1.48 | 1.444 | 1.428 | Over-range | 60 | 1200 | 1497 | 1580 | 4277 | - - - | - - - | - - - | - - - | 1200 | 1497 | 1580 | 4277 | 922 | 668 | -78 | 1511 | - - - | - - - | - - - | - - - | 922 | 668 | -78 | 1511 | 1524 | 1648 | 1612 | 4784 | # # # | # # # | # # # | # # # | 0.787 | 0.908 | 0.98 | 0.894 | # # # | # # # | # # # | - - - | 0.793 | 0.913 | 0.999 | 0.903 | - - - | 0.353 | 1.93 | 1.81 | 1.83 | 1.74 | 1.77 | 1.84 | 10.23 | 9.87 | 18.88 | 0 | - - - | - - - | - - - | - - - | 1524 | 1648 | 1612 | 4784 | Over-range | 939 | 689 | 318 | 2142 | 177 | 168 | 308 | 1519 | 1202 | 1496 | 1579 | 4277 | 1202 | 1496 | 1579 | 4277 | - - - | - - - | - - - | - - -
5/7/2026 | 5:30:00 AM | 284.8 | 282.57 | 280.91 | 492.8 | 486.56 | 489.89 | 5.3414 | 5.824 | 5.7326 | 2.7807 | 1.435 | 1.434 | 1.432 | 1.48 | 1.446 | 1.424 | Over-range | 60.01 | 1199 | 1496 | 1579 | 4274 | - - - | - - - | - - - | - - - | 1199 | 1496 | 1579 | 4274 | 920 | 664 | -80 | 1503 | - - - | - - - | - - - | - - - | 920 | 664 | -80 | 1503 | 1521 | 1646 | 1610 | 4777 | # # # | # # # | # # # | # # # | 0.788 | 0.909 | 0.98 | 0.895 | # # # | # # # | # # # | - - - | 0.795 | 0.914 | 0.999 | 0.904 | - - - | 0.352 | 1.91 | 1.83 | 1.84 | 1.74 | 1.78 | 1.84 | 10.18 | 9.83 | 18.82 | 0 | - - - | - - - | - - - | - - - | 1521 | 1646 | 1610 | 4777 | Over-range | 936 | 685 | 318 | 2134 | 172 | 169 | 307 | 1515 | 1203 | 1495 | 1576 | 4274 | 1203 | 1495 | 1576 | 4274 | - - - | - - - | - - - | - - -
5/7/2026 | 5:45:00 AM | 284.09 | 281.82 | 280.13 | 491.59 | 485.17 | 488.62 | 5.3304 | 5.8181 | 5.7227 | 2.7671 | 1.435 | 1.433 | 1.432 | 1.481 | 1.447 | 1.428 | Over-range | 60 | 1197 | 1495 | 1572 | 4263 | - - - | - - - | - - - | - - - | 1197 | 1495 | 1572 | 4263 | 910 | 655 | -86 | 1478 | - - - | - - - | - - - | - - - | 910 | 655 | -86 | 1478 | 1514 | 1640 | 1603 | 4757 | # # # | # # # | # # # | # # # | 0.79 | 0.912 | 0.981 | 0.896 | # # # | # # # | # # # | - - - | 0.796 | 0.916 | 0.999 | 0.905 | - - - | 0.347 | 1.9 | 1.83 | 1.81 | 1.72 | 1.77 | 1.83 | 10.07 | 9.65 | 18.64 | 0 | - - - | - - - | - - - | - - - | 1514 | 1640 | 1603 | 4757 | Over-range | 928 | 674 | 315 | 2110 | 177 | 161 | 303 | 1506 | 1197 | 1496 | 1571 | 4263 | 1197 | 1496 | 1571 | 4263 | - - - | - - - | - - - | - - -
5/7/2026 | 6:00:00 AM | 283.67 | 281.46 | 279.89 | 490.83 | 484.74 | 488.03 | 5.3194 | 5.8043 | 5.7183 | 2.7632 | 1.435 | 1.434 | 1.432 | 1.481 | 1.45 | 1.417 | Over-range | 60.02 | 1195 | 1491 | 1570 | 4255 | - - - | - - - | - - - | - - - | 1195 | 1491 | 1570 | 4255 | 904 | 649 | -87 | 1465 | - - - | - - - | - - - | - - - | 904 | 649 | -87 | 1465 | 1509 | 1634 | 1600 | 4743 | # # # | # # # | # # # | # # # | 0.792 | 0.913 | 0.981 | 0.897 | # # # | # # # | # # # | - - - | 0.797 | 0.917 | 0.999 | 0.906 | - - - | 0.344 | 1.92 | 1.88 | 1.87 | 1.77 | 1.81 | 1.87 | 9.99 | 9.59 | 18.49 | 0 | - - - | - - - | - - - | - - - | 1509 | 1634 | 1600 | 4743 | Over-range | 922 | 668 | 313 | 2096 | 177 | 160 | 300 | 1498 | 1195 | 1490 | 1571 | 4255 | 1195 | 1490 | 1571 | 4255 | - - - | - - - | - - - | - - -
5/7/2026 | 6:15:00 AM | 282.8 | 280.63 | 278.89 | 489.4 | 483.12 | 486.4 | 5.3121 | 5.7963 | 5.7052 | 2.753 | 1.436 | 1.436 | 1.433 | 1.479 | 1.46 | 1.412 | Over-range | 59.98 | 1192 | 1487 | 1561 | 4240 | - - - | - - - | - - - | - - - | 1192 | 1487 | 1561 | 4240 | 897 | 639 | -90 | 1445 | - - - | - - - | - - - | - - - | 897 | 639 | -90 | 1445 | 1502 | 1627 | 1591 | 4720 | # # # | # # # | # # # | # # # | 0.793 | 0.915 | 0.981 | 0.898 | # # # | # # # | # # # | - - - | 0.798 | 0.918 | 0.998 | 0.907 | - - - | 0.341 | 2.04 | 1.98 | 2.02 | 1.87 | 1.93 | 2.01 | 9.89 | 9.49 | 18.32 | 0 | - - - | - - - | - - - | - - - | 1502 | 1627 | 1591 | 4720 | Over-range | 915 | 658 | 310 | 2074 | 177 | 156 | 296 | 1487 | 1191 | 1486 | 1562 | 4240 | 1191 | 1486 | 1562 | 4240 | - - - | - - - | - - - | - - -
5/7/2026 | 6:30:00 AM | 281.95 | 279.77 | 278.14 | 487.89 | 481.71 | 485.06 | 5.3102 | 5.8042 | 5.7013 | 2.7444 | 1.436 | 1.437 | 1.434 | 1.48 | 1.466 | 1.424 | Over-range | 59.99 | 1191 | 1490 | 1555 | 4236 | - - - | - - - | - - - | - - - | 1191 | 1490 | 1555 | 4236 | 891 | 628 | -98 | 1420 | - - - | - - - | - - - | - - - | 891 | 628 | -98 | 1420 | 1497 | 1624 | 1586 | 4707 | # # # | # # # | # # # | # # # | 0.796 | 0.917 | 0.981 | 0.9 | # # # | # # # | # # # | - - - | 0.8 | 0.922 | 0.998 | 0.908 | - - - | 0.335 | 2.06 | 2.02 | 2.05 | 1.88 | 1.95 | 2.03 | 9.82 | 9.35 | 18.19 | 0 | - - - | - - - | - - - | - - - | 1497 | 1624 | 1586 | 4707 | Over-range | 907 | 646 | 309 | 2052 | 170 | 154 | 293 | 1482 | 1191 | 1491 | 1553 | 4235 | 1191 | 1491 | 1553 | 4235 | - - - | - - - | - - - | - - -
5/7/2026 | 6:45:00 AM | 281.6 | 279.38 | 277.72 | 487.25 | 480.99 | 484.39 | 5.3866 | 5.8008 | 5.7113 | 2.7423 | 1.436 | 1.437 | 1.433 | 1.477 | 1.468 | 1.427 | Over-range | 60 | 1210 | 1489 | 1555 | 4254 | - - - | - - - | - - - | - - - | 1210 | 1489 | 1555 | 4254 | 896 | 621 | -80 | 1436 | - - - | - - - | - - - | - - - | 896 | 621 | -80 | 1436 | 1515 | 1621 | 1586 | 4722 | # # # | # # # | # # # | # # # | 0.799 | 0.919 | 0.98 | 0.901 | # # # | # # # | # # # | - - - | 0.797 | 0.916 | 0.989 | 0.902 | - - - | 0.338 | 2 | 1.97 | 2 | 1.84 | 1.9 | 1.98 | 9.67 | 9.22 | 18.22 | 0 | - - - | - - - | - - - | - - - | 1515 | 1621 | 1586 | 4722 | Over-range | 911 | 640 | 313 | 2050 | 165 | 156 | 293 | 1457 | 1224 | 1499 | 1564 | 4286 | 1224 | 1499 | 1564 | 4286 | - - - | - - - | - - - | - - -
5/7/2026 | 7:00:00 AM | 281.54 | 279.45 | 277.84 | 487.2 | 481.24 | 484.42 | 5.3119 | 5.8164 | 5.706 | 2.745 | 1.436 | 1.437 | 1.433 | 1.479 | 1.472 | 1.43 | Over-range | 60.01 | 1191 | 1494 | 1555 | 4240 | - - - | - - - | - - - | - - - | 1191 | 1494 | 1555 | 4240 | 889 | 621 | -104 | 1406 | - - - | - - - | - - - | - - - | 889 | 621 | -104 | 1406 | 1495 | 1625 | 1585 | 4706 | # # # | # # # | # # # | # # # | 0.797 | 0.919 | 0.981 | 0.901 | # # # | # # # | # # # | - - - | 0.802 | 0.923 | 0.998 | 0.909 | - - - | 0.332 | 1.98 | 1.95 | 1.95 | 1.81 | 1.85 | 1.94 | 9.76 | 9.21 | 18.13 | 0 | - - - | - - - | - - - | - - - | 1495 | 1625 | 1585 | 4706 | Over-range | 904 | 640 | 310 | 2043 | 164 | 157 | 292 | 1482 | 1194 | 1494 | 1552 | 4240 | 1194 | 1494 | 1552 | 4240 | - - - | - - - | - - - | - - -
5/7/2026 | 7:15:00 AM | 282.31 | 280.27 | 278.63 | 488.58 | 482.61 | 485.79 | 4.5815 | 4.4194 | 5.3301 | 2.7594 | 1.436 | 1.437 | 1.433 | 1.477 | 1.465 | 1.432 | Over-range | 60 | 1072 | 1032 | 1449 | 3553 | - - - | - - - | - - - | - - - | 1072 | 1032 | 1449 | 3553 | 697 | 640 | 105 | 1442 | - - - | - - - | - - - | - - - | 697 | 640 | 105 | 1442 | 1291 | 1228 | 1484 | 4003 | # # # | # # # | # # # | # # # | 0.831 | 0.84 | 0.976 | 0.888 | # # # | # # # | # # # | - - - | 0.838 | 0.848 | 0.996 | 0.899 | - - - | 0.406 | 2.03 | 1.99 | 1.99 | 1.85 | 1.89 | 1.98 | 11.68 | 12.16 | 19.16 | 0 | - - - | - - - | - - - | - - - | 1291 | 1228 | 1484 | 4003 | Over-range | 717 | 658 | 321 | 1843 | 169 | 152 | 292 | 1143 | 1072 | 1034 | 1447 | 3552 | 1072 | 1034 | 1447 | 3552 | - - - | - - - | - - - | - - -
5/7/2026 | 7:30:00 AM | 282.6 | 280.59 | 278.88 | 489.15 | 483.09 | 486.25 | 4.783 | 4.7786 | 5.4246 | 2.7534 | 1.436 | 1.437 | 1.432 | 1.476 | 1.43 | 1.424 | Over-range | 60.01 | 1107 | 1166 | 1483 | 3755 | - - - | - - - | - - - | - - - | 1107 | 1166 | 1483 | 3755 | 757 | 640 | 49 | 1446 | - - - | - - - | - - - | - - - | 757 | 640 | 49 | 1446 | 1351 | 1340 | 1513 | 4204 | # # # | # # # | # # # | # # # | 0.819 | 0.87 | 0.98 | 0.893 | # # # | # # # | # # # | - - - | 0.826 | 0.876 | 0.999 | 0.904 | - - - | 0.385 | 2.06 | 1.97 | 2.01 | 1.86 | 1.91 | 2 | 11.11 | 11.21 | 19.07 | 0 | - - - | - - - | - - - | - - - | 1351 | 1340 | 1513 | 4204 | Over-range | 775 | 659 | 300 | 1889 | 167 | 156 | 295 | 1215 | 1109 | 1166 | 1479 | 3755 | 1109 | 1166 | 1479 | 3755 | - - - | - - - | - - - | - - -
5/7/2026 | 7:45:00 AM | 282.36 | 280.25 | 278.59 | 488.59 | 482.55 | 485.84 | 4.852 | 4.9143 | 5.4544 | 2.7429 | 1.436 | 1.437 | 1.432 | 1.477 | 1.437 | 1.395 | Over-range | 60.01 | 1119 | 1212 | 1491 | 3822 | - - - | - - - | - - - | - - - | 1119 | 1212 | 1491 | 3822 | 773 | 635 | 26 | 1435 | - - - | - - - | - - - | - - - | 773 | 635 | 26 | 1435 | 1370 | 1377 | 1520 | 4266 | # # # | # # # | # # # | # # # | 0.817 | 0.88 | 0.982 | 0.896 | # # # | # # # | # # # | - - - | 0.823 | 0.885 | 1 | 0.906 | - - - | 0.375 | 2 | 1.95 | 1.92 | 1.82 | 1.85 | 1.93 | 10.77 | 10.71 | 18.74 | 0 | - - - | - - - | - - - | - - - | 1370 | 1377 | 1520 | 4266 | Over-range | 791 | 653 | 291 | 1896 | 166 | 153 | 289 | 1240 | 1120 | 1212 | 1489 | 3821 | 1120 | 1212 | 1489 | 3821 | - - - | - - - | - - - | - - -
5/7/2026 | 8:00:00 AM | 282.18 | 280.08 | 278.4 | 488.32 | 482.19 | 485.54 | 5.3431 | 5.8949 | 5.707 | 2.7235 | 1.436 | 1.436 | 1.432 | 1.477 | 1.47 | 1.394 | Over-range | 60.02 | 1196 | 1513 | 1557 | 4266 | - - - | - - - | - - - | - - - | 1196 | 1513 | 1557 | 4266 | 898 | 629 | -109 | 1417 | - - - | - - - | - - - | - - - | 898 | 629 | -109 | 1417 | 1506 | 1646 | 1588 | 4741 | # # # | # # # | # # # | # # # | 0.794 | 0.919 | 0.98 | 0.9 | # # # | # # # | # # # | - - - | 0.799 | 0.923 | 0.997 | 0.908 | - - - | 0.332 | 1.96 | 1.92 | 1.88 | 1.78 | 1.81 | 1.89 | 9.74 | 9.2 | 18.11 | 0 | - - - | - - - | - - - | - - - | 1506 | 1646 | 1588 | 4741 | Over-range | 915 | 647 | 315 | 2069 | 175 | 152 | 290 | 1504 | 1195 | 1513 | 1557 | 4265 | 1195 | 1513 | 1557 | 4265 | - - - | - - - | - - - | - - -
5/7/2026 | 8:15:00 AM | 281.86 | 279.63 | 278.05 | 487.63 | 481.43 | 485.05 | 5.3915 | 5.9852 | 5.7491 | 2.7306 | 1.436 | 1.437 | 1.432 | 1.478 | 1.473 | 1.399 | Over-range | 60 | 1204 | 1543 | 1567 | 4313 | - - - | - - - | - - - | - - - | 1204 | 1543 | 1567 | 4313 | 910 | 623 | -124 | 1408 | - - - | - - - | - - - | - - - | 910 | 623 | -124 | 1408 | 1519 | 1671 | 1598 | 4788 | # # # | # # # | # # # | # # # | 0.793 | 0.923 | 0.98 | 0.901 | # # # | # # # | # # # | - - - | 0.798 | 0.927 | 0.997 | 0.909 | - - - | 0.327 | 1.99 | 1.94 | 1.91 | 1.79 | 1.84 | 1.91 | 9.62 | 8.93 | 17.78 | 0 | - - - | - - - | - - - | - - - | 1519 | 1671 | 1598 | 4788 | Over-range | 926 | 641 | 315 | 2079 | 172 | 154 | 287 | 1529 | 1206 | 1540 | 1568 | 4314 | 1206 | 1540 | 1568 | 4314 | - - - | - - - | - - - | - - -
5/7/2026 | 8:30:00 AM | 281.61 | 279.46 | 277.76 | 487.3 | 481.05 | 484.52 | 5.4018 | 5.8382 | 5.7002 | 2.7254 | 1.436 | 1.437 | 1.432 | 1.476 | 1.473 | 1.392 | Over-range | 60.01 | 1213 | 1501 | 1552 | 4267 | - - - | - - - | - - - | - - - | 1213 | 1501 | 1552 | 4267 | 899 | 619 | -88 | 1429 | - - - | - - - | - - - | - - - | 899 | 619 | -88 | 1429 | 1519 | 1631 | 1583 | 4734 | # # # | # # # | # # # | # # # | 0.799 | 0.92 | 0.981 | 0.901 | # # # | # # # | # # # | - - - | 0.796 | 0.917 | 0.986 | 0.901 | - - - | 0.335 | 1.97 | 1.92 | 1.91 | 1.8 | 1.83 | 1.91 | 9.55 | 9.05 | 17.95 | 0 | - - - | - - - | - - - | - - - | 1519 | 1631 | 1583 | 4734 | Over-range | 914 | 638 | 310 | 2050 | 165 | 155 | 288 | 1464 | 1226 | 1511 | 1576 | 4314 | 1226 | 1511 | 1576 | 4314 | - - - | - - - | - - - | - - -
5/7/2026 | 8:45:00 AM | 282.4 | 280.11 | 278.45 | 488.6 | 482.11 | 485.85 | 5.1609 | 5.5634 | 5.6213 | 2.7322 | 1.436 | 1.437 | 1.432 | 1.477 | 1.483 | 1.401 | Over-range | 60.02 | 1165 | 1388 | 1531 | 4085 | - - - | - - - | - - - | - - - | 1165 | 1388 | 1531 | 4085 | 848 | 629 | -53 | 1423 | - - - | - - - | - - - | - - - | 848 | 629 | -53 | 1423 | 1452 | 1539 | 1564 | 4555 | # # # | # # # | # # # | # # # | 0.803 | 0.902 | 0.979 | 0.897 | # # # | # # # | # # # | - - - | 0.809 | 0.907 | 0.996 | 0.906 | - - - | 0.348 | 1.99 | 1.95 | 1.88 | 1.8 | 1.83 | 1.91 | 10.19 | 9.91 | 18.06 | 0 | - - - | - - - | - - - | - - - | 1452 | 1539 | 1564 | 4555 | Over-range | 864 | 648 | 316 | 2013 | 166 | 155 | 286 | 1417 | 1168 | 1388 | 1530 | 4085 | 1168 | 1388 | 1530 | 4085 | - - - | - - - | - - - | - - -
5/7/2026 | 9:00:00 AM | 282.16 | 279.85 | 278.15 | 488.18 | 481.62 | 485.38 | 4.6215 | 4.4875 | 5.3325 | 2.7395 | 1.436 | 1.437 | 1.432 | 1.478 | 1.444 | 1.403 | Over-range | 60.02 | 1081 | 1066 | 1452 | 3599 | - - - | - - - | - - - | - - - | 1081 | 1066 | 1452 | 3599 | 706 | 632 | 84 | 1422 | - - - | - - - | - - - | - - - | 706 | 632 | 84 | 1422 | 1303 | 1250 | 1483 | 4036 | # # # | # # # | # # # | # # # | 0.83 | 0.853 | 0.979 | 0.892 | # # # | # # # | # # # | - - - | 0.837 | 0.859 | 0.997 | 0.902 | - - - | 0.395 | 1.99 | 1.96 | 1.89 | 1.81 | 1.84 | 1.92 | 11.3 | 11.66 | 18.76 | 0 | - - - | - - - | - - - | - - - | 1303 | 1250 | 1483 | 4036 | Over-range | 726 | 649 | 301 | 1826 | 168 | 148 | 284 | 1143 | 1080 | 1068 | 1450 | 3598 | 1080 | 1068 | 1450 | 3598 | - - - | - - - | - - - | - - -
5/7/2026 | 9:15:00 AM | 281.77 | 279.42 | 277.77 | 487.41 | 480.98 | 484.71 | 4.6184 | 4.5017 | 5.3156 | 2.7357 | 1.436 | 1.437 | 1.432 | 1.478 | 1.466 | 1.409 | Over-range | 59.99 | 1078 | 1058 | 1443 | 3578 | - - - | - - - | - - - | - - - | 1078 | 1058 | 1443 | 3578 | 701 | 628 | 84 | 1413 | - - - | - - - | - - - | - - - | 701 | 628 | 84 | 1413 | 1298 | 1244 | 1476 | 4018 | # # # | # # # | # # # | # # # | 0.831 | 0.85 | 0.978 | 0.891 | # # # | # # # | # # # | - - - | 0.837 | 0.856 | 0.996 | 0.901 | - - - | 0.395 | 1.98 | 1.91 | 1.88 | 1.8 | 1.83 | 1.9 | 11.36 | 11.72 | 18.68 | 0 | - - - | - - - | - - - | - - - | 1298 | 1244 | 1476 | 4018 | Over-range | 721 | 645 | 308 | 1825 | 169 | 148 | 282 | 1150 | 1077 | 1058 | 1443 | 3578 | 1077 | 1058 | 1443 | 3578 | - - - | - - - | - - - | - - -
5/7/2026 | 9:30:00 AM | 281.47 | 278.92 | 277.42 | 486.71 | 480.12 | 484.27 | 4.9333 | 5.4361 | 5.2677 | 2.5119 | 1.436 | 1.437 | 1.432 | 1.481 | 1.462 | 1.384 | Over-range | 60 | 1098 | 1366 | 1421 | 3885 | - - - | - - - | - - - | - - - | 1098 | 1366 | 1421 | 3885 | 821 | 614 | -65 | 1369 | - - - | - - - | - - - | - - - | 821 | 614 | -65 | 1369 | 1384 | 1508 | 1452 | 4343 | # # # | # # # | # # # | # # # | 0.794 | 0.906 | 0.979 | 0.895 | # # # | # # # | # # # | - - - | 0.794 | 0.903 | 0.992 | 0.897 | - - - | 0.352 | 1.96 | 1.93 | 1.89 | 1.78 | 1.84 | 1.9 | 10.22 | 9.73 | 18.75 | 0 | - - - | - - - | - - - | - - - | 1384 | 1508 | 1452 | 4343 | Over-range | 837 | 632 | 295 | 1938 | 163 | 149 | 273 | 1366 | 1103 | 1378 | 1423 | 3904 | 1103 | 1378 | 1423 | 3904 | - - - | - - - | - - - | - - -
5/7/2026 | 9:45:00 AM | 281.42 | 278.92 | 277.31 | 486.71 | 480.03 | 484.1 | 4.8926 | 5.1118 | 5.5204 | 2.7248 | 1.436 | 1.437 | 1.432 | 1.481 | 1.484 | 1.405 | Over-range | 60 | 1124 | 1243 | 1498 | 3865 | - - - | - - - | - - - | - - - | 1124 | 1243 | 1498 | 3865 | 763 | 619 | -7 | 1373 | - - - | - - - | - - - | - - - | 763 | 619 | -7 | 1373 | 1371 | 1404 | 1529 | 4304 | # # # | # # # | # # # | # # # | 0.82 | 0.885 | 0.979 | 0.898 | # # # | # # # | # # # | - - - | 0.826 | 0.89 | 0.996 | 0.907 | - - - | 0.355 | 1.95 | 1.94 | 1.86 | 1.78 | 1.83 | 1.88 | 10.84 | 10.55 | 18 | 0 | - - - | - - - | - - - | - - - | 1371 | 1404 | 1529 | 4304 | Over-range | 782 | 636 | 308 | 1893 | 171 | 147 | 281 | 1295 | 1123 | 1244 | 1496 | 3864 | 1123 | 1244 | 1496 | 3864 | - - - | - - - | - - - | - - -
5/7/2026 | 10:00:00 AM | 281.25 | 278.7 | 277.15 | 486.32 | 479.74 | 483.81 | 4.6794 | 4.4308 | 5.3631 | 3.1317 | 1.435 | 1.437 | 1.432 | 1.479 | 1.429 | 1.398 | Over-range | 60 | 1087 | 1033 | 1457 | 3577 | - - - | - - - | - - - | - - - | 1087 | 1033 | 1457 | 3577 | 722 | 647 | 30 | 1399 | - - - | - - - | - - - | - - - | 722 | 647 | 30 | 1399 | 1315 | 1233 | 1486 | 4034 | # # # | # # # | # # # | # # # | 0.827 | 0.838 | 0.981 | 0.887 | # # # | # # # | # # # | - - - | 0.833 | 0.846 | 0.999 | 0.897 | - - - | 0.391 | 1.96 | 1.91 | 1.87 | 1.77 | 1.82 | 1.88 | 10.95 | 12.27 | 18.69 | 0 | - - - | - - - | - - - | - - - | 1315 | 1233 | 1486 | 4034 | Over-range | 740 | 666 | 290 | 1859 | 162 | 156 | 283 | 1222 | 1088 | 1035 | 1454 | 3577 | 1088 | 1035 | 1454 | 3577 | - - - | - - - | - - - | - - -
5/7/2026 | 10:15:00 AM | 281.1 | 278.6 | 277 | 486.18 | 479.49 | 483.52 | 4.7975 | 3.9725 | 5.4473 | 4.1364 | 1.435 | 1.437 | 1.432 | 1.479 | 1.43 | 1.391 | Over-range | 60.01 | 1107 | 801 | 1482 | 3389 | - - - | - - - | - - - | - - - | 1107 | 801 | 1482 | 3389 | 753 | 743 | -5 | 1489 | - - - | - - - | - - - | - - - | 753 | 743 | -5 | 1489 | 1348 | 1106 | 1509 | 3963 | # # # | # # # | # # # | # # # | 0.821 | 0.724 | 0.982 | 0.855 | # # # | # # # | # # # | - - - | 0.827 | 0.733 | 1 | 0.866 | - - - | 0.439 | 1.94 | 1.89 | 1.88 | 1.76 | 1.82 | 1.87 | 10.64 | 15.4 | 18.47 | 0 | - - - | - - - | - - - | - - - | 1348 | 1106 | 1509 | 3963 | Over-range | 770 | 762 | 285 | 2055 | 162 | 172 | 284 | 1415 | 1108 | 802 | 1479 | 3389 | 1108 | 802 | 1479 | 3389 | - - - | - - - | - - - | - - -
5/7/2026 | 10:30:00 AM | 281.09 | 278.53 | 277.01 | 486.06 | 479.4 | 483.61 | 5.1713 | 4.4504 | 5.6153 | 4.1367 | 1.434 | 1.436 | 1.431 | 1.479 | 1.424 | 1.405 | Over-range | 60 | 1173 | 971 | 1523 | 3667 | - - - | - - - | - - - | - - - | 1173 | 971 | 1523 | 3667 | 837 | 734 | -58 | 1513 | - - - | - - - | - - - | - - - | 837 | 734 | -58 | 1513 | 1451 | 1234 | 1555 | 4240 | # # # | # # # | # # # | # # # | 0.808 | 0.786 | 0.98 | 0.865 | # # # | # # # | # # # | - - - | 0.807 | 0.789 | 0.988 | 0.868 | - - - | 0.413 | 1.91 | 1.91 | 1.87 | 1.75 | 1.82 | 1.86 | 9.92 | 14.47 | 18.12 | 0 | - - - | - - - | - - - | - - - | 1451 | 1234 | 1555 | 4240 | Over-range | 853 | 757 | 311 | 2128 | 163 | 183 | 287 | 1490 | 1188 | 975 | 1533 | 3696 | 1188 | 975 | 1533 | 3696 | - - - | - - - | - - - | - - -
5/7/2026 | 10:45:00 AM | 280.85 | 278.35 | 276.82 | 485.67 | 479.17 | 483.18 | 5.5822 | 5.3093 | 5.8671 | 4.1256 | 1.434 | 1.436 | 1.431 | 1.48 | 1.45 | 1.441 | Over-range | 60 | 1231 | 1271 | 1584 | 4085 | - - - | - - - | - - - | - - - | 1231 | 1271 | 1584 | 4085 | 957 | 728 | -214 | 1470 | - - - | - - - | - - - | - - - | 957 | 728 | -214 | 1470 | 1567 | 1477 | 1624 | 4668 | # # # | # # # | # # # | # # # | 0.785 | 0.861 | 0.975 | 0.875 | # # # | # # # | # # # | - - - | 0.79 | 0.868 | 0.991 | 0.884 | - - - | 0.36 | 1.92 | 1.92 | 1.87 | 1.75 | 1.82 | 1.87 | 9.13 | 12.32 | 17.53 | 0 | - - - | - - - | - - - | - - - | 1567 | 1477 | 1624 | 4668 | Over-range | 971 | 751 | 360 | 2259 | 163 | 186 | 288 | 1715 | 1233 | 1272 | 1580 | 4085 | 1233 | 1272 | 1580 | 4085 | - - - | - - - | - - - | - - -
5/7/2026 | 11:00:00 AM | 280.88 | 278.43 | 276.9 | 485.78 | 479.31 | 483.25 | 5.4107 | 4.999 | 5.7908 | 4.1345 | 1.435 | 1.437 | 1.432 | 1.479 | 1.433 | 1.458 | Over-range | 60 | 1203 | 1169 | 1568 | 3941 | - - - | - - - | - - - | - - - | 1203 | 1169 | 1568 | 3941 | 913 | 730 | -166 | 1476 | - - - | - - - | - - - | - - - | 913 | 730 | -166 | 1476 | 1520 | 1391 | 1603 | 4514 | # # # | # # # | # # # | # # # | 0.792 | 0.84 | 0.978 | 0.873 | # # # | # # # | # # # | - - - | 0.797 | 0.848 | 0.994 | 0.882 | - - - | 0.375 | 1.96 | 1.96 | 1.92 | 1.79 | 1.86 | 1.91 | 9.48 | 12.97 | 17.73 | 0 | - - - | - - - | - - - | - - - | 1520 | 1391 | 1603 | 4514 | Over-range | 928 | 753 | 335 | 2202 | 164 | 187 | 290 | 1634 | 1207 | 1168 | 1566 | 3942 | 1207 | 1168 | 1566 | 3942 | - - - | - - - | - - - | - - -
5/7/2026 | 11:15:00 AM | 281.18 | 278.7 | 277.3 | 486.21 | 479.92 | 483.9 | 5.5489 | 5.2467 | 5.8797 | 4.1368 | 1.435 | 1.437 | 1.432 | 1.478 | 1.444 | 1.485 | Over-range | 60.01 | 1226 | 1251 | 1591 | 4068 | - - - | - - - | - - - | - - - | 1226 | 1251 | 1591 | 4068 | 950 | 734 | -201 | 1482 | - - - | - - - | - - - | - - - | 950 | 734 | -201 | 1482 | 1560 | 1462 | 1630 | 4653 | # # # | # # # | # # # | # # # | 0.786 | 0.856 | 0.976 | 0.874 | # # # | # # # | # # # | - - - | 0.791 | 0.863 | 0.992 | 0.883 | - - - | 0.364 | 1.99 | 1.98 | 1.94 | 1.82 | 1.89 | 1.94 | 9.31 | 12.5 | 17.67 | 0 | - - - | - - - | - - - | - - - | 1560 | 1462 | 1630 | 4653 | Over-range | 965 | 757 | 355 | 2258 | 166 | 186 | 292 | 1703 | 1228 | 1253 | 1587 | 4068 | 1228 | 1253 | 1587 | 4068 | - - - | - - - | - - - | - - -
5/7/2026 | 11:30:00 AM | 281.61 | 279.09 | 277.7 | 486.89 | 480.62 | 484.62 | 5.3286 | 4.8624 | 5.7493 | 4.1408 | 1.435 | 1.437 | 1.432 | 1.479 | 1.423 | 1.452 | Over-range | 60 | 1190 | 1115 | 1562 | 3867 | - - - | - - - | - - - | - - - | 1190 | 1115 | 1562 | 3867 | 895 | 742 | -137 | 1499 | - - - | - - - | - - - | - - - | 895 | 742 | -137 | 1499 | 1500 | 1353 | 1596 | 4449 | # # # | # # # | # # # | # # # | 0.794 | 0.824 | 0.979 | 0.869 | # # # | # # # | # # # | - - - | 0.799 | 0.832 | 0.996 | 0.879 | - - - | 0.388 | 1.99 | 1.99 | 1.96 | 1.82 | 1.9 | 1.94 | 9.8 | 13.41 | 18.07 | 0 | - - - | - - - | - - - | - - - | 1500 | 1353 | 1596 | 4449 | Over-range | 912 | 764 | 328 | 2199 | 171 | 182 | 293 | 1608 | 1190 | 1117 | 1559 | 3866 | 1190 | 1117 | 1559 | 3866 | - - - | - - - | - - - | - - -
5/7/2026 | 11:45:00 AM | 282.06 | 279.61 | 278.28 | 487.71 | 481.6 | 485.51 | 5.608 | 5.3654 | 5.9253 | 4.1381 | 1.435 | 1.437 | 1.432 | 1.48 | 1.436 | 1.467 | Over-range | 60 | 1235 | 1286 | 1608 | 4129 | - - - | - - - | - - - | - - - | 1235 | 1286 | 1608 | 4129 | 972 | 748 | -208 | 1511 | - - - | - - - | - - - | - - - | 972 | 748 | -208 | 1511 | 1582 | 1499 | 1649 | 4730 | # # # | # # # | # # # | # # # | 0.781 | 0.857 | 0.975 | 0.873 | # # # | # # # | # # # | - - - | 0.786 | 0.864 | 0.991 | 0.882 | - - - | 0.366 | 2.03 | 2 | 1.95 | 1.84 | 1.92 | 1.96 | 9.38 | 12.51 | 17.79 | 0 | - - - | - - - | - - - | - - - | 1582 | 1499 | 1649 | 4730 | Over-range | 988 | 771 | 363 | 2308 | 177 | 188 | 297 | 1744 | 1235 | 1286 | 1607 | 4128 | 1235 | 1286 | 1607 | 4128 | - - - | - - - | - - - | - - -
5/7/2026 | 12:00:00 PM | 281.97 | 279.57 | 278.21 | 487.64 | 481.48 | 485.35 | 4.82 | 4.0814 | 5.4719 | 4.1469 | 1.435 | 1.437 | 1.432 | 1.482 | 1.453 | 1.435 | Over-range | 60 | 1106 | 789 | 1487 | 3382 | - - - | - - - | - - - | - - - | 1106 | 789 | 1487 | 3382 | 758 | 753 | 8 | 1519 | - - - | - - - | - - - | - - - | 758 | 753 | 8 | 1519 | 1353 | 1126 | 1521 | 4000 | # # # | # # # | # # # | # # # | 0.817 | 0.701 | 0.978 | 0.846 | # # # | # # # | # # # | - - - | 0.824 | 0.711 | 0.996 | 0.857 | - - - | 0.449 | 2.03 | 1.99 | 1.95 | 1.84 | 1.92 | 1.96 | 11.13 | 15.84 | 18.82 | 0 | - - - | - - - | - - - | - - - | 1353 | 1126 | 1521 | 4000 | Over-range | 778 | 773 | 317 | 2126 | 171 | 176 | 292 | 1486 | 1106 | 791 | 1485 | 3382 | 1106 | 791 | 1485 | 3382 | - - - | - - - | - - - | - - -
5/7/2026 | 12:15:00 PM | 281.64 | 279.14 | 277.82 | 486.98 | 480.78 | 484.73 | 4.7589 | 3.8448 | 5.4138 | 4.1457 | 1.435 | 1.437 | 1.433 | 1.481 | 1.463 | 1.427 | Over-range | 60.02 | 1104 | 707 | 1467 | 3278 | - - - | - - - | - - - | - - - | 1104 | 707 | 1467 | 3278 | 727 | 746 | 61 | 1534 | - - - | - - - | - - - | - - - | 727 | 746 | 61 | 1534 | 1334 | 1059 | 1503 | 3896 | # # # | # # # | # # # | # # # | 0.828 | 0.668 | 0.976 | 0.841 | # # # | # # # | # # # | - - - | 0.827 | 0.672 | 0.98 | 0.844 | - - - | 0.468 | 2.03 | 2 | 2 | 1.85 | 1.94 | 1.98 | 11.14 | 16.5 | 18.79 | 0 | - - - | - - - | - - - | - - - | 1334 | 1059 | 1503 | 3896 | Over-range | 747 | 767 | 324 | 2099 | 169 | 178 | 289 | 1427 | 1115 | 711 | 1481 | 3307 | 1115 | 711 | 1481 | 3307 | - - - | - - - | - - - | - - -
5/7/2026 | 12:30:00 PM | 281.6 | 279.09 | 277.74 | 486.92 | 480.68 | 484.6 | 4.5927 | 3.6725 | 5.3419 | 4.1452 | 1.435 | 1.437 | 1.433 | 1.483 | 1.459 | 1.409 | Over-range | 60.01 | 1072 | 662 | 1452 | 3186 | - - - | - - - | - - - | - - - | 1072 | 662 | 1452 | 3186 | 700 | 746 | 61 | 1508 | - - - | - - - | - - - | - - - | 700 | 746 | 61 | 1508 | 1291 | 1020 | 1483 | 3795 | # # # | # # # | # # # | # # # | 0.83 | 0.649 | 0.979 | 0.84 | # # # | # # # | # # # | - - - | 0.838 | 0.658 | 0.998 | 0.852 | - - - | 0.473 | 2.02 | 1.99 | 1.97 | 1.84 | 1.92 | 1.96 | 11.38 | 16.89 | 18.88 | 0 | - - - | - - - | - - - | - - - | 1291 | 1020 | 1483 | 3795 | Over-range | 720 | 767 | 300 | 2058 | 165 | 180 | 286 | 1401 | 1075 | 660 | 1453 | 3188 | 1075 | 660 | 1453 | 3188 | - - - | - - - | - - - | - - -
5/7/2026 | 12:45:00 PM | 281.57 | 279.04 | 277.74 | 486.85 | 480.57 | 484.63 | 4.6077 | 3.7646 | 5.3688 | 4.1401 | 1.436 | 1.437 | 1.433 | 1.482 | 1.464 | 1.412 | Over-range | 60 | 1072 | 670 | 1457 | 3200 | - - - | - - - | - - - | - - - | 1072 | 670 | 1457 | 3200 | 701 | 751 | 56 | 1508 | - - - | - - - | - - - | - - - | 701 | 751 | 56 | 1508 | 1293 | 1039 | 1490 | 3822 | # # # | # # # | # # # | # # # | 0.829 | 0.645 | 0.978 | 0.837 | # # # | # # # | # # # | - - - | 0.837 | 0.655 | 0.997 | 0.85 | - - - | 0.471 | 2.01 | 1.99 | 1.95 | 1.82 | 1.91 | 1.96 | 11.41 | 16.59 | 18.87 | 0 | - - - | - - - | - - - | - - - | 1293 | 1039 | 1490 | 3822 | Over-range | 720 | 772 | 311 | 2082 | 164 | 179 | 288 | 1435 | 1076 | 669 | 1456 | 3201 | 1076 | 669 | 1456 | 3201 | - - - | - - - | - - - | - - -
5/7/2026 | 1:00:00 PM | 281.35 | 278.8 | 277.55 | 486.4 | 480.2 | 484.31 | 5.2369 | 4.6763 | 5.6718 | 4.1302 | 1.435 | 1.437 | 1.432 | 1.482 | 1.425 | 1.405 | Over-range | 60 | 1177 | 1033 | 1541 | 3751 | - - - | - - - | - - - | - - - | 1177 | 1033 | 1541 | 3751 | 863 | 743 | -90 | 1515 | - - - | - - - | - - - | - - - | 863 | 743 | -90 | 1515 | 1470 | 1294 | 1573 | 4337 | # # # | # # # | # # # | # # # | 0.801 | 0.798 | 0.979 | 0.865 | # # # | # # # | # # # | - - - | 0.807 | 0.806 | 0.997 | 0.875 | - - - | 0.404 | 1.98 | 1.96 | 1.93 | 1.8 | 1.89 | 1.93 | 9.91 | 14.01 | 18.22 | 0 | - - - | - - - | - - - | - - - | 1470 | 1294 | 1573 | 4337 | Over-range | 879 | 767 | 319 | 2175 | 167 | 187 | 291 | 1559 | 1181 | 1030 | 1541 | 3753 | 1181 | 1030 | 1541 | 3753 | - - - | - - - | - - - | - - -
5/7/2026 | 1:15:00 PM | 281.33 | 278.78 | 277.46 | 486.38 | 480.15 | 484.16 | 5.2728 | 4.7021 | 5.6839 | 4.1309 | 1.435 | 1.437 | 1.433 | 1.48 | 1.413 | 1.405 | Over-range | 60.01 | 1185 | 1063 | 1546 | 3795 | - - - | - - - | - - - | - - - | 1185 | 1063 | 1546 | 3795 | 875 | 742 | -105 | 1510 | - - - | - - - | - - - | - - - | 875 | 742 | -105 | 1510 | 1483 | 1310 | 1577 | 4370 | # # # | # # # | # # # | # # # | 0.799 | 0.812 | 0.981 | 0.868 | # # # | # # # | # # # | - - - | 0.805 | 0.82 | 0.997 | 0.879 | - - - | 0.398 | 1.98 | 1.96 | 1.94 | 1.8 | 1.89 | 1.93 | 9.78 | 13.54 | 18.09 | 0 | - - - | - - - | - - - | - - - | 1483 | 1310 | 1577 | 4370 | Over-range | 891 | 764 | 310 | 2167 | 170 | 184 | 291 | 1554 | 1188 | 1062 | 1547 | 3796 | 1188 | 1062 | 1547 | 3796 | - - - | - - - | - - - | - - -
5/7/2026 | 1:30:00 PM | 281.02 | 278.26 | 277.02 | 485.73 | 479.15 | 483.61 | 5.0091 | 4.2285 | 5.5216 | 4.1311 | 1.435 | 1.437 | 1.432 | 1.481 | 1.425 | 1.387 | Over-range | 60.01 | 1143 | 896 | 1502 | 3541 | - - - | - - - | - - - | - - - | 1143 | 896 | 1502 | 3541 | 801 | 734 | -35 | 1499 | - - - | - - - | - - - | - - - | 801 | 734 | -35 | 1499 | 1407 | 1173 | 1529 | 4109 | # # # | # # # | # # # | # # # | 0.813 | 0.763 | 0.982 | 0.862 | # # # | # # # | # # # | - - - | 0.819 | 0.772 | 0.999 | 0.872 | - - - | 0.423 | 1.95 | 1.92 | 1.92 | 1.77 | 1.87 | 1.9 | 10.22 | 14.52 | 18.05 | 0 | - - - | - - - | - - - | - - - | 1407 | 1173 | 1529 | 4109 | Over-range | 819 | 754 | 288 | 2084 | 170 | 173 | 281 | 1447 | 1143 | 896 | 1503 | 3541 | 1143 | 896 | 1503 | 3541 | - - - | - - - | - - - | - - -
5/7/2026 | 1:45:00 PM | 281.18 | 278.45 | 277.16 | 486.05 | 479.43 | 483.88 | 5.3694 | 4.7206 | 5.6762 | 4.124 | 1.435 | 1.437 | 1.432 | 1.48 | 1.425 | 1.389 | Over-range | 60 | 1207 | 1063 | 1541 | 3811 | - - - | - - - | - - - | - - - | 1207 | 1063 | 1541 | 3811 | 883 | 734 | -88 | 1528 | - - - | - - - | - - - | - - - | 883 | 734 | -88 | 1528 | 1506 | 1308 | 1573 | 4386 | # # # | # # # | # # # | # # # | 0.802 | 0.813 | 0.98 | 0.869 | # # # | # # # | # # # | - - - | 0.799 | 0.815 | 0.986 | 0.87 | - - - | 0.401 | 1.96 | 1.92 | 1.88 | 1.76 | 1.85 | 1.89 | 9.62 | 13.78 | 17.94 | 0 | - - - | - - - | - - - | - - - | 1506 | 1308 | 1573 | 4386 | Over-range | 900 | 755 | 313 | 2170 | 169 | 178 | 285 | 1535 | 1217 | 1073 | 1565 | 3855 | 1217 | 1073 | 1565 | 3855 | - - - | - - - | - - - | - - -
5/7/2026 | 2:00:00 PM | 281.21 | 278.49 | 277.2 | 486.06 | 479.57 | 483.9 | 5.6176 | 5.2909 | 5.8757 | 4.1277 | 1.435 | 1.436 | 1.432 | 1.481 | 1.44 | 1.399 | Over-range | 60 | 1240 | 1264 | 1592 | 4095 | - - - | - - - | - - - | - - - | 1240 | 1264 | 1592 | 4095 | 962 | 732 | -195 | 1498 | - - - | - - - | - - - | - - - | 962 | 732 | -195 | 1498 | 1579 | 1472 | 1629 | 4680 | # # # | # # # | # # # | # # # | 0.785 | 0.858 | 0.977 | 0.875 | # # # | # # # | # # # | - - - | 0.79 | 0.864 | 0.993 | 0.884 | - - - | 0.366 | 1.92 | 1.86 | 1.85 | 1.73 | 1.81 | 1.85 | 9.08 | 12.28 | 17.25 | 0 | - - - | - - - | - - - | - - - | 1579 | 1472 | 1629 | 4680 | Over-range | 978 | 754 | 345 | 2265 | 176 | 181 | 283 | 1699 | 1240 | 1263 | 1592 | 4095 | 1240 | 1263 | 1592 | 4095 | - - - | - - - | - - - | - - -
5/7/2026 | 2:15:00 PM | 281.72 | 279.05 | 277.7 | 487.04 | 480.46 | 484.75 | 5.4578 | 5.0008 | 5.7735 | 4.1229 | 1.436 | 1.436 | 1.432 | 1.481 | 1.423 | 1.339 | Over-range | 60.01 | 1216 | 1168 | 1571 | 3955 | - - - | - - - | - - - | - - - | 1216 | 1168 | 1571 | 3955 | 925 | 740 | -148 | 1516 | - - - | - - - | - - - | - - - | 925 | 740 | -148 | 1516 | 1537 | 1395 | 1603 | 4536 | # # # | # # # | # # # | # # # | 0.791 | 0.837 | 0.98 | 0.872 | # # # | # # # | # # # | - - - | 0.796 | 0.844 | 0.995 | 0.881 | - - - | 0.383 | 1.93 | 1.87 | 1.81 | 1.73 | 1.78 | 1.84 | 9.29 | 12.9 | 17.38 | 0 | - - - | - - - | - - - | - - - | 1537 | 1395 | 1603 | 4536 | Over-range | 941 | 762 | 318 | 2220 | 173 | 182 | 280 | 1621 | 1216 | 1167 | 1572 | 3956 | 1216 | 1167 | 1572 | 3956 | - - - | - - - | - - - | - - -
5/7/2026 | 2:30:00 PM | 281.72 | 279.08 | 277.73 | 487.07 | 480.51 | 484.79 | 5.4058 | 4.9105 | 5.7303 | 4.1198 | 1.435 | 1.437 | 1.432 | 1.481 | 1.42 | 1.343 | Over-range | 59.99 | 1207 | 1136 | 1560 | 3903 | - - - | - - - | - - - | - - - | 1207 | 1136 | 1560 | 3903 | 912 | 742 | -134 | 1519 | - - - | - - - | - - - | - - - | 912 | 742 | -134 | 1519 | 1523 | 1369 | 1591 | 4483 | # # # | # # # | # # # | # # # | 0.793 | 0.83 | 0.98 | 0.871 | # # # | # # # | # # # | - - - | 0.798 | 0.837 | 0.996 | 0.88 | - - - | 0.389 | 1.94 | 1.86 | 1.81 | 1.73 | 1.79 | 1.84 | 9.39 | 13.11 | 17.57 | 0 | - - - | - - - | - - - | - - - | 1523 | 1369 | 1591 | 4483 | Over-range | 928 | 763 | 313 | 2205 | 173 | 180 | 281 | 1599 | 1207 | 1136 | 1561 | 3903 | 1207 | 1136 | 1561 | 3903 | - - - | - - - | - - - | - - -
5/7/2026 | 2:45:00 PM | 281.64 | 278.95 | 277.68 | 486.82 | 480.41 | 484.68 | 4.8028 | 3.9592 | 5.4161 | 4.1384 | 1.436 | 1.436 | 1.432 | 1.482 | 1.446 | 1.379 | Over-range | 60 | 1107 | 752 | 1472 | 3331 | - - - | - - - | - - - | - - - | 1107 | 752 | 1472 | 3331 | 748 | 744 | 34 | 1526 | - - - | - - - | - - - | - - - | 748 | 744 | 34 | 1526 | 1347 | 1091 | 1503 | 3941 | # # # | # # # | # # # | # # # | 0.822 | 0.689 | 0.98 | 0.845 | # # # | # # # | # # # | - - - | 0.829 | 0.698 | 0.997 | 0.856 | - - - | 0.458 | 1.9 | 1.86 | 1.82 | 1.72 | 1.77 | 1.83 | 10.71 | 15.83 | 18.1 | 0 | - - - | - - - | - - - | - - - | 1347 | 1091 | 1503 | 3941 | Over-range | 766 | 764 | 300 | 2097 | 162 | 175 | 275 | 1437 | 1110 | 751 | 1472 | 3333 | 1110 | 751 | 1472 | 3333 | - - - | - - - | - - - | - - -
5/7/2026 | 3:00:00 PM | 281.77 | 279.04 | 277.74 | 487.08 | 480.46 | 484.84 | 4.7954 | 3.9128 | 5.3911 | 4.1236 | 1.435 | 1.436 | 1.432 | 1.484 | 1.442 | 1.373 | Over-range | 60 | 1109 | 758 | 1469 | 3336 | - - - | - - - | - - - | - - - | 1109 | 758 | 1469 | 3336 | 750 | 745 | 32 | 1526 | - - - | - - - | - - - | - - - | 750 | 745 | 32 | 1526 | 1349 | 1085 | 1497 | 3930 | # # # | # # # | # # # | # # # | 0.822 | 0.699 | 0.981 | 0.849 | # # # | # # # | # # # | - - - | 0.828 | 0.707 | 0.998 | 0.859 | - - - | 0.458 | 1.87 | 1.83 | 1.72 | 1.66 | 1.7 | 1.76 | 10.53 | 16 | 18.25 | 0 | - - - | - - - | - - - | - - - | 1349 | 1085 | 1497 | 3930 | Over-range | 768 | 766 | 288 | 2076 | 164 | 177 | 275 | 1406 | 1110 | 756 | 1471 | 3337 | 1110 | 756 | 1471 | 3337 | - - - | - - - | - - - | - - -
5/7/2026 | 3:15:00 PM | 281.67 | 278.97 | 277.63 | 486.96 | 480.28 | 484.66 | 4.8948 | 4.0361 | 5.4541 | 4.1283 | 1.436 | 1.437 | 1.432 | 1.484 | 1.432 | 1.355 | Over-range | 60.01 | 1126 | 826 | 1489 | 3440 | - - - | - - - | - - - | - - - | 1126 | 826 | 1489 | 3440 | 778 | 742 | 2 | 1523 | - - - | - - - | - - - | - - - | 778 | 742 | 2 | 1523 | 1378 | 1125 | 1514 | 4018 | # # # | # # # | # # # | # # # | 0.817 | 0.734 | 0.983 | 0.856 | # # # | # # # | # # # | - - - | 0.823 | 0.742 | 1 | 0.867 | - - - | 0.443 | 1.87 | 1.81 | 1.75 | 1.68 | 1.71 | 1.77 | 10.24 | 15.25 | 17.93 | 0 | - - - | - - - | - - - | - - - | 1378 | 1125 | 1514 | 4018 | Over-range | 795 | 763 | 275 | 2075 | 162 | 177 | 274 | 1409 | 1128 | 824 | 1490 | 3442 | 1128 | 824 | 1490 | 3442 | - - - | - - - | - - - | - - -
5/7/2026 | 3:30:00 PM | 281.64 | 279 | 277.55 | 486.95 | 480.27 | 484.54 | 5.1937 | 4.4217 | 5.5828 | 4.1259 | 1.436 | 1.437 | 1.433 | 1.481 | 1.425 | 1.348 | Over-range | 60 | 1180 | 958 | 1519 | 3657 | - - - | - - - | - - - | - - - | 1180 | 958 | 1519 | 3657 | 844 | 743 | -36 | 1550 | - - - | - - - | - - - | - - - | 844 | 743 | -36 | 1550 | 1460 | 1229 | 1549 | 4238 | # # # | # # # | # # # | # # # | 0.808 | 0.78 | 0.981 | 0.863 | # # # | # # # | # # # | - - - | 0.806 | 0.783 | 0.982 | 0.864 | - - - | 0.424 | 1.93 | 1.86 | 1.82 | 1.73 | 1.77 | 1.84 | 9.75 | 14.41 | 17.93 | 0 | - - - | - - - | - - - | - - - | 1460 | 1229 | 1549 | 4238 | Over-range | 860 | 764 | 301 | 2141 | 163 | 180 | 280 | 1470 | 1192 | 965 | 1533 | 3690 | 1192 | 965 | 1533 | 3690 | - - - | - - - | - - - | - - -
5/7/2026 | 3:45:00 PM | 281.87 | 279.27 | 277.84 | 487.38 | 480.75 | 485 | 5.5634 | 5.2028 | 5.844 | 4.1206 | 1.436 | 1.437 | 1.433 | 1.482 | 1.433 | 1.311 | Over-range | 60.02 | 1232 | 1231 | 1589 | 4052 | - - - | - - - | - - - | - - - | 1232 | 1231 | 1589 | 4052 | 955 | 743 | -173 | 1524 | - - - | - - - | - - - | - - - | 955 | 743 | -173 | 1524 | 1567 | 1451 | 1623 | 4641 | # # # | # # # | # # # | # # # | 0.786 | 0.849 | 0.979 | 0.873 | # # # | # # # | # # # | - - - | 0.791 | 0.856 | 0.994 | 0.881 | - - - | 0.376 | 1.93 | 1.86 | 1.81 | 1.73 | 1.77 | 1.83 | 9.07 | 12.59 | 17.13 | 0 | - - - | - - - | - - - | - - - | 1567 | 1451 | 1623 | 4641 | Over-range | 969 | 766 | 331 | 2264 | 164 | 185 | 279 | 1673 | 1234 | 1232 | 1586 | 4052 | 1234 | 1232 | 1586 | 4052 | - - - | - - - | - - - | - - -
5/7/2026 | 4:00:00 PM | 281.77 | 279.14 | 277.79 | 487.19 | 480.56 | 484.9 | 4.8343 | 4.0261 | 5.4321 | 4.1266 | 1.436 | 1.437 | 1.433 | 1.482 | 1.444 | 1.368 | Over-range | 60.02 | 1112 | 773 | 1477 | 3362 | - - - | - - - | - - - | - - - | 1112 | 773 | 1477 | 3362 | 756 | 746 | 25 | 1527 | - - - | - - - | - - - | - - - | 756 | 746 | 25 | 1527 | 1356 | 1108 | 1508 | 3972 | # # # | # # # | # # # | # # # | 0.82 | 0.697 | 0.98 | 0.847 | # # # | # # # | # # # | - - - | 0.826 | 0.706 | 0.996 | 0.857 | - - - | 0.454 | 1.86 | 1.84 | 1.77 | 1.69 | 1.72 | 1.79 | 10.55 | 15.64 | 17.91 | 0 | - - - | - - - | - - - | - - - | 1356 | 1108 | 1508 | 3972 | Over-range | 773 | 765 | 299 | 2105 | 163 | 170 | 272 | 1448 | 1112 | 774 | 1476 | 3363 | 1112 | 774 | 1476 | 3363 | - - - | - - - | - - - | - - -
5/7/2026 | 4:15:00 PM | 282.11 | 279.56 | 278.13 | 487.84 | 481.28 | 485.42 | 4.7977 | 3.9149 | 5.3946 | 4.129 | 1.437 | 1.437 | 1.433 | 1.482 | 1.44 | 1.374 | Over-range | 60.02 | 1110 | 758 | 1472 | 3340 | - - - | - - - | - - - | - - - | 1110 | 758 | 1472 | 3340 | 753 | 752 | 34 | 1539 | - - - | - - - | - - - | - - - | 753 | 752 | 34 | 1539 | 1351 | 1088 | 1500 | 3939 | # # # | # # # | # # # | # # # | 0.821 | 0.697 | 0.981 | 0.848 | # # # | # # # | # # # | - - - | 0.827 | 0.707 | 0.999 | 0.859 | - - - | 0.461 | 1.89 | 1.85 | 1.77 | 1.7 | 1.73 | 1.8 | 10.5 | 16.14 | 18.34 | 0 | - - - | - - - | - - - | - - - | 1351 | 1088 | 1500 | 3939 | Over-range | 771 | 772 | 288 | 2086 | 163 | 174 | 277 | 1408 | 1110 | 759 | 1471 | 3340 | 1110 | 759 | 1471 | 3340 | - - - | - - - | - - - | - - -
5/7/2026 | 4:30:00 PM | 281.98 | 279.43 | 278.06 | 487.57 | 481.14 | 485.27 | 4.8629 | 3.9885 | 5.4428 | 4.1307 | 1.437 | 1.437 | 1.432 | 1.482 | 1.435 | 1.362 | Over-range | 60 | 1121 | 805 | 1488 | 3414 | - - - | - - - | - - - | - - - | 1121 | 805 | 1488 | 3414 | 772 | 751 | 15 | 1538 | - - - | - - - | - - - | - - - | 772 | 751 | 15 | 1538 | 1371 | 1114 | 1513 | 3999 | # # # | # # # | # # # | # # # | 0.818 | 0.722 | 0.983 | 0.854 | # # # | # # # | # # # | - - - | 0.824 | 0.731 | 1 | 0.864 | - - - | 0.451 | 1.85 | 1.84 | 1.73 | 1.68 | 1.69 | 1.77 | 10.29 | 15.45 | 18.04 | 0 | - - - | - - - | - - - | - - - | 1371 | 1114 | 1513 | 3999 | Over-range | 789 | 770 | 275 | 2082 | 163 | 172 | 275 | 1403 | 1121 | 806 | 1487 | 3414 | 1121 | 806 | 1487 | 3414 | - - - | - - - | - - - | - - -
5/7/2026 | 4:45:00 PM | 282.18 | 279.68 | 278.28 | 488.01 | 481.52 | 485.64 | 4.9296 | 4.1 | 5.4753 | 4.1293 | 1.437 | 1.437 | 1.433 | 1.482 | 1.431 | 1.352 | Over-range | 60.01 | 1132 | 845 | 1498 | 3475 | - - - | - - - | - - - | - - - | 1132 | 845 | 1498 | 3475 | 792 | 752 | 0 | 1543 | - - - | - - - | - - - | - - - | 792 | 752 | 0 | 1543 | 1391 | 1146 | 1524 | 4060 | # # # | # # # | # # # | # # # | 0.814 | 0.737 | 0.983 | 0.856 | # # # | # # # | # # # | - - - | 0.819 | 0.746 | 0.999 | 0.866 | - - - | 0.444 | 1.89 | 1.85 | 1.78 | 1.71 | 1.73 | 1.8 | 10.2 | 15.23 | 18.05 | 0 | - - - | - - - | - - - | - - - | 1391 | 1146 | 1524 | 4060 | Over-range | 808 | 773 | 277 | 2100 | 161 | 178 | 276 | 1424 | 1134 | 844 | 1497 | 3476 | 1134 | 844 | 1497 | 3476 | - - - | - - - | - - - | - - -
5/7/2026 | 5:00:00 PM | 282.25 | 279.62 | 278.28 | 487.99 | 481.44 | 485.75 | 5.6581 | 5.2326 | 5.8465 | 4.1153 | 1.437 | 1.437 | 1.432 | 1.482 | 1.439 | 1.306 | Over-range | 60 | 1254 | 1239 | 1593 | 4085 | - - - | - - - | - - - | - - - | 1254 | 1239 | 1593 | 4085 | 970 | 746 | -153 | 1562 | - - - | - - - | - - - | - - - | 970 | 746 | -153 | 1562 | 1594 | 1460 | 1626 | 4680 | # # # | # # # | # # # | # # # | 0.787 | 0.848 | 0.979 | 0.873 | # # # | # # # | # # # | - - - | 0.784 | 0.841 | 0.974 | 0.868 | - - - | 0.383 | 1.87 | 1.82 | 1.75 | 1.68 | 1.7 | 1.78 | 9.03 | 12.8 | 17.4 | 0 | - - - | - - - | - - - | - - - | 1594 | 1460 | 1626 | 4680 | Over-range | 984 | 771 | 329 | 2284 | 161 | 189 | 281 | 1661 | 1268 | 1255 | 1619 | 4142 | 1268 | 1255 | 1619 | 4142 | - - - | - - - | - - - | - - -
5/7/2026 | 5:15:00 PM | 282.76 | 280.26 | 278.84 | 488.93 | 482.62 | 486.57 | 5.6251 | 5.31 | 5.8864 | 4.128 | 1.437 | 1.437 | 1.433 | 1.485 | 1.438 | 1.302 | Over-range | 60.01 | 1243 | 1267 | 1606 | 4116 | - - - | - - - | - - - | - - - | 1243 | 1267 | 1606 | 4116 | 979 | 754 | -180 | 1553 | - - - | - - - | - - - | - - - | 979 | 754 | -180 | 1553 | 1590 | 1487 | 1641 | 4719 | # # # | # # # | # # # | # # # | 0.781 | 0.852 | 0.979 | 0.872 | # # # | # # # | # # # | - - - | 0.787 | 0.859 | 0.994 | 0.881 | - - - | 0.377 | 1.82 | 1.76 | 1.69 | 1.65 | 1.65 | 1.72 | 8.99 | 12.58 | 17.27 | 0 | - - - | - - - | - - - | - - - | 1590 | 1487 | 1641 | 4719 | Over-range | 992 | 779 | 337 | 2308 | 163 | 193 | 283 | 1708 | 1247 | 1265 | 1606 | 4117 | 1247 | 1265 | 1606 | 4117 | - - - | - - - | - - - | - - -
5/7/2026 | 5:30:00 PM | 282.82 | 280.42 | 279.02 | 489.13 | 482.95 | 486.75 | 5.4978 | 5.0817 | 5.8029 | 4.1279 | 1.437 | 1.437 | 1.433 | 1.484 | 1.423 | 1.298 | Over-range | 60.01 | 1222 | 1190 | 1587 | 3999 | - - - | - - - | - - - | - - - | 1222 | 1190 | 1587 | 3999 | 946 | 758 | -145 | 1558 | - - - | - - - | - - - | - - - | 946 | 758 | -145 | 1558 | 1555 | 1424 | 1619 | 4598 | # # # | # # # | # # # | # # # | 0.786 | 0.835 | 0.98 | 0.87 | # # # | # # # | # # # | - - - | 0.792 | 0.842 | 0.996 | 0.879 | - - - | 0.39 | 1.84 | 1.76 | 1.67 | 1.65 | 1.64 | 1.72 | 9.2 | 13.06 | 17.53 | 0 | - - - | - - - | - - - | - - - | 1555 | 1424 | 1619 | 4598 | Over-range | 960 | 782 | 320 | 2268 | 166 | 191 | 284 | 1648 | 1226 | 1187 | 1588 | 4001 | 1226 | 1187 | 1588 | 4001 | - - - | - - - | - - - | - - -
5/7/2026 | 5:45:00 PM | 283.05 | 280.65 | 279.31 | 489.52 | 483.39 | 487.21 | 5.3708 | 4.8524 | 5.7251 | 4.1306 | 1.437 | 1.437 | 1.434 | 1.483 | 1.412 | 1.299 | Over-range | 60 | 1202 | 1112 | 1570 | 3884 | - - - | - - - | - - - | - - - | 1202 | 1112 | 1570 | 3884 | 915 | 762 | -109 | 1567 | - - - | - - - | - - - | - - - | 915 | 762 | -109 | 1567 | 1520 | 1362 | 1599 | 4481 | # # # | # # # | # # # | # # # | 0.791 | 0.817 | 0.982 | 0.867 | # # # | # # # | # # # | - - - | 0.796 | 0.825 | 0.997 | 0.876 | - - - | 0.403 | 1.83 | 1.76 | 1.71 | 1.65 | 1.65 | 1.73 | 9.45 | 13.64 | 17.76 | 0 | - - - | - - - | - - - | - - - | 1520 | 1362 | 1599 | 4481 | Over-range | 930 | 786 | 305 | 2234 | 167 | 191 | 285 | 1593 | 1205 | 1110 | 1571 | 3886 | 1205 | 1110 | 1571 | 3886 | - - - | - - - | - - - | - - -
5/7/2026 | 6:00:00 PM | 283.15 | 280.78 | 279.36 | 489.7 | 483.6 | 487.31 | 4.9543 | 4.1539 | 5.5057 | 4.1431 | 1.438 | 1.437 | 1.434 | 1.484 | 1.44 | 1.354 | Over-range | 60 | 1136 | 855 | 1512 | 3503 | - - - | - - - | - - - | - - - | 1136 | 855 | 1512 | 3503 | 806 | 767 | 4 | 1577 | - - - | - - - | - - - | - - - | 806 | 767 | 4 | 1577 | 1402 | 1165 | 1538 | 4105 | # # # | # # # | # # # | # # # | 0.81 | 0.734 | 0.983 | 0.853 | # # # | # # # | # # # | - - - | 0.816 | 0.743 | 0.999 | 0.864 | - - - | 0.45 | 1.81 | 1.73 | 1.68 | 1.64 | 1.63 | 1.71 | 10.27 | 15.23 | 18.14 | 0 | - - - | - - - | - - - | - - - | 1402 | 1165 | 1538 | 4105 | Over-range | 822 | 788 | 283 | 2140 | 160 | 180 | 280 | 1445 | 1139 | 855 | 1510 | 3504 | 1139 | 855 | 1510 | 3504 | - - - | - - - | - - - | - - -
5/7/2026 | 6:15:00 PM | 283.78 | 281.41 | 280.04 | 490.79 | 484.74 | 488.44 | 4.9766 | 4.1995 | 5.5233 | 4.1476 | 1.436 | 1.435 | 1.433 | 1.486 | 1.437 | 1.355 | Over-range | 60.01 | 1141 | 866 | 1519 | 3526 | - - - | - - - | - - - | - - - | 1141 | 866 | 1519 | 3526 | 815 | 777 | 3 | 1595 | - - - | - - - | - - - | - - - | 815 | 777 | 3 | 1595 | 1412 | 1180 | 1547 | 4138 | # # # | # # # | # # # | # # # | 0.808 | 0.734 | 0.982 | 0.852 | # # # | # # # | # # # | - - - | 0.814 | 0.744 | 1 | 0.863 | - - - | 0.452 | 1.7 | 1.64 | 1.56 | 1.55 | 1.53 | 1.59 | 10.32 | 15.57 | 18.49 | 0 | - - - | - - - | - - - | - - - | 1412 | 1180 | 1547 | 4138 | Over-range | 831 | 799 | 289 | 2165 | 161 | 185 | 286 | 1463 | 1143 | 867 | 1517 | 3526 | 1143 | 867 | 1517 | 3526 | - - - | - - - | - - - | - - -
5/7/2026 | 6:30:00 PM | 283.99 | 281.78 | 280.27 | 491.35 | 485.3 | 488.72 | 5.5834 | 5.2349 | 5.853 | 4.1384 | 1.436 | 1.434 | 1.433 | 1.489 | 1.42 | 1.296 | Over-range | 59.99 | 1237 | 1236 | 1606 | 4079 | - - - | - - - | - - - | - - - | 1237 | 1236 | 1606 | 4079 | 978 | 777 | -156 | 1598 | - - - | - - - | - - - | - - - | 978 | 777 | -156 | 1598 | 1585 | 1474 | 1640 | 4700 | # # # | # # # | # # # | # # # | 0.78 | 0.839 | 0.979 | 0.868 | # # # | # # # | # # # | - - - | 0.785 | 0.846 | 0.995 | 0.877 | - - - | 0.392 | 1.71 | 1.61 | 1.53 | 1.54 | 1.51 | 1.58 | 9.24 | 13.15 | 17.92 | 0 | - - - | - - - | - - - | - - - | 1585 | 1474 | 1640 | 4700 | Over-range | 992 | 802 | 333 | 2334 | 166 | 200 | 293 | 1701 | 1241 | 1235 | 1605 | 4081 | 1241 | 1235 | 1605 | 4081 | - - - | - - - | - - - | - - -
5/7/2026 | 6:45:00 PM | 284.14 | 281.87 | 280.41 | 491.49 | 485.58 | 488.97 | 5.4372 | 4.8456 | 5.7566 | 4.1471 | 1.436 | 1.434 | 1.432 | 1.486 | 1.415 | 1.312 | Over-range | 60 | 1221 | 1103 | 1584 | 3908 | - - - | - - - | - - - | - - - | 1221 | 1103 | 1584 | 3908 | 927 | 781 | -77 | 1630 | - - - | - - - | - - - | - - - | 927 | 781 | -77 | 1630 | 1543 | 1365 | 1614 | 4523 | # # # | # # # | # # # | # # # | 0.791 | 0.808 | 0.981 | 0.864 | # # # | # # # | # # # | - - - | 0.789 | 0.809 | 0.988 | 0.866 | - - - | 0.417 | 1.69 | 1.6 | 1.52 | 1.52 | 1.5 | 1.56 | 9.53 | 13.96 | 18.08 | 0 | - - - | - - - | - - - | - - - | 1543 | 1365 | 1614 | 4523 | Over-range | 943 | 805 | 312 | 2277 | 174 | 193 | 292 | 1584 | 1234 | 1109 | 1609 | 3952 | 1234 | 1109 | 1609 | 3952 | - - - | - - - | - - - | - - -
5/7/2026 | 7:00:00 PM | 284.39 | 282.12 | 280.64 | 491.98 | 485.91 | 489.41 | 5.3528 | 4.8281 | 5.7351 | 4.1462 | 1.435 | 1.433 | 1.431 | 1.49 | 1.416 | 1.305 | Over-range | 60 | 1202 | 1097 | 1580 | 3879 | - - - | - - - | - - - | - - - | 1202 | 1097 | 1580 | 3879 | 918 | 785 | -93 | 1609 | - - - | - - - | - - - | - - - | 918 | 785 | -93 | 1609 | 1522 | 1362 | 1610 | 4494 | # # # | # # # | # # # | # # # | 0.789 | 0.805 | 0.982 | 0.863 | # # # | # # # | # # # | - - - | 0.794 | 0.813 | 0.999 | 0.873 | - - - | 0.415 | 1.62 | 1.55 | 1.44 | 1.47 | 1.43 | 1.49 | 9.67 | 14.03 | 18.17 | 0 | - - - | - - - | - - - | - - - | 1522 | 1362 | 1610 | 4494 | Over-range | 934 | 808 | 306 | 2270 | 172 | 191 | 292 | 1600 | 1201 | 1098 | 1580 | 3879 | 1201 | 1098 | 1580 | 3879 | - - - | - - - | - - - | - - -
5/7/2026 | 7:15:00 PM | 284.89 | 282.64 | 281.1 | 492.92 | 486.72 | 490.23 | 5.3637 | 4.8368 | 5.7285 | 4.1581 | 1.435 | 1.433 | 1.43 | 1.492 | 1.418 | 1.308 | Over-range | 59.99 | 1203 | 1096 | 1580 | 3879 | - - - | - - - | - - - | - - - | 1203 | 1096 | 1580 | 3879 | 926 | 793 | -89 | 1629 | - - - | - - - | - - - | - - - | 926 | 793 | -89 | 1629 | 1528 | 1367 | 1610 | 4505 | # # # | # # # | # # # | # # # | 0.787 | 0.802 | 0.981 | 0.861 | # # # | # # # | # # # | - - - | 0.792 | 0.81 | 0.998 | 0.871 | - - - | 0.42 | 1.63 | 1.56 | 1.45 | 1.48 | 1.44 | 1.49 | 9.8 | 14.19 | 18.44 | 0 | - - - | - - - | - - - | - - - | 1528 | 1367 | 1610 | 4505 | Over-range | 942 | 817 | 309 | 2291 | 175 | 196 | 296 | 1611 | 1203 | 1096 | 1581 | 3880 | 1203 | 1096 | 1581 | 3880 | - - - | - - - | - - - | - - -
5/7/2026 | 7:30:00 PM | 284.95 | 282.78 | 281.09 | 493.09 | 486.91 | 490.18 | 20.7162 | 20.1293 | 18.7485 | 3.9269 | 1.433 | 1.431 | 1.428 | 1.466 | 1.432 | 1.389 | Over-range | 60 | 2516 | 2668 | 2799 | 7984 | - - - | - - - | - - - | - - - | 2516 | 2668 | 2799 | 7984 | 3147 | 2760 | 1814 | 7721 | - - - | - - - | - - - | - - - | 3147 | 2760 | 1814 | 7721 | 4089 | 3932 | 3590 | 11611 | # # # | # # # | # # # | # # # | 0.615 | 0.679 | 0.78 | 0.688 | # # # | # # # | # # # | - - - | 0.605 | 0.668 | 0.771 | 0.678 | - - - | 0.967 | 1.63 | 1.55 | 1.45 | 1.48 | 1.44 | 1.48 | 6.52 | 7.48 | 12.12 | 0 | - - - | - - - | - - - | - - - | 4089 | 3932 | 3590 | 11611 | Over-range | 3179 | 2804 | 2047 | 8183 | 179 | 353 | 362 | 1874 | 2538 | 2675 | 2837 | 8050 | 2538 | 2675 | 2837 | 8050 | - - - | - - - | - - - | - - -
5/7/2026 | 7:45:00 PM | 285.29 | 283.21 | 281.44 | 493.8 | 487.59 | 490.74 | 4.8295 | 4.9186 | 5.4809 | 2.777 | 1.433 | 1.432 | 1.428 | 1.488 | 1.483 | 1.389 | Over-range | 59.99 | 1112 | 1168 | 1505 | 3784 | - - - | - - - | - - - | - - - | 1112 | 1168 | 1505 | 3784 | 780 | 678 | 67 | 1525 | - - - | - - - | - - - | - - - | 780 | 678 | 67 | 1525 | 1371 | 1369 | 1541 | 4281 | # # # | # # # | # # # | # # # | 0.811 | 0.853 | 0.977 | 0.884 | # # # | # # # | # # # | - - - | 0.818 | 0.859 | 0.995 | 0.894 | - - - | 0.403 | 1.64 | 1.57 | 1.46 | 1.5 | 1.46 | 1.5 | 11.42 | 11.7 | 19.1 | 0 | - - - | - - - | - - - | - - - | 1371 | 1369 | 1541 | 4281 | Over-range | 800 | 696 | 330 | 1998 | 175 | 158 | 295 | 1281 | 1111 | 1168 | 1505 | 3785 | 1111 | 1168 | 1505 | 3785 | - - - | - - - | - - - | - - -
5/7/2026 | 8:00:00 PM | 284.21 | 282.06 | 280.3 | 491.89 | 485.55 | 488.85 | 4.7868 | 4.7786 | 5.4401 | 2.7839 | 1.431 | 1.43 | 1.426 | 1.488 | 1.438 | 1.383 | Over-range | 60 | 1109 | 1156 | 1494 | 3759 | - - - | - - - | - - - | - - - | 1109 | 1156 | 1494 | 3759 | 768 | 662 | 60 | 1490 | - - - | - - - | - - - | - - - | 768 | 662 | 60 | 1490 | 1359 | 1343 | 1525 | 4227 | # # # | # # # | # # # | # # # | 0.816 | 0.861 | 0.98 | 0.889 | # # # | # # # | # # # | - - - | 0.822 | 0.866 | 0.999 | 0.9 | - - - | 0.397 | 1.58 | 1.52 | 1.42 | 1.44 | 1.4 | 1.43 | 11.12 | 11.21 | 18.96 | 0 | - - - | - - - | - - - | - - - | 1359 | 1343 | 1525 | 4227 | Over-range | 786 | 681 | 303 | 1933 | 166 | 158 | 291 | 1228 | 1112 | 1155 | 1493 | 3760 | 1112 | 1155 | 1493 | 3760 | - - - | - - - | - - - | - - -
5/7/2026 | 8:15:00 PM | 283.87 | 281.9 | 279.94 | 491.51 | 485.17 | 488.11 | 4.8413 | 4.8684 | 5.4638 | 2.7896 | 1.43 | 1.429 | 1.425 | 1.488 | 1.418 | 1.371 | Over-range | 59.99 | 1118 | 1193 | 1501 | 3812 | - - - | - - - | - - - | - - - | 1118 | 1193 | 1501 | 3812 | 782 | 660 | 41 | 1483 | - - - | - - - | - - - | - - - | 782 | 660 | 41 | 1483 | 1374 | 1372 | 1530 | 4276 | # # # | # # # | # # # | # # # | 0.814 | 0.869 | 0.981 | 0.891 | # # # | # # # | # # # | - - - | 0.82 | 0.875 | 0.999 | 0.901 | - - - | 0.389 | 1.57 | 1.49 | 1.39 | 1.42 | 1.38 | 1.41 | 10.94 | 10.85 | 18.89 | 0 | - - - | - - - | - - - | - - - | 1374 | 1372 | 1530 | 4276 | Over-range | 799 | 678 | 294 | 1937 | 166 | 154 | 291 | 1247 | 1119 | 1194 | 1498 | 3812 | 1119 | 1194 | 1498 | 3812 | - - - | - - - | - - - | - - -
5/7/2026 | 8:30:00 PM | 283.99 | 282.04 | 280.09 | 491.7 | 485.46 | 488.35 | 5.3102 | 5.6387 | 5.6986 | 2.7905 | 1.43 | 1.43 | 1.425 | 1.493 | 1.447 | 1.37 | Over-range | 60 | 1200 | 1431 | 1563 | 4194 | - - - | - - - | - - - | - - - | 1200 | 1431 | 1563 | 4194 | 893 | 658 | -41 | 1509 | - - - | - - - | - - - | - - - | 893 | 658 | -41 | 1509 | 1505 | 1585 | 1596 | 4686 | # # # | # # # | # # # | # # # | 0.797 | 0.903 | 0.98 | 0.895 | # # # | # # # | # # # | - - - | 0.795 | 0.901 | 0.984 | 0.895 | - - - | 0.36 | 1.56 | 1.51 | 1.41 | 1.43 | 1.39 | 1.42 | 10.02 | 9.82 | 18.59 | 0 | - - - | - - - | - - - | - - - | 1505 | 1585 | 1596 | 4686 | Over-range | 909 | 678 | 319 | 2090 | 168 | 164 | 298 | 1436 | 1213 | 1439 | 1577 | 4228 | 1213 | 1439 | 1577 | 4228 | - - - | - - - | - - - | - - -
5/7/2026 | 8:45:00 PM | 284.01 | 282.04 | 280.02 | 491.78 | 485.37 | 488.29 | 5.6297 | 6.4091 | 5.9079 | 2.7847 | 1.43 | 1.43 | 1.425 | 1.498 | 1.465 | 1.387 | Over-range | 60 | 1244 | 1674 | 1618 | 4536 | - - - | - - - | - - - | - - - | 1244 | 1674 | 1618 | 4536 | 989 | 656 | -168 | 1475 | - - - | - - - | - - - | - - - | 989 | 656 | -168 | 1475 | 1598 | 1806 | 1654 | 5058 | # # # | # # # | # # # | # # # | 0.778 | 0.927 | 0.978 | 0.897 | # # # | # # # | # # # | - - - | 0.783 | 0.931 | 0.994 | 0.904 | - - - | 0.325 | 1.56 | 1.53 | 1.42 | 1.44 | 1.42 | 1.43 | 9.42 | 8.7 | 17.98 | 0 | - - - | - - - | - - - | - - - | 1598 | 1806 | 1654 | 5058 | Over-range | 1003 | 676 | 344 | 2238 | 170 | 163 | 298 | 1682 | 1245 | 1676 | 1614 | 4536 | 1245 | 1676 | 1614 | 4536 | - - - | - - - | - - - | - - -
5/7/2026 | 9:00:00 PM | 284.22 | 282.24 | 280.25 | 492.1 | 485.74 | 488.69 | 4.7776 | 4.7907 | 5.446 | 2.7971 | 1.43 | 1.43 | 1.425 | 1.487 | 1.473 | 1.404 | Over-range | 60.01 | 1105 | 1138 | 1490 | 3733 | - - - | - - - | - - - | - - - | 1105 | 1138 | 1490 | 3733 | 761 | 665 | 68 | 1493 | - - - | - - - | - - - | - - - | 761 | 665 | 68 | 1493 | 1353 | 1335 | 1525 | 4213 | # # # | # # # | # # # | # # # | 0.817 | 0.852 | 0.977 | 0.886 | # # # | # # # | # # # | - - - | 0.824 | 0.859 | 0.996 | 0.897 | - - - | 0.4 | 1.58 | 1.54 | 1.42 | 1.45 | 1.42 | 1.44 | 11.42 | 11.7 | 19.1 | 0 | - - - | - - - | - - - | - - - | 1353 | 1335 | 1525 | 4213 | Over-range | 779 | 684 | 321 | 1951 | 167 | 161 | 294 | 1249 | 1108 | 1137 | 1489 | 3733 | 1108 | 1137 | 1489 | 3733 | - - - | - - - | - - - | - - -
5/7/2026 | 9:15:00 PM | 284.63 | 282.59 | 280.72 | 492.7 | 486.48 | 489.48 | 4.7103 | 4.6498 | 5.418 | 2.8035 | 1.431 | 1.431 | 1.426 | 1.488 | 1.472 | 1.408 | Over-range | 60.01 | 1095 | 1095 | 1485 | 3675 | - - - | - - - | - - - | - - - | 1095 | 1095 | 1485 | 3675 | 746 | 672 | 90 | 1508 | - - - | - - - | - - - | - - - | 746 | 672 | 90 | 1508 | 1337 | 1301 | 1520 | 4158 | # # # | # # # | # # # | # # # | 0.819 | 0.842 | 0.977 | 0.884 | # # # | # # # | # # # | - - - | 0.826 | 0.849 | 0.996 | 0.895 | - - - | 0.41 | 1.63 | 1.55 | 1.46 | 1.48 | 1.45 | 1.48 | 11.67 | 12.11 | 19.36 | 0 | - - - | - - - | - - - | - - - | 1337 | 1301 | 1520 | 4158 | Over-range | 766 | 691 | 325 | 1943 | 170 | 161 | 298 | 1220 | 1097 | 1096 | 1482 | 3675 | 1097 | 1096 | 1482 | 3675 | - - - | - - - | - - - | - - -
5/7/2026 | 9:30:00 PM | 285.11 | 283.13 | 281.16 | 493.63 | 487.31 | 490.26 | 4.7198 | 4.6455 | 5.4227 | 2.8062 | 1.431 | 1.431 | 1.426 | 1.486 | 1.449 | 1.401 | Over-range | 60.02 | 1098 | 1106 | 1490 | 3694 | - - - | - - - | - - - | - - - | 1098 | 1106 | 1490 | 3694 | 754 | 678 | 89 | 1522 | - - - | - - - | - - - | - - - | 754 | 678 | 89 | 1522 | 1344 | 1310 | 1524 | 4178 | # # # | # # # | # # # | # # # | 0.817 | 0.844 | 0.978 | 0.884 | # # # | # # # | # # # | - - - | 0.824 | 0.851 | 0.997 | 0.895 | - - - | 0.412 | 1.63 | 1.58 | 1.47 | 1.5 | 1.46 | 1.51 | 11.65 | 12.12 | 19.59 | 0 | - - - | - - - | - - - | - - - | 1344 | 1310 | 1524 | 4178 | Over-range | 774 | 698 | 320 | 1951 | 172 | 162 | 301 | 1218 | 1099 | 1107 | 1487 | 3693 | 1099 | 1107 | 1487 | 3693 | - - - | - - - | - - - | - - -
5/7/2026 | 9:45:00 PM | 285.45 | 283.43 | 281.51 | 494.15 | 487.84 | 490.91 | 4.8836 | 4.9428 | 5.5042 | 2.8055 | 1.432 | 1.431 | 1.426 | 1.488 | 1.426 | 1.38 | Over-range | 60.01 | 1125 | 1210 | 1518 | 3853 | - - - | - - - | - - - | - - - | 1125 | 1210 | 1518 | 3853 | 803 | 682 | 47 | 1532 | - - - | - - - | - - - | - - - | 803 | 682 | 47 | 1532 | 1394 | 1399 | 1549 | 4342 | # # # | # # # | # # # | # # # | 0.807 | 0.865 | 0.98 | 0.887 | # # # | # # # | # # # | - - - | 0.815 | 0.87 | 0.999 | 0.898 | - - - | 0.398 | 1.68 | 1.59 | 1.48 | 1.51 | 1.48 | 1.52 | 11.29 | 11.4 | 19.36 | 0 | - - - | - - - | - - - | - - - | 1394 | 1399 | 1549 | 4342 | Over-range | 822 | 701 | 308 | 2001 | 178 | 165 | 302 | 1287 | 1126 | 1208 | 1520 | 3854 | 1126 | 1208 | 1520 | 3854 | - - - | - - - | - - - | - - -
5/7/2026 | 10:00:00 PM | 285.44 | 283.38 | 281.41 | 494.12 | 487.73 | 490.8 | 4.8721 | 4.9149 | 5.4985 | 2.8084 | 1.432 | 1.431 | 1.426 | 1.489 | 1.421 | 1.387 | Over-range | 60.02 | 1124 | 1204 | 1516 | 3844 | - - - | - - - | - - - | - - - | 1124 | 1204 | 1516 | 3844 | 799 | 680 | 48 | 1527 | - - - | - - - | - - - | - - - | 799 | 680 | 48 | 1527 | 1391 | 1392 | 1547 | 4330 | # # # | # # # | # # # | # # # | 0.808 | 0.865 | 0.98 | 0.888 | # # # | # # # | # # # | - - - | 0.815 | 0.87 | 0.999 | 0.898 | - - - | 0.397 | 1.7 | 1.57 | 1.5 | 1.53 | 1.5 | 1.54 | 11.32 | 11.41 | 19.41 | 0 | - - - | - - - | - - - | - - - | 1391 | 1392 | 1547 | 4330 | Over-range | 819 | 700 | 307 | 1993 | 180 | 163 | 303 | 1281 | 1123 | 1203 | 1518 | 3844 | 1123 | 1203 | 1518 | 3844 | - - - | - - - | - - - | - - -
5/7/2026 | 10:15:00 PM | 284.68 | 282.5 | 280.64 | 492.71 | 486.21 | 489.54 | 5.4127 | 5.9727 | 5.7836 | 2.7902 | 1.43 | 1.429 | 1.425 | 1.5 | 1.458 | 1.399 | Over-range | 60 | 1210 | 1537 | 1590 | 4336 | - - - | - - - | - - - | - - - | 1210 | 1537 | 1590 | 4336 | 935 | 665 | -103 | 1496 | - - - | - - - | - - - | - - - | 935 | 665 | -103 | 1496 | 1540 | 1683 | 1623 | 4846 | # # # | # # # | # # # | # # # | 0.786 | 0.913 | 0.98 | 0.895 | # # # | # # # | # # # | - - - | 0.791 | 0.918 | 0.997 | 0.904 | - - - | 0.345 | 1.66 | 1.57 | 1.49 | 1.51 | 1.48 | 1.52 | 10.02 | 9.63 | 18.67 | 0 | - - - | - - - | - - - | - - - | 1540 | 1683 | 1623 | 4846 | Over-range | 952 | 685 | 326 | 2163 | 180 | 164 | 304 | 1560 | 1209 | 1538 | 1589 | 4336 | 1209 | 1538 | 1589 | 4336 | - - - | - - - | - - - | - - -
5/7/2026 | 10:30:00 PM | 284.7 | 282.55 | 280.66 | 492.76 | 486.28 | 489.55 | 5.6167 | 6.2008 | 5.8613 | 2.7872 | 1.43 | 1.428 | 1.424 | 1.498 | 1.46 | 1.398 | Over-range | 60.01 | 1250 | 1610 | 1611 | 4471 | - - - | - - - | - - - | - - - | 1250 | 1610 | 1611 | 4471 | 975 | 662 | -112 | 1524 | - - - | - - - | - - - | - - - | 975 | 662 | -112 | 1524 | 1596 | 1749 | 1645 | 4990 | # # # | # # # | # # # | # # # | 0.783 | 0.92 | 0.979 | 0.896 | # # # | # # # | # # # | - - - | 0.782 | 0.916 | 0.988 | 0.896 | - - - | 0.341 | 1.65 | 1.58 | 1.48 | 1.5 | 1.48 | 1.52 | 9.8 | 9.33 | 18.51 | 0 | - - - | - - - | - - - | - - - | 1596 | 1749 | 1645 | 4990 | Over-range | 991 | 683 | 333 | 2216 | 175 | 164 | 303 | 1603 | 1264 | 1619 | 1621 | 4504 | 1264 | 1619 | 1621 | 4504 | - - - | - - - | - - - | - - -
5/7/2026 | 10:45:00 PM | 285.12 | 282.9 | 281.09 | 493.37 | 486.98 | 490.33 | 5.022 | 5.2318 | 5.5756 | 2.8024 | 1.43 | 1.429 | 1.424 | 1.492 | 1.469 | 1.393 | Over-range | 60.01 | 1145 | 1285 | 1533 | 3963 | - - - | - - - | - - - | - - - | 1145 | 1285 | 1533 | 3963 | 833 | 672 | 11 | 1516 | - - - | - - - | - - - | - - - | 833 | 672 | 11 | 1516 | 1427 | 1466 | 1566 | 4460 | # # # | # # # | # # # | # # # | 0.802 | 0.876 | 0.979 | 0.889 | # # # | # # # | # # # | - - - | 0.809 | 0.882 | 0.997 | 0.899 | - - - | 0.383 | 1.69 | 1.57 | 1.52 | 1.52 | 1.5 | 1.54 | 11.02 | 10.96 | 19.02 | 0 | - - - | - - - | - - - | - - - | 1427 | 1466 | 1566 | 4460 | Over-range | 851 | 692 | 319 | 2043 | 171 | 167 | 300 | 1364 | 1149 | 1284 | 1531 | 3964 | 1149 | 1284 | 1531 | 3964 | - - - | - - - | - - - | - - -
5/7/2026 | 11:00:00 PM | 285.69 | 283.51 | 281.66 | 494.45 | 487.98 | 491.3 | 4.6412 | 4.4867 | 5.3893 | 2.809 | 1.431 | 1.429 | 1.424 | 1.489 | 1.455 | 1.409 | Over-range | 60.01 | 1086 | 1054 | 1482 | 3623 | - - - | - - - | - - - | - - - | 1086 | 1054 | 1482 | 3623 | 739 | 685 | 118 | 1541 | - - - | - - - | - - - | - - - | 739 | 685 | 118 | 1541 | 1325 | 1269 | 1518 | 4112 | # # # | # # # | # # # | # # # | 0.82 | 0.831 | 0.977 | 0.881 | # # # | # # # | # # # | - - - | 0.827 | 0.838 | 0.996 | 0.892 | - - - | 0.426 | 1.68 | 1.58 | 1.51 | 1.52 | 1.5 | 1.54 | 11.93 | 12.45 | 19.69 | 0 | - - - | - - - | - - - | - - - | 1325 | 1269 | 1518 | 4112 | Over-range | 759 | 704 | 326 | 1946 | 173 | 165 | 301 | 1186 | 1088 | 1054 | 1480 | 3623 | 1088 | 1054 | 1480 | 3623 | - - - | - - - | - - - | - - -
5/7/2026 | 11:15:00 PM | 285.56 | 283.22 | 281.43 | 494.12 | 487.45 | 491.02 | 4.811 | 4.7956 | 5.4605 | 2.7996 | 1.43 | 1.428 | 1.424 | 1.493 | 1.428 | 1.386 | Over-range | 59.98 | 1114 | 1162 | 1505 | 3781 | - - - | - - - | - - - | - - - | 1114 | 1162 | 1505 | 3781 | 785 | 681 | 70 | 1536 | - - - | - - - | - - - | - - - | 785 | 681 | 70 | 1536 | 1374 | 1357 | 1537 | 4268 | # # # | # # # | # # # | # # # | 0.811 | 0.856 | 0.98 | 0.886 | # # # | # # # | # # # | - - - | 0.817 | 0.863 | 0.999 | 0.897 | - - - | 0.406 | 1.68 | 1.59 | 1.5 | 1.52 | 1.51 | 1.54 | 11.44 | 11.59 | 19.39 | 0 | - - - | - - - | - - - | - - - | 1374 | 1357 | 1537 | 4268 | Over-range | 804 | 700 | 309 | 1978 | 174 | 161 | 300 | 1246 | 1114 | 1164 | 1503 | 3781 | 1114 | 1164 | 1503 | 3781 | - - - | - - - | - - - | - - -
5/7/2026 | 11:30:00 PM | 285.91 | 283.6 | 281.73 | 494.74 | 488.1 | 491.55 | 4.8646 | 4.8888 | 5.4913 | 2.8083 | 1.43 | 1.429 | 1.424 | 1.493 | 1.419 | 1.378 | Over-range | 60.01 | 1123 | 1194 | 1516 | 3833 | - - - | - - - | - - - | - - - | 1123 | 1194 | 1516 | 3833 | 802 | 684 | 58 | 1545 | - - - | - - - | - - - | - - - | 802 | 684 | 58 | 1545 | 1391 | 1386 | 1547 | 4324 | # # # | # # # | # # # | # # # | 0.807 | 0.862 | 0.98 | 0.886 | # # # | # # # | # # # | - - - | 0.814 | 0.868 | 0.999 | 0.897 | - - - | 0.403 | 1.72 | 1.6 | 1.52 | 1.54 | 1.52 | 1.56 | 11.34 | 11.47 | 19.38 | 0 | - - - | - - - | - - - | - - - | 1391 | 1386 | 1547 | 4324 | Over-range | 821 | 704 | 307 | 2001 | 172 | 166 | 301 | 1272 | 1126 | 1194 | 1514 | 3834 | 1126 | 1194 | 1514 | 3834 | - - - | - - - | - - - | - - -
5/7/2026 | 11:45:00 PM | 286.28 | 283.95 | 282.03 | 495.43 | 488.56 | 492.15 | 5.2482 | 5.6267 | 5.692 | 2.8033 | 1.429 | 1.428 | 1.423 | 1.502 | 1.437 | 1.356 | Over-range | 60.01 | 1184 | 1427 | 1574 | 4185 | - - - | - - - | - - - | - - - | 1184 | 1427 | 1574 | 4185 | 906 | 685 | -40 | 1550 | - - - | - - - | - - - | - - - | 906 | 685 | -40 | 1550 | 1501 | 1593 | 1605 | 4700 | # # # | # # # | # # # | # # # | 0.789 | 0.896 | 0.981 | 0.891 | # # # | # # # | # # # | - - - | 0.795 | 0.901 | 0.999 | 0.9 | - - - | 0.37 | 1.69 | 1.61 | 1.51 | 1.53 | 1.52 | 1.54 | 10.54 | 10.33 | 19.05 | 0 | - - - | - - - | - - - | - - - | 1501 | 1593 | 1605 | 4700 | Over-range | 922 | 707 | 314 | 2137 | 174 | 172 | 306 | 1469 | 1188 | 1426 | 1572 | 4186 | 1188 | 1426 | 1572 | 4186 | - - - | - - - | - - - | - - -
5/8/2026 | 12:00:00 AM | 286.08 | 283.86 | 281.98 | 495.13 | 488.5 | 491.93 | 5.5316 | 6.1728 | 5.8521 | 2.7992 | 1.43 | 1.428 | 1.423 | 1.504 | 1.455 | 1.357 | Over-range | 60 | 1230 | 1603 | 1617 | 4450 | - - - | - - - | - - - | - - - | 1230 | 1603 | 1617 | 4450 | 980 | 683 | -117 | 1545 | - - - | - - - | - - - | - - - | 980 | 683 | -117 | 1545 | 1582 | 1751 | 1650 | 4983 | # # # | # # # | # # # | # # # | 0.777 | 0.915 | 0.98 | 0.893 | # # # | # # # | # # # | - - - | 0.783 | 0.92 | 0.997 | 0.901 | - - - | 0.347 | 1.71 | 1.57 | 1.49 | 1.52 | 1.5 | 1.54 | 9.98 | 9.44 | 18.57 | 0 | - - - | - - - | - - - | - - - | 1582 | 1751 | 1650 | 4983 | Over-range | 995 | 704 | 329 | 2244 | 174 | 174 | 306 | 1627 | 1234 | 1602 | 1614 | 4450 | 1234 | 1602 | 1614 | 4450 | - - - | - - - | - - - | - - -
5/8/2026 | 12:15:00 AM | 284.52 | 282.29 | 280.42 | 492.38 | 485.88 | 489.17 | 4.7576 | 4.7261 | 5.4341 | 2.8 | 1.429 | 1.427 | 1.423 | 1.493 | 1.459 | 1.393 | Over-range | 59.99 | 1102 | 1124 | 1490 | 3716 | - - - | - - - | - - - | - - - | 1102 | 1124 | 1490 | 3716 | 759 | 666 | 78 | 1503 | - - - | - - - | - - - | - - - | 759 | 666 | 78 | 1503 | 1350 | 1322 | 1523 | 4195 | # # # | # # # | # # # | # # # | 0.817 | 0.85 | 0.978 | 0.886 | # # # | # # # | # # # | - - - | 0.824 | 0.856 | 0.996 | 0.896 | - - - | 0.405 | 1.69 | 1.58 | 1.51 | 1.53 | 1.5 | 1.55 | 11.52 | 11.67 | 19.05 | 0 | - - - | - - - | - - - | - - - | 1350 | 1322 | 1523 | 4195 | Over-range | 778 | 685 | 315 | 1945 | 168 | 161 | 292 | 1231 | 1106 | 1122 | 1488 | 3717 | 1106 | 1122 | 1488 | 3717 | - - - | - - - | - - - | - - -
5/8/2026 | 12:30:00 AM | 284.38 | 281.94 | 280.23 | 491.97 | 485.31 | 488.98 | 4.7058 | 4.6104 | 5.3819 | 2.783 | 1.428 | 1.425 | 1.421 | 1.497 | 1.442 | 1.4 | Over-range | 60 | 1096 | 1100 | 1476 | 3671 | - - - | - - - | - - - | - - - | 1096 | 1100 | 1476 | 3671 | 746 | 661 | 84 | 1492 | - - - | - - - | - - - | - - - | 746 | 661 | 84 | 1492 | 1337 | 1295 | 1508 | 4139 | # # # | # # # | # # # | # # # | 0.82 | 0.849 | 0.979 | 0.887 | # # # | # # # | # # # | - - - | 0.828 | 0.855 | 0.998 | 0.898 | - - - | 0.406 | 1.66 | 1.55 | 1.49 | 1.5 | 1.48 | 1.52 | 11.45 | 11.7 | 19.32 | 0 | - - - | - - - | - - - | - - - | 1337 | 1295 | 1508 | 4139 | Over-range | 765 | 680 | 310 | 1911 | 167 | 158 | 292 | 1192 | 1099 | 1099 | 1474 | 3672 | 1099 | 1099 | 1474 | 3672 | - - - | - - - | - - - | - - -
5/8/2026 | 12:45:00 AM | 284.75 | 282.31 | 280.51 | 492.66 | 485.88 | 489.49 | 4.8986 | 4.7785 | 5.4656 | 2.7892 | 1.428 | 1.426 | 1.422 | 1.495 | 1.426 | 1.394 | Over-range | 60 | 1136 | 1161 | 1500 | 3797 | - - - | - - - | - - - | - - - | 1136 | 1161 | 1500 | 3797 | 785 | 665 | 87 | 1538 | - - - | - - - | - - - | - - - | 785 | 665 | 87 | 1538 | 1392 | 1348 | 1533 | 4272 | # # # | # # # | # # # | # # # | 0.816 | 0.861 | 0.978 | 0.889 | # # # | # # # | # # # | - - - | 0.814 | 0.86 | 0.985 | 0.889 | - - - | 0.405 | 1.69 | 1.56 | 1.51 | 1.53 | 1.5 | 1.54 | 11.09 | 11.26 | 19.09 | 0 | - - - | - - - | - - - | - - - | 1392 | 1348 | 1533 | 4272 | Over-range | 804 | 684 | 314 | 1959 | 168 | 159 | 294 | 1207 | 1152 | 1169 | 1510 | 3831 | 1152 | 1169 | 1510 | 3831 | - - - | - - - | - - - | - - -
5/8/2026 | 1:00:00 AM | 284.87 | 282.35 | 280.58 | 492.77 | 485.99 | 489.67 | 5.3231 | 5.7864 | 5.7046 | 2.7791 | 1.429 | 1.426 | 1.422 | 1.506 | 1.448 | 1.331 | Over-range | 60.01 | 1197 | 1482 | 1570 | 4250 | - - - | - - - | - - - | - - - | 1197 | 1482 | 1570 | 4250 | 914 | 660 | -79 | 1494 | - - - | - - - | - - - | - - - | 914 | 660 | -79 | 1494 | 1516 | 1632 | 1600 | 4748 | # # # | # # # | # # # | # # # | 0.79 | 0.909 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.795 | 0.913 | 0.998 | 0.904 | - - - | 0.352 | 1.71 | 1.56 | 1.51 | 1.53 | 1.51 | 1.55 | 10.05 | 9.67 | 18.62 | 0 | - - - | - - - | - - - | - - - | 1516 | 1632 | 1600 | 4748 | Over-range | 930 | 681 | 311 | 2118 | 169 | 165 | 298 | 1500 | 1200 | 1481 | 1568 | 4250 | 1200 | 1481 | 1568 | 4250 | - - - | - - - | - - - | - - -
5/8/2026 | 1:15:00 AM | 284.79 | 282.18 | 280.49 | 492.6 | 485.66 | 489.58 | 5.3524 | 5.8541 | 5.7379 | 2.7777 | 1.428 | 1.425 | 1.421 | 1.506 | 1.447 | 1.333 | Over-range | 60 | 1201 | 1499 | 1578 | 4278 | - - - | - - - | - - - | - - - | 1201 | 1499 | 1578 | 4278 | 920 | 659 | -86 | 1492 | - - - | - - - | - - - | - - - | 920 | 659 | -86 | 1492 | 1523 | 1647 | 1609 | 4778 | # # # | # # # | # # # | # # # | 0.789 | 0.91 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.794 | 0.914 | 0.997 | 0.904 | - - - | 0.349 | 1.69 | 1.56 | 1.46 | 1.51 | 1.49 | 1.52 | 9.98 | 9.49 | 18.31 | 0 | - - - | - - - | - - - | - - - | 1523 | 1647 | 1609 | 4778 | Over-range | 936 | 679 | 312 | 2128 | 172 | 163 | 294 | 1515 | 1204 | 1496 | 1579 | 4279 | 1204 | 1496 | 1579 | 4279 | - - - | - - - | - - - | - - -
5/8/2026 | 1:30:00 AM | 284.84 | 282.09 | 280.47 | 492.58 | 485.48 | 489.67 | 4.5568 | 4.3496 | 5.3074 | 2.772 | 1.428 | 1.425 | 1.422 | 1.492 | 1.48 | 1.423 | Over-range | 60 | 1072 | 1005 | 1452 | 3529 | - - - | - - - | - - - | - - - | 1072 | 1005 | 1452 | 3529 | 707 | 664 | 128 | 1500 | - - - | - - - | - - - | - - - | 707 | 664 | 128 | 1500 | 1296 | 1218 | 1488 | 4002 | # # # | # # # | # # # | # # # | 0.827 | 0.825 | 0.976 | 0.882 | # # # | # # # | # # # | - - - | 0.834 | 0.832 | 0.995 | 0.893 | - - - | 0.425 | 1.69 | 1.57 | 1.5 | 1.52 | 1.5 | 1.54 | 11.91 | 12.34 | 19.22 | 0 | - - - | - - - | - - - | - - - | 1296 | 1218 | 1488 | 4002 | Over-range | 727 | 682 | 323 | 1886 | 168 | 153 | 288 | 1141 | 1072 | 1007 | 1449 | 3528 | 1072 | 1007 | 1449 | 3528 | - - - | - - - | - - - | - - -
5/8/2026 | 1:45:00 AM | 284.82 | 282.22 | 280.57 | 492.62 | 485.81 | 489.66 | 4.6603 | 4.5767 | 5.4064 | 2.7821 | 1.428 | 1.425 | 1.421 | 1.494 | 1.469 | 1.407 | Over-range | 60.02 | 1088 | 1076 | 1482 | 3646 | - - - | - - - | - - - | - - - | 1088 | 1076 | 1482 | 3646 | 735 | 668 | 98 | 1501 | - - - | - - - | - - - | - - - | 735 | 668 | 98 | 1501 | 1324 | 1281 | 1516 | 4122 | # # # | # # # | # # # | # # # | 0.822 | 0.84 | 0.977 | 0.885 | # # # | # # # | # # # | - - - | 0.829 | 0.847 | 0.996 | 0.895 | - - - | 0.411 | 1.69 | 1.54 | 1.48 | 1.5 | 1.48 | 1.51 | 11.58 | 11.9 | 19.05 | 0 | - - - | - - - | - - - | - - - | 1324 | 1281 | 1516 | 4122 | Over-range | 753 | 687 | 318 | 1920 | 166 | 160 | 291 | 1194 | 1091 | 1076 | 1480 | 3646 | 1091 | 1076 | 1480 | 3646 | - - - | - - - | - - - | - - -
5/8/2026 | 2:00:00 AM | 285.15 | 282.37 | 280.77 | 493.11 | 485.97 | 490.21 | 4.7898 | 4.7828 | 5.4235 | 2.7677 | 1.428 | 1.425 | 1.421 | 1.498 | 1.446 | 1.392 | Over-range | 60.01 | 1110 | 1154 | 1491 | 3756 | - - - | - - - | - - - | - - - | 1110 | 1154 | 1491 | 3756 | 773 | 665 | 66 | 1504 | - - - | - - - | - - - | - - - | 773 | 665 | 66 | 1504 | 1364 | 1344 | 1522 | 4230 | # # # | # # # | # # # | # # # | 0.814 | 0.859 | 0.98 | 0.888 | # # # | # # # | # # # | - - - | 0.821 | 0.865 | 0.998 | 0.898 | - - - | 0.401 | 1.68 | 1.56 | 1.49 | 1.51 | 1.49 | 1.52 | 11.2 | 11.36 | 19.08 | 0 | - - - | - - - | - - - | - - - | 1364 | 1344 | 1522 | 4230 | Over-range | 792 | 684 | 306 | 1946 | 171 | 158 | 291 | 1232 | 1111 | 1152 | 1493 | 3757 | 1111 | 1152 | 1493 | 3757 | - - - | - - - | - - - | - - -
5/8/2026 | 2:15:00 AM | 285.15 | 282.34 | 280.77 | 493.07 | 485.91 | 490.24 | 5.0604 | 5.2834 | 5.5731 | 2.7681 | 1.427 | 1.424 | 1.42 | 1.506 | 1.431 | 1.35 | Over-range | 60.01 | 1155 | 1327 | 1537 | 4020 | - - - | - - - | - - - | - - - | 1155 | 1327 | 1537 | 4020 | 847 | 662 | -8 | 1500 | - - - | - - - | - - - | - - - | 847 | 662 | -8 | 1500 | 1443 | 1492 | 1565 | 4499 | # # # | # # # | # # # | # # # | 0.801 | 0.89 | 0.983 | 0.893 | # # # | # # # | # # # | - - - | 0.807 | 0.895 | 1 | 0.903 | - - - | 0.373 | 1.65 | 1.53 | 1.48 | 1.49 | 1.48 | 1.5 | 10.48 | 10.29 | 18.7 | 0 | - - - | - - - | - - - | - - - | 1443 | 1492 | 1565 | 4499 | Over-range | 864 | 681 | 292 | 2021 | 171 | 160 | 291 | 1354 | 1157 | 1325 | 1539 | 4021 | 1157 | 1325 | 1539 | 4021 | - - - | - - - | - - - | - - -
5/8/2026 | 2:30:00 AM | 285.25 | 282.5 | 280.86 | 493.27 | 486.2 | 490.36 | 4.9804 | 5.1256 | 5.5252 | 2.769 | 1.427 | 1.424 | 1.42 | 1.503 | 1.42 | 1.363 | Over-range | 60 | 1142 | 1276 | 1524 | 3942 | - - - | - - - | - - - | - - - | 1142 | 1276 | 1524 | 3942 | 828 | 665 | 15 | 1509 | - - - | - - - | - - - | - - - | 828 | 665 | 15 | 1509 | 1421 | 1448 | 1552 | 4420 | # # # | # # # | # # # | # # # | 0.804 | 0.881 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.81 | 0.887 | 0.999 | 0.901 | - - - | 0.383 | 1.66 | 1.55 | 1.46 | 1.49 | 1.48 | 1.5 | 10.67 | 10.53 | 18.82 | 0 | - - - | - - - | - - - | - - - | 1421 | 1448 | 1552 | 4420 | Over-range | 844 | 684 | 292 | 1999 | 167 | 158 | 291 | 1311 | 1144 | 1276 | 1522 | 3942 | 1144 | 1276 | 1522 | 3942 | - - - | - - - | - - - | - - -
5/8/2026 | 2:45:00 AM | 285.31 | 282.43 | 280.88 | 493.28 | 486.08 | 490.5 | 4.7082 | 4.6153 | 5.3821 | 2.762 | 1.426 | 1.423 | 1.419 | 1.497 | 1.434 | 1.402 | Over-range | 60.01 | 1098 | 1109 | 1482 | 3689 | - - - | - - - | - - - | - - - | 1098 | 1109 | 1482 | 3689 | 754 | 667 | 88 | 1509 | - - - | - - - | - - - | - - - | 754 | 667 | 88 | 1509 | 1343 | 1303 | 1512 | 4158 | # # # | # # # | # # # | # # # | 0.818 | 0.851 | 0.98 | 0.887 | # # # | # # # | # # # | - - - | 0.824 | 0.857 | 0.999 | 0.898 | - - - | 0.409 | 1.66 | 1.53 | 1.46 | 1.49 | 1.48 | 1.49 | 11.34 | 11.36 | 18.91 | 0 | - - - | - - - | - - - | - - - | 1343 | 1303 | 1512 | 4158 | Over-range | 774 | 684 | 300 | 1918 | 171 | 151 | 286 | 1185 | 1097 | 1110 | 1483 | 3689 | 1097 | 1110 | 1483 | 3689 | - - - | - - - | - - - | - - -
5/8/2026 | 3:00:00 AM | 285.53 | 282.65 | 281.05 | 493.68 | 486.4 | 490.81 | 4.8225 | 4.8282 | 5.4509 | 2.7697 | 1.426 | 1.424 | 1.419 | 1.501 | 1.426 | 1.386 | Over-range | 60.01 | 1117 | 1178 | 1503 | 3797 | - - - | - - - | - - - | - - - | 1117 | 1178 | 1503 | 3797 | 786 | 669 | 60 | 1515 | - - - | - - - | - - - | - - - | 786 | 669 | 60 | 1515 | 1377 | 1363 | 1532 | 4272 | # # # | # # # | # # # | # # # | 0.811 | 0.864 | 0.981 | 0.889 | # # # | # # # | # # # | - - - | 0.818 | 0.869 | 0.999 | 0.899 | - - - | 0.399 | 1.66 | 1.54 | 1.46 | 1.49 | 1.48 | 1.49 | 11.09 | 11.09 | 18.88 | 0 | - - - | - - - | - - - | - - - | 1377 | 1363 | 1532 | 4272 | Over-range | 805 | 687 | 296 | 1957 | 172 | 153 | 289 | 1238 | 1116 | 1178 | 1503 | 3797 | 1116 | 1178 | 1503 | 3797 | - - - | - - - | - - - | - - -
5/8/2026 | 3:15:00 AM | 285.82 | 283.02 | 281.47 | 494.17 | 487.18 | 491.4 | 5.3644 | 5.6719 | 5.7015 | 2.768 | 1.427 | 1.424 | 1.419 | 1.505 | 1.439 | 1.336 | Over-range | 60 | 1212 | 1447 | 1575 | 4234 | - - - | - - - | - - - | - - - | 1212 | 1447 | 1575 | 4234 | 916 | 671 | -28 | 1558 | - - - | - - - | - - - | - - - | 916 | 671 | -28 | 1558 | 1530 | 1604 | 1605 | 4738 | # # # | # # # | # # # | # # # | 0.792 | 0.903 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.789 | 0.899 | 0.99 | 0.894 | - - - | 0.368 | 1.66 | 1.53 | 1.45 | 1.49 | 1.47 | 1.49 | 10.08 | 9.91 | 18.62 | 0 | - - - | - - - | - - - | - - - | 1530 | 1604 | 1605 | 4738 | Over-range | 933 | 690 | 308 | 2127 | 175 | 159 | 296 | 1441 | 1222 | 1458 | 1586 | 4266 | 1222 | 1458 | 1586 | 4266 | - - - | - - - | - - - | - - -
5/8/2026 | 3:30:00 AM | 285.97 | 283.22 | 281.63 | 494.56 | 487.46 | 491.64 | 4.7742 | 4.7657 | 5.4378 | 2.7742 | 1.427 | 1.424 | 1.42 | 1.497 | 1.465 | 1.399 | Over-range | 60 | 1106 | 1134 | 1497 | 3737 | - - - | - - - | - - - | - - - | 1106 | 1134 | 1497 | 3737 | 774 | 678 | 86 | 1538 | - - - | - - - | - - - | - - - | 774 | 678 | 86 | 1538 | 1361 | 1337 | 1531 | 4229 | # # # | # # # | # # # | # # # | 0.812 | 0.848 | 0.978 | 0.884 | # # # | # # # | # # # | - - - | 0.819 | 0.855 | 0.996 | 0.894 | - - - | 0.411 | 1.66 | 1.55 | 1.45 | 1.49 | 1.47 | 1.49 | 11.45 | 11.69 | 18.97 | 0 | - - - | - - - | - - - | - - - | 1361 | 1337 | 1531 | 4229 | Over-range | 793 | 696 | 316 | 1977 | 168 | 158 | 289 | 1238 | 1107 | 1135 | 1495 | 3737 | 1107 | 1135 | 1495 | 3737 | - - - | - - - | - - - | - - -
5/8/2026 | 3:45:00 AM | 285.92 | 283.1 | 281.6 | 494.38 | 487.32 | 491.6 | 4.7036 | 4.6487 | 5.4093 | 2.7654 | 1.427 | 1.424 | 1.421 | 1.498 | 1.446 | 1.403 | Over-range | 60.01 | 1093 | 1111 | 1491 | 3696 | - - - | - - - | - - - | - - - | 1093 | 1111 | 1491 | 3696 | 762 | 677 | 93 | 1533 | - - - | - - - | - - - | - - - | 762 | 677 | 93 | 1533 | 1343 | 1312 | 1523 | 4178 | # # # | # # # | # # # | # # # | 0.814 | 0.847 | 0.979 | 0.884 | # # # | # # # | # # # | - - - | 0.821 | 0.854 | 0.997 | 0.895 | - - - | 0.415 | 1.66 | 1.56 | 1.45 | 1.5 | 1.48 | 1.5 | 11.42 | 11.65 | 19.09 | 0 | - - - | - - - | - - - | - - - | 1343 | 1312 | 1523 | 4178 | Over-range | 781 | 694 | 309 | 1949 | 167 | 155 | 290 | 1202 | 1094 | 1113 | 1488 | 3695 | 1094 | 1113 | 1488 | 3695 | - - - | - - - | - - - | - - -
5/8/2026 | 4:00:00 AM | 286.03 | 283.33 | 281.73 | 494.66 | 487.71 | 491.76 | 4.6956 | 4.5875 | 5.3966 | 2.7779 | 1.426 | 1.424 | 1.42 | 1.496 | 1.441 | 1.406 | Over-range | 60.02 | 1096 | 1097 | 1489 | 3682 | - - - | - - - | - - - | - - - | 1096 | 1097 | 1489 | 3682 | 758 | 679 | 102 | 1539 | - - - | - - - | - - - | - - - | 758 | 679 | 102 | 1539 | 1343 | 1299 | 1520 | 4163 | # # # | # # # | # # # | # # # | 0.816 | 0.844 | 0.98 | 0.884 | # # # | # # # | # # # | - - - | 0.822 | 0.851 | 0.997 | 0.895 | - - - | 0.418 | 1.64 | 1.56 | 1.44 | 1.49 | 1.46 | 1.48 | 11.5 | 11.65 | 19.03 | 0 | - - - | - - - | - - - | - - - | 1343 | 1299 | 1520 | 4163 | Over-range | 776 | 697 | 306 | 1942 | 167 | 155 | 289 | 1185 | 1097 | 1098 | 1486 | 3682 | 1097 | 1098 | 1486 | 3682 | - - - | - - - | - - - | - - -
5/8/2026 | 4:15:00 AM | 285.8 | 283.04 | 281.45 | 494.23 | 487.13 | 491.37 | 5.1283 | 5.4149 | 5.6099 | 2.765 | 1.427 | 1.424 | 1.421 | 1.501 | 1.432 | 1.345 | Over-range | 60 | 1165 | 1363 | 1550 | 4079 | - - - | - - - | - - - | - - - | 1165 | 1363 | 1550 | 4079 | 871 | 672 | -15 | 1527 | - - - | - - - | - - - | - - - | 871 | 672 | -15 | 1527 | 1465 | 1529 | 1579 | 4572 | # # # | # # # | # # # | # # # | 0.796 | 0.891 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.802 | 0.896 | 0.999 | 0.901 | - - - | 0.375 | 1.66 | 1.56 | 1.48 | 1.5 | 1.48 | 1.5 | 10.41 | 10.21 | 18.65 | 0 | - - - | - - - | - - - | - - - | 1465 | 1529 | 1579 | 4572 | Over-range | 887 | 691 | 298 | 2067 | 168 | 160 | 292 | 1390 | 1167 | 1364 | 1547 | 4078 | 1167 | 1364 | 1547 | 4078 | - - - | - - - | - - - | - - -
5/8/2026 | 4:30:00 AM | 285.9 | 283.21 | 281.62 | 494.46 | 487.46 | 491.57 | 5.2788 | 5.7127 | 5.6976 | 2.764 | 1.426 | 1.424 | 1.42 | 1.504 | 1.437 | 1.321 | Over-range | 60.01 | 1189 | 1457 | 1575 | 4222 | - - - | - - - | - - - | - - - | 1189 | 1457 | 1575 | 4222 | 910 | 675 | -55 | 1529 | - - - | - - - | - - - | - - - | 910 | 675 | -55 | 1529 | 1508 | 1614 | 1604 | 4727 | # # # | # # # | # # # | # # # | 0.789 | 0.903 | 0.982 | 0.893 | # # # | # # # | # # # | - - - | 0.794 | 0.907 | 0.999 | 0.902 | - - - | 0.362 | 1.66 | 1.54 | 1.46 | 1.49 | 1.47 | 1.49 | 10.15 | 9.73 | 18.36 | 0 | - - - | - - - | - - - | - - - | 1508 | 1614 | 1604 | 4727 | Over-range | 927 | 693 | 303 | 2126 | 175 | 159 | 292 | 1475 | 1188 | 1458 | 1575 | 4221 | 1188 | 1458 | 1575 | 4221 | - - - | - - - | - - - | - - -
5/8/2026 | 4:45:00 AM | 285.56 | 282.82 | 281.28 | 493.78 | 486.89 | 490.99 | 4.812 | 4.8515 | 5.4536 | 2.7659 | 1.426 | 1.424 | 1.421 | 1.494 | 1.463 | 1.391 | Over-range | 59.99 | 1111 | 1160 | 1500 | 3771 | - - - | - - - | - - - | - - - | 1111 | 1160 | 1500 | 3771 | 780 | 672 | 71 | 1524 | - - - | - - - | - - - | - - - | 780 | 672 | 71 | 1524 | 1369 | 1357 | 1533 | 4259 | # # # | # # # | # # # | # # # | 0.811 | 0.855 | 0.979 | 0.885 | # # # | # # # | # # # | - - - | 0.817 | 0.861 | 0.996 | 0.895 | - - - | 0.404 | 1.66 | 1.54 | 1.46 | 1.49 | 1.48 | 1.5 | 11.24 | 11.46 | 18.76 | 0 | - - - | - - - | - - - | - - - | 1369 | 1357 | 1533 | 4259 | Over-range | 799 | 690 | 313 | 1978 | 172 | 154 | 287 | 1255 | 1110 | 1160 | 1501 | 3771 | 1110 | 1160 | 1501 | 3771 | - - - | - - - | - - - | - - -
5/8/2026 | 5:00:00 AM | 285.66 | 282.95 | 281.35 | 494.06 | 486.94 | 491.17 | 4.7004 | 4.6055 | 5.393 | 2.7679 | 1.426 | 1.424 | 1.42 | 1.493 | 1.443 | 1.406 | Over-range | 60.03 | 1096 | 1099 | 1485 | 3681 | - - - | - - - | - - - | - - - | 1096 | 1099 | 1485 | 3681 | 754 | 673 | 97 | 1524 | - - - | - - - | - - - | - - - | 754 | 673 | 97 | 1524 | 1342 | 1299 | 1517 | 4158 | # # # | # # # | # # # | # # # | 0.817 | 0.846 | 0.979 | 0.885 | # # # | # # # | # # # | - - - | 0.823 | 0.852 | 0.997 | 0.895 | - - - | 0.414 | 1.66 | 1.57 | 1.47 | 1.49 | 1.49 | 1.5 | 11.35 | 11.72 | 19.02 | 0 | - - - | - - - | - - - | - - - | 1342 | 1299 | 1517 | 4158 | Over-range | 773 | 690 | 308 | 1934 | 169 | 153 | 288 | 1188 | 1095 | 1101 | 1484 | 3681 | 1095 | 1101 | 1484 | 3681 | - - - | - - - | - - - | - - -
5/8/2026 | 5:15:00 AM | 285.19 | 282.51 | 280.9 | 493.26 | 486.2 | 490.36 | 4.8055 | 4.7981 | 5.4367 | 2.7603 | 1.427 | 1.425 | 1.422 | 1.49 | 1.424 | 1.388 | Over-range | 60.01 | 1113 | 1170 | 1499 | 3781 | - - - | - - - | - - - | - - - | 1113 | 1170 | 1499 | 3781 | 782 | 666 | 64 | 1512 | - - - | - - - | - - - | - - - | 782 | 666 | 64 | 1512 | 1370 | 1355 | 1527 | 4252 | # # # | # # # | # # # | # # # | 0.812 | 0.863 | 0.981 | 0.889 | # # # | # # # | # # # | - - - | 0.818 | 0.868 | 0.999 | 0.899 | - - - | 0.4 | 1.67 | 1.6 | 1.55 | 1.53 | 1.53 | 1.56 | 10.96 | 11.08 | 18.7 | 0 | - - - | - - - | - - - | - - - | 1370 | 1355 | 1527 | 4252 | Over-range | 800 | 684 | 293 | 1946 | 168 | 154 | 285 | 1224 | 1113 | 1169 | 1500 | 3782 | 1113 | 1169 | 1500 | 3782 | - - - | - - - | - - - | - - -
5/8/2026 | 5:30:00 AM | 285.13 | 282.53 | 280.93 | 493.19 | 486.34 | 490.27 | 4.8549 | 4.8936 | 5.4481 | 2.7521 | 1.427 | 1.425 | 1.422 | 1.49 | 1.42 | 1.383 | Over-range | 60 | 1120 | 1201 | 1502 | 3824 | - - - | - - - | - - - | - - - | 1120 | 1201 | 1502 | 3824 | 796 | 665 | 52 | 1513 | - - - | - - - | - - - | - - - | 796 | 665 | 52 | 1513 | 1384 | 1382 | 1530 | 4297 | # # # | # # # | # # # | # # # | 0.809 | 0.869 | 0.982 | 0.89 | # # # | # # # | # # # | - - - | 0.815 | 0.875 | 0.999 | 0.9 | - - - | 0.396 | 1.7 | 1.62 | 1.55 | 1.54 | 1.54 | 1.57 | 10.79 | 10.98 | 18.81 | 0 | - - - | - - - | - - - | - - - | 1384 | 1382 | 1530 | 4297 | Over-range | 813 | 684 | 293 | 1961 | 167 | 158 | 288 | 1246 | 1122 | 1199 | 1504 | 3825 | 1122 | 1199 | 1504 | 3825 | - - - | - - - | - - - | - - -
5/8/2026 | 5:45:00 AM | 284.97 | 282.39 | 280.74 | 492.97 | 485.97 | 490.01 | 4.885 | 4.8276 | 5.458 | 2.7593 | 1.427 | 1.425 | 1.422 | 1.487 | 1.422 | 1.393 | Over-range | 60 | 1130 | 1179 | 1502 | 3811 | - - - | - - - | - - - | - - - | 1130 | 1179 | 1502 | 3811 | 793 | 664 | 76 | 1533 | - - - | - - - | - - - | - - - | 793 | 664 | 76 | 1533 | 1390 | 1363 | 1532 | 4284 | # # # | # # # | # # # | # # # | 0.813 | 0.865 | 0.98 | 0.889 | # # # | # # # | # # # | - - - | 0.811 | 0.871 | 0.997 | 0.896 | - - - | 0.402 | 1.7 | 1.63 | 1.56 | 1.54 | 1.55 | 1.58 | 10.73 | 11.01 | 18.65 | 0 | - - - | - - - | - - - | - - - | 1390 | 1363 | 1532 | 4284 | Over-range | 809 | 682 | 300 | 1958 | 163 | 155 | 286 | 1214 | 1142 | 1179 | 1499 | 3820 | 1142 | 1179 | 1499 | 3820 | - - - | - - - | - - - | - - -
5/8/2026 | 6:00:00 AM | 284.55 | 281.92 | 280.34 | 492.16 | 485.19 | 489.35 | 5.4114 | 5.9088 | 5.7439 | 2.7456 | 1.427 | 1.426 | 1.422 | 1.495 | 1.458 | 1.308 | Over-range | 60 | 1212 | 1519 | 1579 | 4311 | - - - | - - - | - - - | - - - | 1212 | 1519 | 1579 | 4311 | 932 | 652 | -81 | 1503 | - - - | - - - | - - - | - - - | 932 | 652 | -81 | 1503 | 1538 | 1662 | 1610 | 4810 | # # # | # # # | # # # | # # # | 0.788 | 0.914 | 0.981 | 0.896 | # # # | # # # | # # # | - - - | 0.794 | 0.918 | 0.997 | 0.905 | - - - | 0.349 | 1.72 | 1.63 | 1.58 | 1.55 | 1.57 | 1.61 | 9.52 | 9.33 | 17.93 | 0 | - - - | - - - | - - - | - - - | 1538 | 1662 | 1610 | 4810 | Over-range | 947 | 672 | 311 | 2135 | 166 | 161 | 287 | 1509 | 1216 | 1517 | 1580 | 4312 | 1216 | 1517 | 1580 | 4312 | - - - | - - - | - - - | - - -
5/8/2026 | 6:15:00 AM | 283.86 | 281.29 | 279.53 | 491.05 | 483.97 | 487.99 | 5.2262 | 5.6294 | 5.6483 | 2.7398 | 1.426 | 1.426 | 1.422 | 1.488 | 1.449 | 1.32 | Over-range | 59.98 | 1177 | 1432 | 1551 | 4160 | - - - | - - - | - - - | - - - | 1177 | 1432 | 1551 | 4160 | 885 | 645 | -57 | 1472 | - - - | - - - | - - - | - - - | 885 | 645 | -57 | 1472 | 1482 | 1579 | 1578 | 4640 | # # # | # # # | # # # | # # # | 0.794 | 0.907 | 0.983 | 0.897 | # # # | # # # | # # # | - - - | 0.8 | 0.911 | 0.999 | 0.905 | - - - | 0.354 | 1.74 | 1.72 | 1.63 | 1.58 | 1.61 | 1.65 | 9.78 | 9.46 | 17.78 | 0 | - - - | - - - | - - - | - - - | 1482 | 1579 | 1578 | 4640 | Over-range | 900 | 663 | 292 | 2053 | 166 | 153 | 280 | 1429 | 1179 | 1429 | 1554 | 4162 | 1179 | 1429 | 1554 | 4162 | - - - | - - - | - - - | - - -
5/8/2026 | 6:30:00 AM | 284 | 281.57 | 279.77 | 491.43 | 484.41 | 488.32 | 4.9371 | 5.0581 | 5.4926 | 2.7443 | 1.426 | 1.426 | 1.422 | 1.483 | 1.426 | 1.36 | Over-range | 60 | 1132 | 1258 | 1511 | 3901 | - - - | - - - | - - - | - - - | 1132 | 1258 | 1511 | 3901 | 811 | 651 | 20 | 1481 | - - - | - - - | - - - | - - - | 811 | 651 | 20 | 1481 | 1402 | 1424 | 1537 | 4363 | # # # | # # # | # # # | # # # | 0.808 | 0.883 | 0.983 | 0.894 | # # # | # # # | # # # | - - - | 0.813 | 0.887 | 1 | 0.903 | - - - | 0.38 | 1.73 | 1.68 | 1.6 | 1.56 | 1.58 | 1.62 | 10.35 | 10.21 | 18.13 | 0 | - - - | - - - | - - - | - - - | 1402 | 1424 | 1537 | 4363 | Over-range | 827 | 668 | 280 | 1954 | 164 | 151 | 279 | 1274 | 1134 | 1255 | 1513 | 3902 | 1134 | 1255 | 1513 | 3902 | - - - | - - - | - - - | - - -
5/8/2026 | 6:45:00 AM | 283.94 | 281.57 | 279.77 | 491.35 | 484.44 | 488.27 | 5.1883 | 5.5633 | 5.6304 | 2.7382 | 1.426 | 1.426 | 1.421 | 1.487 | 1.447 | 1.325 | Over-range | 59.99 | 1171 | 1411 | 1548 | 4129 | - - - | - - - | - - - | - - - | 1171 | 1411 | 1548 | 4129 | 876 | 650 | -46 | 1478 | - - - | - - - | - - - | - - - | 876 | 650 | -46 | 1478 | 1472 | 1562 | 1575 | 4609 | # # # | # # # | # # # | # # # | 0.795 | 0.903 | 0.983 | 0.896 | # # # | # # # | # # # | - - - | 0.801 | 0.908 | 0.999 | 0.905 | - - - | 0.358 | 1.73 | 1.67 | 1.57 | 1.54 | 1.56 | 1.61 | 9.85 | 9.65 | 17.98 | 0 | - - - | - - - | - - - | - - - | 1472 | 1562 | 1575 | 4609 | Over-range | 892 | 668 | 292 | 2047 | 169 | 152 | 282 | 1413 | 1171 | 1410 | 1549 | 4130 | 1171 | 1410 | 1549 | 4130 | - - - | - - - | - - - | - - -
5/8/2026 | 7:00:00 AM | 283.66 | 281.24 | 279.47 | 490.79 | 483.89 | 487.8 | 5.3347 | 5.8479 | 5.7117 | 2.7342 | 1.426 | 1.425 | 1.42 | 1.488 | 1.458 | 1.301 | Over-range | 60 | 1195 | 1502 | 1568 | 4265 | - - - | - - - | - - - | - - - | 1195 | 1502 | 1568 | 4265 | 911 | 644 | -89 | 1465 | - - - | - - - | - - - | - - - | 911 | 644 | -89 | 1465 | 1512 | 1642 | 1596 | 4750 | # # # | # # # | # # # | # # # | 0.79 | 0.915 | 0.982 | 0.898 | # # # | # # # | # # # | - - - | 0.795 | 0.919 | 0.998 | 0.906 | - - - | 0.344 | 1.71 | 1.67 | 1.56 | 1.53 | 1.55 | 1.6 | 9.52 | 9.09 | 17.68 | 0 | - - - | - - - | - - - | - - - | 1512 | 1642 | 1596 | 4750 | Over-range | 927 | 661 | 298 | 2092 | 168 | 152 | 280 | 1491 | 1196 | 1500 | 1570 | 4266 | 1196 | 1500 | 1570 | 4266 | - - - | - - - | - - - | - - -
5/8/2026 | 7:15:00 AM | 283.49 | 281.19 | 279.34 | 490.63 | 483.68 | 487.54 | 4.9676 | 5.195 | 5.5188 | 2.7316 | 1.425 | 1.425 | 1.419 | 1.484 | 1.476 | 1.356 | Over-range | 60 | 1131 | 1262 | 1508 | 3901 | - - - | - - - | - - - | - - - | 1131 | 1262 | 1508 | 3901 | 806 | 645 | 15 | 1466 | - - - | - - - | - - - | - - - | 806 | 645 | 15 | 1466 | 1401 | 1434 | 1540 | 4375 | # # # | # # # | # # # | # # # | 0.808 | 0.879 | 0.979 | 0.892 | # # # | # # # | # # # | - - - | 0.813 | 0.884 | 0.995 | 0.9 | - - - | 0.376 | 1.72 | 1.71 | 1.58 | 1.54 | 1.56 | 1.61 | 10.44 | 10.53 | 18.02 | 0 | - - - | - - - | - - - | - - - | 1401 | 1434 | 1540 | 4375 | Over-range | 824 | 662 | 310 | 1979 | 166 | 149 | 276 | 1317 | 1131 | 1261 | 1510 | 3902 | 1131 | 1261 | 1510 | 3902 | - - - | - - - | - - - | - - -
5/8/2026 | 7:30:00 AM | 283.64 | 281.34 | 279.7 | 490.77 | 484.21 | 488.03 | 4.615 | 4.4588 | 5.3368 | 2.7359 | 1.425 | 1.425 | 1.42 | 1.481 | 1.432 | 1.404 | Over-range | 60.02 | 1080 | 1062 | 1463 | 3605 | - - - | - - - | - - - | - - - | 1080 | 1062 | 1463 | 3605 | 721 | 648 | 104 | 1472 | - - - | - - - | - - - | - - - | 721 | 648 | 104 | 1472 | 1309 | 1253 | 1493 | 4054 | # # # | # # # | # # # | # # # | 0.825 | 0.848 | 0.98 | 0.889 | # # # | # # # | # # # | - - - | 0.831 | 0.853 | 0.997 | 0.899 | - - - | 0.408 | 1.75 | 1.7 | 1.62 | 1.57 | 1.58 | 1.64 | 11.02 | 11.43 | 18.46 | 0 | - - - | - - - | - - - | - - - | 1309 | 1253 | 1493 | 4054 | Over-range | 739 | 664 | 296 | 1855 | 162 | 147 | 276 | 1128 | 1080 | 1061 | 1464 | 3606 | 1080 | 1061 | 1464 | 3606 | - - - | - - - | - - - | - - -
5/8/2026 | 7:45:00 AM | 283.43 | 281.15 | 279.47 | 490.39 | 483.89 | 487.64 | 4.6617 | 4.4304 | 5.3663 | 3.025 | 1.425 | 1.425 | 1.42 | 1.484 | 1.429 | 1.395 | Over-range | 60.01 | 1084 | 1029 | 1471 | 3585 | - - - | - - - | - - - | - - - | 1084 | 1029 | 1471 | 3585 | 738 | 668 | 84 | 1490 | - - - | - - - | - - - | - - - | 738 | 668 | 84 | 1490 | 1321 | 1243 | 1500 | 4064 | # # # | # # # | # # # | # # # | 0.821 | 0.828 | 0.981 | 0.882 | # # # | # # # | # # # | - - - | 0.827 | 0.835 | 0.999 | 0.892 | - - - | 0.416 | 1.72 | 1.69 | 1.63 | 1.55 | 1.57 | 1.63 | 10.78 | 12.22 | 18.5 | 0 | - - - | - - - | - - - | - - - | 1321 | 1243 | 1500 | 4064 | Over-range | 754 | 685 | 290 | 1908 | 157 | 152 | 277 | 1191 | 1085 | 1031 | 1469 | 3585 | 1085 | 1031 | 1469 | 3585 | - - - | - - - | - - - | - - -
5/8/2026 | 8:00:00 AM | 283.14 | 280.77 | 279.22 | 489.84 | 483.26 | 487.23 | 4.7088 | 3.7547 | 5.3673 | 4.131 | 1.426 | 1.426 | 1.42 | 1.484 | 1.449 | 1.391 | Over-range | 60.02 | 1096 | 702 | 1471 | 3269 | - - - | - - - | - - - | - - - | 1096 | 702 | 1471 | 3269 | 743 | 765 | 74 | 1583 | - - - | - - - | - - - | - - - | 743 | 765 | 74 | 1583 | 1333 | 1054 | 1499 | 3886 | # # # | # # # | # # # | # # # | 0.822 | 0.666 | 0.982 | 0.841 | # # # | # # # | # # # | - - - | 0.828 | 0.676 | 0.999 | 0.852 | - - - | 0.484 | 1.74 | 1.74 | 1.62 | 1.57 | 1.59 | 1.64 | 10.64 | 16.87 | 18.43 | 0 | - - - | - - - | - - - | - - - | 1333 | 1054 | 1499 | 3886 | Over-range | 759 | 786 | 285 | 2101 | 154 | 179 | 276 | 1381 | 1099 | 702 | 1469 | 3271 | 1099 | 702 | 1469 | 3271 | - - - | - - - | - - - | - - -
5/8/2026 | 8:15:00 AM | 282.62 | 280.23 | 278.59 | 488.95 | 482.23 | 486.21 | 4.7921 | 3.9046 | 5.3975 | 4.1135 | 1.427 | 1.427 | 1.421 | 1.486 | 1.44 | 1.375 | Over-range | 60.01 | 1106 | 767 | 1477 | 3350 | - - - | - - - | - - - | - - - | 1106 | 767 | 1477 | 3350 | 766 | 757 | 40 | 1563 | - - - | - - - | - - - | - - - | 766 | 757 | 40 | 1563 | 1354 | 1093 | 1504 | 3951 | # # # | # # # | # # # | # # # | 0.817 | 0.702 | 0.983 | 0.848 | # # # | # # # | # # # | - - - | 0.823 | 0.712 | 1 | 0.859 | - - - | 0.466 | 1.74 | 1.74 | 1.63 | 1.58 | 1.6 | 1.65 | 10.35 | 16.35 | 18.36 | 0 | - - - | - - - | - - - | - - - | 1354 | 1093 | 1504 | 3951 | Over-range | 781 | 778 | 279 | 2094 | 153 | 180 | 275 | 1394 | 1109 | 767 | 1476 | 3351 | 1109 | 767 | 1476 | 3351 | - - - | - - - | - - - | - - -
5/8/2026 | 8:30:00 AM | 282.74 | 280.25 | 278.71 | 489.06 | 482.34 | 486.47 | 5.5359 | 4.9542 | 5.7704 | 4.1243 | 1.428 | 1.428 | 1.421 | 1.49 | 1.433 | 1.298 | Over-range | 60.01 | 1236 | 1144 | 1578 | 3959 | - - - | - - - | - - - | - - - | 1236 | 1144 | 1578 | 3959 | 938 | 751 | -99 | 1589 | - - - | - - - | - - - | - - - | 938 | 751 | -99 | 1589 | 1561 | 1384 | 1608 | 4553 | # # # | # # # | # # # | # # # | 0.792 | 0.827 | 0.982 | 0.87 | # # # | # # # | # # # | - - - | 0.789 | 0.827 | 0.988 | 0.871 | - - - | 0.401 | 1.76 | 1.75 | 1.63 | 1.59 | 1.61 | 1.66 | 9.23 | 13.7 | 17.5 | 0 | - - - | - - - | - - - | - - - | 1561 | 1384 | 1608 | 4553 | Over-range | 952 | 775 | 307 | 2248 | 161 | 187 | 277 | 1584 | 1249 | 1150 | 1604 | 4003 | 1249 | 1150 | 1604 | 4003 | - - - | - - - | - - - | - - -
5/8/2026 | 8:45:00 AM | 282.61 | 280.22 | 278.65 | 488.95 | 482.25 | 486.27 | 5.5129 | 5.0964 | 5.8066 | 4.1215 | 1.427 | 1.428 | 1.421 | 1.493 | 1.436 | 1.273 | Over-range | 60.01 | 1224 | 1196 | 1587 | 4007 | - - - | - - - | - - - | - - - | 1224 | 1196 | 1587 | 4007 | 949 | 752 | -148 | 1552 | - - - | - - - | - - - | - - - | 949 | 752 | -148 | 1552 | 1557 | 1426 | 1618 | 4602 | # # # | # # # | # # # | # # # | 0.786 | 0.839 | 0.981 | 0.871 | # # # | # # # | # # # | - - - | 0.791 | 0.846 | 0.996 | 0.88 | - - - | 0.387 | 1.76 | 1.77 | 1.63 | 1.59 | 1.61 | 1.66 | 9.04 | 13.07 | 17.22 | 0 | - - - | - - - | - - - | - - - | 1557 | 1426 | 1618 | 4602 | Over-range | 963 | 775 | 315 | 2263 | 162 | 190 | 276 | 1645 | 1227 | 1195 | 1587 | 4008 | 1227 | 1195 | 1587 | 4008 | - - - | - - - | - - - | - - -
5/8/2026 | 9:00:00 AM | 282.31 | 279.79 | 278.17 | 488.31 | 481.43 | 485.64 | 4.9699 | 4.236 | 5.4943 | 4.1294 | 1.428 | 1.428 | 1.421 | 1.483 | 1.444 | 1.349 | Over-range | 60.01 | 1134 | 847 | 1497 | 3477 | - - - | - - - | - - - | - - - | 1134 | 847 | 1497 | 3477 | 798 | 750 | 1 | 1548 | - - - | - - - | - - - | - - - | 798 | 750 | 1 | 1548 | 1396 | 1168 | 1527 | 4091 | # # # | # # # | # # # | # # # | 0.812 | 0.725 | 0.98 | 0.85 | # # # | # # # | # # # | - - - | 0.818 | 0.733 | 0.996 | 0.86 | - - - | 0.445 | 1.77 | 1.77 | 1.63 | 1.59 | 1.61 | 1.67 | 10.19 | 15.28 | 17.69 | 0 | - - - | - - - | - - - | - - - | 1396 | 1168 | 1527 | 4091 | Over-range | 813 | 771 | 299 | 2145 | 153 | 176 | 269 | 1483 | 1137 | 847 | 1494 | 3478 | 1137 | 847 | 1494 | 3478 | - - - | - - - | - - - | - - -
5/8/2026 | 9:15:00 AM | 281.86 | 279.24 | 277.72 | 487.43 | 480.54 | 484.9 | 4.6388 | 3.645 | 5.3106 | 4.1278 | 1.429 | 1.428 | 1.421 | 1.482 | 1.455 | 1.393 | Over-range | 60 | 1084 | 661 | 1447 | 3191 | - - - | - - - | - - - | - - - | 1084 | 661 | 1447 | 3191 | 713 | 745 | 78 | 1536 | - - - | - - - | - - - | - - - | 713 | 745 | 78 | 1536 | 1306 | 1015 | 1475 | 3796 | # # # | # # # | # # # | # # # | 0.83 | 0.651 | 0.981 | 0.841 | # # # | # # # | # # # | - - - | 0.835 | 0.66 | 0.997 | 0.851 | - - - | 0.481 | 1.75 | 1.75 | 1.64 | 1.59 | 1.61 | 1.66 | 10.63 | 16.89 | 18.17 | 0 | - - - | - - - | - - - | - - - | 1306 | 1015 | 1475 | 3796 | Over-range | 729 | 765 | 284 | 2053 | 152 | 175 | 268 | 1362 | 1086 | 659 | 1447 | 3193 | 1086 | 659 | 1447 | 3193 | - - - | - - - | - - - | - - -
5/8/2026 | 9:30:00 AM | 281.99 | 279.3 | 277.86 | 487.58 | 480.67 | 485.17 | 4.8144 | 3.9083 | 5.4263 | 4.1281 | 1.429 | 1.429 | 1.422 | 1.484 | 1.444 | 1.364 | Over-range | 60 | 1114 | 776 | 1483 | 3374 | - - - | - - - | - - - | - - - | 1114 | 776 | 1483 | 3374 | 760 | 745 | 27 | 1532 | - - - | - - - | - - - | - - - | 760 | 745 | 27 | 1532 | 1357 | 1091 | 1508 | 3956 | # # # | # # # | # # # | # # # | 0.821 | 0.712 | 0.984 | 0.853 | # # # | # # # | # # # | - - - | 0.827 | 0.721 | 1 | 0.863 | - - - | 0.454 | 1.78 | 1.79 | 1.65 | 1.62 | 1.65 | 1.69 | 10.27 | 15.82 | 17.83 | 0 | - - - | - - - | - - - | - - - | 1357 | 1091 | 1508 | 3956 | Over-range | 775 | 766 | 271 | 2066 | 154 | 177 | 268 | 1386 | 1118 | 775 | 1483 | 3375 | 1118 | 775 | 1483 | 3375 | - - - | - - - | - - - | - - -
5/8/2026 | 9:45:00 AM | 282.77 | 280 | 278.62 | 488.83 | 481.94 | 486.54 | 4.8199 | 3.9532 | 5.4587 | 4.1317 | 1.43 | 1.429 | 1.423 | 1.486 | 1.443 | 1.359 | Over-range | 60.01 | 1118 | 789 | 1496 | 3402 | - - - | - - - | - - - | - - - | 1118 | 789 | 1496 | 3402 | 763 | 754 | 20 | 1538 | - - - | - - - | - - - | - - - | 763 | 754 | 20 | 1538 | 1363 | 1106 | 1521 | 3990 | # # # | # # # | # # # | # # # | 0.82 | 0.713 | 0.984 | 0.853 | # # # | # # # | # # # | - - - | 0.826 | 0.722 | 1 | 0.863 | - - - | 0.452 | 1.79 | 1.78 | 1.65 | 1.61 | 1.65 | 1.69 | 10.45 | 15.87 | 17.93 | 0 | - - - | - - - | - - - | - - - | 1363 | 1106 | 1521 | 3990 | Over-range | 780 | 775 | 274 | 2084 | 158 | 180 | 273 | 1406 | 1121 | 787 | 1496 | 3404 | 1121 | 787 | 1496 | 3404 | - - - | - - - | - - - | - - -
5/8/2026 | 10:00:00 AM | 282.6 | 279.87 | 278.44 | 488.59 | 481.7 | 486.18 | 5.1667 | 4.559 | 5.6283 | 4.1299 | 1.429 | 1.429 | 1.423 | 1.49 | 1.422 | 1.306 | Over-range | 60.01 | 1167 | 1013 | 1540 | 3719 | - - - | - - - | - - - | - - - | 1167 | 1013 | 1540 | 3719 | 862 | 750 | -85 | 1527 | - - - | - - - | - - - | - - - | 862 | 750 | -85 | 1527 | 1460 | 1274 | 1567 | 4301 | # # # | # # # | # # # | # # # | 0.8 | 0.795 | 0.983 | 0.865 | # # # | # # # | # # # | - - - | 0.804 | 0.803 | 0.998 | 0.874 | - - - | 0.41 | 1.77 | 1.78 | 1.64 | 1.6 | 1.64 | 1.67 | 9.6 | 14.34 | 17.71 | 0 | - - - | - - - | - - - | - - - | 1460 | 1274 | 1567 | 4301 | Over-range | 877 | 773 | 291 | 2160 | 160 | 184 | 276 | 1528 | 1168 | 1012 | 1539 | 3720 | 1168 | 1012 | 1539 | 3720 | - - - | - - - | - - - | - - -
5/8/2026 | 10:15:00 AM | 282.24 | 279.33 | 278 | 487.82 | 480.77 | 485.56 | 5.2692 | 4.7338 | 5.6866 | 4.1256 | 1.43 | 1.43 | 1.423 | 1.491 | 1.424 | 1.29 | Over-range | 60.01 | 1184 | 1076 | 1552 | 3812 | - - - | - - - | - - - | - - - | 1184 | 1076 | 1552 | 3812 | 884 | 743 | -117 | 1509 | - - - | - - - | - - - | - - - | 884 | 743 | -117 | 1509 | 1487 | 1321 | 1581 | 4388 | # # # | # # # | # # # | # # # | 0.796 | 0.815 | 0.982 | 0.869 | # # # | # # # | # # # | - - - | 0.801 | 0.823 | 0.997 | 0.878 | - - - | 0.396 | 1.77 | 1.76 | 1.66 | 1.6 | 1.64 | 1.67 | 9.4 | 13.73 | 17.37 | 0 | - - - | - - - | - - - | - - - | 1487 | 1321 | 1581 | 4388 | Over-range | 899 | 765 | 299 | 2174 | 163 | 179 | 273 | 1564 | 1183 | 1077 | 1551 | 3811 | 1183 | 1077 | 1551 | 3811 | - - - | - - - | - - - | - - -
5/8/2026 | 10:30:00 AM | 282.25 | 279.41 | 278 | 487.92 | 480.9 | 485.5 | 5.2629 | 4.7365 | 5.6832 | 4.1293 | 1.43 | 1.43 | 1.424 | 1.491 | 1.435 | 1.294 | Over-range | 60.01 | 1182 | 1069 | 1550 | 3801 | - - - | - - - | - - - | - - - | 1182 | 1069 | 1550 | 3801 | 882 | 744 | -115 | 1510 | - - - | - - - | - - - | - - - | 882 | 744 | -115 | 1510 | 1484 | 1318 | 1580 | 4381 | # # # | # # # | # # # | # # # | 0.796 | 0.811 | 0.981 | 0.868 | # # # | # # # | # # # | - - - | 0.801 | 0.819 | 0.996 | 0.877 | - - - | 0.397 | 1.77 | 1.77 | 1.67 | 1.62 | 1.66 | 1.69 | 9.44 | 13.7 | 17.41 | 0 | - - - | - - - | - - - | - - - | 1484 | 1318 | 1580 | 4381 | Over-range | 897 | 766 | 303 | 2179 | 165 | 180 | 273 | 1569 | 1181 | 1069 | 1551 | 3801 | 1181 | 1069 | 1551 | 3801 | - - - | - - - | - - - | - - -
5/8/2026 | 10:45:00 AM | 281.81 | 278.85 | 277.57 | 487.01 | 480.03 | 484.81 | 4.4769 | 3.498 | 5.2529 | 4.1382 | 1.431 | 1.431 | 1.424 | 1.483 | 1.469 | 1.403 | Over-range | 60 | 1054 | 583 | 1428 | 3065 | - - - | - - - | - - - | - - - | 1054 | 583 | 1428 | 3065 | 670 | 744 | 94 | 1507 | - - - | - - - | - - - | - - - | 670 | 744 | 94 | 1507 | 1259 | 970 | 1458 | 3686 | # # # | # # # | # # # | # # # | 0.837 | 0.601 | 0.98 | 0.832 | # # # | # # # | # # # | - - - | 0.843 | 0.61 | 0.996 | 0.842 | - - - | 0.492 | 1.8 | 1.82 | 1.67 | 1.63 | 1.67 | 1.71 | 11.11 | 17.22 | 18.17 | 0 | - - - | - - - | - - - | - - - | 1259 | 970 | 1458 | 3686 | Over-range | 688 | 762 | 292 | 2043 | 155 | 166 | 266 | 1379 | 1054 | 583 | 1427 | 3065 | 1054 | 583 | 1427 | 3065 | - - - | - - - | - - - | - - -
5/8/2026 | 11:00:00 AM | 281.79 | 278.88 | 277.6 | 487.01 | 480.06 | 484.84 | 4.8137 | 3.9701 | 5.4402 | 4.138 | 1.431 | 1.431 | 1.425 | 1.487 | 1.441 | 1.352 | Over-range | 60 | 1110 | 796 | 1485 | 3392 | - - - | - - - | - - - | - - - | 1110 | 796 | 1485 | 3392 | 762 | 742 | 1 | 1505 | - - - | - - - | - - - | - - - | 762 | 742 | 1 | 1505 | 1356 | 1104 | 1510 | 3970 | # # # | # # # | # # # | # # # | 0.819 | 0.721 | 0.984 | 0.854 | # # # | # # # | # # # | - - - | 0.825 | 0.731 | 0.999 | 0.865 | - - - | 0.444 | 1.8 | 1.8 | 1.69 | 1.63 | 1.68 | 1.71 | 10.25 | 15.63 | 17.85 | 0 | - - - | - - - | - - - | - - - | 1356 | 1104 | 1510 | 3970 | Over-range | 777 | 762 | 273 | 2062 | 155 | 170 | 269 | 1409 | 1111 | 798 | 1482 | 3391 | 1111 | 798 | 1482 | 3391 | - - - | - - - | - - - | - - -
5/8/2026 | 11:15:00 AM | 281.7 | 278.76 | 277.48 | 486.84 | 479.84 | 484.64 | 4.9136 | 3.946 | 5.4392 | 4.1399 | 1.43 | 1.431 | 1.424 | 1.483 | 1.44 | 1.364 | Over-range | 60 | 1135 | 794 | 1482 | 3411 | - - - | - - - | - - - | - - - | 1135 | 794 | 1482 | 3411 | 772 | 740 | 26 | 1538 | - - - | - - - | - - - | - - - | 772 | 740 | 26 | 1538 | 1381 | 1100 | 1509 | 3990 | # # # | # # # | # # # | # # # | 0.822 | 0.722 | 0.982 | 0.855 | # # # | # # # | # # # | - - - | 0.819 | 0.731 | 0.999 | 0.862 | - - - | 0.451 | 1.8 | 1.81 | 1.67 | 1.63 | 1.67 | 1.7 | 10.04 | 15.6 | 17.91 | 0 | - - - | - - - | - - - | - - - | 1381 | 1100 | 1509 | 3990 | Over-range | 787 | 760 | 282 | 2070 | 154 | 173 | 271 | 1379 | 1148 | 794 | 1480 | 3422 | 1148 | 794 | 1480 | 3422 | - - - | - - - | - - - | - - -
5/8/2026 | 11:30:00 AM | 281.53 | 278.68 | 277.36 | 486.6 | 479.73 | 484.36 | 5.2985 | 4.7898 | 5.7172 | 4.1365 | 1.431 | 1.431 | 1.425 | 1.492 | 1.431 | 1.286 | Over-range | 60 | 1187 | 1093 | 1556 | 3835 | - - - | - - - | - - - | - - - | 1187 | 1093 | 1556 | 3835 | 887 | 734 | -130 | 1491 | - - - | - - - | - - - | - - - | 887 | 734 | -130 | 1491 | 1491 | 1331 | 1585 | 4408 | # # # | # # # | # # # | # # # | 0.796 | 0.821 | 0.981 | 0.87 | # # # | # # # | # # # | - - - | 0.801 | 0.828 | 0.996 | 0.879 | - - - | 0.389 | 1.8 | 1.8 | 1.68 | 1.63 | 1.68 | 1.71 | 9.28 | 13.64 | 17.26 | 0 | - - - | - - - | - - - | - - - | 1491 | 1331 | 1585 | 4408 | Over-range | 902 | 757 | 306 | 2171 | 160 | 184 | 272 | 1578 | 1189 | 1091 | 1556 | 3836 | 1189 | 1091 | 1556 | 3836 | - - - | - - - | - - - | - - -
5/8/2026 | 11:45:00 AM | 281.39 | 278.47 | 277.25 | 486.28 | 479.42 | 484.22 | 5.5093 | 5.1697 | 5.8237 | 4.1229 | 1.431 | 1.431 | 1.425 | 1.495 | 1.447 | 1.274 | Over-range | 60 | 1220 | 1221 | 1579 | 4020 | - - - | - - - | - - - | - - - | 1220 | 1221 | 1579 | 4020 | 941 | 731 | -189 | 1482 | - - - | - - - | - - - | - - - | 941 | 731 | -189 | 1482 | 1549 | 1436 | 1614 | 4600 | # # # | # # # | # # # | # # # | 0.787 | 0.85 | 0.978 | 0.874 | # # # | # # # | # # # | - - - | 0.792 | 0.857 | 0.992 | 0.882 | - - - | 0.369 | 1.79 | 1.83 | 1.69 | 1.63 | 1.68 | 1.72 | 8.93 | 12.64 | 17 | 0 | - - - | - - - | - - - | - - - | 1549 | 1436 | 1614 | 4600 | Over-range | 955 | 754 | 334 | 2236 | 166 | 182 | 272 | 1673 | 1220 | 1220 | 1581 | 4021 | 1220 | 1220 | 1581 | 4021 | - - - | - - - | - - - | - - -
5/8/2026 | 12:00:00 PM | 281.04 | 278.1 | 276.94 | 485.58 | 478.85 | 483.68 | 5.1432 | 4.5068 | 5.6132 | 4.1295 | 1.431 | 1.431 | 1.425 | 1.491 | 1.421 | 1.3 | Over-range | 60 | 1163 | 1004 | 1528 | 3694 | - - - | - - - | - - - | - - - | 1163 | 1004 | 1528 | 3694 | 843 | 729 | -96 | 1476 | - - - | - - - | - - - | - - - | 843 | 729 | -96 | 1476 | 1445 | 1253 | 1555 | 4253 | # # # | # # # | # # # | # # # | 0.804 | 0.801 | 0.983 | 0.869 | # # # | # # # | # # # | - - - | 0.809 | 0.809 | 0.998 | 0.878 | - - - | 0.399 | 1.79 | 1.77 | 1.69 | 1.62 | 1.68 | 1.7 | 9.47 | 13.96 | 17.32 | 0 | - - - | - - - | - - - | - - - | 1445 | 1253 | 1555 | 4253 | Over-range | 859 | 750 | 286 | 2107 | 162 | 176 | 268 | 1504 | 1162 | 1003 | 1529 | 3694 | 1162 | 1003 | 1529 | 3694 | - - - | - - - | - - - | - - -
5/8/2026 | 12:15:00 PM | 280.99 | 278.1 | 276.88 | 485.54 | 478.83 | 483.55 | 4.7724 | 3.9948 | 5.4142 | 4.1353 | 1.431 | 1.431 | 1.425 | 1.486 | 1.457 | 1.358 | Over-range | 59.99 | 1098 | 756 | 1467 | 3321 | - - - | - - - | - - - | - - - | 1098 | 756 | 1467 | 3321 | 737 | 732 | 12 | 1481 | - - - | - - - | - - - | - - - | 737 | 732 | 12 | 1481 | 1333 | 1090 | 1497 | 3921 | # # # | # # # | # # # | # # # | 0.823 | 0.694 | 0.98 | 0.847 | # # # | # # # | # # # | - - - | 0.829 | 0.703 | 0.995 | 0.857 | - - - | 0.446 | 1.79 | 1.78 | 1.69 | 1.63 | 1.68 | 1.71 | 10.44 | 15.93 | 17.75 | 0 | - - - | - - - | - - - | - - - | 1333 | 1090 | 1497 | 3921 | Over-range | 755 | 752 | 299 | 2075 | 159 | 171 | 266 | 1452 | 1097 | 756 | 1468 | 3321 | 1097 | 756 | 1468 | 3321 | - - - | - - - | - - - | - - -
5/8/2026 | 12:30:00 PM | 281.12 | 278.18 | 276.98 | 485.76 | 478.92 | 483.76 | 4.7579 | 3.8885 | 5.3884 | 4.1309 | 1.431 | 1.431 | 1.425 | 1.485 | 1.441 | 1.359 | Over-range | 59.98 | 1100 | 763 | 1466 | 3329 | - - - | - - - | - - - | - - - | 1100 | 763 | 1466 | 3329 | 741 | 734 | 10 | 1485 | - - - | - - - | - - - | - - - | 741 | 734 | 10 | 1485 | 1336 | 1077 | 1492 | 3905 | # # # | # # # | # # # | # # # | 0.823 | 0.708 | 0.983 | 0.852 | # # # | # # # | # # # | - - - | 0.829 | 0.718 | 0.999 | 0.863 | - - - | 0.446 | 1.79 | 1.8 | 1.68 | 1.62 | 1.68 | 1.71 | 10.27 | 15.88 | 17.95 | 0 | - - - | - - - | - - - | - - - | 1336 | 1077 | 1492 | 3905 | Over-range | 758 | 754 | 276 | 2040 | 158 | 171 | 268 | 1398 | 1099 | 763 | 1467 | 3329 | 1099 | 763 | 1467 | 3329 | - - - | - - - | - - - | - - -
5/8/2026 | 12:45:00 PM | 281.23 | 278.38 | 277.11 | 486.06 | 479.26 | 483.92 | 4.8455 | 4.0105 | 5.4545 | 4.1388 | 1.431 | 1.431 | 1.426 | 1.486 | 1.435 | 1.344 | Over-range | 59.99 | 1115 | 821 | 1487 | 3423 | - - - | - - - | - - - | - - - | 1115 | 821 | 1487 | 3423 | 767 | 736 | -13 | 1489 | - - - | - - - | - - - | - - - | 767 | 736 | -13 | 1489 | 1363 | 1116 | 1511 | 3990 | # # # | # # # | # # # | # # # | 0.818 | 0.735 | 0.984 | 0.858 | # # # | # # # | # # # | - - - | 0.823 | 0.744 | 1 | 0.868 | - - - | 0.435 | 1.8 | 1.81 | 1.69 | 1.63 | 1.69 | 1.71 | 10.07 | 15.3 | 17.72 | 0 | - - - | - - - | - - - | - - - | 1363 | 1116 | 1511 | 3990 | Over-range | 784 | 756 | 269 | 2050 | 159 | 172 | 268 | 1410 | 1114 | 820 | 1489 | 3423 | 1114 | 820 | 1489 | 3423 | - - - | - - - | - - - | - - -
5/8/2026 | 1:00:00 PM | 281.14 | 278.37 | 277.14 | 485.89 | 479.37 | 483.84 | 5.4996 | 5.0711 | 5.7819 | 4.1341 | 1.432 | 1.432 | 1.426 | 1.493 | 1.439 | 1.287 | Over-range | 59.98 | 1220 | 1182 | 1569 | 3971 | - - - | - - - | - - - | - - - | 1220 | 1182 | 1569 | 3971 | 932 | 732 | -159 | 1504 | - - - | - - - | - - - | - - - | 932 | 732 | -159 | 1504 | 1544 | 1405 | 1602 | 4551 | # # # | # # # | # # # | # # # | 0.79 | 0.841 | 0.979 | 0.873 | # # # | # # # | # # # | - - - | 0.794 | 0.849 | 0.994 | 0.881 | - - - | 0.379 | 1.82 | 1.8 | 1.7 | 1.64 | 1.69 | 1.72 | 8.95 | 13 | 17.15 | 0 | - - - | - - - | - - - | - - - | 1544 | 1405 | 1602 | 4551 | Over-range | 946 | 755 | 323 | 2224 | 160 | 182 | 273 | 1635 | 1221 | 1183 | 1566 | 3970 | 1221 | 1183 | 1566 | 3970 | - - - | - - - | - - - | - - -
5/8/2026 | 1:15:00 PM | 281.05 | 278.32 | 277.01 | 485.84 | 479.16 | 483.63 | 5.7209 | 5.4647 | 5.9347 | 4.1323 | 1.431 | 1.431 | 1.426 | 1.496 | 1.458 | 1.27 | Over-range | 59.97 | 1255 | 1319 | 1606 | 4180 | - - - | - - - | - - - | - - - | 1255 | 1319 | 1606 | 4180 | 991 | 730 | -218 | 1502 | - - - | - - - | - - - | - - - | 991 | 730 | -218 | 1502 | 1607 | 1519 | 1644 | 4771 | # # # | # # # | # # # | # # # | 0.781 | 0.868 | 0.977 | 0.876 | # # # | # # # | # # # | - - - | 0.785 | 0.875 | 0.991 | 0.884 | - - - | 0.359 | 1.78 | 1.79 | 1.68 | 1.62 | 1.67 | 1.7 | 8.58 | 12.02 | 16.68 | 0 | - - - | - - - | - - - | - - - | 1607 | 1519 | 1644 | 4771 | Over-range | 1004 | 753 | 350 | 2299 | 159 | 187 | 272 | 1740 | 1258 | 1318 | 1605 | 4181 | 1258 | 1318 | 1605 | 4181 | - - - | - - - | - - - | - - -
5/8/2026 | 1:30:00 PM | 280.75 | 277.92 | 276.58 | 485.27 | 478.4 | 483.01 | 5.4831 | 4.8722 | 5.726 | 4.1271 | 1.431 | 1.432 | 1.426 | 1.489 | 1.442 | 1.3 | Over-range | 59.98 | 1226 | 1120 | 1552 | 3898 | - - - | - - - | - - - | - - - | 1226 | 1120 | 1552 | 3898 | 910 | 727 | -111 | 1525 | - - - | - - - | - - - | - - - | 910 | 727 | -111 | 1525 | 1536 | 1349 | 1583 | 4469 | # # # | # # # | # # # | # # # | 0.798 | 0.83 | 0.98 | 0.872 | # # # | # # # | # # # | - - - | 0.795 | 0.831 | 0.987 | 0.873 | - - - | 0.391 | 1.78 | 1.77 | 1.7 | 1.62 | 1.67 | 1.7 | 8.97 | 13.08 | 17.13 | 0 | - - - | - - - | - - - | - - - | 1536 | 1349 | 1583 | 4469 | Over-range | 925 | 748 | 312 | 2184 | 164 | 177 | 270 | 1555 | 1237 | 1127 | 1563 | 3927 | 1237 | 1127 | 1563 | 3927 | - - - | - - - | - - - | - - -
5/8/2026 | 1:45:00 PM | 280.49 | 277.6 | 276.28 | 484.72 | 477.89 | 482.54 | 4.6163 | 3.6289 | 5.3061 | 4.1442 | 1.432 | 1.432 | 1.426 | 1.484 | 1.457 | 1.391 | Over-range | 59.98 | 1077 | 641 | 1437 | 3155 | - - - | - - - | - - - | - - - | 1077 | 641 | 1437 | 3155 | 694 | 727 | 73 | 1494 | - - - | - - - | - - - | - - - | 694 | 727 | 73 | 1494 | 1291 | 998 | 1465 | 3754 | # # # | # # # | # # # | # # # | 0.834 | 0.642 | 0.98 | 0.84 | # # # | # # # | # # # | - - - | 0.84 | 0.651 | 0.997 | 0.851 | - - - | 0.473 | 1.79 | 1.8 | 1.69 | 1.62 | 1.66 | 1.71 | 10.64 | 16.57 | 17.79 | 0 | - - - | - - - | - - - | - - - | 1291 | 998 | 1465 | 3754 | Over-range | 710 | 746 | 287 | 2029 | 151 | 168 | 262 | 1372 | 1080 | 640 | 1436 | 3156 | 1080 | 640 | 1436 | 3156 | - - - | - - - | - - - | - - -
5/8/2026 | 2:00:00 PM | 280.34 | 277.48 | 276.11 | 484.56 | 477.57 | 482.26 | 4.88 | 3.9989 | 5.4172 | 4.1319 | 1.431 | 1.432 | 1.426 | 1.487 | 1.435 | 1.353 | Over-range | 59.99 | 1122 | 812 | 1470 | 3403 | - - - | - - - | - - - | - - - | 1122 | 812 | 1470 | 3403 | 765 | 723 | -4 | 1482 | - - - | - - - | - - - | - - - | 765 | 723 | -4 | 1482 | 1367 | 1105 | 1495 | 3966 | # # # | # # # | # # # | # # # | 0.821 | 0.735 | 0.983 | 0.858 | # # # | # # # | # # # | - - - | 0.826 | 0.743 | 0.999 | 0.868 | - - - | 0.436 | 1.78 | 1.79 | 1.68 | 1.61 | 1.67 | 1.7 | 9.99 | 15.36 | 17.76 | 0 | - - - | - - - | - - - | - - - | 1367 | 1105 | 1495 | 3966 | Over-range | 780 | 743 | 273 | 2036 | 154 | 173 | 266 | 1395 | 1124 | 810 | 1470 | 3404 | 1124 | 810 | 1470 | 3404 | - - - | - - - | - - - | - - -
5/8/2026 | 2:15:00 PM | 280.46 | 277.67 | 276.36 | 484.79 | 478 | 482.56 | 4.8904 | 4.0011 | 5.4436 | 4.1372 | 1.431 | 1.432 | 1.427 | 1.487 | 1.432 | 1.349 | Over-range | 59.97 | 1124 | 821 | 1480 | 3426 | - - - | - - - | - - - | - - - | 1124 | 821 | 1480 | 3426 | 769 | 728 | -6 | 1490 | - - - | - - - | - - - | - - - | 769 | 728 | -6 | 1490 | 1371 | 1111 | 1504 | 3986 | # # # | # # # | # # # | # # # | 0.82 | 0.74 | 0.984 | 0.859 | # # # | # # # | # # # | - - - | 0.825 | 0.749 | 1 | 0.87 | - - - | 0.435 | 1.78 | 1.78 | 1.71 | 1.63 | 1.67 | 1.71 | 9.99 | 15.2 | 17.65 | 0 | - - - | - - - | - - - | - - - | 1371 | 1111 | 1504 | 3986 | Over-range | 786 | 747 | 267 | 2038 | 159 | 169 | 266 | 1390 | 1123 | 822 | 1480 | 3426 | 1123 | 822 | 1480 | 3426 | - - - | - - - | - - - | - - -
5/8/2026 | 2:30:00 PM | 280.36 | 277.63 | 276.29 | 484.64 | 477.95 | 482.4 | 5.448 | 4.9808 | 5.7516 | 4.1289 | 1.432 | 1.432 | 1.427 | 1.492 | 1.446 | 1.285 | Over-range | 59.98 | 1211 | 1157 | 1556 | 3924 | - - - | - - - | - - - | - - - | 1211 | 1157 | 1556 | 3924 | 913 | 722 | -155 | 1479 | - - - | - - - | - - - | - - - | 913 | 722 | -155 | 1479 | 1526 | 1378 | 1589 | 4492 | # # # | # # # | # # # | # # # | 0.794 | 0.84 | 0.98 | 0.874 | # # # | # # # | # # # | - - - | 0.799 | 0.847 | 0.994 | 0.882 | - - - | 0.377 | 1.8 | 1.78 | 1.71 | 1.64 | 1.68 | 1.72 | 8.99 | 13.08 | 17.11 | 0 | - - - | - - - | - - - | - - - | 1526 | 1378 | 1589 | 4492 | Over-range | 928 | 744 | 317 | 2186 | 166 | 179 | 270 | 1608 | 1211 | 1157 | 1557 | 3924 | 1211 | 1157 | 1557 | 3924 | - - - | - - - | - - - | - - -
5/8/2026 | 2:45:00 PM | 280.04 | 277.2 | 275.89 | 484.02 | 477.17 | 481.82 | 5.4018 | 4.8871 | 5.7288 | 4.1295 | 1.431 | 1.432 | 1.427 | 1.493 | 1.443 | 1.278 | Over-range | 59.97 | 1204 | 1131 | 1550 | 3885 | - - - | - - - | - - - | - - - | 1204 | 1131 | 1550 | 3885 | 900 | 716 | -146 | 1469 | - - - | - - - | - - - | - - - | 900 | 716 | -146 | 1469 | 1512 | 1352 | 1580 | 4445 | # # # | # # # | # # # | # # # | 0.796 | 0.837 | 0.981 | 0.874 | # # # | # # # | # # # | - - - | 0.801 | 0.844 | 0.996 | 0.883 | - - - | 0.378 | 1.77 | 1.79 | 1.72 | 1.63 | 1.68 | 1.71 | 9.02 | 13.03 | 16.93 | 0 | - - - | - - - | - - - | - - - | 1512 | 1352 | 1580 | 4445 | Over-range | 915 | 738 | 307 | 2158 | 162 | 180 | 267 | 1580 | 1206 | 1129 | 1552 | 3887 | 1206 | 1129 | 1552 | 3887 | - - - | - - - | - - - | - - -
5/8/2026 | 3:00:00 PM | 280.14 | 277.39 | 276.05 | 484.27 | 477.47 | 482.04 | 4.8013 | 3.93 | 5.4007 | 4.1365 | 1.431 | 1.432 | 1.427 | 1.486 | 1.449 | 1.363 | Over-range | 59.98 | 1106 | 754 | 1461 | 3321 | - - - | - - - | - - - | - - - | 1106 | 754 | 1461 | 3321 | 738 | 722 | 20 | 1480 | - - - | - - - | - - - | - - - | 738 | 722 | 20 | 1480 | 1340 | 1077 | 1490 | 3907 | # # # | # # # | # # # | # # # | 0.825 | 0.7 | 0.981 | 0.85 | # # # | # # # | # # # | - - - | 0.831 | 0.709 | 0.997 | 0.86 | - - - | 0.446 | 1.8 | 1.84 | 1.71 | 1.64 | 1.69 | 1.73 | 10.32 | 15.77 | 17.62 | 0 | - - - | - - - | - - - | - - - | 1340 | 1077 | 1490 | 3907 | Over-range | 755 | 742 | 288 | 2048 | 159 | 171 | 263 | 1415 | 1106 | 753 | 1464 | 3322 | 1106 | 753 | 1464 | 3322 | - - - | - - - | - - - | - - -
5/8/2026 | 3:15:00 PM | 280.38 | 277.72 | 276.3 | 484.73 | 478.05 | 482.42 | 4.8132 | 3.9063 | 5.3852 | 4.135 | 1.432 | 1.433 | 1.428 | 1.486 | 1.44 | 1.363 | Over-range | 59.99 | 1110 | 769 | 1461 | 3340 | - - - | - - - | - - - | - - - | 1110 | 769 | 1461 | 3340 | 746 | 726 | 14 | 1486 | - - - | - - - | - - - | - - - | 746 | 726 | 14 | 1486 | 1347 | 1077 | 1487 | 3912 | # # # | # # # | # # # | # # # | 0.824 | 0.714 | 0.983 | 0.854 | # # # | # # # | # # # | - - - | 0.83 | 0.723 | 0.999 | 0.864 | - - - | 0.445 | 1.83 | 1.82 | 1.72 | 1.66 | 1.7 | 1.75 | 10.2 | 15.66 | 17.86 | 0 | - - - | - - - | - - - | - - - | 1347 | 1077 | 1487 | 3912 | Over-range | 762 | 745 | 277 | 2034 | 157 | 167 | 266 | 1388 | 1110 | 770 | 1460 | 3340 | 1110 | 770 | 1460 | 3340 | - - - | - - - | - - - | - - -
5/8/2026 | 3:30:00 PM | 280.19 | 277.39 | 275.99 | 484.29 | 477.46 | 482.03 | 4.9695 | 3.9829 | 5.4555 | 4.1378 | 1.432 | 1.432 | 1.427 | 1.484 | 1.433 | 1.356 | Over-range | 59.99 | 1144 | 818 | 1480 | 3442 | - - - | - - - | - - - | - - - | 1144 | 818 | 1480 | 3442 | 774 | 722 | 13 | 1509 | - - - | - - - | - - - | - - - | 774 | 722 | 13 | 1509 | 1390 | 1104 | 1506 | 4000 | # # # | # # # | # # # | # # # | 0.823 | 0.741 | 0.983 | 0.86 | # # # | # # # | # # # | - - - | 0.821 | 0.743 | 0.986 | 0.862 | - - - | 0.438 | 1.82 | 1.83 | 1.72 | 1.65 | 1.7 | 1.74 | 9.83 | 14.98 | 17.46 | 0 | - - - | - - - | - - - | - - - | 1390 | 1104 | 1506 | 4000 | Over-range | 790 | 741 | 276 | 2039 | 159 | 168 | 265 | 1366 | 1154 | 823 | 1493 | 3470 | 1154 | 823 | 1493 | 3470 | - - - | - - - | - - - | - - -
5/8/2026 | 3:45:00 PM | 280.32 | 277.59 | 276.13 | 484.61 | 477.75 | 482.23 | 5.1436 | 4.4843 | 5.5775 | 4.1117 | 1.432 | 1.433 | 1.428 | 1.488 | 1.431 | 1.31 | Over-range | 59.98 | 1159 | 990 | 1513 | 3661 | - - - | - - - | - - - | - - - | 1159 | 990 | 1513 | 3661 | 841 | 722 | -81 | 1480 | - - - | - - - | - - - | - - - | 841 | 722 | -81 | 1480 | 1441 | 1240 | 1540 | 4221 | # # # | # # # | # # # | # # # | 0.804 | 0.798 | 0.983 | 0.867 | # # # | # # # | # # # | - - - | 0.81 | 0.806 | 0.997 | 0.877 | - - - | 0.404 | 1.83 | 1.83 | 1.71 | 1.67 | 1.71 | 1.75 | 9.45 | 13.93 | 17.37 | 0 | - - - | - - - | - - - | - - - | 1441 | 1240 | 1540 | 4221 | Over-range | 856 | 743 | 286 | 2099 | 158 | 177 | 268 | 1487 | 1162 | 987 | 1514 | 3663 | 1162 | 987 | 1514 | 3663 | - - - | - - - | - - - | - - -
5/8/2026 | 4:00:00 PM | 280.46 | 277.79 | 276.36 | 484.91 | 478.14 | 482.54 | 5.6194 | 5.3276 | 5.8832 | 4.1137 | 1.432 | 1.432 | 1.427 | 1.494 | 1.457 | 1.274 | Over-range | 59.99 | 1235 | 1276 | 1589 | 4100 | - - - | - - - | - - - | - - - | 1235 | 1276 | 1589 | 4100 | 964 | 722 | -206 | 1479 | - - - | - - - | - - - | - - - | 964 | 722 | -206 | 1479 | 1575 | 1478 | 1626 | 4679 | # # # | # # # | # # # | # # # | 0.784 | 0.864 | 0.978 | 0.876 | # # # | # # # | # # # | - - - | 0.789 | 0.87 | 0.991 | 0.884 | - - - | 0.361 | 1.81 | 1.8 | 1.72 | 1.66 | 1.69 | 1.73 | 8.7 | 12.03 | 16.63 | 0 | - - - | - - - | - - - | - - - | 1575 | 1478 | 1626 | 4679 | Over-range | 978 | 744 | 341 | 2254 | 167 | 178 | 268 | 1700 | 1235 | 1276 | 1590 | 4100 | 1235 | 1276 | 1590 | 4100 | - - - | - - - | - - - | - - -
5/8/2026 | 4:15:00 PM | 280.6 | 278.04 | 276.52 | 485.2 | 478.59 | 482.73 | 5.2826 | 4.6713 | 5.667 | 4.1406 | 1.432 | 1.433 | 1.427 | 1.488 | 1.428 | 1.291 | Over-range | 59.99 | 1186 | 1059 | 1539 | 3784 | - - - | - - - | - - - | - - - | 1186 | 1059 | 1539 | 3784 | 873 | 728 | -109 | 1490 | - - - | - - - | - - - | - - - | 873 | 728 | -109 | 1490 | 1482 | 1297 | 1567 | 4346 | # # # | # # # | # # # | # # # | 0.801 | 0.816 | 0.983 | 0.871 | # # # | # # # | # # # | - - - | 0.805 | 0.824 | 0.997 | 0.879 | - - - | 0.394 | 1.84 | 1.81 | 1.74 | 1.67 | 1.7 | 1.75 | 9.32 | 13.39 | 17.14 | 0 | - - - | - - - | - - - | - - - | 1482 | 1297 | 1567 | 4346 | Over-range | 888 | 748 | 292 | 2136 | 162 | 173 | 268 | 1530 | 1186 | 1060 | 1537 | 3784 | 1186 | 1060 | 1537 | 3784 | - - - | - - - | - - - | - - -
5/8/2026 | 4:30:00 PM | 280.55 | 278.08 | 276.56 | 485.22 | 478.66 | 482.69 | 4.6703 | 3.7743 | 5.3335 | 4.1213 | 1.433 | 1.433 | 1.428 | 1.484 | 1.454 | 1.379 | Over-range | 59.98 | 1080 | 689 | 1444 | 3214 | - - - | - - - | - - - | - - - | 1080 | 689 | 1444 | 3214 | 713 | 733 | 52 | 1498 | - - - | - - - | - - - | - - - | 713 | 733 | 52 | 1498 | 1305 | 1037 | 1474 | 3817 | # # # | # # # | # # # | # # # | 0.828 | 0.664 | 0.98 | 0.842 | # # # | # # # | # # # | - - - | 0.834 | 0.674 | 0.997 | 0.853 | - - - | 0.466 | 1.84 | 1.81 | 1.73 | 1.67 | 1.69 | 1.76 | 10.64 | 16.27 | 18.04 | 0 | - - - | - - - | - - - | - - - | 1305 | 1037 | 1474 | 3817 | Over-range | 731 | 752 | 292 | 2051 | 158 | 168 | 267 | 1400 | 1080 | 689 | 1445 | 3214 | 1080 | 689 | 1445 | 3214 | - - - | - - - | - - - | - - -
5/8/2026 | 4:45:00 PM | 280.43 | 277.92 | 276.46 | 484.96 | 478.44 | 482.53 | 4.8506 | 3.9622 | 5.4267 | 4.1429 | 1.433 | 1.433 | 1.428 | 1.486 | 1.436 | 1.353 | Over-range | 59.99 | 1116 | 793 | 1474 | 3383 | - - - | - - - | - - - | - - - | 1116 | 793 | 1474 | 3383 | 757 | 730 | 6 | 1493 | - - - | - - - | - - - | - - - | 757 | 730 | 6 | 1493 | 1359 | 1096 | 1500 | 3954 | # # # | # # # | # # # | # # # | 0.822 | 0.724 | 0.983 | 0.856 | # # # | # # # | # # # | - - - | 0.827 | 0.732 | 0.999 | 0.866 | - - - | 0.441 | 1.84 | 1.81 | 1.71 | 1.67 | 1.69 | 1.75 | 10.17 | 15.58 | 17.79 | 0 | - - - | - - - | - - - | - - - | 1359 | 1096 | 1500 | 3954 | Over-range | 774 | 749 | 276 | 2045 | 160 | 169 | 268 | 1397 | 1115 | 794 | 1473 | 3383 | 1115 | 794 | 1473 | 3383 | - - - | - - - | - - - | - - -
5/8/2026 | 5:00:00 PM | 280.46 | 278.02 | 276.4 | 485.08 | 478.52 | 482.42 | 4.8555 | 3.9705 | 5.419 | 4.1324 | 1.432 | 1.432 | 1.427 | 1.483 | 1.433 | 1.35 | Over-range | 60 | 1116 | 810 | 1474 | 3400 | - - - | - - - | - - - | - - - | 1116 | 810 | 1474 | 3400 | 764 | 730 | -2 | 1491 | - - - | - - - | - - - | - - - | 764 | 730 | -2 | 1491 | 1362 | 1104 | 1498 | 3963 | # # # | # # # | # # # | # # # | 0.819 | 0.734 | 0.984 | 0.858 | # # # | # # # | # # # | - - - | 0.825 | 0.743 | 1 | 0.868 | - - - | 0.438 | 1.79 | 1.78 | 1.69 | 1.63 | 1.67 | 1.71 | 10.09 | 15.18 | 17.81 | 0 | - - - | - - - | - - - | - - - | 1362 | 1104 | 1498 | 3963 | Over-range | 781 | 749 | 268 | 2037 | 161 | 167 | 268 | 1388 | 1115 | 811 | 1473 | 3399 | 1115 | 811 | 1473 | 3399 | - - - | - - - | - - - | - - -
5/8/2026 | 5:15:00 PM | 281.05 | 278.63 | 277.09 | 486.15 | 479.68 | 483.48 | 5.3824 | 4.7381 | 5.7051 | 4.1423 | 1.432 | 1.432 | 1.427 | 1.487 | 1.43 | 1.317 | Over-range | 59.99 | 1208 | 1070 | 1550 | 3827 | - - - | - - - | - - - | - - - | 1208 | 1070 | 1550 | 3827 | 889 | 736 | -89 | 1536 | - - - | - - - | - - - | - - - | 889 | 736 | -89 | 1536 | 1509 | 1314 | 1580 | 4404 | # # # | # # # | # # # | # # # | 0.8 | 0.814 | 0.981 | 0.869 | # # # | # # # | # # # | - - - | 0.798 | 0.816 | 0.988 | 0.871 | - - - | 0.401 | 1.8 | 1.76 | 1.68 | 1.63 | 1.65 | 1.7 | 9.29 | 13.68 | 17.47 | 0 | - - - | - - - | - - - | - - - | 1509 | 1314 | 1580 | 4404 | Over-range | 904 | 758 | 308 | 2177 | 162 | 179 | 276 | 1536 | 1218 | 1078 | 1558 | 3854 | 1218 | 1078 | 1558 | 3854 | - - - | - - - | - - - | - - -
5/8/2026 | 5:30:00 PM | 281.14 | 278.77 | 277.13 | 486.4 | 479.84 | 483.53 | 5.4716 | 5.0546 | 5.7866 | 4.1277 | 1.432 | 1.432 | 1.428 | 1.491 | 1.436 | 1.301 | Over-range | 59.98 | 1212 | 1186 | 1571 | 3969 | - - - | - - - | - - - | - - - | 1212 | 1186 | 1571 | 3969 | 934 | 736 | -160 | 1509 | - - - | - - - | - - - | - - - | 934 | 736 | -160 | 1509 | 1538 | 1408 | 1604 | 4550 | # # # | # # # | # # # | # # # | 0.788 | 0.842 | 0.98 | 0.872 | # # # | # # # | # # # | - - - | 0.793 | 0.849 | 0.995 | 0.881 | - - - | 0.38 | 1.78 | 1.79 | 1.7 | 1.65 | 1.67 | 1.72 | 9.1 | 12.84 | 17.29 | 0 | - - - | - - - | - - - | - - - | 1538 | 1408 | 1604 | 4550 | Over-range | 947 | 759 | 321 | 2225 | 157 | 186 | 277 | 1635 | 1216 | 1185 | 1569 | 3970 | 1216 | 1185 | 1569 | 3970 | - - - | - - - | - - - | - - -
5/8/2026 | 5:45:00 PM | 281.19 | 278.88 | 277.26 | 486.46 | 480.12 | 483.72 | 5.1732 | 4.5258 | 5.6196 | 4.1414 | 1.432 | 1.432 | 1.427 | 1.487 | 1.426 | 1.318 | Over-range | 59.99 | 1166 | 1000 | 1530 | 3696 | - - - | - - - | - - - | - - - | 1166 | 1000 | 1530 | 3696 | 853 | 739 | -78 | 1512 | - - - | - - - | - - - | - - - | 853 | 739 | -78 | 1512 | 1454 | 1258 | 1558 | 4270 | # # # | # # # | # # # | # # # | 0.802 | 0.795 | 0.982 | 0.866 | # # # | # # # | # # # | - - - | 0.807 | 0.803 | 0.999 | 0.875 | - - - | 0.409 | 1.78 | 1.74 | 1.66 | 1.62 | 1.64 | 1.68 | 9.67 | 14.05 | 17.62 | 0 | - - - | - - - | - - - | - - - | 1454 | 1258 | 1558 | 4270 | Over-range | 868 | 761 | 291 | 2138 | 163 | 179 | 276 | 1510 | 1167 | 1000 | 1531 | 3697 | 1167 | 1000 | 1531 | 3697 | - - - | - - - | - - - | - - -
5/8/2026 | 6:00:00 PM | 281.47 | 279.22 | 277.62 | 486.99 | 480.73 | 484.27 | 4.5177 | 3.4935 | 5.2771 | 4.1647 | 1.432 | 1.431 | 1.427 | 1.484 | 1.472 | 1.406 | Over-range | 59.99 | 1063 | 581 | 1433 | 3077 | - - - | - - - | - - - | - - - | 1063 | 581 | 1433 | 3077 | 674 | 749 | 107 | 1530 | - - - | - - - | - - - | - - - | 674 | 749 | 107 | 1530 | 1270 | 971 | 1465 | 3706 | # # # | # # # | # # # | # # # | 0.837 | 0.598 | 0.979 | 0.83 | # # # | # # # | # # # | - - - | 0.844 | 0.608 | 0.996 | 0.842 | - - - | 0.497 | 1.75 | 1.7 | 1.64 | 1.6 | 1.61 | 1.65 | 11.33 | 17.4 | 18.48 | 0 | - - - | - - - | - - - | - - - | 1270 | 971 | 1465 | 3706 | Over-range | 693 | 768 | 301 | 2061 | 162 | 169 | 274 | 1380 | 1062 | 582 | 1432 | 3077 | 1062 | 582 | 1432 | 3077 | - - - | - - - | - - - | - - -
5/8/2026 | 6:15:00 PM | 281.42 | 279.23 | 277.59 | 486.93 | 480.75 | 484.19 | 4.7305 | 3.9011 | 5.3864 | 4.1468 | 1.43 | 1.429 | 1.425 | 1.49 | 1.461 | 1.387 | Over-range | 59.99 | 1091 | 718 | 1462 | 3270 | - - - | - - - | - - - | - - - | 1091 | 718 | 1462 | 3270 | 732 | 748 | 44 | 1525 | - - - | - - - | - - - | - - - | 732 | 748 | 44 | 1525 | 1326 | 1072 | 1494 | 3892 | # # # | # # # | # # # | # # # | 0.823 | 0.67 | 0.978 | 0.84 | # # # | # # # | # # # | - - - | 0.829 | 0.68 | 0.996 | 0.852 | - - - | 0.466 | 1.65 | 1.59 | 1.51 | 1.5 | 1.5 | 1.53 | 10.95 | 16.5 | 18.54 | 0 | - - - | - - - | - - - | - - - | 1326 | 1072 | 1494 | 3892 | Over-range | 750 | 768 | 308 | 2101 | 161 | 173 | 279 | 1444 | 1091 | 720 | 1459 | 3270 | 1091 | 720 | 1459 | 3270 | - - - | - - - | - - - | - - -
5/8/2026 | 6:30:00 PM | 281.24 | 278.91 | 277.33 | 486.48 | 480.23 | 483.83 | 4.8354 | 3.9465 | 5.4361 | 4.1691 | 1.43 | 1.429 | 1.425 | 1.491 | 1.44 | 1.363 | Over-range | 59.97 | 1115 | 779 | 1480 | 3373 | - - - | - - - | - - - | - - - | 1115 | 779 | 1480 | 3373 | 760 | 743 | 17 | 1521 | - - - | - - - | - - - | - - - | 760 | 743 | 17 | 1521 | 1358 | 1096 | 1507 | 3962 | # # # | # # # | # # # | # # # | 0.821 | 0.711 | 0.982 | 0.851 | # # # | # # # | # # # | - - - | 0.827 | 0.721 | 0.999 | 0.862 | - - - | 0.451 | 1.62 | 1.61 | 1.5 | 1.49 | 1.5 | 1.52 | 10.57 | 16.11 | 18.37 | 0 | - - - | - - - | - - - | - - - | 1358 | 1096 | 1507 | 3962 | Over-range | 776 | 765 | 286 | 2076 | 158 | 179 | 279 | 1413 | 1118 | 779 | 1477 | 3374 | 1118 | 779 | 1477 | 3374 | - - - | - - - | - - - | - - -
5/8/2026 | 6:45:00 PM | 281.29 | 279.03 | 277.36 | 486.66 | 480.39 | 483.83 | 4.9526 | 4.179 | 5.4986 | 4.145 | 1.43 | 1.429 | 1.425 | 1.493 | 1.43 | 1.353 | Over-range | 59.97 | 1128 | 870 | 1497 | 3496 | - - - | - - - | - - - | - - - | 1128 | 870 | 1497 | 3496 | 798 | 744 | -23 | 1519 | - - - | - - - | - - - | - - - | 798 | 744 | -23 | 1519 | 1392 | 1162 | 1525 | 4079 | # # # | # # # | # # # | # # # | 0.811 | 0.749 | 0.982 | 0.857 | # # # | # # # | # # # | - - - | 0.816 | 0.759 | 0.999 | 0.868 | - - - | 0.435 | 1.62 | 1.56 | 1.52 | 1.49 | 1.5 | 1.52 | 10.26 | 15.38 | 18.41 | 0 | - - - | - - - | - - - | - - - | 1392 | 1162 | 1525 | 4079 | Over-range | 814 | 766 | 288 | 2100 | 159 | 180 | 282 | 1449 | 1130 | 872 | 1494 | 3496 | 1130 | 872 | 1494 | 3496 | - - - | - - - | - - - | - - -
5/8/2026 | 7:00:00 PM | 281.52 | 279.16 | 277.58 | 486.95 | 480.63 | 484.31 | 5.617 | 5.8425 | 5.8604 | 3.4527 | 1.431 | 1.429 | 1.425 | 1.501 | 1.451 | 1.359 | Over-range | 59.98 | 1245 | 1448 | 1592 | 4285 | - - - | - - - | - - - | - - - | 1245 | 1448 | 1592 | 4285 | 957 | 671 | -153 | 1473 | - - - | - - - | - - - | - - - | 957 | 671 | -153 | 1473 | 1579 | 1616 | 1627 | 4821 | # # # | # # # | # # # | # # # | 0.789 | 0.896 | 0.979 | 0.889 | # # # | # # # | # # # | - - - | 0.786 | 0.894 | 0.983 | 0.888 | - - - | 0.344 | 1.62 | 1.55 | 1.45 | 1.47 | 1.47 | 1.48 | 9.22 | 10.61 | 17.6 | 0 | - - - | - - - | - - - | - - - | 1579 | 1616 | 1627 | 4821 | Over-range | 971 | 692 | 335 | 2204 | 162 | 167 | 285 | 1632 | 1257 | 1460 | 1615 | 4332 | 1257 | 1460 | 1615 | 4332 | - - - | - - - | - - - | - - -
5/8/2026 | 7:15:00 PM | 281.23 | 278.82 | 277.2 | 486.46 | 479.93 | 483.75 | 5.3486 | 5.9012 | 5.7083 | 2.7366 | 1.43 | 1.429 | 1.425 | 1.502 | 1.466 | 1.345 | Over-range | 59.99 | 1198 | 1519 | 1552 | 4268 | - - - | - - - | - - - | - - - | 1198 | 1519 | 1552 | 4268 | 896 | 613 | -126 | 1381 | - - - | - - - | - - - | - - - | 896 | 613 | -126 | 1381 | 1504 | 1645 | 1582 | 4731 | # # # | # # # | # # # | # # # | 0.796 | 0.923 | 0.981 | 0.902 | # # # | # # # | # # # | - - - | 0.802 | 0.927 | 0.997 | 0.91 | - - - | 0.324 | 1.59 | 1.52 | 1.45 | 1.46 | 1.46 | 1.46 | 9.52 | 8.79 | 17.8 | 0 | - - - | - - - | - - - | - - - | 1504 | 1645 | 1582 | 4731 | Over-range | 910 | 631 | 310 | 2042 | 161 | 153 | 282 | 1504 | 1201 | 1518 | 1550 | 4269 | 1201 | 1518 | 1550 | 4269 | - - - | - - - | - - - | - - -
5/8/2026 | 7:30:00 PM | 281.31 | 278.96 | 277.25 | 486.65 | 480.16 | 483.82 | 5.1886 | 5.6192 | 5.6502 | 2.752 | 1.43 | 1.429 | 1.424 | 1.499 | 1.459 | 1.353 | Over-range | 59.99 | 1168 | 1430 | 1538 | 4135 | - - - | - - - | - - - | - - - | 1168 | 1430 | 1538 | 4135 | 860 | 617 | -87 | 1388 | - - - | - - - | - - - | - - - | 860 | 617 | -87 | 1388 | 1459 | 1565 | 1566 | 4590 | # # # | # # # | # # # | # # # | 0.8 | 0.913 | 0.982 | 0.901 | # # # | # # # | # # # | - - - | 0.806 | 0.918 | 0.998 | 0.909 | - - - | 0.336 | 1.57 | 1.55 | 1.46 | 1.45 | 1.46 | 1.46 | 9.78 | 9.27 | 17.93 | 0 | - - - | - - - | - - - | - - - | 1459 | 1565 | 1566 | 4590 | Over-range | 874 | 636 | 299 | 1993 | 159 | 154 | 282 | 1429 | 1171 | 1429 | 1536 | 4136 | 1171 | 1429 | 1536 | 4136 | - - - | - - - | - - - | - - -
5/8/2026 | 7:45:00 PM | 281.44 | 279.02 | 277.4 | 486.84 | 480.29 | 484.09 | 4.9484 | 5.1106 | 5.4855 | 2.7523 | 1.43 | 1.429 | 1.424 | 1.494 | 1.442 | 1.353 | Over-range | 59.98 | 1133 | 1275 | 1495 | 3902 | - - - | - - - | - - - | - - - | 1133 | 1275 | 1495 | 3902 | 793 | 622 | -20 | 1394 | - - - | - - - | - - - | - - - | 793 | 622 | -20 | 1394 | 1393 | 1426 | 1522 | 4340 | # # # | # # # | # # # | # # # | 0.813 | 0.894 | 0.983 | 0.899 | # # # | # # # | # # # | - - - | 0.819 | 0.899 | 1 | 0.908 | - - - | 0.357 | 1.59 | 1.52 | 1.45 | 1.45 | 1.46 | 1.46 | 10.31 | 9.99 | 18.35 | 0 | - - - | - - - | - - - | - - - | 1393 | 1426 | 1522 | 4340 | Over-range | 810 | 639 | 282 | 1900 | 166 | 146 | 282 | 1290 | 1132 | 1275 | 1495 | 3902 | 1132 | 1275 | 1495 | 3902 | - - - | - - - | - - - | - - -
5/8/2026 | 8:00:00 PM | 281.75 | 279.37 | 277.69 | 487.42 | 480.86 | 484.58 | 5.3562 | 5.9351 | 5.7461 | 2.7548 | 1.43 | 1.429 | 1.425 | 1.502 | 1.466 | 1.363 | Over-range | 59.98 | 1196 | 1524 | 1563 | 4283 | - - - | - - - | - - - | - - - | 1196 | 1524 | 1563 | 4283 | 902 | 624 | -126 | 1399 | - - - | - - - | - - - | - - - | 902 | 624 | -126 | 1399 | 1508 | 1654 | 1595 | 4757 | # # # | # # # | # # # | # # # | 0.793 | 0.921 | 0.98 | 0.9 | # # # | # # # | # # # | - - - | 0.798 | 0.925 | 0.996 | 0.909 | - - - | 0.327 | 1.59 | 1.54 | 1.47 | 1.46 | 1.47 | 1.47 | 9.6 | 9.07 | 17.88 | 0 | - - - | - - - | - - - | - - - | 1508 | 1654 | 1595 | 4757 | Over-range | 918 | 642 | 317 | 2071 | 169 | 152 | 286 | 1524 | 1195 | 1526 | 1562 | 4282 | 1195 | 1526 | 1562 | 4282 | - - - | - - - | - - - | - - -
5/8/2026 | 8:15:00 PM | 281.8 | 279.4 | 277.74 | 487.48 | 480.95 | 484.66 | 4.9221 | 5.1253 | 5.4901 | 2.7566 | 1.43 | 1.429 | 1.424 | 1.496 | 1.481 | 1.384 | Over-range | 59.98 | 1123 | 1244 | 1491 | 3858 | - - - | - - - | - - - | - - - | 1123 | 1244 | 1491 | 3858 | 783 | 627 | -4 | 1405 | - - - | - - - | - - - | - - - | 783 | 627 | -4 | 1405 | 1381 | 1409 | 1523 | 4313 | # # # | # # # | # # # | # # # | 0.813 | 0.883 | 0.979 | 0.894 | # # # | # # # | # # # | - - - | 0.819 | 0.888 | 0.996 | 0.904 | - - - | 0.364 | 1.59 | 1.52 | 1.44 | 1.44 | 1.45 | 1.45 | 10.66 | 10.6 | 18.43 | 0 | - - - | - - - | - - - | - - - | 1381 | 1409 | 1523 | 4313 | Over-range | 801 | 644 | 311 | 1928 | 165 | 149 | 283 | 1310 | 1123 | 1246 | 1489 | 3857 | 1123 | 1246 | 1489 | 3857 | - - - | - - - | - - - | - - -
5/8/2026 | 8:30:00 PM | 281.77 | 279.33 | 277.6 | 487.45 | 480.71 | 484.5 | 4.786 | 4.7963 | 5.4185 | 2.7669 | 1.43 | 1.429 | 1.424 | 1.493 | 1.438 | 1.385 | Over-range | 59.98 | 1107 | 1161 | 1474 | 3742 | - - - | - - - | - - - | - - - | 1107 | 1161 | 1474 | 3742 | 748 | 627 | 34 | 1409 | - - - | - - - | - - - | - - - | 748 | 627 | 34 | 1409 | 1346 | 1330 | 1504 | 4180 | # # # | # # # | # # # | # # # | 0.822 | 0.873 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.829 | 0.878 | 0.998 | 0.905 | - - - | 0.377 | 1.54 | 1.54 | 1.45 | 1.44 | 1.45 | 1.45 | 10.82 | 10.79 | 18.57 | 0 | - - - | - - - | - - - | - - - | 1346 | 1330 | 1504 | 4180 | Over-range | 766 | 644 | 294 | 1863 | 162 | 148 | 282 | 1214 | 1108 | 1162 | 1472 | 3742 | 1108 | 1162 | 1472 | 3742 | - - - | - - - | - - - | - - -
5/8/2026 | 8:45:00 PM | 281.75 | 279.3 | 277.56 | 487.43 | 480.64 | 484.45 | 4.9125 | 5.0205 | 5.4623 | 2.759 | 1.43 | 1.429 | 1.424 | 1.492 | 1.432 | 1.36 | Over-range | 59.98 | 1129 | 1245 | 1490 | 3864 | - - - | - - - | - - - | - - - | 1129 | 1245 | 1490 | 3864 | 785 | 625 | -3 | 1406 | - - - | - - - | - - - | - - - | 785 | 625 | -3 | 1406 | 1384 | 1402 | 1516 | 4302 | # # # | # # # | # # # | # # # | 0.815 | 0.888 | 0.983 | 0.898 | # # # | # # # | # # # | - - - | 0.821 | 0.894 | 1 | 0.907 | - - - | 0.364 | 1.56 | 1.54 | 1.48 | 1.45 | 1.46 | 1.46 | 10.47 | 10.03 | 18.41 | 0 | - - - | - - - | - - - | - - - | 1384 | 1402 | 1516 | 4302 | Over-range | 801 | 643 | 282 | 1891 | 161 | 149 | 281 | 1265 | 1131 | 1245 | 1488 | 3864 | 1131 | 1245 | 1488 | 3864 | - - - | - - - | - - - | - - -
5/8/2026 | 9:00:00 PM | 281.73 | 279.28 | 277.49 | 487.37 | 480.59 | 484.35 | 5.1444 | 5.3145 | 5.5842 | 2.7705 | 1.43 | 1.43 | 1.424 | 1.492 | 1.448 | 1.366 | Over-range | 59.98 | 1173 | 1335 | 1520 | 4028 | - - - | - - - | - - - | - - - | 1173 | 1335 | 1520 | 4028 | 832 | 623 | -21 | 1433 | - - - | - - - | - - - | - - - | 832 | 623 | -21 | 1433 | 1447 | 1482 | 1549 | 4478 | # # # | # # # | # # # | # # # | 0.81 | 0.901 | 0.981 | 0.899 | # # # | # # # | # # # | - - - | 0.808 | 0.899 | 0.985 | 0.9 | - - - | 0.356 | 1.61 | 1.58 | 1.46 | 1.47 | 1.47 | 1.48 | 10 | 9.7 | 18.11 | 0 | - - - | - - - | - - - | - - - | 1447 | 1482 | 1549 | 4478 | Over-range | 847 | 642 | 298 | 1957 | 161 | 153 | 284 | 1324 | 1186 | 1342 | 1545 | 4073 | 1186 | 1342 | 1545 | 4073 | - - - | - - - | - - - | - - -
5/8/2026 | 9:15:00 PM | 282.01 | 279.71 | 277.92 | 487.98 | 481.35 | 484.95 | 5.6657 | 6.5114 | 5.907 | 2.7549 | 1.431 | 1.43 | 1.425 | 1.502 | 1.476 | 1.384 | Over-range | 59.97 | 1247 | 1702 | 1603 | 4553 | - - - | - - - | - - - | - - - | 1247 | 1702 | 1603 | 4553 | 983 | 625 | -200 | 1408 | - - - | - - - | - - - | - - - | 983 | 625 | -200 | 1408 | 1598 | 1820 | 1642 | 5059 | # # # | # # # | # # # | # # # | 0.781 | 0.935 | 0.977 | 0.9 | # # # | # # # | # # # | - - - | 0.786 | 0.938 | 0.993 | 0.908 | - - - | 0.309 | 1.64 | 1.57 | 1.48 | 1.49 | 1.49 | 1.5 | 9.09 | 8.27 | 17.46 | 0 | - - - | - - - | - - - | - - - | 1598 | 1820 | 1642 | 5059 | Over-range | 998 | 645 | 351 | 2206 | 171 | 156 | 288 | 1698 | 1250 | 1699 | 1605 | 4554 | 1250 | 1699 | 1605 | 4554 | - - - | - - - | - - - | - - -
5/8/2026 | 9:30:00 PM | 282.4 | 280.07 | 278.33 | 488.59 | 482.06 | 485.66 | 5.4999 | 6.1774 | 5.8145 | 2.7607 | 1.431 | 1.43 | 1.425 | 1.5 | 1.47 | 1.371 | Over-range | 59.98 | 1222 | 1603 | 1585 | 4410 | - - - | - - - | - - - | - - - | 1222 | 1603 | 1585 | 4410 | 943 | 631 | -153 | 1420 | - - - | - - - | - - - | - - - | 943 | 631 | -153 | 1420 | 1553 | 1729 | 1618 | 4901 | # # # | # # # | # # # | # # # | 0.787 | 0.927 | 0.979 | 0.9 | # # # | # # # | # # # | - - - | 0.792 | 0.93 | 0.996 | 0.908 | - - - | 0.322 | 1.63 | 1.56 | 1.49 | 1.49 | 1.48 | 1.5 | 9.41 | 8.66 | 17.71 | 0 | - - - | - - - | - - - | - - - | 1553 | 1729 | 1618 | 4901 | Over-range | 958 | 650 | 327 | 2138 | 171 | 156 | 288 | 1598 | 1224 | 1600 | 1587 | 4411 | 1224 | 1600 | 1587 | 4411 | - - - | - - - | - - - | - - -
5/8/2026 | 9:45:00 PM | 282.48 | 280.26 | 278.4 | 488.82 | 482.35 | 485.71 | 4.9153 | 5.0738 | 5.4947 | 2.7748 | 1.431 | 1.43 | 1.425 | 1.493 | 1.475 | 1.386 | Over-range | 59.99 | 1125 | 1229 | 1496 | 3850 | - - - | - - - | - - - | - - - | 1125 | 1229 | 1496 | 3850 | 783 | 636 | 11 | 1430 | - - - | - - - | - - - | - - - | 783 | 636 | 11 | 1430 | 1382 | 1400 | 1528 | 4311 | # # # | # # # | # # # | # # # | 0.814 | 0.877 | 0.979 | 0.893 | # # # | # # # | # # # | - - - | 0.82 | 0.883 | 0.996 | 0.903 | - - - | 0.371 | 1.65 | 1.57 | 1.45 | 1.48 | 1.46 | 1.49 | 10.76 | 10.72 | 18.41 | 0 | - - - | - - - | - - - | - - - | 1382 | 1400 | 1528 | 4311 | Over-range | 801 | 654 | 310 | 1937 | 166 | 153 | 284 | 1299 | 1127 | 1227 | 1497 | 3851 | 1127 | 1227 | 1497 | 3851 | - - - | - - - | - - - | - - -
5/8/2026 | 10:00:00 PM | 282.43 | 280.15 | 278.38 | 488.69 | 482.19 | 485.71 | 4.7282 | 4.6741 | 5.38 | 2.7668 | 1.431 | 1.43 | 1.425 | 1.492 | 1.438 | 1.39 | Over-range | 59.99 | 1099 | 1126 | 1467 | 3692 | - - - | - - - | - - - | - - - | 1099 | 1126 | 1467 | 3692 | 738 | 637 | 54 | 1429 | - - - | - - - | - - - | - - - | 738 | 637 | 54 | 1429 | 1334 | 1304 | 1497 | 4135 | # # # | # # # | # # # | # # # | 0.824 | 0.864 | 0.98 | 0.893 | # # # | # # # | # # # | - - - | 0.83 | 0.87 | 0.999 | 0.903 | - - - | 0.387 | 1.63 | 1.55 | 1.46 | 1.48 | 1.46 | 1.49 | 10.98 | 11.19 | 18.94 | 0 | - - - | - - - | - - - | - - - | 1334 | 1304 | 1497 | 4135 | Over-range | 756 | 654 | 297 | 1862 | 166 | 150 | 286 | 1191 | 1098 | 1127 | 1467 | 3692 | 1098 | 1127 | 1467 | 3692 | - - - | - - - | - - - | - - -
5/8/2026 | 10:15:00 PM | 282.54 | 280.18 | 278.37 | 488.86 | 482.13 | 485.81 | 4.8312 | 4.8615 | 5.4493 | 2.772 | 1.43 | 1.429 | 1.424 | 1.493 | 1.427 | 1.371 | Over-range | 59.97 | 1116 | 1192 | 1489 | 3797 | - - - | - - - | - - - | - - - | 1116 | 1192 | 1489 | 3797 | 768 | 638 | 28 | 1434 | - - - | - - - | - - - | - - - | 768 | 638 | 28 | 1434 | 1365 | 1361 | 1517 | 4242 | # # # | # # # | # # # | # # # | 0.818 | 0.876 | 0.982 | 0.895 | # # # | # # # | # # # | - - - | 0.824 | 0.881 | 0.999 | 0.904 | - - - | 0.378 | 1.65 | 1.56 | 1.48 | 1.49 | 1.48 | 1.5 | 10.78 | 10.63 | 18.58 | 0 | - - - | - - - | - - - | - - - | 1365 | 1361 | 1517 | 4242 | Over-range | 785 | 655 | 287 | 1891 | 165 | 149 | 284 | 1232 | 1116 | 1193 | 1487 | 3797 | 1116 | 1193 | 1487 | 3797 | - - - | - - - | - - - | - - -
5/8/2026 | 10:30:00 PM | 282.83 | 280.48 | 278.71 | 489.34 | 482.74 | 486.34 | 5.0628 | 5.3061 | 5.5759 | 2.7766 | 1.43 | 1.428 | 1.424 | 1.498 | 1.444 | 1.371 | Over-range | 59.98 | 1153 | 1331 | 1526 | 4009 | - - - | - - - | - - - | - - - | 1153 | 1331 | 1526 | 4009 | 831 | 639 | -29 | 1441 | - - - | - - - | - - - | - - - | 831 | 639 | -29 | 1441 | 1431 | 1485 | 1554 | 4470 | # # # | # # # | # # # | # # # | 0.806 | 0.896 | 0.982 | 0.897 | # # # | # # # | # # # | - - - | 0.812 | 0.901 | 0.999 | 0.906 | - - - | 0.359 | 1.67 | 1.54 | 1.51 | 1.51 | 1.49 | 1.53 | 10.35 | 10.11 | 18.55 | 0 | - - - | - - - | - - - | - - - | 1431 | 1485 | 1554 | 4470 | Over-range | 847 | 658 | 295 | 1977 | 164 | 157 | 290 | 1352 | 1155 | 1332 | 1522 | 4009 | 1155 | 1332 | 1522 | 4009 | - - - | - - - | - - - | - - -
5/8/2026 | 10:45:00 PM | 282.98 | 280.7 | 278.92 | 489.65 | 483.14 | 486.62 | 5.508 | 6.1749 | 5.8311 | 2.7767 | 1.431 | 1.429 | 1.424 | 1.504 | 1.468 | 1.383 | Over-range | 59.98 | 1224 | 1602 | 1593 | 4418 | - - - | - - - | - - - | - - - | 1224 | 1602 | 1593 | 4418 | 950 | 638 | -146 | 1442 | - - - | - - - | - - - | - - - | 950 | 638 | -146 | 1442 | 1558 | 1732 | 1626 | 4917 | # # # | # # # | # # # | # # # | 0.786 | 0.925 | 0.979 | 0.899 | # # # | # # # | # # # | - - - | 0.791 | 0.929 | 0.996 | 0.907 | - - - | 0.326 | 1.67 | 1.58 | 1.51 | 1.52 | 1.5 | 1.54 | 9.54 | 8.91 | 17.98 | 0 | - - - | - - - | - - - | - - - | 1558 | 1732 | 1626 | 4917 | Over-range | 964 | 659 | 329 | 2157 | 165 | 163 | 293 | 1603 | 1228 | 1601 | 1590 | 4419 | 1228 | 1601 | 1590 | 4419 | - - - | - - - | - - - | - - -
5/8/2026 | 11:00:00 PM | 283.26 | 281.08 | 279.32 | 490.22 | 483.84 | 487.2 | 5.2792 | 5.5581 | 5.6669 | 2.7863 | 1.431 | 1.429 | 1.425 | 1.497 | 1.451 | 1.372 | Over-range | 59.99 | 1195 | 1413 | 1553 | 4161 | - - - | - - - | - - - | - - - | 1195 | 1413 | 1553 | 4161 | 879 | 646 | -41 | 1483 | - - - | - - - | - - - | - - - | 879 | 646 | -41 | 1483 | 1493 | 1562 | 1583 | 4638 | # # # | # # # | # # # | # # # | 0.8 | 0.905 | 0.981 | 0.897 | # # # | # # # | # # # | - - - | 0.798 | 0.902 | 0.989 | 0.898 | - - - | 0.357 | 1.7 | 1.6 | 1.51 | 1.54 | 1.52 | 1.56 | 10.04 | 9.77 | 18.45 | 0 | - - - | - - - | - - - | - - - | 1493 | 1562 | 1583 | 4638 | Over-range | 895 | 666 | 304 | 2048 | 168 | 161 | 294 | 1408 | 1208 | 1432 | 1577 | 4217 | 1208 | 1432 | 1577 | 4217 | - - - | - - - | - - - | - - -
5/8/2026 | 11:15:00 PM | 283.38 | 280.96 | 279.22 | 490.25 | 483.52 | 487.29 | 4.9017 | 5.015 | 5.4805 | 2.7796 | 1.431 | 1.429 | 1.425 | 1.496 | 1.481 | 1.403 | Over-range | 59.97 | 1124 | 1201 | 1494 | 3818 | - - - | - - - | - - - | - - - | 1124 | 1201 | 1494 | 3818 | 782 | 649 | 33 | 1463 | - - - | - - - | - - - | - - - | 782 | 649 | 33 | 1463 | 1381 | 1383 | 1528 | 4293 | # # # | # # # | # # # | # # # | 0.814 | 0.868 | 0.977 | 0.889 | # # # | # # # | # # # | - - - | 0.82 | 0.873 | 0.996 | 0.9 | - - - | 0.383 | 1.72 | 1.61 | 1.53 | 1.55 | 1.54 | 1.57 | 11.06 | 11.31 | 18.85 | 0 | - - - | - - - | - - - | - - - | 1381 | 1383 | 1528 | 4293 | Over-range | 801 | 667 | 321 | 1959 | 171 | 155 | 290 | 1292 | 1124 | 1201 | 1494 | 3818 | 1124 | 1201 | 1494 | 3818 | - - - | - - - | - - - | - - -
5/8/2026 | 11:30:00 PM | 283.43 | 281.04 | 279.21 | 490.4 | 483.59 | 487.3 | 4.7362 | 4.6703 | 5.4077 | 2.7894 | 1.432 | 1.43 | 1.426 | 1.493 | 1.44 | 1.39 | Over-range | 59.98 | 1101 | 1123 | 1479 | 3703 | - - - | - - - | - - - | - - - | 1101 | 1123 | 1479 | 3703 | 748 | 650 | 65 | 1463 | - - - | - - - | - - - | - - - | 748 | 650 | 65 | 1463 | 1341 | 1308 | 1510 | 4159 | # # # | # # # | # # # | # # # | 0.821 | 0.859 | 0.98 | 0.89 | # # # | # # # | # # # | - - - | 0.827 | 0.865 | 0.999 | 0.901 | - - - | 0.395 | 1.72 | 1.61 | 1.56 | 1.56 | 1.55 | 1.59 | 11.21 | 11.4 | 18.94 | 0 | - - - | - - - | - - - | - - - | 1341 | 1308 | 1510 | 4159 | Over-range | 766 | 668 | 300 | 1893 | 166 | 154 | 289 | 1200 | 1102 | 1124 | 1477 | 3703 | 1102 | 1124 | 1477 | 3703 | - - - | - - - | - - - | - - -
5/8/2026 | 11:45:00 PM | 283.85 | 281.46 | 279.75 | 491.07 | 484.45 | 488.17 | 4.7261 | 4.6375 | 5.3858 | 2.785 | 1.431 | 1.429 | 1.425 | 1.492 | 1.426 | 1.391 | Over-range | 59.99 | 1100 | 1117 | 1477 | 3694 | - - - | - - - | - - - | - - - | 1100 | 1117 | 1477 | 3694 | 750 | 656 | 71 | 1477 | - - - | - - - | - - - | - - - | 750 | 656 | 71 | 1477 | 1341 | 1305 | 1507 | 4153 | # # # | # # # | # # # | # # # | 0.82 | 0.856 | 0.98 | 0.889 | # # # | # # # | # # # | - - - | 0.827 | 0.862 | 0.999 | 0.9 | - - - | 0.4 | 1.72 | 1.64 | 1.55 | 1.57 | 1.55 | 1.59 | 11.27 | 11.42 | 19.1 | 0 | - - - | - - - | - - - | - - - | 1341 | 1305 | 1507 | 4153 | Over-range | 768 | 674 | 298 | 1898 | 165 | 156 | 290 | 1192 | 1103 | 1116 | 1475 | 3694 | 1103 | 1116 | 1475 | 3694 | - - - | - - - | - - - | - - -
5/9/2026 | 12:00:00 AM | 283.95 | 281.59 | 279.8 | 491.3 | 484.63 | 488.25 | 4.796 | 4.7696 | 5.4398 | 2.7933 | 1.431 | 1.429 | 1.424 | 1.494 | 1.423 | 1.379 | Over-range | 59.99 | 1111 | 1161 | 1493 | 3765 | - - - | - - - | - - - | - - - | 1111 | 1161 | 1493 | 3765 | 769 | 656 | 54 | 1479 | - - - | - - - | - - - | - - - | 769 | 656 | 54 | 1479 | 1362 | 1343 | 1522 | 4227 | # # # | # # # | # # # | # # # | 0.816 | 0.864 | 0.981 | 0.891 | # # # | # # # | # # # | - - - | 0.823 | 0.87 | 0.999 | 0.901 | - - - | 0.393 | 1.73 | 1.66 | 1.56 | 1.58 | 1.57 | 1.61 | 11.09 | 11.24 | 18.93 | 0 | - - - | - - - | - - - | - - - | 1362 | 1343 | 1522 | 4227 | Over-range | 787 | 675 | 295 | 1921 | 167 | 159 | 290 | 1225 | 1114 | 1158 | 1493 | 3766 | 1114 | 1158 | 1493 | 3766 | - - - | - - - | - - - | - - -
5/9/2026 | 12:15:00 AM | 283.98 | 281.46 | 279.77 | 491.19 | 484.47 | 488.28 | 5.2644 | 5.6809 | 5.6729 | 2.7807 | 1.431 | 1.428 | 1.424 | 1.505 | 1.45 | 1.351 | Over-range | 59.98 | 1186 | 1444 | 1556 | 4187 | - - - | - - - | - - - | - - - | 1186 | 1444 | 1556 | 4187 | 892 | 652 | -70 | 1473 | - - - | - - - | - - - | - - - | 892 | 652 | -70 | 1473 | 1494 | 1594 | 1587 | 4675 | # # # | # # # | # # # | # # # | 0.794 | 0.906 | 0.981 | 0.896 | # # # | # # # | # # # | - - - | 0.8 | 0.91 | 0.999 | 0.905 | - - - | 0.352 | 1.74 | 1.64 | 1.56 | 1.58 | 1.57 | 1.6 | 10.07 | 9.87 | 18.6 | 0 | - - - | - - - | - - - | - - - | 1494 | 1594 | 1587 | 4675 | Over-range | 908 | 672 | 309 | 2080 | 169 | 164 | 295 | 1466 | 1189 | 1441 | 1557 | 4187 | 1189 | 1441 | 1557 | 4187 | - - - | - - - | - - - | - - -
5/9/2026 | 12:30:00 AM | 284.45 | 281.93 | 280.25 | 492.06 | 485.28 | 489.05 | 5.3893 | 5.9178 | 5.7609 | 2.7892 | 1.43 | 1.428 | 1.423 | 1.506 | 1.454 | 1.346 | Over-range | 59.99 | 1207 | 1520 | 1583 | 4310 | - - - | - - - | - - - | - - - | 1207 | 1520 | 1583 | 4310 | 927 | 659 | -100 | 1484 | - - - | - - - | - - - | - - - | 927 | 659 | -100 | 1484 | 1532 | 1665 | 1614 | 4811 | # # # | # # # | # # # | # # # | 0.788 | 0.913 | 0.981 | 0.896 | # # # | # # # | # # # | - - - | 0.794 | 0.917 | 0.997 | 0.905 | - - - | 0.344 | 1.75 | 1.64 | 1.55 | 1.58 | 1.56 | 1.6 | 9.93 | 9.48 | 18.28 | 0 | - - - | - - - | - - - | - - - | 1532 | 1665 | 1614 | 4811 | Over-range | 943 | 678 | 315 | 2138 | 177 | 159 | 295 | 1537 | 1207 | 1520 | 1583 | 4310 | 1207 | 1520 | 1583 | 4310 | - - - | - - - | - - - | - - -
5/9/2026 | 12:45:00 AM | 284.84 | 282.3 | 280.7 | 492.66 | 486.04 | 489.79 | 4.7382 | 4.6934 | 5.4211 | 2.7936 | 1.431 | 1.428 | 1.423 | 1.496 | 1.462 | 1.393 | Over-range | 59.98 | 1100 | 1112 | 1487 | 3699 | - - - | - - - | - - - | - - - | 1100 | 1112 | 1487 | 3699 | 755 | 670 | 83 | 1508 | - - - | - - - | - - - | - - - | 755 | 670 | 83 | 1508 | 1346 | 1314 | 1521 | 4181 | # # # | # # # | # # # | # # # | 0.817 | 0.847 | 0.978 | 0.885 | # # # | # # # | # # # | - - - | 0.823 | 0.854 | 0.997 | 0.895 | - - - | 0.408 | 1.77 | 1.61 | 1.56 | 1.59 | 1.56 | 1.6 | 11.57 | 11.94 | 19.09 | 0 | - - - | - - - | - - - | - - - | 1346 | 1314 | 1521 | 4181 | Over-range | 775 | 688 | 316 | 1946 | 175 | 157 | 292 | 1227 | 1098 | 1113 | 1488 | 3699 | 1098 | 1113 | 1488 | 3699 | - - - | - - - | - - - | - - -
5/9/2026 | 1:00:00 AM | 285.1 | 282.58 | 280.84 | 493.19 | 486.37 | 490.11 | 4.7356 | 4.668 | 5.4205 | 2.799 | 1.43 | 1.428 | 1.424 | 1.496 | 1.447 | 1.394 | Over-range | 59.99 | 1101 | 1115 | 1490 | 3706 | - - - | - - - | - - - | - - - | 1101 | 1115 | 1490 | 3706 | 759 | 674 | 83 | 1516 | - - - | - - - | - - - | - - - | 759 | 674 | 83 | 1516 | 1349 | 1314 | 1522 | 4185 | # # # | # # # | # # # | # # # | 0.817 | 0.848 | 0.979 | 0.885 | # # # | # # # | # # # | - - - | 0.823 | 0.855 | 0.998 | 0.896 | - - - | 0.409 | 1.75 | 1.64 | 1.58 | 1.59 | 1.57 | 1.62 | 11.5 | 11.87 | 19.31 | 0 | - - - | - - - | - - - | - - - | 1349 | 1314 | 1522 | 4185 | Over-range | 778 | 692 | 311 | 1944 | 172 | 159 | 294 | 1215 | 1101 | 1116 | 1489 | 3705 | 1101 | 1116 | 1489 | 3705 | - - - | - - - | - - - | - - -
5/9/2026 | 1:15:00 AM | 285.06 | 282.51 | 280.94 | 493.03 | 486.39 | 490.23 | 4.7505 | 4.6799 | 5.4264 | 2.7981 | 1.431 | 1.428 | 1.424 | 1.497 | 1.432 | 1.391 | Over-range | 59.98 | 1104 | 1126 | 1494 | 3724 | - - - | - - - | - - - | - - - | 1104 | 1126 | 1494 | 3724 | 766 | 674 | 80 | 1519 | - - - | - - - | - - - | - - - | 766 | 674 | 80 | 1519 | 1354 | 1322 | 1524 | 4201 | # # # | # # # | # # # | # # # | 0.815 | 0.852 | 0.98 | 0.886 | # # # | # # # | # # # | - - - | 0.822 | 0.857 | 0.998 | 0.897 | - - - | 0.408 | 1.76 | 1.64 | 1.59 | 1.6 | 1.57 | 1.61 | 11.46 | 11.67 | 19.2 | 0 | - - - | - - - | - - - | - - - | 1354 | 1322 | 1524 | 4201 | Over-range | 784 | 693 | 304 | 1944 | 168 | 161 | 293 | 1212 | 1107 | 1124 | 1492 | 3724 | 1107 | 1124 | 1492 | 3724 | - - - | - - - | - - - | - - -
5/9/2026 | 1:30:00 AM | 285.12 | 282.56 | 280.97 | 493.12 | 486.48 | 490.29 | 4.8769 | 4.9213 | 5.4747 | 2.7932 | 1.431 | 1.429 | 1.424 | 1.498 | 1.426 | 1.375 | Over-range | 59.99 | 1125 | 1204 | 1508 | 3837 | - - - | - - - | - - - | - - - | 1125 | 1204 | 1508 | 3837 | 799 | 672 | 44 | 1515 | - - - | - - - | - - - | - - - | 799 | 672 | 44 | 1515 | 1390 | 1389 | 1538 | 4318 | # # # | # # # | # # # | # # # | 0.809 | 0.867 | 0.981 | 0.889 | # # # | # # # | # # # | - - - | 0.816 | 0.873 | 0.999 | 0.899 | - - - | 0.395 | 1.77 | 1.65 | 1.58 | 1.6 | 1.58 | 1.62 | 11.14 | 11.28 | 19.22 | 0 | - - - | - - - | - - - | - - - | 1390 | 1389 | 1538 | 4318 | Over-range | 817 | 692 | 301 | 1979 | 172 | 163 | 296 | 1272 | 1127 | 1202 | 1509 | 3838 | 1127 | 1202 | 1509 | 3838 | - - - | - - - | - - - | - - -
5/9/2026 | 1:45:00 AM | 285.32 | 282.81 | 281.15 | 493.51 | 486.88 | 490.59 | 5.6005 | 6.1644 | 5.8818 | 2.7977 | 1.43 | 1.428 | 1.424 | 1.505 | 1.456 | 1.351 | Over-range | 59.99 | 1250 | 1594 | 1618 | 4462 | - - - | - - - | - - - | - - - | 1250 | 1594 | 1618 | 4462 | 975 | 676 | -98 | 1552 | - - - | - - - | - - - | - - - | 975 | 676 | -98 | 1552 | 1596 | 1740 | 1653 | 4989 | # # # | # # # | # # # | # # # | 0.783 | 0.916 | 0.979 | 0.894 | # # # | # # # | # # # | - - - | 0.782 | 0.913 | 0.988 | 0.896 | - - - | 0.348 | 1.78 | 1.67 | 1.56 | 1.6 | 1.57 | 1.61 | 9.71 | 9.44 | 18.43 | 0 | - - - | - - - | - - - | - - - | 1596 | 1740 | 1653 | 4989 | Over-range | 992 | 697 | 339 | 2234 | 182 | 170 | 305 | 1595 | 1261 | 1601 | 1631 | 4492 | 1261 | 1601 | 1631 | 4492 | - - - | - - - | - - - | - - -
5/9/2026 | 2:00:00 AM | 285.43 | 282.91 | 281.26 | 493.72 | 487.01 | 490.81 | 5.3757 | 5.8734 | 5.7585 | 2.7985 | 1.431 | 1.428 | 1.424 | 1.508 | 1.452 | 1.335 | Over-range | 59.99 | 1205 | 1509 | 1589 | 4303 | - - - | - - - | - - - | - - - | 1205 | 1509 | 1589 | 4303 | 933 | 674 | -84 | 1522 | - - - | - - - | - - - | - - - | 933 | 674 | -84 | 1522 | 1534 | 1661 | 1620 | 4815 | # # # | # # # | # # # | # # # | 0.785 | 0.908 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.791 | 0.913 | 0.998 | 0.902 | - - - | 0.354 | 1.77 | 1.65 | 1.58 | 1.61 | 1.58 | 1.61 | 10.13 | 9.78 | 18.59 | 0 | - - - | - - - | - - - | - - - | 1534 | 1661 | 1620 | 4815 | Over-range | 950 | 694 | 313 | 2161 | 177 | 168 | 301 | 1534 | 1207 | 1506 | 1590 | 4304 | 1207 | 1506 | 1590 | 4304 | - - - | - - - | - - - | - - -
5/9/2026 | 2:15:00 AM | 285.28 | 282.72 | 281.11 | 493.4 | 486.75 | 490.55 | 4.8867 | 4.9719 | 5.4837 | 2.7978 | 1.431 | 1.429 | 1.424 | 1.497 | 1.467 | 1.381 | Over-range | 59.98 | 1123 | 1194 | 1506 | 3823 | - - - | - - - | - - - | - - - | 1123 | 1194 | 1506 | 3823 | 798 | 675 | 51 | 1524 | - - - | - - - | - - - | - - - | 798 | 675 | 51 | 1524 | 1389 | 1389 | 1541 | 4319 | # # # | # # # | # # # | # # # | 0.808 | 0.86 | 0.978 | 0.885 | # # # | # # # | # # # | - - - | 0.815 | 0.866 | 0.996 | 0.896 | - - - | 0.399 | 1.78 | 1.69 | 1.61 | 1.63 | 1.6 | 1.64 | 11.36 | 11.62 | 19.15 | 0 | - - - | - - - | - - - | - - - | 1389 | 1389 | 1541 | 4319 | Over-range | 816 | 695 | 320 | 2006 | 170 | 164 | 296 | 1298 | 1126 | 1193 | 1504 | 3823 | 1126 | 1193 | 1504 | 3823 | - - - | - - - | - - - | - - -
5/9/2026 | 2:30:00 AM | 285.53 | 282.92 | 281.32 | 493.77 | 487.1 | 490.97 | 4.7297 | 4.6431 | 5.4212 | 2.807 | 1.431 | 1.428 | 1.424 | 1.498 | 1.444 | 1.399 | Over-range | 60.01 | 1101 | 1107 | 1492 | 3700 | - - - | - - - | - - - | - - - | 1101 | 1107 | 1492 | 3700 | 761 | 677 | 91 | 1529 | - - - | - - - | - - - | - - - | 761 | 677 | 91 | 1529 | 1349 | 1310 | 1525 | 4184 | # # # | # # # | # # # | # # # | 0.816 | 0.845 | 0.979 | 0.884 | # # # | # # # | # # # | - - - | 0.823 | 0.851 | 0.997 | 0.895 | - - - | 0.413 | 1.81 | 1.68 | 1.6 | 1.63 | 1.61 | 1.65 | 11.61 | 12.08 | 19.38 | 0 | - - - | - - - | - - - | - - - | 1349 | 1310 | 1525 | 4184 | Over-range | 780 | 697 | 314 | 1953 | 170 | 165 | 296 | 1213 | 1104 | 1105 | 1491 | 3700 | 1104 | 1105 | 1491 | 3700 | - - - | - - - | - - - | - - -
5/9/2026 | 2:45:00 AM | 285.56 | 283.02 | 281.3 | 493.97 | 487.13 | 490.93 | 4.7865 | 4.7425 | 5.4449 | 2.8047 | 1.431 | 1.429 | 1.424 | 1.496 | 1.431 | 1.389 | Over-range | 59.99 | 1110 | 1145 | 1501 | 3756 | - - - | - - - | - - - | - - - | 1110 | 1145 | 1501 | 3756 | 778 | 679 | 75 | 1532 | - - - | - - - | - - - | - - - | 778 | 679 | 75 | 1532 | 1367 | 1341 | 1532 | 4240 | # # # | # # # | # # # | # # # | 0.812 | 0.854 | 0.98 | 0.886 | # # # | # # # | # # # | - - - | 0.82 | 0.86 | 0.999 | 0.896 | - - - | 0.408 | 1.81 | 1.69 | 1.62 | 1.64 | 1.62 | 1.65 | 11.54 | 11.68 | 19.22 | 0 | - - - | - - - | - - - | - - - | 1367 | 1341 | 1532 | 4240 | Over-range | 797 | 698 | 306 | 1966 | 171 | 163 | 296 | 1232 | 1113 | 1144 | 1499 | 3756 | 1113 | 1144 | 1499 | 3756 | - - - | - - - | - - - | - - -
5/9/2026 | 3:00:00 AM | 285.49 | 282.88 | 281.15 | 493.76 | 486.85 | 490.78 | 4.8188 | 4.8097 | 5.4582 | 2.7983 | 1.431 | 1.428 | 1.424 | 1.499 | 1.425 | 1.384 | Over-range | 59.98 | 1115 | 1168 | 1504 | 3788 | - - - | - - - | - - - | - - - | 1115 | 1168 | 1504 | 3788 | 787 | 676 | 64 | 1527 | - - - | - - - | - - - | - - - | 787 | 676 | 64 | 1527 | 1376 | 1360 | 1535 | 4270 | # # # | # # # | # # # | # # # | 0.811 | 0.859 | 0.98 | 0.887 | # # # | # # # | # # # | - - - | 0.817 | 0.865 | 0.999 | 0.897 | - - - | 0.403 | 1.8 | 1.67 | 1.6 | 1.63 | 1.6 | 1.64 | 11.41 | 11.51 | 19.2 | 0 | - - - | - - - | - - - | - - - | 1376 | 1360 | 1535 | 4270 | Over-range | 806 | 696 | 303 | 1972 | 173 | 163 | 296 | 1247 | 1117 | 1166 | 1504 | 3788 | 1117 | 1166 | 1504 | 3788 | - - - | - - - | - - - | - - -
5/9/2026 | 3:15:00 AM | 285.54 | 282.98 | 281.2 | 493.9 | 487.02 | 490.83 | 5.3541 | 5.8351 | 5.7438 | 2.7965 | 1.43 | 1.428 | 1.423 | 1.507 | 1.449 | 1.342 | Over-range | 59.99 | 1201 | 1495 | 1584 | 4280 | - - - | - - - | - - - | - - - | 1201 | 1495 | 1584 | 4280 | 928 | 673 | -78 | 1523 | - - - | - - - | - - - | - - - | 928 | 673 | -78 | 1523 | 1528 | 1649 | 1615 | 4792 | # # # | # # # | # # # | # # # | 0.786 | 0.907 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.792 | 0.911 | 0.998 | 0.902 | - - - | 0.356 | 1.81 | 1.65 | 1.6 | 1.62 | 1.6 | 1.64 | 10.23 | 9.9 | 18.67 | 0 | - - - | - - - | - - - | - - - | 1528 | 1649 | 1615 | 4792 | Over-range | 944 | 694 | 314 | 2154 | 174 | 169 | 301 | 1522 | 1204 | 1494 | 1582 | 4280 | 1204 | 1494 | 1582 | 4280 | - - - | - - - | - - - | - - -
5/9/2026 | 3:30:00 AM | 285.86 | 283.27 | 281.55 | 494.43 | 487.54 | 491.44 | 5.3841 | 5.892 | 5.758 | 2.794 | 1.431 | 1.428 | 1.424 | 1.504 | 1.445 | 1.339 | Over-range | 59.98 | 1206 | 1513 | 1590 | 4309 | - - - | - - - | - - - | - - - | 1206 | 1513 | 1590 | 4309 | 939 | 678 | -82 | 1534 | - - - | - - - | - - - | - - - | 939 | 678 | -82 | 1534 | 1538 | 1667 | 1621 | 4826 | # # # | # # # | # # # | # # # | 0.784 | 0.908 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.789 | 0.912 | 0.998 | 0.901 | - - - | 0.356 | 1.79 | 1.67 | 1.6 | 1.63 | 1.6 | 1.64 | 10.24 | 9.78 | 18.63 | 0 | - - - | - - - | - - - | - - - | 1538 | 1667 | 1621 | 4826 | Over-range | 955 | 699 | 315 | 2174 | 175 | 167 | 301 | 1539 | 1207 | 1514 | 1586 | 4308 | 1207 | 1514 | 1586 | 4308 | - - - | - - - | - - - | - - -
5/9/2026 | 3:45:00 AM | 285.76 | 283.28 | 281.5 | 494.35 | 487.58 | 491.26 | 5.1351 | 5.43 | 5.6279 | 2.7985 | 1.429 | 1.427 | 1.423 | 1.501 | 1.45 | 1.353 | Over-range | 59.98 | 1164 | 1354 | 1552 | 4071 | - - - | - - - | - - - | - - - | 1164 | 1354 | 1552 | 4071 | 869 | 681 | -13 | 1536 | - - - | - - - | - - - | - - - | 869 | 681 | -13 | 1536 | 1465 | 1529 | 1584 | 4577 | # # # | # # # | # # # | # # # | 0.795 | 0.886 | 0.98 | 0.889 | # # # | # # # | # # # | - - - | 0.801 | 0.891 | 0.998 | 0.899 | - - - | 0.377 | 1.76 | 1.66 | 1.59 | 1.6 | 1.58 | 1.62 | 10.84 | 10.64 | 18.93 | 0 | - - - | - - - | - - - | - - - | 1465 | 1529 | 1584 | 4577 | Over-range | 888 | 701 | 312 | 2091 | 179 | 163 | 299 | 1415 | 1164 | 1355 | 1551 | 4071 | 1164 | 1355 | 1551 | 4071 | - - - | - - - | - - - | - - -
5/9/2026 | 4:00:00 AM | 285.9 | 283.4 | 281.63 | 494.54 | 487.78 | 491.51 | 4.5713 | 4.3661 | 5.3521 | 2.8033 | 1.43 | 1.428 | 1.423 | 1.494 | 1.471 | 1.422 | Over-range | 59.99 | 1074 | 1010 | 1470 | 3554 | - - - | - - - | - - - | - - - | 1074 | 1010 | 1470 | 3554 | 722 | 685 | 137 | 1545 | - - - | - - - | - - - | - - - | 722 | 685 | 137 | 1545 | 1306 | 1234 | 1507 | 4047 | # # # | # # # | # # # | # # # | 0.822 | 0.819 | 0.975 | 0.878 | # # # | # # # | # # # | - - - | 0.83 | 0.826 | 0.995 | 0.89 | - - - | 0.435 | 1.78 | 1.66 | 1.6 | 1.62 | 1.59 | 1.63 | 12.2 | 12.9 | 19.61 | 0 | - - - | - - - | - - - | - - - | 1306 | 1234 | 1507 | 4047 | Over-range | 743 | 705 | 331 | 1935 | 176 | 165 | 297 | 1164 | 1075 | 1008 | 1472 | 3555 | 1075 | 1008 | 1472 | 3555 | - - - | - - - | - - - | - - -
5/9/2026 | 4:15:00 AM | 285.99 | 283.52 | 281.71 | 494.77 | 487.94 | 491.64 | 4.8779 | 4.7309 | 5.4738 | 2.8048 | 1.43 | 1.427 | 1.423 | 1.493 | 1.435 | 1.403 | Over-range | 59.99 | 1133 | 1138 | 1505 | 3776 | - - - | - - - | - - - | - - - | 1133 | 1138 | 1505 | 3776 | 789 | 687 | 109 | 1586 | - - - | - - - | - - - | - - - | 789 | 687 | 109 | 1586 | 1392 | 1340 | 1542 | 4274 | # # # | # # # | # # # | # # # | 0.814 | 0.849 | 0.976 | 0.883 | # # # | # # # | # # # | - - - | 0.813 | 0.849 | 0.985 | 0.886 | - - - | 0.42 | 1.8 | 1.65 | 1.59 | 1.62 | 1.59 | 1.63 | 11.43 | 11.89 | 19.41 | 0 | - - - | - - - | - - - | - - - | 1392 | 1340 | 1542 | 4274 | Over-range | 809 | 707 | 330 | 2003 | 176 | 165 | 301 | 1215 | 1146 | 1144 | 1517 | 3806 | 1146 | 1144 | 1517 | 3806 | - - - | - - - | - - - | - - -
5/9/2026 | 4:30:00 AM | 286.14 | 283.72 | 281.94 | 495.03 | 488.36 | 491.96 | 4.7739 | 4.7301 | 5.4492 | 2.801 | 1.43 | 1.427 | 1.423 | 1.496 | 1.433 | 1.393 | Over-range | 59.99 | 1108 | 1139 | 1504 | 3751 | - - - | - - - | - - - | - - - | 1108 | 1139 | 1504 | 3751 | 779 | 690 | 84 | 1554 | - - - | - - - | - - - | - - - | 779 | 690 | 84 | 1554 | 1366 | 1342 | 1536 | 4244 | # # # | # # # | # # # | # # # | 0.811 | 0.849 | 0.979 | 0.884 | # # # | # # # | # # # | - - - | 0.818 | 0.855 | 0.999 | 0.895 | - - - | 0.414 | 1.82 | 1.65 | 1.58 | 1.62 | 1.59 | 1.63 | 11.66 | 11.95 | 19.5 | 0 | - - - | - - - | - - - | - - - | 1366 | 1342 | 1536 | 4244 | Over-range | 799 | 709 | 313 | 1986 | 177 | 162 | 301 | 1236 | 1107 | 1140 | 1503 | 3750 | 1107 | 1140 | 1503 | 3750 | - - - | - - - | - - - | - - -
5/9/2026 | 4:45:00 AM | 285.97 | 283.57 | 281.85 | 494.71 | 488.21 | 491.73 | 4.8206 | 4.816 | 5.4703 | 2.805 | 1.431 | 1.428 | 1.424 | 1.496 | 1.426 | 1.385 | Over-range | 60 | 1115 | 1168 | 1510 | 3793 | - - - | - - - | - - - | - - - | 1115 | 1168 | 1510 | 3793 | 791 | 687 | 70 | 1548 | - - - | - - - | - - - | - - - | 791 | 687 | 70 | 1548 | 1378 | 1365 | 1542 | 4285 | # # # | # # # | # # # | # # # | 0.809 | 0.855 | 0.98 | 0.885 | # # # | # # # | # # # | - - - | 0.817 | 0.861 | 0.999 | 0.896 | - - - | 0.408 | 1.8 | 1.66 | 1.6 | 1.62 | 1.59 | 1.63 | 11.49 | 11.74 | 19.42 | 0 | - - - | - - - | - - - | - - - | 1378 | 1365 | 1542 | 4285 | Over-range | 810 | 707 | 309 | 1994 | 175 | 167 | 300 | 1256 | 1118 | 1165 | 1511 | 3794 | 1118 | 1165 | 1511 | 3794 | - - - | - - - | - - - | - - -
5/9/2026 | 5:00:00 AM | 285.76 | 283.29 | 281.55 | 494.33 | 487.62 | 491.32 | 5.3845 | 5.896 | 5.764 | 2.7958 | 1.43 | 1.427 | 1.424 | 1.506 | 1.448 | 1.338 | Over-range | 59.99 | 1206 | 1513 | 1591 | 4310 | - - - | - - - | - - - | - - - | 1206 | 1513 | 1591 | 4310 | 937 | 678 | -82 | 1532 | - - - | - - - | - - - | - - - | 937 | 678 | -82 | 1532 | 1538 | 1667 | 1623 | 4828 | # # # | # # # | # # # | # # # | 0.784 | 0.907 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.79 | 0.912 | 0.998 | 0.902 | - - - | 0.356 | 1.8 | 1.69 | 1.61 | 1.63 | 1.61 | 1.65 | 10.2 | 9.95 | 18.73 | 0 | - - - | - - - | - - - | - - - | 1538 | 1667 | 1623 | 4828 | Over-range | 954 | 699 | 318 | 2176 | 180 | 170 | 303 | 1543 | 1208 | 1510 | 1593 | 4310 | 1208 | 1510 | 1593 | 4310 | - - - | - - - | - - - | - - -
5/9/2026 | 5:15:00 AM | 285.66 | 283.2 | 281.52 | 494.13 | 487.51 | 491.23 | 5.3187 | 5.7652 | 5.722 | 2.7933 | 1.43 | 1.428 | 1.424 | 1.504 | 1.446 | 1.33 | Over-range | 60 | 1195 | 1475 | 1581 | 4251 | - - - | - - - | - - - | - - - | 1195 | 1475 | 1581 | 4251 | 921 | 675 | -67 | 1529 | - - - | - - - | - - - | - - - | 921 | 675 | -67 | 1529 | 1519 | 1631 | 1611 | 4761 | # # # | # # # | # # # | # # # | 0.787 | 0.904 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.793 | 0.909 | 0.999 | 0.902 | - - - | 0.36 | 1.82 | 1.72 | 1.66 | 1.66 | 1.65 | 1.69 | 10.29 | 10.01 | 18.67 | 0 | - - - | - - - | - - - | - - - | 1519 | 1631 | 1611 | 4761 | Over-range | 937 | 696 | 309 | 2144 | 171 | 170 | 300 | 1502 | 1199 | 1474 | 1579 | 4251 | 1199 | 1474 | 1579 | 4251 | - - - | - - - | - - - | - - -
5/9/2026 | 5:30:00 AM | 285.52 | 283.15 | 281.39 | 493.99 | 487.41 | 490.94 | 4.8395 | 4.8939 | 5.4797 | 2.8025 | 1.43 | 1.428 | 1.425 | 1.493 | 1.476 | 1.39 | Over-range | 60.01 | 1115 | 1164 | 1505 | 3784 | - - - | - - - | - - - | - - - | 1115 | 1164 | 1505 | 3784 | 786 | 678 | 67 | 1532 | - - - | - - - | - - - | - - - | 786 | 678 | 67 | 1532 | 1376 | 1366 | 1541 | 4283 | # # # | # # # | # # # | # # # | 0.81 | 0.852 | 0.977 | 0.884 | # # # | # # # | # # # | - - - | 0.817 | 0.858 | 0.995 | 0.894 | - - - | 0.405 | 1.85 | 1.7 | 1.65 | 1.65 | 1.65 | 1.7 | 11.55 | 12 | 19.11 | 0 | - - - | - - - | - - - | - - - | 1376 | 1366 | 1541 | 4283 | Over-range | 805 | 698 | 326 | 2003 | 170 | 164 | 296 | 1282 | 1117 | 1164 | 1502 | 3784 | 1117 | 1164 | 1502 | 3784 | - - - | - - - | - - - | - - -
5/9/2026 | 5:45:00 AM | 285.41 | 282.94 | 281.27 | 493.71 | 487.05 | 490.81 | 4.7432 | 4.6703 | 5.4237 | 2.7965 | 1.43 | 1.427 | 1.424 | 1.494 | 1.438 | 1.395 | Over-range | 60.01 | 1103 | 1118 | 1493 | 3714 | - - - | - - - | - - - | - - - | 1103 | 1118 | 1493 | 3714 | 764 | 677 | 86 | 1527 | - - - | - - - | - - - | - - - | 764 | 677 | 86 | 1527 | 1353 | 1318 | 1525 | 4197 | # # # | # # # | # # # | # # # | 0.815 | 0.848 | 0.979 | 0.885 | # # # | # # # | # # # | - - - | 0.822 | 0.855 | 0.998 | 0.896 | - - - | 0.411 | 1.81 | 1.7 | 1.63 | 1.63 | 1.62 | 1.66 | 11.57 | 11.97 | 19.36 | 0 | - - - | - - - | - - - | - - - | 1353 | 1318 | 1525 | 4197 | Over-range | 783 | 696 | 312 | 1953 | 174 | 159 | 297 | 1216 | 1102 | 1120 | 1491 | 3713 | 1102 | 1120 | 1491 | 3713 | - - - | - - - | - - - | - - -
5/9/2026 | 6:00:00 AM | 285.34 | 282.96 | 281.24 | 493.65 | 487.12 | 490.67 | 4.7743 | 4.7206 | 5.44 | 2.7982 | 1.43 | 1.428 | 1.424 | 1.493 | 1.425 | 1.388 | Over-range | 60 | 1108 | 1140 | 1499 | 3747 | - - - | - - - | - - - | - - - | 1108 | 1140 | 1499 | 3747 | 773 | 677 | 77 | 1527 | - - - | - - - | - - - | - - - | 773 | 677 | 77 | 1527 | 1362 | 1336 | 1530 | 4228 | # # # | # # # | # # # | # # # | 0.814 | 0.854 | 0.98 | 0.886 | # # # | # # # | # # # | - - - | 0.82 | 0.86 | 0.999 | 0.897 | - - - | 0.407 | 1.81 | 1.7 | 1.63 | 1.63 | 1.62 | 1.67 | 11.46 | 11.74 | 19.29 | 0 | - - - | - - - | - - - | - - - | 1362 | 1336 | 1530 | 4228 | Over-range | 792 | 695 | 306 | 1957 | 174 | 158 | 296 | 1225 | 1108 | 1142 | 1497 | 3747 | 1108 | 1142 | 1497 | 3747 | - - - | - - - | - - - | - - -
5/9/2026 | 6:15:00 AM | 285.14 | 282.75 | 281.06 | 493.25 | 486.84 | 490.32 | 4.7943 | 4.7688 | 5.4483 | 2.7922 | 1.431 | 1.428 | 1.425 | 1.493 | 1.421 | 1.383 | Over-range | 60 | 1111 | 1157 | 1501 | 3769 | - - - | - - - | - - - | - - - | 1111 | 1157 | 1501 | 3769 | 777 | 674 | 68 | 1518 | - - - | - - - | - - - | - - - | 777 | 674 | 68 | 1518 | 1367 | 1348 | 1531 | 4247 | # # # | # # # | # # # | # # # | 0.813 | 0.858 | 0.98 | 0.887 | # # # | # # # | # # # | - - - | 0.819 | 0.864 | 0.999 | 0.898 | - - - | 0.403 | 1.8 | 1.68 | 1.62 | 1.63 | 1.61 | 1.66 | 11.37 | 11.59 | 19.2 | 0 | - - - | - - - | - - - | - - - | 1367 | 1348 | 1531 | 4247 | Over-range | 797 | 692 | 304 | 1957 | 176 | 158 | 296 | 1234 | 1110 | 1157 | 1502 | 3769 | 1110 | 1157 | 1502 | 3769 | - - - | - - - | - - - | - - -
5/9/2026 | 6:30:00 AM | 284.98 | 282.69 | 280.94 | 493.1 | 486.68 | 490.05 | 5.1412 | 5.4388 | 5.6281 | 2.7876 | 1.43 | 1.428 | 1.424 | 1.5 | 1.441 | 1.35 | Over-range | 60.01 | 1167 | 1369 | 1551 | 4087 | - - - | - - - | - - - | - - - | 1167 | 1369 | 1551 | 4087 | 866 | 669 | -25 | 1509 | - - - | - - - | - - - | - - - | 866 | 669 | -25 | 1509 | 1464 | 1534 | 1581 | 4579 | # # # | # # # | # # # | # # # | 0.797 | 0.893 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.802 | 0.898 | 0.999 | 0.902 | - - - | 0.369 | 1.79 | 1.7 | 1.61 | 1.63 | 1.61 | 1.65 | 10.55 | 10.48 | 18.89 | 0 | - - - | - - - | - - - | - - - | 1464 | 1534 | 1581 | 4579 | Over-range | 884 | 689 | 305 | 2064 | 178 | 162 | 299 | 1406 | 1166 | 1368 | 1552 | 4087 | 1166 | 1368 | 1552 | 4087 | - - - | - - - | - - - | - - -
5/9/2026 | 6:45:00 AM | 285.06 | 282.74 | 281.08 | 493.15 | 486.89 | 490.26 | 5.449 | 6.0279 | 5.8002 | 2.7894 | 1.43 | 1.427 | 1.424 | 1.503 | 1.454 | 1.342 | Over-range | 60.01 | 1216 | 1556 | 1598 | 4371 | - - - | - - - | - - - | - - - | 1216 | 1556 | 1598 | 4371 | 949 | 667 | -106 | 1509 | - - - | - - - | - - - | - - - | 949 | 667 | -106 | 1509 | 1553 | 1702 | 1630 | 4885 | # # # | # # # | # # # | # # # | 0.783 | 0.915 | 0.98 | 0.895 | # # # | # # # | # # # | - - - | 0.789 | 0.918 | 0.998 | 0.903 | - - - | 0.345 | 1.77 | 1.66 | 1.63 | 1.62 | 1.6 | 1.64 | 9.97 | 9.5 | 18.39 | 0 | - - - | - - - | - - - | - - - | 1553 | 1702 | 1630 | 4885 | Over-range | 965 | 687 | 321 | 2181 | 174 | 167 | 300 | 1573 | 1219 | 1555 | 1597 | 4371 | 1219 | 1555 | 1597 | 4371 | - - - | - - - | - - - | - - -
5/9/2026 | 7:00:00 AM | 285 | 282.72 | 281.02 | 493.04 | 486.86 | 490.17 | 4.7966 | 4.6225 | 5.4469 | 2.7949 | 1.431 | 1.428 | 1.425 | 1.487 | 1.47 | 1.408 | Over-range | 60.01 | 1119 | 1087 | 1488 | 3694 | - - - | - - - | - - - | - - - | 1119 | 1087 | 1488 | 3694 | 757 | 673 | 125 | 1555 | - - - | - - - | - - - | - - - | 757 | 673 | 125 | 1555 | 1363 | 1294 | 1530 | 4188 | # # # | # # # | # # # | # # # | 0.821 | 0.84 | 0.972 | 0.882 | # # # | # # # | # # # | - - - | 0.819 | 0.84 | 0.977 | 0.883 | - - - | 0.421 | 1.81 | 1.71 | 1.68 | 1.65 | 1.65 | 1.7 | 11.56 | 12.2 | 19.11 | 0 | - - - | - - - | - - - | - - - | 1363 | 1294 | 1530 | 4188 | Over-range | 777 | 691 | 345 | 1970 | 175 | 158 | 295 | 1197 | 1128 | 1096 | 1502 | 3726 | 1128 | 1096 | 1502 | 3726 | - - - | - - - | - - - | - - -
5/9/2026 | 7:15:00 AM | 284.63 | 282.34 | 280.63 | 492.41 | 486.15 | 489.52 | 4.7875 | 4.7697 | 5.4415 | 2.7849 | 1.43 | 1.428 | 1.425 | 1.491 | 1.441 | 1.384 | Over-range | 60 | 1108 | 1151 | 1495 | 3754 | - - - | - - - | - - - | - - - | 1108 | 1151 | 1495 | 3754 | 771 | 667 | 69 | 1507 | - - - | - - - | - - - | - - - | 771 | 667 | 69 | 1507 | 1361 | 1342 | 1527 | 4230 | # # # | # # # | # # # | # # # | 0.814 | 0.858 | 0.98 | 0.887 | # # # | # # # | # # # | - - - | 0.822 | 0.864 | 0.998 | 0.898 | - - - | 0.402 | 1.87 | 1.75 | 1.73 | 1.69 | 1.69 | 1.74 | 11.36 | 11.69 | 19.1 | 0 | - - - | - - - | - - - | - - - | 1361 | 1342 | 1527 | 4230 | Over-range | 790 | 686 | 307 | 1948 | 173 | 162 | 294 | 1232 | 1110 | 1148 | 1497 | 3755 | 1110 | 1148 | 1497 | 3755 | - - - | - - - | - - - | - - -
5/9/2026 | 7:30:00 AM | 284.31 | 282.04 | 280.3 | 491.89 | 485.57 | 488.96 | 4.7968 | 4.7704 | 5.4408 | 2.787 | 1.43 | 1.429 | 1.425 | 1.488 | 1.42 | 1.378 | Over-range | 60.01 | 1111 | 1160 | 1496 | 3767 | - - - | - - - | - - - | - - - | 1111 | 1160 | 1496 | 3767 | 772 | 662 | 61 | 1495 | - - - | - - - | - - - | - - - | 772 | 662 | 61 | 1495 | 1364 | 1345 | 1525 | 4234 | # # # | # # # | # # # | # # # | 0.814 | 0.863 | 0.981 | 0.89 | # # # | # # # | # # # | - - - | 0.822 | 0.868 | 0.999 | 0.9 | - - - | 0.397 | 1.87 | 1.77 | 1.73 | 1.7 | 1.71 | 1.76 | 11.25 | 11.4 | 18.9 | 0 | - - - | - - - | - - - | - - - | 1364 | 1345 | 1525 | 4234 | Over-range | 791 | 680 | 297 | 1933 | 172 | 159 | 290 | 1225 | 1113 | 1157 | 1498 | 3768 | 1113 | 1157 | 1498 | 3768 | - - - | - - - | - - - | - - -
5/9/2026 | 7:45:00 AM | 283.95 | 281.69 | 279.9 | 491.27 | 484.95 | 488.28 | 5.0633 | 5.2959 | 5.5766 | 2.7788 | 1.43 | 1.429 | 1.425 | 1.493 | 1.442 | 1.357 | Over-range | 60 | 1152 | 1325 | 1532 | 4010 | - - - | - - - | - - - | - - - | 1152 | 1325 | 1532 | 4010 | 841 | 653 | -13 | 1481 | - - - | - - - | - - - | - - - | 841 | 653 | -13 | 1481 | 1437 | 1488 | 1561 | 4485 | # # # | # # # | # # # | # # # | 0.802 | 0.891 | 0.982 | 0.894 | # # # | # # # | # # # | - - - | 0.809 | 0.896 | 0.999 | 0.904 | - - - | 0.369 | 1.88 | 1.81 | 1.77 | 1.73 | 1.75 | 1.8 | 10.55 | 10.57 | 18.71 | 0 | - - - | - - - | - - - | - - - | 1437 | 1488 | 1561 | 4485 | Over-range | 858 | 674 | 298 | 2010 | 169 | 163 | 293 | 1356 | 1156 | 1322 | 1532 | 4010 | 1156 | 1322 | 1532 | 4010 | - - - | - - - | - - - | - - -
5/9/2026 | 8:00:00 AM | 283.61 | 281.28 | 279.61 | 490.63 | 484.29 | 487.79 | 5.4498 | 6.0481 | 5.7888 | 2.77 | 1.43 | 1.429 | 1.426 | 1.497 | 1.468 | 1.351 | Over-range | 60.01 | 1215 | 1563 | 1587 | 4365 | - - - | - - - | - - - | - - - | 1215 | 1563 | 1587 | 4365 | 939 | 645 | -120 | 1464 | - - - | - - - | - - - | - - - | 939 | 645 | -120 | 1464 | 1545 | 1699 | 1618 | 4863 | # # # | # # # | # # # | # # # | 0.786 | 0.92 | 0.98 | 0.898 | # # # | # # # | # # # | - - - | 0.792 | 0.924 | 0.997 | 0.906 | - - - | 0.335 | 1.89 | 1.83 | 1.79 | 1.74 | 1.77 | 1.81 | 9.73 | 9.32 | 18.03 | 0 | - - - | - - - | - - - | - - - | 1545 | 1699 | 1618 | 4863 | Over-range | 955 | 666 | 319 | 2144 | 169 | 165 | 292 | 1566 | 1219 | 1560 | 1587 | 4365 | 1219 | 1560 | 1587 | 4365 | - - - | - - - | - - - | - - -
5/9/2026 | 8:15:00 AM | 283.22 | 280.97 | 279.23 | 489.97 | 483.74 | 487.12 | 4.7029 | 4.6318 | 5.3919 | 2.7785 | 1.431 | 1.431 | 1.426 | 1.486 | 1.477 | 1.395 | Over-range | 59.99 | 1092 | 1096 | 1472 | 3660 | - - - | - - - | - - - | - - - | 1092 | 1096 | 1472 | 3660 | 735 | 648 | 81 | 1465 | - - - | - - - | - - - | - - - | 735 | 648 | 81 | 1465 | 1329 | 1289 | 1505 | 4123 | # # # | # # # | # # # | # # # | 0.822 | 0.85 | 0.978 | 0.888 | # # # | # # # | # # # | - - - | 0.829 | 0.857 | 0.997 | 0.899 | - - - | 0.4 | 1.95 | 1.87 | 1.85 | 1.78 | 1.82 | 1.86 | 11.45 | 11.95 | 18.74 | 0 | - - - | - - - | - - - | - - - | 1329 | 1289 | 1505 | 4123 | Over-range | 756 | 669 | 311 | 1896 | 173 | 164 | 287 | 1201 | 1093 | 1094 | 1474 | 3661 | 1093 | 1094 | 1474 | 3661 | - - - | - - - | - - - | - - -
5/9/2026 | 8:30:00 AM | 283.03 | 280.81 | 279.14 | 489.62 | 483.59 | 486.86 | 4.755 | 4.7183 | 5.4142 | 2.772 | 1.43 | 1.431 | 1.426 | 1.488 | 1.451 | 1.389 | Over-range | 60.01 | 1102 | 1138 | 1480 | 3720 | - - - | - - - | - - - | - - - | 1102 | 1138 | 1480 | 3720 | 748 | 645 | 61 | 1454 | - - - | - - - | - - - | - - - | 748 | 645 | 61 | 1454 | 1344 | 1320 | 1511 | 4175 | # # # | # # # | # # # | # # # | 0.82 | 0.862 | 0.98 | 0.891 | # # # | # # # | # # # | - - - | 0.826 | 0.869 | 0.999 | 0.902 | - - - | 0.391 | 1.93 | 1.88 | 1.83 | 1.78 | 1.81 | 1.86 | 11.18 | 11.59 | 18.93 | 0 | - - - | - - - | - - - | - - - | 1344 | 1320 | 1511 | 4175 | Over-range | 769 | 665 | 302 | 1894 | 176 | 162 | 290 | 1212 | 1102 | 1139 | 1478 | 3719 | 1102 | 1139 | 1478 | 3719 | - - - | - - - | - - - | - - -
5/9/2026 | 8:45:00 AM | 282.56 | 280.29 | 278.56 | 488.84 | 482.54 | 485.97 | 4.7512 | 4.6964 | 5.4005 | 2.7705 | 1.431 | 1.431 | 1.426 | 1.486 | 1.428 | 1.382 | Over-range | 60 | 1102 | 1140 | 1476 | 3718 | - - - | - - - | - - - | - - - | 1102 | 1140 | 1476 | 3718 | 748 | 637 | 55 | 1440 | - - - | - - - | - - - | - - - | 748 | 637 | 55 | 1440 | 1342 | 1316 | 1504 | 4162 | # # # | # # # | # # # | # # # | 0.821 | 0.867 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.828 | 0.873 | 0.999 | 0.904 | - - - | 0.387 | 1.92 | 1.87 | 1.87 | 1.78 | 1.82 | 1.86 | 11.13 | 11.35 | 18.74 | 0 | - - - | - - - | - - - | - - - | 1342 | 1316 | 1504 | 4162 | Over-range | 766 | 656 | 291 | 1871 | 165 | 155 | 285 | 1193 | 1105 | 1139 | 1475 | 3719 | 1105 | 1139 | 1475 | 3719 | - - - | - - - | - - - | - - -
5/9/2026 | 9:00:00 AM | 282.51 | 280.2 | 278.57 | 488.66 | 482.49 | 485.98 | 5.2614 | 5.696 | 5.6797 | 2.7661 | 1.431 | 1.432 | 1.427 | 1.492 | 1.466 | 1.384 | Over-range | 60.01 | 1183 | 1450 | 1552 | 4185 | - - - | - - - | - - - | - - - | 1183 | 1450 | 1552 | 4185 | 880 | 632 | -81 | 1430 | - - - | - - - | - - - | - - - | 880 | 632 | -81 | 1430 | 1485 | 1591 | 1582 | 4658 | # # # | # # # | # # # | # # # | 0.797 | 0.912 | 0.981 | 0.899 | # # # | # # # | # # # | - - - | 0.803 | 0.915 | 0.998 | 0.907 | - - - | 0.342 | 1.95 | 1.94 | 1.86 | 1.8 | 1.84 | 1.89 | 10.09 | 9.87 | 18.27 | 0 | - - - | - - - | - - - | - - - | 1485 | 1591 | 1582 | 4658 | Over-range | 897 | 652 | 307 | 2044 | 173 | 160 | 291 | 1458 | 1185 | 1447 | 1553 | 4185 | 1185 | 1447 | 1553 | 4185 | - - - | - - - | - - - | - - -
5/9/2026 | 9:15:00 AM | 283 | 280.89 | 279.17 | 489.66 | 483.73 | 486.83 | 5.6069 | 6.3631 | 5.8923 | 2.7789 | 1.432 | 1.432 | 1.427 | 1.494 | 1.476 | 1.412 | Over-range | 60.01 | 1239 | 1658 | 1609 | 4506 | - - - | - - - | - - - | - - - | 1239 | 1658 | 1609 | 4506 | 975 | 638 | -167 | 1445 | - - - | - - - | - - - | - - - | 975 | 638 | -167 | 1445 | 1586 | 1785 | 1645 | 5016 | # # # | # # # | # # # | # # # | 0.781 | 0.929 | 0.978 | 0.898 | # # # | # # # | # # # | - - - | 0.787 | 0.933 | 0.994 | 0.906 | - - - | 0.321 | 1.95 | 1.89 | 1.87 | 1.8 | 1.83 | 1.88 | 9.56 | 9 | 17.9 | 0 | - - - | - - - | - - - | - - - | 1586 | 1785 | 1645 | 5016 | Over-range | 990 | 659 | 342 | 2203 | 172 | 167 | 295 | 1662 | 1243 | 1655 | 1608 | 4506 | 1243 | 1655 | 1608 | 4506 | - - - | - - - | - - - | - - -
5/9/2026 | 9:30:00 AM | 282.77 | 280.49 | 278.89 | 489.09 | 483.03 | 486.51 | 5.4597 | 5.888 | 5.7716 | 2.7709 | 1.432 | 1.432 | 1.427 | 1.489 | 1.468 | 1.402 | Over-range | 60.01 | 1227 | 1516 | 1578 | 4321 | - - - | - - - | - - - | - - - | 1227 | 1516 | 1578 | 4321 | 915 | 635 | -85 | 1464 | - - - | - - - | - - - | - - - | 915 | 635 | -85 | 1464 | 1541 | 1651 | 1610 | 4802 | # # # | # # # | # # # | # # # | 0.796 | 0.918 | 0.98 | 0.9 | # # # | # # # | # # # | - - - | 0.793 | 0.915 | 0.986 | 0.9 | - - - | 0.339 | 1.94 | 1.87 | 1.85 | 1.78 | 1.82 | 1.86 | 9.95 | 9.57 | 18.16 | 0 | - - - | - - - | - - - | - - - | 1541 | 1651 | 1610 | 4802 | Over-range | 933 | 655 | 318 | 2096 | 176 | 158 | 293 | 1492 | 1237 | 1536 | 1605 | 4378 | 1237 | 1536 | 1605 | 4378 | - - - | - - - | - - - | - - -
5/9/2026 | 9:45:00 AM | 282.46 | 280.1 | 278.49 | 488.53 | 482.32 | 485.88 | 4.6852 | 4.6595 | 5.4109 | 2.7691 | 1.433 | 1.434 | 1.428 | 1.486 | 1.483 | 1.414 | Over-range | 60.01 | 1092 | 1104 | 1473 | 3669 | - - - | - - - | - - - | - - - | 1092 | 1104 | 1473 | 3669 | 717 | 636 | 60 | 1413 | - - - | - - - | - - - | - - - | 717 | 636 | 60 | 1413 | 1319 | 1290 | 1506 | 4114 | # # # | # # # | # # # | # # # | 0.828 | 0.856 | 0.978 | 0.892 | # # # | # # # | # # # | - - - | 0.836 | 0.863 | 0.997 | 0.903 | - - - | 0.385 | 1.94 | 1.86 | 1.87 | 1.78 | 1.82 | 1.87 | 11.78 | 11.84 | 18.8 | 0 | - - - | - - - | - - - | - - - | 1319 | 1290 | 1506 | 4114 | Over-range | 738 | 654 | 311 | 1860 | 173 | 153 | 288 | 1205 | 1092 | 1105 | 1471 | 3668 | 1092 | 1105 | 1471 | 3668 | - - - | - - - | - - - | - - -
5/9/2026 | 10:00:00 AM | 282.28 | 280.12 | 278.48 | 488.3 | 482.49 | 485.64 | 4.7204 | 4.7432 | 5.4288 | 2.7803 | 1.434 | 1.433 | 1.429 | 1.486 | 1.44 | 1.399 | Over-range | 60.01 | 1093 | 1149 | 1482 | 3724 | - - - | - - - | - - - | - - - | 1093 | 1149 | 1482 | 3724 | 740 | 635 | 35 | 1410 | - - - | - - - | - - - | - - - | 740 | 635 | 35 | 1410 | 1331 | 1323 | 1511 | 4166 | # # # | # # # | # # # | # # # | 0.821 | 0.868 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.828 | 0.874 | 0.999 | 0.904 | - - - | 0.379 | 1.92 | 1.85 | 1.83 | 1.77 | 1.79 | 1.85 | 11.34 | 11.44 | 18.85 | 0 | - - - | - - - | - - - | - - - | 1331 | 1323 | 1511 | 4166 | Over-range | 759 | 654 | 297 | 1867 | 167 | 157 | 289 | 1222 | 1096 | 1147 | 1481 | 3724 | 1096 | 1147 | 1481 | 3724 | - - - | - - - | - - - | - - -
5/9/2026 | 10:15:00 AM | 282.15 | 279.93 | 278.34 | 488.1 | 482.12 | 485.42 | 4.7724 | 4.8345 | 5.4485 | 2.7711 | 1.433 | 1.433 | 1.428 | 1.486 | 1.433 | 1.392 | Over-range | 60.01 | 1103 | 1186 | 1489 | 3778 | - - - | - - - | - - - | - - - | 1103 | 1186 | 1489 | 3778 | 754 | 633 | 18 | 1404 | - - - | - - - | - - - | - - - | 754 | 633 | 18 | 1404 | 1346 | 1353 | 1517 | 4216 | # # # | # # # | # # # | # # # | 0.819 | 0.876 | 0.982 | 0.896 | # # # | # # # | # # # | - - - | 0.825 | 0.882 | 1 | 0.906 | - - - | 0.372 | 1.93 | 1.85 | 1.81 | 1.76 | 1.79 | 1.85 | 11.16 | 11.03 | 18.75 | 0 | - - - | - - - | - - - | - - - | 1346 | 1353 | 1517 | 4216 | Over-range | 773 | 651 | 289 | 1872 | 170 | 152 | 288 | 1238 | 1102 | 1186 | 1488 | 3777 | 1102 | 1186 | 1488 | 3777 | - - - | - - - | - - - | - - -
5/9/2026 | 10:30:00 AM | 281.98 | 279.74 | 278.13 | 487.79 | 481.75 | 485.12 | 5.1354 | 5.5572 | 5.6313 | 2.7565 | 1.433 | 1.434 | 1.428 | 1.489 | 1.462 | 1.403 | Over-range | 60 | 1160 | 1407 | 1535 | 4101 | - - - | - - - | - - - | - - - | 1160 | 1407 | 1535 | 4101 | 847 | 627 | -80 | 1393 | - - - | - - - | - - - | - - - | 847 | 627 | -80 | 1393 | 1447 | 1549 | 1566 | 4561 | # # # | # # # | # # # | # # # | 0.802 | 0.908 | 0.98 | 0.899 | # # # | # # # | # # # | - - - | 0.807 | 0.912 | 0.997 | 0.908 | - - - | 0.34 | 1.89 | 1.85 | 1.82 | 1.75 | 1.78 | 1.84 | 10.35 | 9.95 | 18.51 | 0 | - - - | - - - | - - - | - - - | 1447 | 1549 | 1566 | 4561 | Over-range | 865 | 646 | 309 | 1997 | 175 | 156 | 292 | 1428 | 1159 | 1405 | 1536 | 4101 | 1159 | 1405 | 1536 | 4101 | - - - | - - - | - - - | - - -
5/9/2026 | 10:45:00 AM | 281.73 | 279.44 | 277.86 | 487.28 | 481.27 | 484.68 | 5.422 | 6.1175 | 5.8157 | 2.7639 | 1.433 | 1.433 | 1.428 | 1.492 | 1.475 | 1.423 | Over-range | 60.02 | 1206 | 1583 | 1581 | 4370 | - - - | - - - | - - - | - - - | 1206 | 1583 | 1581 | 4370 | 920 | 619 | -161 | 1377 | - - - | - - - | - - - | - - - | 920 | 619 | -161 | 1377 | 1527 | 1707 | 1616 | 4850 | # # # | # # # | # # # | # # # | 0.79 | 0.927 | 0.979 | 0.901 | # # # | # # # | # # # | - - - | 0.795 | 0.931 | 0.995 | 0.909 | - - - | 0.315 | 1.9 | 1.86 | 1.8 | 1.75 | 1.78 | 1.83 | 9.74 | 9.01 | 17.77 | 0 | - - - | - - - | - - - | - - - | 1527 | 1707 | 1616 | 4850 | Over-range | 936 | 638 | 333 | 2104 | 172 | 157 | 289 | 1589 | 1207 | 1582 | 1581 | 4370 | 1207 | 1582 | 1581 | 4370 | - - - | - - - | - - - | - - -
5/9/2026 | 11:00:00 AM | 281.71 | 279.4 | 277.8 | 487.28 | 481.1 | 484.65 | 5.2065 | 5.6881 | 5.671 | 2.7543 | 1.433 | 1.433 | 1.428 | 1.49 | 1.468 | 1.411 | Over-range | 60.01 | 1172 | 1454 | 1545 | 4171 | - - - | - - - | - - - | - - - | 1172 | 1454 | 1545 | 4171 | 865 | 620 | -103 | 1382 | - - - | - - - | - - - | - - - | 865 | 620 | -103 | 1382 | 1467 | 1589 | 1575 | 4631 | # # # | # # # | # # # | # # # | 0.799 | 0.915 | 0.981 | 0.901 | # # # | # # # | # # # | - - - | 0.805 | 0.92 | 0.997 | 0.91 | - - - | 0.331 | 1.89 | 1.84 | 1.81 | 1.74 | 1.78 | 1.82 | 10.15 | 9.54 | 18.23 | 0 | - - - | - - - | - - - | - - - | 1467 | 1589 | 1575 | 4631 | Over-range | 882 | 640 | 308 | 2012 | 168 | 158 | 290 | 1462 | 1175 | 1452 | 1544 | 4171 | 1175 | 1452 | 1544 | 4171 | - - - | - - - | - - - | - - -
5/9/2026 | 11:15:00 AM | 281.57 | 279.27 | 277.72 | 487.04 | 480.92 | 484.46 | 4.5232 | 4.3977 | 5.3169 | 2.7671 | 1.434 | 1.434 | 1.429 | 1.485 | 1.482 | 1.42 | Over-range | 60.01 | 1059 | 1021 | 1442 | 3522 | - - - | - - - | - - - | - - - | 1059 | 1021 | 1442 | 3522 | 678 | 626 | 84 | 1389 | - - - | - - - | - - - | - - - | 678 | 626 | 84 | 1389 | 1270 | 1213 | 1476 | 3958 | # # # | # # # | # # # | # # # | 0.834 | 0.842 | 0.977 | 0.89 | # # # | # # # | # # # | - - - | 0.841 | 0.849 | 0.996 | 0.901 | - - - | 0.394 | 1.89 | 1.85 | 1.82 | 1.75 | 1.78 | 1.84 | 11.9 | 12.25 | 18.84 | 0 | - - - | - - - | - - - | - - - | 1270 | 1213 | 1476 | 3958 | Over-range | 699 | 644 | 311 | 1804 | 165 | 152 | 283 | 1145 | 1060 | 1021 | 1440 | 3522 | 1060 | 1021 | 1440 | 3522 | - - - | - - - | - - - | - - -
5/9/2026 | 11:30:00 AM | 281.49 | 279.28 | 277.64 | 486.95 | 480.95 | 484.26 | 4.7721 | 4.5216 | 5.4446 | 3.3959 | 1.434 | 1.434 | 1.429 | 1.487 | 1.45 | 1.399 | Over-range | 60.02 | 1102 | 1022 | 1484 | 3608 | - - - | - - - | - - - | - - - | 1102 | 1022 | 1484 | 3608 | 748 | 671 | 11 | 1430 | - - - | - - - | - - - | - - - | 748 | 671 | 11 | 1430 | 1343 | 1250 | 1511 | 4104 | # # # | # # # | # # # | # # # | 0.821 | 0.817 | 0.982 | 0.879 | # # # | # # # | # # # | - - - | 0.828 | 0.825 | 1 | 0.89 | - - - | 0.397 | 1.9 | 1.85 | 1.82 | 1.75 | 1.78 | 1.84 | 11.09 | 13.02 | 18.66 | 0 | - - - | - - - | - - - | - - - | 1343 | 1250 | 1511 | 4104 | Over-range | 766 | 691 | 289 | 1945 | 166 | 162 | 286 | 1318 | 1104 | 1022 | 1482 | 3607 | 1104 | 1022 | 1482 | 3607 | - - - | - - - | - - - | - - -
5/9/2026 | 11:45:00 AM | 281.29 | 279 | 277.44 | 486.58 | 480.44 | 483.97 | 4.813 | 3.9644 | 5.4415 | 4.162 | 1.434 | 1.435 | 1.43 | 1.487 | 1.435 | 1.4 | Over-range | 60.01 | 1109 | 797 | 1482 | 3388 | - - - | - - - | - - - | - - - | 1109 | 797 | 1482 | 3388 | 757 | 744 | -2 | 1498 | - - - | - - - | - - - | - - - | 757 | 744 | -2 | 1498 | 1354 | 1105 | 1510 | 3969 | # # # | # # # | # # # | # # # | 0.819 | 0.721 | 0.982 | 0.854 | # # # | # # # | # # # | - - - | 0.826 | 0.731 | 0.999 | 0.865 | - - - | 0.442 | 1.91 | 1.86 | 1.82 | 1.76 | 1.79 | 1.84 | 11.01 | 15.96 | 18.76 | 0 | - - - | - - - | - - - | - - - | 1354 | 1105 | 1510 | 3969 | Over-range | 776 | 765 | 288 | 2066 | 171 | 178 | 287 | 1423 | 1108 | 797 | 1482 | 3388 | 1108 | 797 | 1482 | 3388 | - - - | - - - | - - - | - - -
5/9/2026 | 12:00:00 PM | 281.09 | 278.87 | 277.3 | 486.26 | 480.23 | 483.67 | 5.5303 | 5.0285 | 5.832 | 4.1645 | 1.434 | 1.434 | 1.429 | 1.49 | 1.435 | 1.43 | Over-range | 60.02 | 1232 | 1173 | 1581 | 3985 | - - - | - - - | - - - | - - - | 1232 | 1173 | 1581 | 3985 | 926 | 735 | -142 | 1518 | - - - | - - - | - - - | - - - | 926 | 735 | -142 | 1518 | 1552 | 1399 | 1617 | 4567 | # # # | # # # | # # # | # # # | 0.794 | 0.839 | 0.978 | 0.873 | # # # | # # # | # # # | - - - | 0.791 | 0.84 | 0.983 | 0.874 | - - - | 0.381 | 1.88 | 1.86 | 1.84 | 1.75 | 1.79 | 1.84 | 9.63 | 13.38 | 17.82 | 0 | - - - | - - - | - - - | - - - | 1552 | 1399 | 1617 | 4567 | Over-range | 943 | 759 | 339 | 2230 | 173 | 187 | 290 | 1626 | 1242 | 1189 | 1605 | 4037 | 1242 | 1189 | 1605 | 4037 | - - - | - - - | - - - | - - -
5/9/2026 | 12:15:00 PM | 281.19 | 278.9 | 277.36 | 486.35 | 480.31 | 483.84 | 5.6064 | 5.3319 | 5.9224 | 4.1679 | 1.435 | 1.435 | 1.43 | 1.492 | 1.446 | 1.45 | Over-range | 60.01 | 1235 | 1278 | 1602 | 4116 | - - - | - - - | - - - | - - - | 1235 | 1278 | 1602 | 4116 | 965 | 733 | -214 | 1483 | - - - | - - - | - - - | - - - | 965 | 733 | -214 | 1483 | 1576 | 1486 | 1643 | 4705 | # # # | # # # | # # # | # # # | 0.784 | 0.86 | 0.976 | 0.875 | # # # | # # # | # # # | - - - | 0.789 | 0.867 | 0.991 | 0.884 | - - - | 0.36 | 1.89 | 1.85 | 1.8 | 1.74 | 1.77 | 1.82 | 9.43 | 12.51 | 17.47 | 0 | - - - | - - - | - - - | - - - | 1576 | 1486 | 1643 | 4705 | Over-range | 980 | 758 | 361 | 2281 | 168 | 192 | 289 | 1732 | 1239 | 1276 | 1601 | 4116 | 1239 | 1276 | 1601 | 4116 | - - - | - - - | - - - | - - -
5/9/2026 | 12:30:00 PM | 281.27 | 278.95 | 277.37 | 486.54 | 480.27 | 483.93 | 5.102 | 4.448 | 5.6026 | 4.1645 | 1.434 | 1.434 | 1.429 | 1.488 | 1.426 | 1.421 | Over-range | 60 | 1155 | 970 | 1524 | 3649 | - - - | - - - | - - - | - - - | 1155 | 970 | 1524 | 3649 | 833 | 740 | -79 | 1493 | - - - | - - - | - - - | - - - | 833 | 740 | -79 | 1493 | 1434 | 1236 | 1554 | 4224 | # # # | # # # | # # # | # # # | 0.805 | 0.785 | 0.981 | 0.864 | # # # | # # # | # # # | - - - | 0.811 | 0.793 | 0.998 | 0.874 | - - - | 0.409 | 1.86 | 1.85 | 1.8 | 1.73 | 1.77 | 1.81 | 10.41 | 14.42 | 18.3 | 0 | - - - | - - - | - - - | - - - | 1434 | 1236 | 1554 | 4224 | Over-range | 850 | 762 | 303 | 2127 | 166 | 180 | 287 | 1513 | 1156 | 971 | 1521 | 3648 | 1156 | 971 | 1521 | 3648 | - - - | - - - | - - - | - - -
5/9/2026 | 12:45:00 PM | 281.2 | 278.94 | 277.36 | 486.44 | 480.29 | 483.85 | 4.9163 | 4.1252 | 5.513 | 4.1709 | 1.435 | 1.434 | 1.43 | 1.487 | 1.428 | 1.41 | Over-range | 60 | 1126 | 861 | 1502 | 3489 | - - - | - - - | - - - | - - - | 1126 | 861 | 1502 | 3489 | 785 | 742 | -31 | 1496 | - - - | - - - | - - - | - - - | 785 | 742 | -31 | 1496 | 1382 | 1151 | 1529 | 4062 | # # # | # # # | # # # | # # # | 0.814 | 0.748 | 0.982 | 0.859 | # # # | # # # | # # # | - - - | 0.821 | 0.757 | 1 | 0.87 | - - - | 0.429 | 1.88 | 1.82 | 1.8 | 1.73 | 1.76 | 1.81 | 10.77 | 15.26 | 18.45 | 0 | - - - | - - - | - - - | - - - | 1382 | 1151 | 1529 | 4062 | Over-range | 803 | 763 | 287 | 2081 | 166 | 178 | 285 | 1447 | 1127 | 862 | 1499 | 3488 | 1127 | 862 | 1499 | 3488 | - - - | - - - | - - - | - - -
5/9/2026 | 1:00:00 PM | 281.23 | 278.93 | 277.35 | 486.42 | 480.31 | 483.87 | 5.4394 | 4.9529 | 5.7821 | 4.1703 | 1.435 | 1.435 | 1.43 | 1.491 | 1.427 | 1.444 | Over-range | 60.01 | 1212 | 1147 | 1570 | 3928 | - - - | - - - | - - - | - - - | 1212 | 1147 | 1570 | 3928 | 915 | 736 | -144 | 1506 | - - - | - - - | - - - | - - - | 915 | 736 | -144 | 1506 | 1529 | 1378 | 1603 | 4510 | # # # | # # # | # # # | # # # | 0.793 | 0.833 | 0.979 | 0.871 | # # # | # # # | # # # | - - - | 0.798 | 0.84 | 0.996 | 0.881 | - - - | 0.383 | 1.86 | 1.83 | 1.77 | 1.71 | 1.74 | 1.79 | 9.79 | 13.39 | 17.79 | 0 | - - - | - - - | - - - | - - - | 1529 | 1378 | 1603 | 4510 | Over-range | 932 | 760 | 325 | 2214 | 177 | 187 | 287 | 1622 | 1212 | 1145 | 1572 | 3929 | 1212 | 1145 | 1572 | 3929 | - - - | - - - | - - - | - - -
5/9/2026 | 1:15:00 PM | 281.46 | 279.17 | 277.59 | 486.89 | 480.66 | 484.27 | 5.3226 | 4.7438 | 5.696 | 4.1627 | 1.435 | 1.434 | 1.43 | 1.49 | 1.42 | 1.434 | Over-range | 60 | 1194 | 1077 | 1550 | 3821 | - - - | - - - | - - - | - - - | 1194 | 1077 | 1550 | 3821 | 887 | 742 | -111 | 1517 | - - - | - - - | - - - | - - - | 887 | 742 | -111 | 1517 | 1497 | 1322 | 1581 | 4401 | # # # | # # # | # # # | # # # | 0.797 | 0.815 | 0.98 | 0.868 | # # # | # # # | # # # | - - - | 0.803 | 0.822 | 0.997 | 0.878 | - - - | 0.397 | 1.83 | 1.77 | 1.74 | 1.69 | 1.72 | 1.76 | 10.05 | 13.79 | 18.14 | 0 | - - - | - - - | - - - | - - - | 1497 | 1322 | 1581 | 4401 | Over-range | 904 | 765 | 312 | 2183 | 174 | 186 | 289 | 1570 | 1195 | 1075 | 1551 | 3821 | 1195 | 1075 | 1551 | 3821 | - - - | - - - | - - - | - - -
5/9/2026 | 1:30:00 PM | 281.42 | 279.02 | 277.5 | 486.72 | 480.42 | 484.2 | 4.5181 | 3.4911 | 5.2794 | 4.175 | 1.435 | 1.433 | 1.43 | 1.487 | 1.5 | 1.427 | Over-range | 60.01 | 1063 | 577 | 1431 | 3071 | - - - | - - - | - - - | - - - | 1063 | 577 | 1431 | 3071 | 672 | 745 | 107 | 1524 | - - - | - - - | - - - | - - - | 672 | 745 | 107 | 1524 | 1269 | 969 | 1465 | 3703 | # # # | # # # | # # # | # # # | 0.837 | 0.596 | 0.977 | 0.83 | # # # | # # # | # # # | - - - | 0.845 | 0.606 | 0.996 | 0.842 | - - - | 0.496 | 1.81 | 1.77 | 1.75 | 1.68 | 1.71 | 1.75 | 11.95 | 17.61 | 18.9 | 0 | - - - | - - - | - - - | - - - | 1269 | 969 | 1465 | 3703 | Over-range | 693 | 766 | 310 | 2063 | 167 | 177 | 282 | 1390 | 1065 | 576 | 1432 | 3072 | 1065 | 576 | 1432 | 3072 | - - - | - - - | - - - | - - -
5/9/2026 | 1:45:00 PM | 281.48 | 279.24 | 277.65 | 486.91 | 480.88 | 484.31 | 4.926 | 4.0786 | 5.4926 | 4.1711 | 1.434 | 1.432 | 1.429 | 1.489 | 1.433 | 1.413 | Over-range | 60.01 | 1130 | 837 | 1497 | 3464 | - - - | - - - | - - - | - - - | 1130 | 837 | 1497 | 3464 | 784 | 745 | -4 | 1524 | - - - | - - - | - - - | - - - | 784 | 745 | -4 | 1524 | 1386 | 1137 | 1525 | 4048 | # # # | # # # | # # # | # # # | 0.815 | 0.736 | 0.982 | 0.856 | # # # | # # # | # # # | - - - | 0.822 | 0.745 | 1 | 0.867 | - - - | 0.44 | 1.8 | 1.76 | 1.73 | 1.68 | 1.7 | 1.74 | 10.83 | 15.72 | 18.63 | 0 | - - - | - - - | - - - | - - - | 1386 | 1137 | 1525 | 4048 | Over-range | 802 | 767 | 290 | 2093 | 168 | 184 | 288 | 1435 | 1133 | 835 | 1497 | 3465 | 1133 | 835 | 1497 | 3465 | - - - | - - - | - - - | - - -
5/9/2026 | 2:00:00 PM | 281.57 | 279.26 | 277.77 | 487.01 | 480.94 | 484.54 | 4.9839 | 4.1691 | 5.522 | 4.1704 | 1.434 | 1.432 | 1.429 | 1.491 | 1.43 | 1.41 | Over-range | 60.01 | 1140 | 874 | 1506 | 3520 | - - - | - - - | - - - | - - - | 1140 | 874 | 1506 | 3520 | 800 | 745 | -21 | 1523 | - - - | - - - | - - - | - - - | 800 | 745 | -21 | 1523 | 1403 | 1164 | 1534 | 4101 | # # # | # # # | # # # | # # # | 0.812 | 0.751 | 0.982 | 0.859 | # # # | # # # | # # # | - - - | 0.819 | 0.76 | 0.999 | 0.87 | - - - | 0.433 | 1.76 | 1.71 | 1.65 | 1.63 | 1.64 | 1.68 | 10.65 | 15.4 | 18.5 | 0 | - - - | - - - | - - - | - - - | 1403 | 1164 | 1534 | 4101 | Over-range | 818 | 768 | 289 | 2103 | 169 | 186 | 288 | 1450 | 1143 | 872 | 1507 | 3521 | 1143 | 872 | 1507 | 3521 | - - - | - - - | - - - | - - -
5/9/2026 | 2:15:00 PM | 281.48 | 279.2 | 277.68 | 486.88 | 480.81 | 484.37 | 5.5348 | 4.9788 | 5.8077 | 4.1659 | 1.434 | 1.432 | 1.429 | 1.494 | 1.432 | 1.446 | Over-range | 60.01 | 1236 | 1152 | 1576 | 3964 | - - - | - - - | - - - | - - - | 1236 | 1152 | 1576 | 3964 | 927 | 740 | -120 | 1546 | - - - | - - - | - - - | - - - | 927 | 740 | -120 | 1546 | 1556 | 1385 | 1612 | 4553 | # # # | # # # | # # # | # # # | 0.795 | 0.832 | 0.978 | 0.871 | # # # | # # # | # # # | - - - | 0.793 | 0.833 | 0.983 | 0.873 | - - - | 0.39 | 1.79 | 1.69 | 1.64 | 1.62 | 1.63 | 1.66 | 9.65 | 13.53 | 17.87 | 0 | - - - | - - - | - - - | - - - | 1556 | 1385 | 1612 | 4553 | Over-range | 944 | 764 | 337 | 2239 | 177 | 191 | 291 | 1609 | 1248 | 1155 | 1605 | 4008 | 1248 | 1155 | 1605 | 4008 | - - - | - - - | - - - | - - -
5/9/2026 | 2:30:00 PM | 281.24 | 279 | 277.5 | 486.43 | 480.54 | 484.01 | 5.3938 | 4.8824 | 5.761 | 4.1674 | 1.435 | 1.433 | 1.43 | 1.494 | 1.424 | 1.447 | Over-range | 60 | 1204 | 1124 | 1566 | 3895 | - - - | - - - | - - - | - - - | 1204 | 1124 | 1566 | 3895 | 904 | 739 | -134 | 1508 | - - - | - - - | - - - | - - - | 904 | 739 | -134 | 1508 | 1516 | 1360 | 1598 | 4474 | # # # | # # # | # # # | # # # | 0.794 | 0.827 | 0.98 | 0.87 | # # # | # # # | # # # | - - - | 0.8 | 0.835 | 0.996 | 0.88 | - - - | 0.387 | 1.77 | 1.69 | 1.65 | 1.63 | 1.63 | 1.67 | 9.88 | 13.49 | 17.88 | 0 | - - - | - - - | - - - | - - - | 1516 | 1360 | 1598 | 4474 | Over-range | 921 | 762 | 321 | 2202 | 175 | 187 | 289 | 1604 | 1205 | 1123 | 1567 | 3895 | 1205 | 1123 | 1567 | 3895 | - - - | - - - | - - - | - - -
5/9/2026 | 2:45:00 PM | 281.04 | 278.7 | 277.23 | 486.06 | 480.01 | 483.62 | 5.214 | 4.5579 | 5.6479 | 4.1685 | 1.435 | 1.433 | 1.43 | 1.492 | 1.418 | 1.432 | Over-range | 60.01 | 1176 | 1017 | 1536 | 3729 | - - - | - - - | - - - | - - - | 1176 | 1017 | 1536 | 3729 | 856 | 736 | -90 | 1501 | - - - | - - - | - - - | - - - | 856 | 736 | -90 | 1501 | 1465 | 1269 | 1566 | 4300 | # # # | # # # | # # # | # # # | 0.803 | 0.801 | 0.981 | 0.867 | # # # | # # # | # # # | - - - | 0.808 | 0.81 | 0.998 | 0.877 | - - - | 0.403 | 1.75 | 1.72 | 1.64 | 1.62 | 1.63 | 1.67 | 10.17 | 14.23 | 18.11 | 0 | - - - | - - - | - - - | - - - | 1465 | 1269 | 1566 | 4300 | Over-range | 873 | 758 | 302 | 2140 | 172 | 183 | 286 | 1525 | 1176 | 1017 | 1536 | 3729 | 1176 | 1017 | 1536 | 3729 | - - - | - - - | - - - | - - -
5/9/2026 | 3:00:00 PM | 280.92 | 278.65 | 277.18 | 485.88 | 479.92 | 483.48 | 4.6903 | 3.7913 | 5.3733 | 4.1703 | 1.436 | 1.434 | 1.431 | 1.491 | 1.48 | 1.437 | Over-range | 60 | 1088 | 681 | 1455 | 3224 | - - - | - - - | - - - | - - - | 1088 | 681 | 1455 | 3224 | 710 | 740 | 57 | 1507 | - - - | - - - | - - - | - - - | 710 | 740 | 57 | 1507 | 1312 | 1041 | 1488 | 3840 | # # # | # # # | # # # | # # # | 0.829 | 0.654 | 0.978 | 0.839 | # # # | # # # | # # # | - - - | 0.836 | 0.664 | 0.996 | 0.851 | - - - | 0.467 | 1.76 | 1.7 | 1.64 | 1.62 | 1.63 | 1.67 | 11.53 | 16.92 | 18.7 | 0 | - - - | - - - | - - - | - - - | 1312 | 1041 | 1488 | 3840 | Over-range | 731 | 761 | 312 | 2079 | 171 | 177 | 283 | 1431 | 1087 | 681 | 1455 | 3223 | 1087 | 681 | 1455 | 3223 | - - - | - - - | - - - | - - -
5/9/2026 | 3:15:00 PM | 280.81 | 278.58 | 277.14 | 485.7 | 479.88 | 483.33 | 4.8653 | 3.985 | 5.4569 | 4.1729 | 1.436 | 1.434 | 1.431 | 1.492 | 1.438 | 1.419 | Over-range | 60 | 1119 | 801 | 1484 | 3405 | - - - | - - - | - - - | - - - | 1119 | 801 | 1484 | 3405 | 763 | 738 | 4 | 1505 | - - - | - - - | - - - | - - - | 763 | 738 | 4 | 1505 | 1365 | 1107 | 1512 | 3984 | # # # | # # # | # # # | # # # | 0.82 | 0.724 | 0.981 | 0.855 | # # # | # # # | # # # | - - - | 0.826 | 0.734 | 0.999 | 0.866 | - - - | 0.442 | 1.73 | 1.69 | 1.67 | 1.62 | 1.62 | 1.66 | 10.9 | 15.97 | 18.63 | 0 | - - - | - - - | - - - | - - - | 1365 | 1107 | 1512 | 3984 | Over-range | 781 | 760 | 290 | 2069 | 166 | 181 | 286 | 1419 | 1121 | 801 | 1482 | 3405 | 1121 | 801 | 1482 | 3405 | - - - | - - - | - - - | - - -
5/9/2026 | 3:30:00 PM | 280.62 | 278.33 | 276.78 | 485.36 | 479.31 | 482.85 | 4.9286 | 4.0696 | 5.4864 | 4.1725 | 1.436 | 1.434 | 1.431 | 1.491 | 1.429 | 1.42 | Over-range | 60.01 | 1130 | 844 | 1492 | 3466 | - - - | - - - | - - - | - - - | 1130 | 844 | 1492 | 3466 | 779 | 734 | -17 | 1495 | - - - | - - - | - - - | - - - | 779 | 734 | -17 | 1495 | 1383 | 1132 | 1518 | 4034 | # # # | # # # | # # # | # # # | 0.817 | 0.745 | 0.982 | 0.859 | # # # | # # # | # # # | - - - | 0.824 | 0.754 | 1 | 0.87 | - - - | 0.431 | 1.76 | 1.69 | 1.63 | 1.61 | 1.62 | 1.66 | 10.68 | 15.43 | 18.42 | 0 | - - - | - - - | - - - | - - - | 1383 | 1132 | 1518 | 4034 | Over-range | 797 | 755 | 285 | 2064 | 165 | 177 | 284 | 1423 | 1132 | 845 | 1488 | 3465 | 1132 | 845 | 1488 | 3465 | - - - | - - - | - - - | - - -
5/9/2026 | 3:45:00 PM | 280.68 | 278.31 | 276.85 | 485.41 | 479.29 | 483.01 | 5.434 | 4.9548 | 5.7787 | 4.164 | 1.436 | 1.434 | 1.431 | 1.495 | 1.428 | 1.451 | Over-range | 60 | 1210 | 1149 | 1565 | 3925 | - - - | - - - | - - - | - - - | 1210 | 1149 | 1565 | 3925 | 911 | 731 | -151 | 1489 | - - - | - - - | - - - | - - - | 911 | 731 | -151 | 1489 | 1524 | 1376 | 1600 | 4500 | # # # | # # # | # # # | # # # | 0.794 | 0.835 | 0.979 | 0.872 | # # # | # # # | # # # | - - - | 0.799 | 0.843 | 0.995 | 0.881 | - - - | 0.379 | 1.74 | 1.7 | 1.63 | 1.6 | 1.62 | 1.65 | 9.74 | 13.36 | 17.82 | 0 | - - - | - - - | - - - | - - - | 1524 | 1376 | 1600 | 4500 | Over-range | 927 | 754 | 328 | 2200 | 171 | 184 | 287 | 1619 | 1210 | 1151 | 1562 | 3924 | 1210 | 1151 | 1562 | 3924 | - - - | - - - | - - - | - - -
5/9/2026 | 4:00:00 PM | 280.65 | 278.33 | 276.79 | 485.44 | 479.23 | 482.92 | 5.3657 | 4.6811 | 5.702 | 4.1672 | 1.436 | 1.434 | 1.431 | 1.49 | 1.423 | 1.446 | Over-range | 60.01 | 1207 | 1057 | 1546 | 3810 | - - - | - - - | - - - | - - - | 1207 | 1057 | 1546 | 3810 | 879 | 731 | -89 | 1521 | - - - | - - - | - - - | - - - | 879 | 731 | -89 | 1521 | 1504 | 1299 | 1578 | 4381 | # # # | # # # | # # # | # # # | 0.803 | 0.813 | 0.98 | 0.87 | # # # | # # # | # # # | - - - | 0.801 | 0.815 | 0.985 | 0.871 | - - - | 0.399 | 1.72 | 1.7 | 1.61 | 1.6 | 1.61 | 1.64 | 9.86 | 13.77 | 17.95 | 0 | - - - | - - - | - - - | - - - | 1504 | 1299 | 1578 | 4381 | Over-range | 896 | 753 | 317 | 2163 | 167 | 181 | 286 | 1530 | 1219 | 1065 | 1555 | 3839 | 1219 | 1065 | 1555 | 3839 | - - - | - - - | - - - | - - -
5/9/2026 | 4:15:00 PM | 280.59 | 278.28 | 276.76 | 485.29 | 479.26 | 482.79 | 4.5243 | 3.4881 | 5.2797 | 4.1805 | 1.436 | 1.434 | 1.431 | 1.489 | 1.486 | 1.43 | Over-range | 60.01 | 1064 | 586 | 1429 | 3079 | - - - | - - - | - - - | - - - | 1064 | 586 | 1429 | 3079 | 668 | 736 | 94 | 1498 | - - - | - - - | - - - | - - - | 668 | 736 | 94 | 1498 | 1267 | 966 | 1461 | 3694 | # # # | # # # | # # # | # # # | 0.839 | 0.607 | 0.978 | 0.833 | # # # | # # # | # # # | - - - | 0.847 | 0.617 | 0.997 | 0.846 | - - - | 0.487 | 1.72 | 1.66 | 1.63 | 1.6 | 1.59 | 1.64 | 11.75 | 17.46 | 18.79 | 0 | - - - | - - - | - - - | - - - | 1267 | 966 | 1461 | 3694 | Over-range | 688 | 756 | 303 | 2037 | 163 | 172 | 280 | 1380 | 1066 | 587 | 1426 | 3079 | 1066 | 587 | 1426 | 3079 | - - - | - - - | - - - | - - -
5/9/2026 | 4:30:00 PM | 280.54 | 278.26 | 276.75 | 485.25 | 479.19 | 482.76 | 4.9415 | 4.1047 | 5.4933 | 4.1693 | 1.435 | 1.434 | 1.431 | 1.491 | 1.43 | 1.425 | Over-range | 60 | 1132 | 851 | 1492 | 3475 | - - - | - - - | - - - | - - - | 1132 | 851 | 1492 | 3475 | 780 | 733 | -22 | 1490 | - - - | - - - | - - - | - - - | 780 | 733 | -22 | 1490 | 1385 | 1139 | 1520 | 4045 | # # # | # # # | # # # | # # # | 0.817 | 0.747 | 0.982 | 0.859 | # # # | # # # | # # # | - - - | 0.823 | 0.757 | 0.999 | 0.87 | - - - | 0.429 | 1.69 | 1.66 | 1.63 | 1.58 | 1.59 | 1.62 | 10.68 | 15.44 | 18.47 | 0 | - - - | - - - | - - - | - - - | 1385 | 1139 | 1520 | 4045 | Over-range | 799 | 754 | 289 | 2069 | 170 | 179 | 285 | 1435 | 1131 | 852 | 1492 | 3475 | 1131 | 852 | 1492 | 3475 | - - - | - - - | - - - | - - -
5/9/2026 | 4:45:00 PM | 280.45 | 278.14 | 276.61 | 485.09 | 478.96 | 482.56 | 5.145 | 4.45 | 5.6079 | 4.1645 | 1.436 | 1.434 | 1.431 | 1.491 | 1.421 | 1.441 | Over-range | 60 | 1164 | 977 | 1522 | 3662 | - - - | - - - | - - - | - - - | 1164 | 977 | 1522 | 3662 | 833 | 729 | -77 | 1485 | - - - | - - - | - - - | - - - | 833 | 729 | -77 | 1485 | 1442 | 1234 | 1551 | 4227 | # # # | # # # | # # # | # # # | 0.807 | 0.791 | 0.981 | 0.866 | # # # | # # # | # # # | - - - | 0.814 | 0.799 | 0.998 | 0.877 | - - - | 0.406 | 1.74 | 1.71 | 1.62 | 1.6 | 1.61 | 1.65 | 10.24 | 14.56 | 18.19 | 0 | - - - | - - - | - - - | - - - | 1442 | 1234 | 1551 | 4227 | Over-range | 851 | 752 | 300 | 2111 | 171 | 183 | 286 | 1500 | 1165 | 975 | 1522 | 3662 | 1165 | 975 | 1522 | 3662 | - - - | - - - | - - - | - - -
5/9/2026 | 5:00:00 PM | 280.44 | 278.03 | 276.53 | 484.95 | 478.8 | 482.5 | 5.6157 | 5.2785 | 5.8883 | 4.1624 | 1.436 | 1.434 | 1.431 | 1.494 | 1.442 | 1.47 | Over-range | 60.01 | 1239 | 1262 | 1590 | 4090 | - - - | - - - | - - - | - - - | 1239 | 1262 | 1590 | 4090 | 955 | 724 | -204 | 1474 | - - - | - - - | - - - | - - - | 955 | 724 | -204 | 1474 | 1575 | 1467 | 1628 | 4669 | # # # | # # # | # # # | # # # | 0.787 | 0.86 | 0.976 | 0.876 | # # # | # # # | # # # | - - - | 0.792 | 0.867 | 0.992 | 0.885 | - - - | 0.36 | 1.73 | 1.69 | 1.62 | 1.6 | 1.61 | 1.65 | 9.35 | 12.53 | 17.4 | 0 | - - - | - - - | - - - | - - - | 1575 | 1467 | 1628 | 4669 | Over-range | 972 | 747 | 352 | 2252 | 176 | 184 | 285 | 1702 | 1238 | 1262 | 1589 | 4090 | 1238 | 1262 | 1589 | 4090 | - - - | - - - | - - - | - - -
5/9/2026 | 5:15:00 PM | 280.66 | 278.4 | 276.81 | 485.49 | 479.39 | 482.9 | 5.2904 | 4.6999 | 5.6929 | 4.165 | 1.435 | 1.434 | 1.431 | 1.491 | 1.419 | 1.444 | Over-range | 60.01 | 1188 | 1066 | 1545 | 3798 | - - - | - - - | - - - | - - - | 1188 | 1066 | 1545 | 3798 | 873 | 731 | -115 | 1488 | - - - | - - - | - - - | - - - | 873 | 731 | -115 | 1488 | 1484 | 1306 | 1576 | 4366 | # # # | # # # | # # # | # # # | 0.8 | 0.816 | 0.98 | 0.87 | # # # | # # # | # # # | - - - | 0.805 | 0.824 | 0.997 | 0.88 | - - - | 0.392 | 1.72 | 1.67 | 1.6 | 1.59 | 1.59 | 1.62 | 9.95 | 13.74 | 17.92 | 0 | - - - | - - - | - - - | - - - | 1484 | 1306 | 1576 | 4366 | Over-range | 890 | 754 | 310 | 2154 | 174 | 183 | 285 | 1556 | 1187 | 1065 | 1546 | 3798 | 1187 | 1065 | 1546 | 3798 | - - - | - - - | - - - | - - -
5/9/2026 | 5:30:00 PM | 280.58 | 278.36 | 276.83 | 485.36 | 479.41 | 482.83 | 4.6214 | 3.6571 | 5.3305 | 4.1734 | 1.436 | 1.434 | 1.431 | 1.489 | 1.471 | 1.435 | Over-range | 60.01 | 1078 | 645 | 1443 | 3166 | - - - | - - - | - - - | - - - | 1078 | 645 | 1443 | 3166 | 692 | 735 | 69 | 1496 | - - - | - - - | - - - | - - - | 692 | 735 | 69 | 1496 | 1293 | 1008 | 1475 | 3776 | # # # | # # # | # # # | # # # | 0.834 | 0.64 | 0.978 | 0.838 | # # # | # # # | # # # | - - - | 0.841 | 0.65 | 0.997 | 0.851 | - - - | 0.472 | 1.75 | 1.68 | 1.62 | 1.61 | 1.61 | 1.65 | 11.56 | 16.91 | 18.67 | 0 | - - - | - - - | - - - | - - - | 1293 | 1008 | 1475 | 3776 | Over-range | 712 | 756 | 304 | 2051 | 167 | 177 | 281 | 1403 | 1080 | 644 | 1444 | 3167 | 1080 | 644 | 1444 | 3167 | - - - | - - - | - - - | - - -
5/9/2026 | 5:45:00 PM | 280.77 | 278.71 | 277.16 | 485.78 | 480.08 | 483.24 | 4.7903 | 3.8214 | 5.4175 | 4.1778 | 1.436 | 1.434 | 1.431 | 1.489 | 1.462 | 1.445 | Over-range | 60.01 | 1112 | 700 | 1463 | 3275 | - - - | - - - | - - - | - - - | 1112 | 700 | 1463 | 3275 | 725 | 739 | 68 | 1532 | - - - | - - - | - - - | - - - | 725 | 739 | 68 | 1532 | 1340 | 1052 | 1500 | 3893 | # # # | # # # | # # # | # # # | 0.83 | 0.665 | 0.975 | 0.841 | # # # | # # # | # # # | - - - | 0.83 | 0.669 | 0.978 | 0.844 | - - - | 0.468 | 1.76 | 1.68 | 1.59 | 1.6 | 1.6 | 1.64 | 11.19 | 16.77 | 18.64 | 0 | - - - | - - - | - - - | - - - | 1340 | 1052 | 1500 | 3893 | Over-range | 746 | 761 | 325 | 2096 | 171 | 180 | 285 | 1426 | 1122 | 701 | 1480 | 3302 | 1122 | 701 | 1480 | 3302 | - - - | - - - | - - - | - - -
5/9/2026 | 6:00:00 PM | 280.75 | 278.64 | 277.06 | 485.71 | 479.92 | 483.14 | 4.7491 | 3.864 | 5.4022 | 4.1766 | 1.435 | 1.434 | 1.431 | 1.491 | 1.463 | 1.436 | Over-range | 60.02 | 1098 | 721 | 1464 | 3283 | - - - | - - - | - - - | - - - | 1098 | 721 | 1464 | 3283 | 725 | 738 | 36 | 1500 | - - - | - - - | - - - | - - - | 725 | 738 | 36 | 1500 | 1328 | 1062 | 1496 | 3886 | # # # | # # # | # # # | # # # | 0.827 | 0.679 | 0.979 | 0.845 | # # # | # # # | # # # | - - - | 0.834 | 0.69 | 0.997 | 0.857 | - - - | 0.457 | 1.71 | 1.67 | 1.59 | 1.58 | 1.58 | 1.62 | 11.27 | 16.54 | 18.66 | 0 | - - - | - - - | - - - | - - - | 1328 | 1062 | 1496 | 3886 | Over-range | 745 | 759 | 306 | 2073 | 170 | 175 | 284 | 1430 | 1097 | 723 | 1463 | 3283 | 1097 | 723 | 1463 | 3283 | - - - | - - - | - - - | - - -
5/9/2026 | 6:15:00 PM | 280.91 | 278.85 | 277.26 | 486.06 | 480.25 | 483.43 | 4.6461 | 3.6808 | 5.3482 | 4.1768 | 1.435 | 1.434 | 1.431 | 1.49 | 1.464 | 1.43 | Over-range | 60.02 | 1083 | 663 | 1451 | 3197 | - - - | - - - | - - - | - - - | 1083 | 663 | 1451 | 3197 | 703 | 741 | 64 | 1508 | - - - | - - - | - - - | - - - | 703 | 741 | 64 | 1508 | 1303 | 1019 | 1482 | 3804 | # # # | # # # | # # # | # # # | 0.832 | 0.651 | 0.979 | 0.84 | # # # | # # # | # # # | - - - | 0.839 | 0.66 | 0.997 | 0.853 | - - - | 0.472 | 1.72 | 1.64 | 1.6 | 1.58 | 1.58 | 1.62 | 11.48 | 17.06 | 18.89 | 0 | - - - | - - - | - - - | - - - | 1303 | 1019 | 1482 | 3804 | Over-range | 723 | 762 | 302 | 2058 | 167 | 179 | 285 | 1399 | 1085 | 662 | 1450 | 3197 | 1085 | 662 | 1450 | 3197 | - - - | - - - | - - - | - - -
5/9/2026 | 6:30:00 PM | 280.91 | 278.87 | 277.25 | 486.09 | 480.28 | 483.39 | 5.3523 | 4.8018 | 5.7347 | 4.1764 | 1.435 | 1.433 | 1.431 | 1.492 | 1.416 | 1.457 | Over-range | 60.01 | 1197 | 1101 | 1558 | 3856 | - - - | - - - | - - - | - - - | 1197 | 1101 | 1558 | 3856 | 893 | 736 | -126 | 1502 | - - - | - - - | - - - | - - - | 893 | 736 | -126 | 1502 | 1503 | 1338 | 1590 | 4431 | # # # | # # # | # # # | # # # | 0.797 | 0.823 | 0.98 | 0.87 | # # # | # # # | # # # | - - - | 0.802 | 0.831 | 0.997 | 0.88 | - - - | 0.39 | 1.72 | 1.64 | 1.57 | 1.57 | 1.57 | 1.61 | 9.88 | 13.67 | 18.03 | 0 | - - - | - - - | - - - | - - - | 1503 | 1338 | 1590 | 4431 | Over-range | 909 | 760 | 318 | 2184 | 167 | 190 | 290 | 1584 | 1201 | 1099 | 1557 | 3857 | 1201 | 1099 | 1557 | 3857 | - - - | - - - | - - - | - - -
5/9/2026 | 6:45:00 PM | 280.97 | 278.91 | 277.35 | 486.13 | 480.45 | 483.53 | 5.0709 | 4.3121 | 5.572 | 4.1797 | 1.435 | 1.433 | 1.43 | 1.49 | 1.421 | 1.436 | Over-range | 60.01 | 1153 | 931 | 1517 | 3601 | - - - | - - - | - - - | - - - | 1153 | 931 | 1517 | 3601 | 820 | 739 | -51 | 1506 | - - - | - - - | - - - | - - - | 820 | 739 | -51 | 1506 | 1425 | 1203 | 1545 | 4173 | # # # | # # # | # # # | # # # | 0.809 | 0.774 | 0.982 | 0.863 | # # # | # # # | # # # | - - - | 0.815 | 0.783 | 0.999 | 0.874 | - - - | 0.418 | 1.7 | 1.65 | 1.59 | 1.58 | 1.57 | 1.6 | 10.45 | 14.79 | 18.37 | 0 | - - - | - - - | - - - | - - - | 1425 | 1203 | 1545 | 4173 | Over-range | 837 | 761 | 293 | 2108 | 169 | 184 | 288 | 1475 | 1155 | 929 | 1518 | 3602 | 1155 | 929 | 1518 | 3602 | - - - | - - - | - - - | - - -
5/9/2026 | 7:00:00 PM | 281.17 | 279.15 | 277.56 | 486.54 | 480.81 | 483.89 | 4.5447 | 3.54 | 5.3028 | 4.1827 | 1.435 | 1.433 | 1.43 | 1.49 | 1.478 | 1.438 | Over-range | 60.02 | 1067 | 598 | 1438 | 3103 | - - - | - - - | - - - | - - - | 1067 | 598 | 1438 | 3103 | 677 | 747 | 95 | 1518 | - - - | - - - | - - - | - - - | 677 | 747 | 95 | 1518 | 1275 | 982 | 1471 | 3729 | # # # | # # # | # # # | # # # | 0.837 | 0.608 | 0.977 | 0.832 | # # # | # # # | # # # | - - - | 0.843 | 0.619 | 0.997 | 0.844 | - - - | 0.489 | 1.73 | 1.66 | 1.6 | 1.59 | 1.58 | 1.63 | 11.84 | 17.4 | 18.96 | 0 | - - - | - - - | - - - | - - - | 1275 | 982 | 1471 | 3729 | Over-range | 698 | 767 | 309 | 2064 | 168 | 172 | 285 | 1397 | 1066 | 599 | 1437 | 3102 | 1066 | 599 | 1437 | 3102 | - - - | - - - | - - - | - - -
5/9/2026 | 7:15:00 PM | 280.9 | 278.85 | 277.32 | 486.04 | 480.32 | 483.46 | 4.7378 | 3.866 | 5.4015 | 4.1797 | 1.435 | 1.433 | 1.43 | 1.491 | 1.468 | 1.44 | Over-range | 60 | 1095 | 709 | 1463 | 3268 | - - - | - - - | - - - | - - - | 1095 | 709 | 1463 | 3268 | 723 | 742 | 44 | 1510 | - - - | - - - | - - - | - - - | 723 | 742 | 44 | 1510 | 1325 | 1062 | 1497 | 3884 | # # # | # # # | # # # | # # # | 0.827 | 0.668 | 0.978 | 0.841 | # # # | # # # | # # # | - - - | 0.833 | 0.678 | 0.996 | 0.853 | - - - | 0.462 | 1.71 | 1.66 | 1.6 | 1.59 | 1.58 | 1.62 | 11.41 | 16.72 | 18.76 | 0 | - - - | - - - | - - - | - - - | 1325 | 1062 | 1497 | 3884 | Over-range | 744 | 764 | 312 | 2090 | 171 | 178 | 285 | 1444 | 1094 | 710 | 1463 | 3267 | 1094 | 710 | 1463 | 3267 | - - - | - - - | - - - | - - -
5/9/2026 | 7:30:00 PM | 280.86 | 278.83 | 277.21 | 485.99 | 480.28 | 483.29 | 4.8466 | 4.4844 | 5.4344 | 3.4433 | 1.435 | 1.433 | 1.43 | 1.489 | 1.481 | 1.442 | Over-range | 60.01 | 1119 | 970 | 1471 | 3560 | - - - | - - - | - - - | - - - | 1119 | 970 | 1471 | 3560 | 739 | 668 | 56 | 1463 | - - - | - - - | - - - | - - - | 739 | 668 | 56 | 1463 | 1353 | 1217 | 1505 | 4075 | # # # | # # # | # # # | # # # | 0.827 | 0.797 | 0.977 | 0.874 | # # # | # # # | # # # | - - - | 0.826 | 0.799 | 0.98 | 0.875 | - - - | 0.411 | 1.71 | 1.62 | 1.61 | 1.58 | 1.57 | 1.61 | 11.17 | 13.55 | 18.72 | 0 | - - - | - - - | - - - | - - - | 1353 | 1217 | 1505 | 4075 | Over-range | 758 | 687 | 317 | 1968 | 167 | 160 | 287 | 1306 | 1130 | 977 | 1484 | 3590 | 1130 | 977 | 1484 | 3590 | - - - | - - - | - - - | - - -
5/9/2026 | 7:45:00 PM | 280.96 | 278.98 | 277.35 | 486.22 | 480.48 | 483.51 | 4.7326 | 4.7162 | 5.3984 | 2.764 | 1.435 | 1.433 | 1.43 | 1.491 | 1.442 | 1.431 | Over-range | 59.99 | 1096 | 1134 | 1466 | 3695 | - - - | - - - | - - - | - - - | 1096 | 1134 | 1466 | 3695 | 728 | 620 | 44 | 1392 | - - - | - - - | - - - | - - - | 728 | 620 | 44 | 1392 | 1327 | 1304 | 1496 | 4128 | # # # | # # # | # # # | # # # | 0.826 | 0.869 | 0.979 | 0.895 | # # # | # # # | # # # | - - - | 0.832 | 0.875 | 0.998 | 0.905 | - - - | 0.377 | 1.7 | 1.63 | 1.59 | 1.57 | 1.56 | 1.59 | 11.3 | 11.18 | 18.79 | 0 | - - - | - - - | - - - | - - - | 1327 | 1304 | 1496 | 4128 | Over-range | 747 | 638 | 302 | 1839 | 165 | 152 | 286 | 1196 | 1097 | 1134 | 1463 | 3694 | 1097 | 1134 | 1463 | 3694 | - - - | - - - | - - - | - - -
5/9/2026 | 8:00:00 PM | 280.33 | 278.39 | 276.79 | 485.11 | 479.53 | 482.5 | 5.381 | 5.9779 | 5.7395 | 2.7507 | 1.434 | 1.433 | 1.43 | 1.49 | 1.462 | 1.463 | Over-range | 60.01 | 1200 | 1540 | 1555 | 4295 | - - - | - - - | - - - | - - - | 1200 | 1540 | 1555 | 4295 | 897 | 609 | -141 | 1365 | - - - | - - - | - - - | - - - | 897 | 609 | -141 | 1365 | 1508 | 1663 | 1589 | 4760 | # # # | # # # | # # # | # # # | 0.796 | 0.926 | 0.979 | 0.902 | # # # | # # # | # # # | - - - | 0.801 | 0.929 | 0.996 | 0.911 | - - - | 0.318 | 1.72 | 1.67 | 1.63 | 1.59 | 1.61 | 1.64 | 9.84 | 8.93 | 18.12 | 0 | - - - | - - - | - - - | - - - | 1508 | 1663 | 1589 | 4760 | Over-range | 913 | 629 | 324 | 2052 | 169 | 157 | 291 | 1532 | 1203 | 1537 | 1555 | 4295 | 1203 | 1537 | 1555 | 4295 | - - - | - - - | - - - | - - -
5/9/2026 | 8:15:00 PM | 280.66 | 278.77 | 277.21 | 485.7 | 480.3 | 483.1 | 5.1823 | 5.5902 | 5.6466 | 2.7562 | 1.433 | 1.432 | 1.431 | 1.484 | 1.453 | 1.52 | Over-range | 60 | 1168 | 1418 | 1533 | 4119 | - - - | - - - | - - - | - - - | 1168 | 1418 | 1533 | 4119 | 847 | 615 | -81 | 1380 | - - - | - - - | - - - | - - - | 847 | 615 | -81 | 1380 | 1454 | 1555 | 1565 | 4574 | # # # | # # # | # # # | # # # | 0.804 | 0.912 | 0.98 | 0.901 | # # # | # # # | # # # | - - - | 0.81 | 0.917 | 0.998 | 0.91 | - - - | 0.335 | 1.81 | 1.77 | 1.8 | 1.68 | 1.74 | 1.77 | 10.59 | 9.91 | 18.84 | 0 | - - - | - - - | - - - | - - - | 1454 | 1555 | 1565 | 4574 | Over-range | 865 | 636 | 315 | 1988 | 175 | 162 | 300 | 1430 | 1170 | 1416 | 1533 | 4120 | 1170 | 1416 | 1533 | 4120 | - - - | - - - | - - - | - - -
5/9/2026 | 8:30:00 PM | 280.99 | 278.93 | 277.49 | 486.2 | 480.56 | 483.66 | 4.5086 | 4.2955 | 5.2882 | 2.7449 | 1.433 | 1.432 | 1.431 | 1.489 | 1.455 | 1.429 | Over-range | 60 | 1060 | 1002 | 1434 | 3496 | - - - | - - - | - - - | - - - | 1060 | 1002 | 1434 | 3496 | 668 | 622 | 104 | 1394 | - - - | - - - | - - - | - - - | 668 | 622 | 104 | 1394 | 1265 | 1193 | 1467 | 3925 | # # # | # # # | # # # | # # # | 0.838 | 0.84 | 0.977 | 0.891 | # # # | # # # | # # # | - - - | 0.845 | 0.847 | 0.997 | 0.902 | - - - | 0.399 | 1.71 | 1.67 | 1.66 | 1.57 | 1.63 | 1.65 | 11.88 | 12.3 | 19.2 | 0 | - - - | - - - | - - - | - - - | 1265 | 1193 | 1467 | 3925 | Over-range | 690 | 641 | 311 | 1783 | 169 | 156 | 287 | 1111 | 1061 | 1000 | 1435 | 3497 | 1061 | 1000 | 1435 | 3497 | - - - | - - - | - - - | - - -
5/9/2026 | 8:45:00 PM | 281.18 | 279.08 | 277.59 | 486.55 | 480.73 | 483.92 | 5.3384 | 5.9056 | 5.7132 | 2.7248 | 1.433 | 1.431 | 1.43 | 1.488 | 1.456 | 1.383 | Over-range | 60 | 1195 | 1518 | 1555 | 4268 | - - - | - - - | - - - | - - - | 1195 | 1518 | 1555 | 4268 | 891 | 619 | -122 | 1387 | - - - | - - - | - - - | - - - | 891 | 619 | -122 | 1387 | 1501 | 1647 | 1586 | 4733 | # # # | # # # | # # # | # # # | 0.796 | 0.922 | 0.98 | 0.902 | # # # | # # # | # # # | - - - | 0.801 | 0.926 | 0.997 | 0.91 | - - - | 0.325 | 1.64 | 1.55 | 1.51 | 1.48 | 1.49 | 1.53 | 9.59 | 8.85 | 17.88 | 0 | - - - | - - - | - - - | - - - | 1501 | 1647 | 1586 | 4733 | Over-range | 907 | 637 | 312 | 2046 | 170 | 150 | 285 | 1503 | 1195 | 1517 | 1556 | 4268 | 1195 | 1517 | 1556 | 4268 | - - - | - - - | - - - | - - -
5/9/2026 | 9:00:00 PM | 281.06 | 278.88 | 277.43 | 486.25 | 480.44 | 483.66 | 4.492 | 4.2599 | 5.2545 | 2.7366 | 1.433 | 1.431 | 1.43 | 1.488 | 1.448 | 1.417 | Over-range | 60.01 | 1059 | 990 | 1425 | 3474 | - - - | - - - | - - - | - - - | 1059 | 990 | 1425 | 3474 | 665 | 621 | 106 | 1392 | - - - | - - - | - - - | - - - | 665 | 621 | 106 | 1392 | 1261 | 1181 | 1457 | 3899 | # # # | # # # | # # # | # # # | 0.84 | 0.839 | 0.978 | 0.891 | # # # | # # # | # # # | - - - | 0.847 | 0.846 | 0.996 | 0.902 | - - - | 0.401 | 1.62 | 1.56 | 1.48 | 1.46 | 1.46 | 1.51 | 11.35 | 11.73 | 18.76 | 0 | - - - | - - - | - - - | - - - | 1261 | 1181 | 1457 | 3899 | Over-range | 683 | 638 | 304 | 1768 | 156 | 145 | 277 | 1089 | 1061 | 991 | 1423 | 3475 | 1061 | 991 | 1423 | 3475 | - - - | - - - | - - - | - - -
5/9/2026 | 9:15:00 PM | 281.07 | 278.93 | 277.37 | 486.37 | 480.37 | 483.6 | 4.7214 | 4.7384 | 5.3934 | 2.7375 | 1.433 | 1.431 | 1.43 | 1.488 | 1.458 | 1.403 | Over-range | 59.97 | 1092 | 1122 | 1462 | 3676 | - - - | - - - | - - - | - - - | 1092 | 1122 | 1462 | 3676 | 723 | 622 | 52 | 1397 | - - - | - - - | - - - | - - - | 723 | 622 | 52 | 1397 | 1321 | 1299 | 1495 | 4115 | # # # | # # # | # # # | # # # | 0.827 | 0.864 | 0.978 | 0.893 | # # # | # # # | # # # | - - - | 0.833 | 0.87 | 0.995 | 0.903 | - - - | 0.38 | 1.65 | 1.55 | 1.48 | 1.48 | 1.48 | 1.52 | 10.92 | 11.14 | 18.51 | 0 | - - - | - - - | - - - | - - - | 1321 | 1299 | 1495 | 4115 | Over-range | 741 | 640 | 309 | 1846 | 159 | 148 | 280 | 1197 | 1094 | 1123 | 1459 | 3677 | 1094 | 1123 | 1459 | 3677 | - - - | - - - | - - - | - - -
5/9/2026 | 9:30:00 PM | 281.38 | 279.25 | 277.74 | 486.9 | 481 | 484.21 | 5.16 | 5.4178 | 5.5929 | 2.7289 | 1.433 | 1.431 | 1.43 | 1.487 | 1.446 | 1.376 | Over-range | 60 | 1174 | 1353 | 1519 | 4046 | - - - | - - - | - - - | - - - | 1174 | 1353 | 1519 | 4046 | 831 | 623 | -27 | 1426 | - - - | - - - | - - - | - - - | 831 | 623 | -27 | 1426 | 1449 | 1501 | 1553 | 4502 | # # # | # # # | # # # | # # # | 0.81 | 0.902 | 0.978 | 0.899 | # # # | # # # | # # # | - - - | 0.809 | 0.9 | 0.986 | 0.9 | - - - | 0.353 | 1.62 | 1.55 | 1.49 | 1.47 | 1.48 | 1.52 | 9.9 | 9.73 | 18.22 | 0 | - - - | - - - | - - - | - - - | 1449 | 1501 | 1553 | 4502 | Over-range | 848 | 641 | 318 | 1974 | 164 | 149 | 285 | 1347 | 1184 | 1362 | 1527 | 4072 | 1184 | 1362 | 1527 | 4072 | - - - | - - - | - - - | - - -
5/9/2026 | 9:45:00 PM | 281.9 | 279.69 | 278.2 | 487.69 | 481.8 | 485.06 | 5.4834 | 6.1875 | 5.8224 | 2.7332 | 1.431 | 1.429 | 1.428 | 1.495 | 1.463 | 1.339 | Over-range | 60 | 1219 | 1605 | 1587 | 4411 | - - - | - - - | - - - | - - - | 1219 | 1605 | 1587 | 4411 | 934 | 626 | -154 | 1405 | - - - | - - - | - - - | - - - | 934 | 626 | -154 | 1405 | 1545 | 1730 | 1620 | 4895 | # # # | # # # | # # # | # # # | 0.789 | 0.928 | 0.98 | 0.901 | # # # | # # # | # # # | - - - | 0.794 | 0.932 | 0.995 | 0.909 | - - - | 0.319 | 1.55 | 1.45 | 1.39 | 1.39 | 1.38 | 1.41 | 9.3 | 8.53 | 17.58 | 0 | - - - | - - - | - - - | - - - | 1545 | 1730 | 1620 | 4895 | Over-range | 949 | 644 | 325 | 2121 | 169 | 151 | 284 | 1589 | 1219 | 1606 | 1586 | 4411 | 1219 | 1606 | 1586 | 4411 | - - - | - - - | - - - | - - -
5/9/2026 | 10:00:00 PM | 282.27 | 280.09 | 278.58 | 488.37 | 482.48 | 485.7 | 5.0459 | 5.3611 | 5.5561 | 2.7321 | 1.431 | 1.428 | 1.426 | 1.493 | 1.476 | 1.346 | Over-range | 60.03 | 1146 | 1320 | 1515 | 3981 | - - - | - - - | - - - | - - - | 1146 | 1320 | 1515 | 3981 | 816 | 631 | -27 | 1420 | - - - | - - - | - - - | - - - | 816 | 631 | -27 | 1420 | 1418 | 1479 | 1546 | 4444 | # # # | # # # | # # # | # # # | 0.809 | 0.892 | 0.98 | 0.896 | # # # | # # # | # # # | - - - | 0.815 | 0.897 | 0.996 | 0.905 | - - - | 0.357 | 1.55 | 1.44 | 1.34 | 1.39 | 1.35 | 1.39 | 10.21 | 9.96 | 18.07 | 0 | - - - | - - - | - - - | - - - | 1418 | 1479 | 1546 | 4444 | Over-range | 832 | 649 | 309 | 1971 | 160 | 150 | 279 | 1358 | 1149 | 1321 | 1513 | 3982 | 1149 | 1321 | 1513 | 3982 | - - - | - - - | - - - | - - -
5/9/2026 | 10:15:00 PM | 282.01 | 279.7 | 278.16 | 487.86 | 481.66 | 485.17 | 4.6998 | 4.649 | 5.3743 | 2.7393 | 1.433 | 1.43 | 1.428 | 1.489 | 1.435 | 1.39 | Over-range | 60.01 | 1094 | 1118 | 1466 | 3677 | - - - | - - - | - - - | - - - | 1094 | 1118 | 1466 | 3677 | 728 | 630 | 59 | 1416 | - - - | - - - | - - - | - - - | 728 | 630 | 59 | 1416 | 1324 | 1294 | 1495 | 4112 | # # # | # # # | # # # | # # # | 0.826 | 0.864 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.833 | 0.87 | 0.998 | 0.904 | - - - | 0.385 | 1.63 | 1.52 | 1.48 | 1.47 | 1.46 | 1.5 | 10.76 | 10.92 | 18.49 | 0 | - - - | - - - | - - - | - - - | 1324 | 1294 | 1495 | 4112 | Over-range | 745 | 647 | 291 | 1839 | 159 | 145 | 278 | 1170 | 1094 | 1120 | 1463 | 3677 | 1094 | 1120 | 1463 | 3677 | - - - | - - - | - - - | - - -
5/9/2026 | 10:30:00 PM | 282.28 | 280 | 278.4 | 488.37 | 482.16 | 485.57 | 4.862 | 4.9471 | 5.4418 | 2.736 | 1.433 | 1.43 | 1.429 | 1.488 | 1.42 | 1.367 | Over-range | 60.01 | 1121 | 1221 | 1488 | 3830 | - - - | - - - | - - - | - - - | 1121 | 1221 | 1488 | 3830 | 775 | 632 | 15 | 1422 | - - - | - - - | - - - | - - - | 775 | 632 | 15 | 1422 | 1372 | 1383 | 1515 | 4270 | # # # | # # # | # # # | # # # | 0.817 | 0.883 | 0.982 | 0.897 | # # # | # # # | # # # | - - - | 0.823 | 0.888 | 0.999 | 0.906 | - - - | 0.371 | 1.67 | 1.55 | 1.51 | 1.49 | 1.49 | 1.53 | 10.42 | 10.26 | 18.44 | 0 | - - - | - - - | - - - | - - - | 1372 | 1383 | 1515 | 4270 | Over-range | 791 | 649 | 283 | 1888 | 159 | 148 | 281 | 1241 | 1123 | 1222 | 1485 | 3830 | 1123 | 1222 | 1485 | 3830 | - - - | - - - | - - - | - - -
5/9/2026 | 10:45:00 PM | 282.39 | 280.03 | 278.48 | 488.46 | 482.24 | 485.78 | 5.0304 | 5.2781 | 5.553 | 2.7427 | 1.434 | 1.431 | 1.429 | 1.489 | 1.435 | 1.354 | Over-range | 60.02 | 1148 | 1324 | 1519 | 3991 | - - - | - - - | - - - | - - - | 1148 | 1324 | 1519 | 3991 | 818 | 631 | -29 | 1419 | - - - | - - - | - - - | - - - | 818 | 631 | -29 | 1419 | 1420 | 1475 | 1546 | 4441 | # # # | # # # | # # # | # # # | 0.809 | 0.898 | 0.982 | 0.899 | # # # | # # # | # # # | - - - | 0.814 | 0.902 | 0.999 | 0.907 | - - - | 0.355 | 1.67 | 1.58 | 1.55 | 1.52 | 1.53 | 1.57 | 10.14 | 9.92 | 18.34 | 0 | - - - | - - - | - - - | - - - | 1420 | 1475 | 1546 | 4441 | Over-range | 835 | 649 | 290 | 1947 | 166 | 150 | 285 | 1332 | 1148 | 1325 | 1518 | 3991 | 1148 | 1325 | 1518 | 3991 | - - - | - - - | - - - | - - -
5/9/2026 | 11:00:00 PM | 282.76 | 280.47 | 278.85 | 489.21 | 482.91 | 486.38 | 5.6794 | 6.5599 | 5.9195 | 2.7308 | 1.434 | 1.431 | 1.429 | 1.493 | 1.468 | 1.368 | Over-range | 60.01 | 1251 | 1719 | 1612 | 4582 | - - - | - - - | - - - | - - - | 1251 | 1719 | 1612 | 4582 | 990 | 633 | -199 | 1423 | - - - | - - - | - - - | - - - | 990 | 633 | -199 | 1423 | 1605 | 1838 | 1650 | 5094 | # # # | # # # | # # # | # # # | 0.779 | 0.935 | 0.977 | 0.899 | # # # | # # # | # # # | - - - | 0.784 | 0.938 | 0.993 | 0.907 | - - - | 0.311 | 1.72 | 1.6 | 1.58 | 1.54 | 1.56 | 1.6 | 9.09 | 8.39 | 17.67 | 0 | - - - | - - - | - - - | - - - | 1605 | 1838 | 1650 | 5094 | Over-range | 1006 | 652 | 354 | 2227 | 176 | 156 | 291 | 1712 | 1251 | 1718 | 1613 | 4582 | 1251 | 1718 | 1613 | 4582 | - - - | - - - | - - - | - - -
5/9/2026 | 11:15:00 PM | 283.15 | 280.83 | 279.31 | 489.81 | 483.66 | 487.14 | 5.3171 | 5.8302 | 5.7076 | 2.7417 | 1.434 | 1.431 | 1.43 | 1.489 | 1.45 | 1.346 | Over-range | 60.01 | 1194 | 1498 | 1564 | 4256 | - - - | - - - | - - - | - - - | 1194 | 1498 | 1564 | 4256 | 900 | 640 | -98 | 1442 | - - - | - - - | - - - | - - - | 900 | 640 | -98 | 1442 | 1505 | 1636 | 1594 | 4736 | # # # | # # # | # # # | # # # | 0.794 | 0.915 | 0.981 | 0.899 | # # # | # # # | # # # | - - - | 0.799 | 0.92 | 0.998 | 0.907 | - - - | 0.339 | 1.73 | 1.64 | 1.6 | 1.57 | 1.58 | 1.63 | 9.76 | 9.28 | 18.19 | 0 | - - - | - - - | - - - | - - - | 1505 | 1636 | 1594 | 4736 | Over-range | 916 | 659 | 308 | 2077 | 171 | 156 | 291 | 1495 | 1195 | 1498 | 1564 | 4256 | 1195 | 1498 | 1564 | 4256 | - - - | - - - | - - - | - - -
5/9/2026 | 11:30:00 PM | 283.39 | 281.13 | 279.47 | 490.32 | 484.08 | 487.43 | 5.3055 | 5.6188 | 5.6696 | 2.75 | 1.434 | 1.431 | 1.43 | 1.488 | 1.445 | 1.353 | Over-range | 60.02 | 1201 | 1433 | 1554 | 4188 | - - - | - - - | - - - | - - - | 1201 | 1433 | 1554 | 4188 | 883 | 644 | -43 | 1482 | - - - | - - - | - - - | - - - | 883 | 644 | -43 | 1482 | 1501 | 1579 | 1584 | 4664 | # # # | # # # | # # # | # # # | 0.8 | 0.908 | 0.981 | 0.898 | # # # | # # # | # # # | - - - | 0.799 | 0.904 | 0.99 | 0.899 | - - - | 0.354 | 1.72 | 1.64 | 1.62 | 1.57 | 1.58 | 1.63 | 9.88 | 9.66 | 18.41 | 0 | - - - | - - - | - - - | - - - | 1501 | 1579 | 1584 | 4664 | Over-range | 900 | 663 | 306 | 2052 | 173 | 158 | 293 | 1414 | 1213 | 1441 | 1567 | 4220 | 1213 | 1441 | 1567 | 4220 | - - - | - - - | - - - | - - -
5/9/2026 | 11:45:00 PM | 283.61 | 281.24 | 279.63 | 490.62 | 484.23 | 487.82 | 5.3187 | 5.8202 | 5.7058 | 2.7482 | 1.434 | 1.431 | 1.429 | 1.49 | 1.451 | 1.341 | Over-range | 60.02 | 1196 | 1496 | 1565 | 4257 | - - - | - - - | - - - | - - - | 1196 | 1496 | 1565 | 4257 | 905 | 644 | -94 | 1454 | - - - | - - - | - - - | - - - | 905 | 644 | -94 | 1454 | 1508 | 1637 | 1596 | 4741 | # # # | # # # | # # # | # # # | 0.793 | 0.914 | 0.981 | 0.898 | # # # | # # # | # # # | - - - | 0.798 | 0.918 | 0.998 | 0.907 | - - - | 0.342 | 1.74 | 1.64 | 1.61 | 1.57 | 1.59 | 1.63 | 9.8 | 9.41 | 18.34 | 0 | - - - | - - - | - - - | - - - | 1508 | 1637 | 1596 | 4741 | Over-range | 920 | 664 | 308 | 2087 | 165 | 163 | 293 | 1496 | 1199 | 1494 | 1564 | 4258 | 1199 | 1494 | 1564 | 4258 | - - - | - - - | - - - | - - -
5/10/2026 | 12:00:00 AM | 283.94 | 281.55 | 279.95 | 491.18 | 484.77 | 488.37 | 4.7972 | 4.8641 | 5.4433 | 2.7588 | 1.435 | 1.432 | 1.43 | 1.488 | 1.465 | 1.398 | Over-range | 60.01 | 1107 | 1155 | 1487 | 3749 | - - - | - - - | - - - | - - - | 1107 | 1155 | 1487 | 3749 | 761 | 655 | 58 | 1474 | - - - | - - - | - - - | - - - | 761 | 655 | 58 | 1474 | 1355 | 1346 | 1522 | 4224 | # # # | # # # | # # # | # # # | 0.817 | 0.858 | 0.977 | 0.888 | # # # | # # # | # # # | - - - | 0.824 | 0.864 | 0.995 | 0.898 | - - - | 0.393 | 1.79 | 1.64 | 1.64 | 1.6 | 1.61 | 1.66 | 11.21 | 11.59 | 18.86 | 0 | - - - | - - - | - - - | - - - | 1355 | 1346 | 1522 | 4224 | Over-range | 779 | 674 | 323 | 1942 | 166 | 157 | 290 | 1254 | 1109 | 1156 | 1485 | 3749 | 1109 | 1156 | 1485 | 3749 | - - - | - - - | - - - | - - -
5/10/2026 | 12:15:00 AM | 284.05 | 281.65 | 279.98 | 491.36 | 484.93 | 488.46 | 19.5634 | 19.2457 | 18.0586 | 2.8616 | 1.435 | 1.432 | 1.429 | 1.461 | 1.425 | 1.423 | Over-range | 60 | 2297 | 2473 | 2580 | 7350 | - - - | - - - | - - - | - - - | 2297 | 2473 | 2580 | 7350 | 2699 | 2403 | 1698 | 6800 | - - - | - - - | - - - | - - - | 2699 | 2403 | 1698 | 6800 | 3610 | 3510 | 3302 | 10423 | # # # | # # # | # # # | # # # | 0.636 | 0.705 | 0.781 | 0.705 | # # # | # # # | # # # | - - - | 0.63 | 0.692 | 0.771 | 0.695 | - - - | 0.925 | 1.76 | 1.66 | 1.62 | 1.6 | 1.6 | 1.65 | 7.81 | 8.12 | 13.41 | 0 | - - - | - - - | - - - | - - - | 3610 | 3510 | 3302 | 10423 | Over-range | 2732 | 2431 | 1859 | 7143 | 228 | 160 | 421 | 1561 | 2336 | 2506 | 2610 | 7451 | 2336 | 2506 | 2610 | 7451 | - - - | - - - | - - - | - - -
5/10/2026 | 12:30:00 AM | 284.58 | 282.08 | 280.51 | 492.22 | 485.66 | 489.43 | 5.7383 | 5.7047 | 6.0306 | 2.7691 | 1.434 | 1.431 | 1.429 | 1.486 | 1.415 | 1.38 | Over-range | 60 | 1173 | 1253 | 1551 | 3977 | - - - | - - - | - - - | - - - | 1173 | 1253 | 1551 | 3977 | 875 | 745 | 124 | 1744 | - - - | - - - | - - - | - - - | 875 | 745 | 124 | 1744 | 1481 | 1472 | 1611 | 4564 | # # # | # # # | # # # | # # # | 0.792 | 0.851 | 0.963 | 0.871 | # # # | # # # | # # # | - - - | 0.797 | 0.856 | 0.979 | 0.88 | - - - | 0.439 | 1.76 | 1.65 | 1.61 | 1.59 | 1.59 | 1.64 | 10.82 | 10.86 | 18.6 | 0 | - - - | - - - | - - - | - - - | 1481 | 1472 | 1611 | 4564 | Over-range | 894 | 763 | 367 | 2188 | 180 | 152 | 289 | 1256 | 1173 | 1256 | 1548 | 3977 | 1173 | 1256 | 1548 | 3977 | - - - | - - - | - - - | - - -
5/10/2026 | 12:45:00 AM | 284.86 | 282.55 | 280.88 | 492.85 | 486.49 | 489.94 | 5.1909 | 5.5647 | 5.6553 | 2.7673 | 1.434 | 1.431 | 1.429 | 1.492 | 1.435 | 1.342 | Over-range | 60 | 1174 | 1408 | 1558 | 4140 | - - - | - - - | - - - | - - - | 1174 | 1408 | 1558 | 4140 | 878 | 668 | -43 | 1502 | - - - | - - - | - - - | - - - | 878 | 668 | -43 | 1502 | 1477 | 1568 | 1588 | 4633 | # # # | # # # | # # # | # # # | 0.795 | 0.898 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.8 | 0.903 | 0.999 | 0.903 | - - - | 0.363 | 1.77 | 1.63 | 1.6 | 1.59 | 1.58 | 1.64 | 10.28 | 10.16 | 18.7 | 0 | - - - | - - - | - - - | - - - | 1477 | 1568 | 1588 | 4633 | Over-range | 896 | 687 | 306 | 2079 | 177 | 160 | 297 | 1434 | 1173 | 1408 | 1559 | 4140 | 1173 | 1408 | 1559 | 4140 | - - - | - - - | - - - | - - -
5/10/2026 | 1:00:00 AM | 284.86 | 282.5 | 280.86 | 492.77 | 486.49 | 489.9 | 5.5106 | 6.1891 | 5.8385 | 2.7656 | 1.434 | 1.43 | 1.429 | 1.496 | 1.451 | 1.336 | Over-range | 60.01 | 1225 | 1603 | 1606 | 4434 | - - - | - - - | - - - | - - - | 1225 | 1603 | 1606 | 4434 | 963 | 664 | -129 | 1497 | - - - | - - - | - - - | - - - | 963 | 664 | -129 | 1497 | 1568 | 1744 | 1639 | 4952 | # # # | # # # | # # # | # # # | 0.781 | 0.919 | 0.98 | 0.896 | # # # | # # # | # # # | - - - | 0.787 | 0.923 | 0.996 | 0.904 | - - - | 0.338 | 1.75 | 1.64 | 1.57 | 1.58 | 1.57 | 1.62 | 9.67 | 9.2 | 18.19 | 0 | - - - | - - - | - - - | - - - | 1568 | 1744 | 1639 | 4952 | Over-range | 979 | 684 | 329 | 2204 | 177 | 164 | 297 | 1614 | 1227 | 1601 | 1607 | 4435 | 1227 | 1601 | 1607 | 4435 | - - - | - - - | - - - | - - -
5/10/2026 | 1:15:00 AM | 284.82 | 282.37 | 280.78 | 492.67 | 486.18 | 489.87 | 5.0196 | 5.2222 | 5.5396 | 2.7606 | 1.434 | 1.43 | 1.428 | 1.489 | 1.419 | 1.355 | Over-range | 60 | 1147 | 1304 | 1527 | 3979 | - - - | - - - | - - - | - - - | 1147 | 1304 | 1527 | 3979 | 835 | 666 | 0 | 1501 | - - - | - - - | - - - | - - - | 835 | 666 | 0 | 1501 | 1429 | 1474 | 1555 | 4458 | # # # | # # # | # # # | # # # | 0.803 | 0.885 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.809 | 0.89 | 1 | 0.902 | - - - | 0.377 | 1.75 | 1.67 | 1.6 | 1.58 | 1.59 | 1.63 | 10.63 | 10.5 | 18.87 | 0 | - - - | - - - | - - - | - - - | 1429 | 1474 | 1555 | 4458 | Over-range | 852 | 685 | 295 | 2011 | 172 | 160 | 294 | 1338 | 1150 | 1302 | 1528 | 3980 | 1150 | 1302 | 1528 | 3980 | - - - | - - - | - - - | - - -
5/10/2026 | 1:30:00 AM | 284.85 | 282.32 | 280.81 | 492.63 | 486.14 | 489.98 | 5.3039 | 5.7767 | 5.7026 | 2.7633 | 1.434 | 1.43 | 1.428 | 1.494 | 1.441 | 1.333 | Over-range | 60.01 | 1193 | 1474 | 1570 | 4237 | - - - | - - - | - - - | - - - | 1193 | 1474 | 1570 | 4237 | 909 | 662 | -73 | 1497 | - - - | - - - | - - - | - - - | 909 | 662 | -73 | 1497 | 1509 | 1626 | 1601 | 4736 | # # # | # # # | # # # | # # # | 0.79 | 0.907 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.796 | 0.911 | 0.998 | 0.903 | - - - | 0.353 | 1.76 | 1.65 | 1.61 | 1.59 | 1.59 | 1.64 | 10.06 | 9.78 | 18.54 | 0 | - - - | - - - | - - - | - - - | 1509 | 1626 | 1601 | 4736 | Over-range | 925 | 683 | 311 | 2116 | 168 | 167 | 296 | 1492 | 1197 | 1472 | 1569 | 4238 | 1197 | 1472 | 1569 | 4238 | - - - | - - - | - - - | - - -
5/10/2026 | 1:45:00 AM | 285.12 | 282.7 | 281.11 | 493.18 | 486.82 | 490.38 | 5.4534 | 6.0825 | 5.8204 | 2.7702 | 1.434 | 1.43 | 1.429 | 1.494 | 1.448 | 1.322 | Over-range | 60 | 1217 | 1574 | 1604 | 4395 | - - - | - - - | - - - | - - - | 1217 | 1574 | 1604 | 4395 | 953 | 671 | -114 | 1508 | - - - | - - - | - - - | - - - | 953 | 671 | -114 | 1508 | 1555 | 1719 | 1636 | 4910 | # # # | # # # | # # # | # # # | 0.783 | 0.915 | 0.98 | 0.895 | # # # | # # # | # # # | - - - | 0.789 | 0.92 | 0.998 | 0.904 | - - - | 0.343 | 1.79 | 1.64 | 1.58 | 1.58 | 1.58 | 1.64 | 9.79 | 9.37 | 18.37 | 0 | - - - | - - - | - - - | - - - | 1555 | 1719 | 1636 | 4910 | Over-range | 967 | 693 | 322 | 2190 | 168 | 171 | 301 | 1587 | 1221 | 1574 | 1601 | 4395 | 1221 | 1574 | 1601 | 4395 | - - - | - - - | - - - | - - -
5/10/2026 | 2:00:00 AM | 285.35 | 282.92 | 281.32 | 493.63 | 487.12 | 490.78 | 5.4854 | 5.9242 | 5.7728 | 2.7658 | 1.434 | 1.43 | 1.428 | 1.492 | 1.445 | 1.333 | Over-range | 60 | 1231 | 1526 | 1593 | 4350 | - - - | - - - | - - - | - - - | 1231 | 1526 | 1593 | 4350 | 945 | 671 | -65 | 1550 | - - - | - - - | - - - | - - - | 945 | 671 | -65 | 1550 | 1562 | 1675 | 1624 | 4862 | # # # | # # # | # # # | # # # | 0.788 | 0.911 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.785 | 0.908 | 0.988 | 0.895 | - - - | 0.356 | 1.73 | 1.61 | 1.58 | 1.57 | 1.56 | 1.61 | 9.97 | 9.71 | 18.62 | 0 | - - - | - - - | - - - | - - - | 1562 | 1675 | 1624 | 4862 | Over-range | 961 | 691 | 316 | 2171 | 170 | 162 | 299 | 1514 | 1243 | 1549 | 1615 | 4407 | 1243 | 1549 | 1615 | 4407 | - - - | - - - | - - - | - - -
5/10/2026 | 2:15:00 AM | 285.12 | 282.61 | 281.1 | 493.12 | 486.63 | 490.47 | 4.8252 | 4.9099 | 5.4594 | 2.7654 | 1.434 | 1.43 | 1.428 | 1.489 | 1.472 | 1.392 | Over-range | 60 | 1112 | 1163 | 1497 | 3772 | - - - | - - - | - - - | - - - | 1112 | 1163 | 1497 | 3772 | 776 | 673 | 65 | 1514 | - - - | - - - | - - - | - - - | 776 | 673 | 65 | 1514 | 1368 | 1362 | 1533 | 4264 | # # # | # # # | # # # | # # # | 0.812 | 0.854 | 0.977 | 0.885 | # # # | # # # | # # # | - - - | 0.819 | 0.86 | 0.995 | 0.895 | - - - | 0.401 | 1.73 | 1.6 | 1.58 | 1.56 | 1.55 | 1.61 | 11.38 | 11.71 | 19.03 | 0 | - - - | - - - | - - - | - - - | 1368 | 1362 | 1533 | 4264 | Over-range | 796 | 691 | 328 | 1987 | 175 | 157 | 292 | 1276 | 1110 | 1164 | 1498 | 3772 | 1110 | 1164 | 1498 | 3772 | - - - | - - - | - - - | - - -
5/10/2026 | 2:30:00 AM | 285.12 | 282.57 | 281.04 | 493.08 | 486.58 | 490.37 | 4.8044 | 4.8197 | 5.4529 | 2.7735 | 1.434 | 1.43 | 1.428 | 1.49 | 1.435 | 1.385 | Over-range | 60.01 | 1112 | 1166 | 1501 | 3779 | - - - | - - - | - - - | - - - | 1112 | 1166 | 1501 | 3779 | 777 | 671 | 63 | 1511 | - - - | - - - | - - - | - - - | 777 | 671 | 63 | 1511 | 1368 | 1356 | 1532 | 4257 | # # # | # # # | # # # | # # # | 0.813 | 0.86 | 0.98 | 0.888 | # # # | # # # | # # # | - - - | 0.82 | 0.865 | 0.998 | 0.898 | - - - | 0.4 | 1.73 | 1.61 | 1.59 | 1.57 | 1.56 | 1.61 | 11.2 | 11.39 | 19.03 | 0 | - - - | - - - | - - - | - - - | 1368 | 1356 | 1532 | 4257 | Over-range | 796 | 689 | 305 | 1958 | 173 | 158 | 292 | 1242 | 1113 | 1164 | 1503 | 3780 | 1113 | 1164 | 1503 | 3780 | - - - | - - - | - - - | - - -
5/10/2026 | 2:45:00 AM | 285.48 | 282.85 | 281.21 | 493.71 | 486.87 | 490.84 | 4.9653 | 5.0885 | 5.514 | 2.7931 | 1.434 | 1.43 | 1.427 | 1.496 | 1.426 | 1.363 | Over-range | 60.01 | 1139 | 1257 | 1521 | 3917 | - - - | - - - | - - - | - - - | 1139 | 1257 | 1521 | 3917 | 825 | 673 | 22 | 1520 | - - - | - - - | - - - | - - - | 825 | 673 | 22 | 1520 | 1417 | 1437 | 1550 | 4404 | # # # | # # # | # # # | # # # | 0.804 | 0.875 | 0.981 | 0.89 | # # # | # # # | # # # | - - - | 0.811 | 0.881 | 0.999 | 0.899 | - - - | 0.388 | 1.75 | 1.64 | 1.57 | 1.59 | 1.57 | 1.62 | 10.88 | 10.97 | 19.09 | 0 | - - - | - - - | - - - | - - - | 1417 | 1437 | 1550 | 4404 | Over-range | 842 | 693 | 299 | 2011 | 169 | 165 | 295 | 1315 | 1142 | 1255 | 1520 | 3918 | 1142 | 1255 | 1520 | 3918 | - - - | - - - | - - - | - - -
5/10/2026 | 3:00:00 AM | 285.6 | 283.06 | 281.32 | 494.01 | 487.17 | 491.02 | 5.6509 | 6.4145 | 5.9191 | 2.8023 | 1.433 | 1.431 | 1.427 | 1.506 | 1.459 | 1.346 | Over-range | 60 | 1248 | 1674 | 1629 | 4552 | - - - | - - - | - - - | - - - | 1248 | 1674 | 1629 | 4552 | 1006 | 672 | -158 | 1518 | - - - | - - - | - - - | - - - | 1006 | 672 | -158 | 1518 | 1613 | 1813 | 1665 | 5091 | # # # | # # # | # # # | # # # | 0.774 | 0.924 | 0.978 | 0.894 | # # # | # # # | # # # | - - - | 0.78 | 0.928 | 0.995 | 0.902 | - - - | 0.334 | 1.77 | 1.63 | 1.61 | 1.61 | 1.58 | 1.64 | 9.7 | 9.17 | 18.21 | 0 | - - - | - - - | - - - | - - - | 1613 | 1813 | 1665 | 5091 | Over-range | 1021 | 693 | 344 | 2280 | 178 | 172 | 302 | 1700 | 1252 | 1671 | 1629 | 4552 | 1252 | 1671 | 1629 | 4552 | - - - | - - - | - - - | - - -
5/10/2026 | 3:15:00 AM | 285.53 | 282.98 | 281.2 | 493.86 | 487.06 | 490.82 | 5.4301 | 5.9756 | 5.7869 | 2.8066 | 1.433 | 1.431 | 1.427 | 1.503 | 1.444 | 1.358 | Over-range | 60 | 1214 | 1541 | 1595 | 4351 | - - - | - - - | - - - | - - - | 1214 | 1541 | 1595 | 4351 | 948 | 672 | -100 | 1519 | - - - | - - - | - - - | - - - | 948 | 672 | -100 | 1519 | 1550 | 1690 | 1627 | 4868 | # # # | # # # | # # # | # # # | 0.783 | 0.912 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.789 | 0.917 | 0.998 | 0.903 | - - - | 0.349 | 1.79 | 1.68 | 1.63 | 1.63 | 1.62 | 1.66 | 10.12 | 9.66 | 18.55 | 0 | - - - | - - - | - - - | - - - | 1550 | 1690 | 1627 | 4868 | Over-range | 964 | 693 | 319 | 2183 | 175 | 170 | 302 | 1567 | 1217 | 1539 | 1595 | 4351 | 1217 | 1539 | 1595 | 4351 | - - - | - - - | - - - | - - -
5/10/2026 | 3:30:00 AM | 285.5 | 282.96 | 281.07 | 493.89 | 486.85 | 490.67 | 5.1884 | 5.5119 | 5.6496 | 2.8061 | 1.433 | 1.431 | 1.427 | 1.498 | 1.426 | 1.367 | Over-range | 60.01 | 1175 | 1393 | 1558 | 4127 | - - - | - - - | - - - | - - - | 1175 | 1393 | 1558 | 4127 | 883 | 673 | -37 | 1518 | - - - | - - - | - - - | - - - | 883 | 673 | -37 | 1518 | 1480 | 1557 | 1588 | 4625 | # # # | # # # | # # # | # # # | 0.794 | 0.895 | 0.981 | 0.892 | # # # | # # # | # # # | - - - | 0.8 | 0.9 | 0.999 | 0.902 | - - - | 0.368 | 1.79 | 1.69 | 1.66 | 1.64 | 1.64 | 1.67 | 10.65 | 10.29 | 18.88 | 0 | - - - | - - - | - - - | - - - | 1480 | 1557 | 1588 | 4625 | Over-range | 900 | 693 | 306 | 2089 | 175 | 163 | 300 | 1432 | 1176 | 1395 | 1555 | 4126 | 1176 | 1395 | 1555 | 4126 | - - - | - - - | - - - | - - -
5/10/2026 | 3:45:00 AM | 285.53 | 282.93 | 281.12 | 493.87 | 486.87 | 490.77 | 5.0111 | 5.1678 | 5.5542 | 2.8065 | 1.433 | 1.431 | 1.427 | 1.495 | 1.414 | 1.373 | Over-range | 60.01 | 1147 | 1287 | 1532 | 3966 | - - - | - - - | - - - | - - - | 1147 | 1287 | 1532 | 3966 | 836 | 675 | 9 | 1519 | - - - | - - - | - - - | - - - | 836 | 675 | 9 | 1519 | 1431 | 1462 | 1561 | 4454 | # # # | # # # | # # # | # # # | 0.802 | 0.88 | 0.981 | 0.89 | # # # | # # # | # # # | - - - | 0.808 | 0.886 | 1 | 0.901 | - - - | 0.383 | 1.83 | 1.72 | 1.65 | 1.66 | 1.67 | 1.69 | 11.08 | 10.92 | 19.15 | 0 | - - - | - - - | - - - | - - - | 1431 | 1462 | 1561 | 4454 | Over-range | 855 | 694 | 301 | 2027 | 179 | 162 | 301 | 1342 | 1147 | 1288 | 1530 | 3965 | 1147 | 1288 | 1530 | 3965 | - - - | - - - | - - - | - - -
5/10/2026 | 4:00:00 AM | 285.73 | 283.23 | 281.37 | 494.28 | 487.43 | 491.09 | 5.4335 | 5.9847 | 5.7928 | 2.8113 | 1.433 | 1.431 | 1.427 | 1.502 | 1.441 | 1.393 | Over-range | 59.99 | 1214 | 1542 | 1597 | 4353 | - - - | - - - | - - - | - - - | 1214 | 1542 | 1597 | 4353 | 949 | 676 | -99 | 1526 | - - - | - - - | - - - | - - - | 949 | 676 | -99 | 1526 | 1552 | 1693 | 1630 | 4874 | # # # | # # # | # # # | # # # | 0.782 | 0.911 | 0.98 | 0.893 | # # # | # # # | # # # | - - - | 0.788 | 0.916 | 0.998 | 0.902 | - - - | 0.351 | 1.82 | 1.74 | 1.7 | 1.68 | 1.68 | 1.71 | 10.27 | 9.84 | 18.77 | 0 | - - - | - - - | - - - | - - - | 1552 | 1693 | 1630 | 4874 | Over-range | 967 | 697 | 325 | 2194 | 184 | 170 | 307 | 1575 | 1215 | 1540 | 1598 | 4353 | 1215 | 1540 | 1598 | 4353 | - - - | - - - | - - - | - - -
5/10/2026 | 4:15:00 AM | 285.67 | 283.07 | 281.33 | 494.07 | 487.17 | 491.1 | 5.365 | 5.804 | 5.7434 | 2.8076 | 1.434 | 1.431 | 1.427 | 1.499 | 1.438 | 1.394 | Over-range | 60 | 1206 | 1488 | 1584 | 4279 | - - - | - - - | - - - | - - - | 1206 | 1488 | 1584 | 4279 | 927 | 674 | -71 | 1528 | - - - | - - - | - - - | - - - | 927 | 674 | -71 | 1528 | 1532 | 1643 | 1616 | 4790 | # # # | # # # | # # # | # # # | 0.787 | 0.906 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.786 | 0.903 | 0.991 | 0.895 | - - - | 0.357 | 1.82 | 1.75 | 1.68 | 1.67 | 1.68 | 1.71 | 10.41 | 10.03 | 18.95 | 0 | - - - | - - - | - - - | - - - | 1532 | 1643 | 1616 | 4790 | Over-range | 945 | 695 | 317 | 2154 | 181 | 168 | 306 | 1516 | 1218 | 1496 | 1597 | 4311 | 1218 | 1496 | 1597 | 4311 | - - - | - - - | - - - | - - -
5/10/2026 | 4:30:00 AM | 285.76 | 283.19 | 281.4 | 494.31 | 487.32 | 491.21 | 5.4302 | 5.8158 | 5.7541 | 2.8101 | 1.434 | 1.432 | 1.428 | 1.496 | 1.437 | 1.397 | Over-range | 60 | 1222 | 1492 | 1587 | 4301 | - - - | - - - | - - - | - - - | 1222 | 1492 | 1587 | 4301 | 937 | 675 | -57 | 1554 | - - - | - - - | - - - | - - - | 937 | 675 | -57 | 1554 | 1550 | 1647 | 1619 | 4816 | # # # | # # # | # # # | # # # | 0.788 | 0.906 | 0.98 | 0.893 | # # # | # # # | # # # | - - - | 0.794 | 0.911 | 0.998 | 0.902 | - - - | 0.361 | 1.86 | 1.75 | 1.7 | 1.69 | 1.7 | 1.73 | 10.38 | 10.07 | 18.91 | 0 | - - - | - - - | - - - | - - - | 1550 | 1647 | 1619 | 4816 | Over-range | 954 | 696 | 321 | 2167 | 177 | 168 | 306 | 1505 | 1223 | 1493 | 1583 | 4299 | 1223 | 1493 | 1583 | 4299 | - - - | - - - | - - - | - - -
5/10/2026 | 4:45:00 AM | 285.78 | 283.23 | 281.4 | 494.32 | 487.42 | 491.2 | 5.3667 | 5.8411 | 5.7527 | 2.8165 | 1.433 | 1.431 | 1.427 | 1.499 | 1.437 | 1.396 | Over-range | 60 | 1205 | 1500 | 1587 | 4292 | - - - | - - - | - - - | - - - | 1205 | 1500 | 1587 | 4292 | 932 | 676 | -81 | 1526 | - - - | - - - | - - - | - - - | 932 | 676 | -81 | 1526 | 1534 | 1654 | 1619 | 4807 | # # # | # # # | # # # | # # # | 0.785 | 0.907 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.791 | 0.912 | 0.999 | 0.902 | - - - | 0.356 | 1.85 | 1.75 | 1.69 | 1.68 | 1.69 | 1.72 | 10.4 | 9.98 | 18.89 | 0 | - - - | - - - | - - - | - - - | 1534 | 1654 | 1619 | 4807 | Over-range | 949 | 697 | 317 | 2164 | 177 | 168 | 307 | 1534 | 1206 | 1502 | 1584 | 4291 | 1206 | 1502 | 1584 | 4291 | - - - | - - - | - - - | - - -
5/10/2026 | 5:00:00 AM | 285.27 | 282.73 | 281.02 | 493.41 | 486.65 | 490.48 | 5.3384 | 5.8177 | 5.7154 | 2.7813 | 1.435 | 1.432 | 1.429 | 1.492 | 1.436 | 1.393 | Over-range | 60.02 | 1200 | 1494 | 1575 | 4269 | - - - | - - - | - - - | - - - | 1200 | 1494 | 1575 | 4269 | 920 | 669 | -83 | 1504 | - - - | - - - | - - - | - - - | 920 | 669 | -83 | 1504 | 1523 | 1645 | 1606 | 4774 | # # # | # # # | # # # | # # # | 0.788 | 0.908 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.794 | 0.913 | 0.999 | 0.903 | - - - | 0.352 | 1.87 | 1.74 | 1.74 | 1.69 | 1.71 | 1.76 | 10.34 | 9.83 | 18.85 | 0 | - - - | - - - | - - - | - - - | 1523 | 1645 | 1606 | 4774 | Over-range | 937 | 689 | 315 | 2137 | 181 | 163 | 304 | 1518 | 1199 | 1496 | 1573 | 4268 | 1199 | 1496 | 1573 | 4268 | - - - | - - - | - - - | - - -
5/10/2026 | 5:15:00 AM | 285.77 | 283.31 | 281.65 | 494.35 | 487.71 | 491.42 | 5.3313 | 5.8049 | 5.7332 | 2.7775 | 1.434 | 1.431 | 1.429 | 1.49 | 1.433 | 1.36 | Over-range | 60.01 | 1199 | 1489 | 1584 | 4272 | - - - | - - - | - - - | - - - | 1199 | 1489 | 1584 | 4272 | 923 | 678 | -71 | 1529 | - - - | - - - | - - - | - - - | 923 | 678 | -71 | 1529 | 1524 | 1645 | 1615 | 4783 | # # # | # # # | # # # | # # # | 0.787 | 0.906 | 0.981 | 0.893 | # # # | # # # | # # # | - - - | 0.792 | 0.91 | 0.999 | 0.902 | - - - | 0.358 | 1.85 | 1.73 | 1.71 | 1.67 | 1.69 | 1.74 | 10.3 | 9.89 | 18.78 | 0 | - - - | - - - | - - - | - - - | 1524 | 1645 | 1615 | 4783 | Over-range | 940 | 698 | 311 | 2150 | 178 | 165 | 303 | 1511 | 1199 | 1491 | 1582 | 4272 | 1199 | 1491 | 1582 | 4272 | - - - | - - - | - - - | - - -
5/10/2026 | 5:30:00 AM | 285.76 | 283.21 | 281.66 | 494.2 | 487.66 | 491.44 | 4.8287 | 4.8972 | 5.4769 | 2.7836 | 1.434 | 1.43 | 1.428 | 1.487 | 1.476 | 1.4 | Over-range | 60.01 | 1113 | 1160 | 1505 | 3778 | - - - | - - - | - - - | - - - | 1113 | 1160 | 1505 | 3778 | 782 | 681 | 72 | 1535 | - - - | - - - | - - - | - - - | 782 | 681 | 72 | 1535 | 1373 | 1364 | 1541 | 4278 | # # # | # # # | # # # | # # # | 0.811 | 0.851 | 0.976 | 0.883 | # # # | # # # | # # # | - - - | 0.817 | 0.858 | 0.995 | 0.893 | - - - | 0.406 | 1.79 | 1.65 | 1.63 | 1.62 | 1.6 | 1.66 | 11.57 | 11.83 | 19.13 | 0 | - - - | - - - | - - - | - - - | 1373 | 1364 | 1541 | 4278 | Over-range | 802 | 699 | 330 | 2004 | 174 | 160 | 296 | 1280 | 1113 | 1162 | 1503 | 3778 | 1113 | 1162 | 1503 | 3778 | - - - | - - - | - - - | - - -
5/10/2026 | 5:45:00 AM | 285.61 | 283.06 | 281.48 | 494 | 487.35 | 491.14 | 4.6836 | 4.5787 | 5.3981 | 2.7797 | 1.433 | 1.429 | 1.427 | 1.487 | 1.441 | 1.404 | Over-range | 60 | 1093 | 1089 | 1486 | 3669 | - - - | - - - | - - - | - - - | 1093 | 1089 | 1486 | 3669 | 750 | 680 | 103 | 1533 | - - - | - - - | - - - | - - - | 750 | 680 | 103 | 1533 | 1337 | 1294 | 1519 | 4151 | # # # | # # # | # # # | # # # | 0.818 | 0.841 | 0.978 | 0.884 | # # # | # # # | # # # | - - - | 0.825 | 0.847 | 0.997 | 0.895 | - - - | 0.418 | 1.76 | 1.64 | 1.6 | 1.6 | 1.58 | 1.64 | 11.66 | 12.01 | 19.34 | 0 | - - - | - - - | - - - | - - - | 1337 | 1294 | 1519 | 4151 | Over-range | 770 | 699 | 315 | 1942 | 174 | 161 | 295 | 1192 | 1094 | 1087 | 1488 | 3669 | 1094 | 1087 | 1488 | 3669 | - - - | - - - | - - - | - - -
5/10/2026 | 6:00:00 AM | 285.75 | 283.24 | 281.72 | 494.24 | 487.73 | 491.5 | 4.7305 | 4.6601 | 5.4204 | 2.7793 | 1.434 | 1.429 | 1.427 | 1.488 | 1.429 | 1.398 | Over-range | 60.01 | 1102 | 1119 | 1495 | 3715 | - - - | - - - | - - - | - - - | 1102 | 1119 | 1495 | 3715 | 765 | 681 | 92 | 1537 | - - - | - - - | - - - | - - - | 765 | 681 | 92 | 1537 | 1352 | 1320 | 1527 | 4199 | # # # | # # # | # # # | # # # | 0.815 | 0.848 | 0.979 | 0.885 | # # # | # # # | # # # | - - - | 0.823 | 0.854 | 0.998 | 0.896 | - - - | 0.414 | 1.77 | 1.61 | 1.61 | 1.59 | 1.57 | 1.63 | 11.5 | 11.81 | 19.3 | 0 | - - - | - - - | - - - | - - - | 1352 | 1320 | 1527 | 4199 | Over-range | 783 | 700 | 310 | 1955 | 171 | 164 | 295 | 1208 | 1105 | 1116 | 1496 | 3716 | 1105 | 1116 | 1496 | 3716 | - - - | - - - | - - - | - - -
5/10/2026 | 6:15:00 AM | 285.74 | 283.31 | 281.7 | 494.29 | 487.84 | 491.4 | 4.8873 | 4.9569 | 5.4994 | 2.7804 | 1.433 | 1.43 | 1.427 | 1.492 | 1.418 | 1.375 | Over-range | 60 | 1126 | 1216 | 1519 | 3861 | - - - | - - - | - - - | - - - | 1126 | 1216 | 1519 | 3861 | 807 | 680 | 50 | 1537 | - - - | - - - | - - - | - - - | 807 | 680 | 50 | 1537 | 1396 | 1403 | 1549 | 4349 | # # # | # # # | # # # | # # # | 0.807 | 0.866 | 0.981 | 0.888 | # # # | # # # | # # # | - - - | 0.814 | 0.872 | 0.999 | 0.898 | - - - | 0.398 | 1.78 | 1.64 | 1.59 | 1.6 | 1.57 | 1.63 | 11.1 | 11.35 | 19.24 | 0 | - - - | - - - | - - - | - - - | 1396 | 1403 | 1549 | 4349 | Over-range | 825 | 700 | 304 | 2000 | 172 | 167 | 298 | 1280 | 1130 | 1213 | 1519 | 3862 | 1130 | 1213 | 1519 | 3862 | - - - | - - - | - - - | - - -
5/10/2026 | 6:30:00 AM | 285.43 | 282.96 | 281.39 | 493.72 | 487.21 | 490.92 | 5.5059 | 6.1647 | 5.8168 | 2.7585 | 1.434 | 1.429 | 1.428 | 1.498 | 1.449 | 1.322 | Over-range | 60.01 | 1226 | 1598 | 1603 | 4427 | - - - | - - - | - - - | - - - | 1226 | 1598 | 1603 | 4427 | 965 | 671 | -123 | 1513 | - - - | - - - | - - - | - - - | 965 | 671 | -123 | 1513 | 1571 | 1741 | 1636 | 4949 | # # # | # # # | # # # | # # # | 0.781 | 0.918 | 0.98 | 0.895 | # # # | # # # | # # # | - - - | 0.785 | 0.922 | 0.997 | 0.903 | - - - | 0.342 | 1.78 | 1.61 | 1.59 | 1.58 | 1.57 | 1.63 | 9.77 | 9.32 | 18.38 | 0 | - - - | - - - | - - - | - - - | 1571 | 1741 | 1636 | 4949 | Over-range | 982 | 691 | 327 | 2211 | 180 | 163 | 299 | 1611 | 1225 | 1599 | 1603 | 4427 | 1225 | 1599 | 1603 | 4427 | - - - | - - - | - - - | - - -
5/10/2026 | 6:45:00 AM | 285.55 | 283.1 | 281.52 | 493.96 | 487.43 | 491.13 | 5.3079 | 5.7723 | 5.7193 | 2.7685 | 1.434 | 1.43 | 1.428 | 1.495 | 1.435 | 1.326 | Over-range | 60.01 | 1195 | 1478 | 1581 | 4254 | - - - | - - - | - - - | - - - | 1195 | 1478 | 1581 | 4254 | 915 | 675 | -68 | 1521 | - - - | - - - | - - - | - - - | 915 | 675 | -68 | 1521 | 1515 | 1633 | 1610 | 4759 | # # # | # # # | # # # | # # # | 0.788 | 0.905 | 0.982 | 0.894 | # # # | # # # | # # # | - - - | 0.794 | 0.91 | 0.999 | 0.903 | - - - | 0.358 | 1.77 | 1.65 | 1.62 | 1.6 | 1.6 | 1.64 | 10.16 | 9.76 | 18.5 | 0 | - - - | - - - | - - - | - - - | 1515 | 1633 | 1610 | 4759 | Over-range | 932 | 694 | 307 | 2134 | 179 | 160 | 298 | 1495 | 1194 | 1480 | 1580 | 4253 | 1194 | 1480 | 1580 | 4253 | - - - | - - - | - - - | - - -
5/10/2026 | 7:00:00 AM | 285.58 | 283.18 | 281.65 | 493.98 | 487.73 | 491.24 | 5.2178 | 5.4609 | 5.65 | 2.7664 | 1.434 | 1.43 | 1.428 | 1.49 | 1.46 | 1.36 | Over-range | 60 | 1188 | 1353 | 1550 | 4092 | - - - | - - - | - - - | - - - | 1188 | 1353 | 1550 | 4092 | 874 | 678 | 15 | 1567 | - - - | - - - | - - - | - - - | 874 | 678 | 15 | 1567 | 1487 | 1530 | 1591 | 4608 | # # # | # # # | # # # | # # # | 0.799 | 0.885 | 0.975 | 0.888 | # # # | # # # | # # # | - - - | 0.799 | 0.885 | 0.978 | 0.889 | - - - | 0.383 | 1.79 | 1.65 | 1.61 | 1.6 | 1.59 | 1.65 | 10.45 | 10.66 | 18.79 | 0 | - - - | - - - | - - - | - - - | 1487 | 1530 | 1591 | 4608 | Over-range | 892 | 697 | 343 | 2115 | 175 | 162 | 299 | 1401 | 1198 | 1361 | 1563 | 4121 | 1198 | 1361 | 1563 | 4121 | - - - | - - - | - - - | - - -
5/10/2026 | 7:15:00 AM | 285.54 | 283.26 | 281.65 | 494.04 | 487.79 | 491.16 | 4.6171 | 4.4646 | 5.3719 | 2.7779 | 1.433 | 1.43 | 1.428 | 1.486 | 1.45 | 1.414 | Over-range | 60 | 1082 | 1048 | 1478 | 3608 | - - - | - - - | - - - | - - - | 1082 | 1048 | 1478 | 3608 | 732 | 682 | 123 | 1537 | - - - | - - - | - - - | - - - | 732 | 682 | 123 | 1537 | 1318 | 1262 | 1513 | 4092 | # # # | # # # | # # # | # # # | 0.821 | 0.83 | 0.977 | 0.882 | # # # | # # # | # # # | - - - | 0.828 | 0.837 | 0.996 | 0.892 | - - - | 0.426 | 1.77 | 1.64 | 1.59 | 1.59 | 1.57 | 1.63 | 11.79 | 12.34 | 19.36 | 0 | - - - | - - - | - - - | - - - | 1318 | 1262 | 1513 | 4092 | Over-range | 751 | 701 | 322 | 1931 | 169 | 161 | 294 | 1167 | 1084 | 1048 | 1476 | 3608 | 1084 | 1048 | 1476 | 3608 | - - - | - - - | - - - | - - -
5/10/2026 | 7:30:00 AM | 285.34 | 283.03 | 281.39 | 493.7 | 487.31 | 490.78 | 4.797 | 4.7912 | 5.4322 | 2.7687 | 1.433 | 1.43 | 1.428 | 1.488 | 1.424 | 1.389 | Over-range | 60 | 1112 | 1163 | 1498 | 3772 | - - - | - - - | - - - | - - - | 1112 | 1163 | 1498 | 3772 | 780 | 676 | 69 | 1526 | - - - | - - - | - - - | - - - | 780 | 676 | 69 | 1526 | 1368 | 1355 | 1528 | 4252 | # # # | # # # | # # # | # # # | 0.812 | 0.858 | 0.98 | 0.887 | # # # | # # # | # # # | - - - | 0.819 | 0.864 | 0.999 | 0.897 | - - - | 0.404 | 1.77 | 1.64 | 1.59 | 1.6 | 1.57 | 1.64 | 11.21 | 11.42 | 19.28 | 0 | - - - | - - - | - - - | - - - | 1368 | 1355 | 1528 | 4252 | Over-range | 798 | 695 | 304 | 1962 | 168 | 163 | 295 | 1233 | 1115 | 1161 | 1497 | 3773 | 1115 | 1161 | 1497 | 3773 | - - - | - - - | - - - | - - -
5/10/2026 | 7:45:00 AM | 285 | 282.66 | 281.1 | 493.02 | 486.8 | 490.26 | 4.8127 | 4.8244 | 5.4572 | 2.7708 | 1.433 | 1.43 | 1.428 | 1.489 | 1.416 | 1.383 | Over-range | 60 | 1114 | 1176 | 1505 | 3795 | - - - | - - - | - - - | - - - | 1114 | 1176 | 1505 | 3795 | 782 | 671 | 62 | 1515 | - - - | - - - | - - - | - - - | 782 | 671 | 62 | 1515 | 1372 | 1364 | 1534 | 4269 | # # # | # # # | # # # | # # # | 0.812 | 0.862 | 0.981 | 0.889 | # # # | # # # | # # # | - - - | 0.82 | 0.868 | 0.999 | 0.899 | - - - | 0.399 | 1.77 | 1.62 | 1.61 | 1.6 | 1.57 | 1.63 | 11.1 | 11.28 | 19.02 | 0 | - - - | - - - | - - - | - - - | 1372 | 1364 | 1534 | 4269 | Over-range | 800 | 690 | 299 | 1956 | 170 | 162 | 292 | 1238 | 1117 | 1173 | 1506 | 3796 | 1117 | 1173 | 1506 | 3796 | - - - | - - - | - - - | - - -
5/10/2026 | 8:00:00 AM | 284.91 | 282.59 | 281.04 | 492.86 | 486.69 | 490.14 | 5.24 | 5.6633 | 5.6655 | 2.7535 | 1.433 | 1.43 | 1.429 | 1.495 | 1.441 | 1.335 | Over-range | 60.01 | 1182 | 1438 | 1561 | 4181 | - - - | - - - | - - - | - - - | 1182 | 1438 | 1561 | 4181 | 893 | 665 | -54 | 1503 | - - - | - - - | - - - | - - - | 893 | 665 | -54 | 1503 | 1491 | 1594 | 1592 | 4677 | # # # | # # # | # # # | # # # | 0.793 | 0.902 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.799 | 0.907 | 0.998 | 0.903 | - - - | 0.36 | 1.76 | 1.62 | 1.61 | 1.6 | 1.57 | 1.63 | 10.15 | 10.02 | 18.71 | 0 | - - - | - - - | - - - | - - - | 1491 | 1594 | 1592 | 4677 | Over-range | 909 | 686 | 309 | 2096 | 167 | 167 | 296 | 1457 | 1186 | 1437 | 1559 | 4182 | 1186 | 1437 | 1559 | 4182 | - - - | - - - | - - - | - - -
5/10/2026 | 8:15:00 AM | 284.74 | 282.42 | 280.85 | 492.6 | 486.34 | 489.86 | 5.4819 | 5.662 | 5.8135 | 3.5317 | 1.433 | 1.43 | 1.428 | 1.498 | 1.44 | 1.312 | Over-range | 60 | 1221 | 1376 | 1600 | 4197 | - - - | - - - | - - - | - - - | 1221 | 1376 | 1600 | 4197 | 955 | 727 | -122 | 1559 | - - - | - - - | - - - | - - - | 955 | 727 | -122 | 1559 | 1560 | 1580 | 1632 | 4773 | # # # | # # # | # # # | # # # | 0.783 | 0.871 | 0.98 | 0.879 | # # # | # # # | # # # | - - - | 0.788 | 0.876 | 0.996 | 0.888 | - - - | 0.372 | 1.74 | 1.63 | 1.59 | 1.59 | 1.55 | 1.62 | 9.66 | 11.65 | 18.11 | 0 | - - - | - - - | - - - | - - - | 1560 | 1580 | 1632 | 4773 | Over-range | 971 | 749 | 322 | 2265 | 176 | 179 | 294 | 1641 | 1220 | 1377 | 1599 | 4197 | 1220 | 1377 | 1599 | 4197 | - - - | - - - | - - - | - - -
5/10/2026 | 8:30:00 AM | 284.42 | 282.12 | 280.52 | 492.03 | 485.84 | 489.27 | 5.2984 | 4.7336 | 5.6889 | 4.1432 | 1.434 | 1.43 | 1.429 | 1.496 | 1.417 | 1.317 | Over-range | 60.02 | 1193 | 1063 | 1567 | 3823 | - - - | - - - | - - - | - - - | 1193 | 1063 | 1567 | 3823 | 905 | 784 | -78 | 1610 | - - - | - - - | - - - | - - - | 905 | 784 | -78 | 1610 | 1507 | 1335 | 1596 | 4438 | # # # | # # # | # # # | # # # | 0.792 | 0.796 | 0.982 | 0.861 | # # # | # # # | # # # | - - - | 0.797 | 0.806 | 0.999 | 0.872 | - - - | 0.421 | 1.75 | 1.62 | 1.57 | 1.58 | 1.55 | 1.61 | 9.93 | 14.45 | 18.43 | 0 | - - - | - - - | - - - | - - - | 1507 | 1335 | 1596 | 4438 | Over-range | 921 | 808 | 304 | 2254 | 169 | 194 | 293 | 1578 | 1194 | 1065 | 1564 | 3823 | 1194 | 1065 | 1564 | 3823 | - - - | - - - | - - - | - - -
5/10/2026 | 8:45:00 AM | 284.35 | 282.01 | 280.51 | 491.86 | 485.71 | 489.23 | 4.8446 | 4.1038 | 5.4751 | 4.1516 | 1.434 | 1.431 | 1.429 | 1.489 | 1.458 | 1.388 | Over-range | 60 | 1115 | 763 | 1499 | 3377 | - - - | - - - | - - - | - - - | 1115 | 763 | 1499 | 3377 | 775 | 788 | 53 | 1616 | - - - | - - - | - - - | - - - | 775 | 788 | 53 | 1616 | 1370 | 1138 | 1534 | 4042 | # # # | # # # | # # # | # # # | 0.814 | 0.671 | 0.977 | 0.836 | # # # | # # # | # # # | - - - | 0.82 | 0.68 | 0.995 | 0.847 | - - - | 0.479 | 1.75 | 1.64 | 1.59 | 1.59 | 1.56 | 1.62 | 11.13 | 16.67 | 18.79 | 0 | - - - | - - - | - - - | - - - | 1370 | 1138 | 1534 | 4042 | Over-range | 794 | 810 | 324 | 2209 | 168 | 186 | 289 | 1505 | 1115 | 764 | 1497 | 3377 | 1115 | 764 | 1497 | 3377 | - - - | - - - | - - - | - - -
5/10/2026 | 9:00:00 AM | 283.97 | 281.65 | 280.1 | 491.27 | 484.99 | 488.57 | 4.7969 | 3.9468 | 5.4212 | 4.1422 | 1.433 | 1.43 | 1.429 | 1.489 | 1.453 | 1.385 | Over-range | 60 | 1111 | 753 | 1488 | 3352 | - - - | - - - | - - - | - - - | 1111 | 753 | 1488 | 3352 | 766 | 783 | 53 | 1602 | - - - | - - - | - - - | - - - | 766 | 783 | 53 | 1602 | 1360 | 1107 | 1518 | 3985 | # # # | # # # | # # # | # # # | 0.817 | 0.68 | 0.98 | 0.841 | # # # | # # # | # # # | - - - | 0.823 | 0.69 | 0.998 | 0.852 | - - - | 0.478 | 1.72 | 1.62 | 1.56 | 1.56 | 1.54 | 1.6 | 10.96 | 16.68 | 18.97 | 0 | - - - | - - - | - - - | - - - | 1360 | 1107 | 1518 | 3985 | Over-range | 785 | 804 | 301 | 2154 | 170 | 185 | 289 | 1439 | 1110 | 754 | 1488 | 3352 | 1110 | 754 | 1488 | 3352 | - - - | - - - | - - - | - - -
5/10/2026 | 9:15:00 AM | 283.53 | 281.08 | 279.65 | 490.32 | 484.11 | 487.86 | 4.9104 | 4.087 | 5.4888 | 4.1478 | 1.433 | 1.431 | 1.429 | 1.49 | 1.441 | 1.364 | Over-range | 59.99 | 1130 | 828 | 1508 | 3465 | - - - | - - - | - - - | - - - | 1130 | 828 | 1508 | 3465 | 796 | 774 | 17 | 1587 | - - - | - - - | - - - | - - - | 796 | 774 | 17 | 1587 | 1392 | 1148 | 1535 | 4075 | # # # | # # # | # # # | # # # | 0.812 | 0.721 | 0.982 | 0.85 | # # # | # # # | # # # | - - - | 0.818 | 0.73 | 1 | 0.861 | - - - | 0.458 | 1.71 | 1.62 | 1.57 | 1.57 | 1.56 | 1.6 | 10.57 | 15.95 | 18.66 | 0 | - - - | - - - | - - - | - - - | 1392 | 1148 | 1535 | 4075 | Over-range | 813 | 795 | 288 | 2144 | 163 | 184 | 287 | 1442 | 1131 | 829 | 1504 | 3465 | 1131 | 829 | 1504 | 3465 | - - - | - - - | - - - | - - -
5/10/2026 | 9:30:00 AM | 283.16 | 280.76 | 279.31 | 489.75 | 483.56 | 487.21 | 5.4238 | 4.811 | 5.7339 | 4.1319 | 1.433 | 1.431 | 1.43 | 1.493 | 1.424 | 1.344 | Over-range | 60 | 1221 | 1085 | 1569 | 3875 | - - - | - - - | - - - | - - - | 1221 | 1085 | 1569 | 3875 | 907 | 765 | -75 | 1597 | - - - | - - - | - - - | - - - | 907 | 765 | -75 | 1597 | 1531 | 1345 | 1601 | 4477 | # # # | # # # | # # # | # # # | 0.798 | 0.807 | 0.98 | 0.866 | # # # | # # # | # # # | - - - | 0.795 | 0.809 | 0.988 | 0.867 | - - - | 0.412 | 1.71 | 1.64 | 1.6 | 1.58 | 1.57 | 1.62 | 9.79 | 14.24 | 18.3 | 0 | - - - | - - - | - - - | - - - | 1531 | 1345 | 1601 | 4477 | Over-range | 923 | 788 | 316 | 2240 | 166 | 185 | 290 | 1563 | 1232 | 1094 | 1576 | 3903 | 1232 | 1094 | 1576 | 3903 | - - - | - - - | - - - | - - -
5/10/2026 | 9:45:00 AM | 282.97 | 280.5 | 279.04 | 489.4 | 483.02 | 486.86 | 5.5002 | 5.156 | 5.8738 | 4.1316 | 1.433 | 1.43 | 1.429 | 1.499 | 1.422 | 1.331 | Over-range | 60.01 | 1227 | 1210 | 1604 | 4041 | - - - | - - - | - - - | - - - | 1227 | 1210 | 1604 | 4041 | 941 | 760 | -164 | 1537 | - - - | - - - | - - - | - - - | 941 | 760 | -164 | 1537 | 1555 | 1443 | 1639 | 4637 | # # # | # # # | # # # | # # # | 0.789 | 0.839 | 0.979 | 0.872 | # # # | # # # | # # # | - - - | 0.794 | 0.847 | 0.994 | 0.881 | - - - | 0.38 | 1.7 | 1.65 | 1.58 | 1.56 | 1.57 | 1.6 | 9.52 | 13.04 | 17.56 | 0 | - - - | - - - | - - - | - - - | 1555 | 1443 | 1639 | 4637 | Over-range | 956 | 783 | 334 | 2274 | 169 | 189 | 288 | 1675 | 1228 | 1213 | 1601 | 4041 | 1228 | 1213 | 1601 | 4041 | - - - | - - - | - - - | - - -
5/10/2026 | 10:00:00 AM | 282.57 | 280.09 | 278.72 | 488.62 | 482.43 | 486.25 | 5.3049 | 4.8319 | 5.7258 | 4.1292 | 1.433 | 1.431 | 1.429 | 1.493 | 1.413 | 1.325 | Over-range | 60.02 | 1190 | 1108 | 1565 | 3862 | - - - | - - - | - - - | - - - | 1190 | 1108 | 1565 | 3862 | 897 | 754 | -129 | 1521 | - - - | - - - | - - - | - - - | 897 | 754 | -129 | 1521 | 1499 | 1353 | 1596 | 4448 | # # # | # # # | # # # | # # # | 0.794 | 0.819 | 0.98 | 0.868 | # # # | # # # | # # # | - - - | 0.799 | 0.827 | 0.996 | 0.878 | - - - | 0.394 | 1.68 | 1.64 | 1.59 | 1.55 | 1.56 | 1.6 | 9.63 | 13.63 | 17.95 | 0 | - - - | - - - | - - - | - - - | 1499 | 1353 | 1596 | 4448 | Over-range | 912 | 777 | 314 | 2207 | 164 | 187 | 286 | 1599 | 1191 | 1109 | 1562 | 3862 | 1191 | 1109 | 1562 | 3862 | - - - | - - - | - - - | - - -
5/10/2026 | 10:15:00 AM | 281.99 | 279.47 | 278.09 | 487.56 | 481.33 | 485.25 | 5.0178 | 4.3372 | 5.5713 | 4.1321 | 1.433 | 1.431 | 1.429 | 1.489 | 1.427 | 1.332 | Over-range | 60.01 | 1143 | 935 | 1522 | 3599 | - - - | - - - | - - - | - - - | 1143 | 935 | 1522 | 3599 | 818 | 747 | -56 | 1508 | - - - | - - - | - - - | - - - | 818 | 747 | -56 | 1508 | 1415 | 1211 | 1549 | 4175 | # # # | # # # | # # # | # # # | 0.808 | 0.772 | 0.983 | 0.862 | # # # | # # # | # # # | - - - | 0.813 | 0.78 | 0.999 | 0.872 | - - - | 0.419 | 1.67 | 1.61 | 1.55 | 1.52 | 1.55 | 1.57 | 10.1 | 14.57 | 18.02 | 0 | - - - | - - - | - - - | - - - | 1415 | 1211 | 1549 | 4175 | Over-range | 834 | 769 | 287 | 2115 | 162 | 182 | 280 | 1482 | 1145 | 933 | 1523 | 3601 | 1145 | 933 | 1523 | 3601 | - - - | - - - | - - - | - - -
5/10/2026 | 10:30:00 AM | 281.71 | 278.99 | 277.77 | 486.89 | 480.53 | 484.85 | 5.067 | 4.4238 | 5.5787 | 4.1202 | 1.432 | 1.431 | 1.429 | 1.491 | 1.424 | 1.331 | Over-range | 60.01 | 1150 | 966 | 1521 | 3637 | - - - | - - - | - - - | - - - | 1150 | 966 | 1521 | 3637 | 829 | 740 | -74 | 1494 | - - - | - - - | - - - | - - - | 829 | 740 | -74 | 1494 | 1427 | 1232 | 1549 | 4208 | # # # | # # # | # # # | # # # | 0.806 | 0.784 | 0.982 | 0.864 | # # # | # # # | # # # | - - - | 0.812 | 0.792 | 0.999 | 0.875 | - - - | 0.411 | 1.65 | 1.6 | 1.55 | 1.51 | 1.55 | 1.55 | 9.98 | 14.46 | 18.05 | 0 | - - - | - - - | - - - | - - - | 1427 | 1232 | 1549 | 4208 | Over-range | 844 | 763 | 293 | 2116 | 161 | 185 | 281 | 1498 | 1153 | 963 | 1522 | 3638 | 1153 | 963 | 1522 | 3638 | - - - | - - - | - - - | - - -
5/10/2026 | 10:45:00 AM | 281.34 | 278.54 | 277.36 | 486.16 | 479.75 | 484.22 | 5.4969 | 5.1816 | 5.852 | 4.1178 | 1.432 | 1.431 | 1.429 | 1.496 | 1.429 | 1.327 | Over-range | 60.01 | 1218 | 1229 | 1587 | 4033 | - - - | - - - | - - - | - - - | 1218 | 1229 | 1587 | 4033 | 940 | 732 | -192 | 1478 | - - - | - - - | - - - | - - - | 940 | 732 | -192 | 1478 | 1546 | 1443 | 1623 | 4612 | # # # | # # # | # # # | # # # | 0.787 | 0.852 | 0.978 | 0.875 | # # # | # # # | # # # | - - - | 0.792 | 0.859 | 0.992 | 0.883 | - - - | 0.366 | 1.61 | 1.58 | 1.53 | 1.48 | 1.53 | 1.53 | 9.13 | 12.64 | 17.22 | 0 | - - - | - - - | - - - | - - - | 1546 | 1443 | 1623 | 4612 | Over-range | 953 | 756 | 340 | 2237 | 161 | 189 | 280 | 1679 | 1221 | 1227 | 1586 | 4035 | 1221 | 1227 | 1586 | 4035 | - - - | - - - | - - - | - - -
5/10/2026 | 11:00:00 AM | 281 | 278.16 | 277 | 485.51 | 479.13 | 483.61 | 4.9873 | 4.3797 | 5.5364 | 4.1198 | 1.432 | 1.431 | 1.429 | 1.492 | 1.441 | 1.353 | Over-range | 60.01 | 1131 | 898 | 1498 | 3528 | - - - | - - - | - - - | - - - | 1131 | 898 | 1498 | 3528 | 794 | 730 | -51 | 1472 | - - - | - - - | - - - | - - - | 794 | 730 | -51 | 1472 | 1393 | 1196 | 1532 | 4121 | # # # | # # # | # # # | # # # | 0.812 | 0.751 | 0.978 | 0.856 | # # # | # # # | # # # | - - - | 0.818 | 0.759 | 0.995 | 0.866 | - - - | 0.417 | 1.58 | 1.57 | 1.51 | 1.46 | 1.5 | 1.51 | 10.21 | 14.81 | 17.83 | 0 | - - - | - - - | - - - | - - - | 1393 | 1196 | 1532 | 4121 | Over-range | 810 | 751 | 316 | 2119 | 155 | 175 | 274 | 1522 | 1134 | 899 | 1496 | 3528 | 1134 | 899 | 1496 | 3528 | - - - | - - - | - - - | - - -
5/10/2026 | 11:15:00 AM | 280.69 | 277.85 | 276.71 | 485.01 | 478.56 | 483.12 | 4.7058 | 3.8315 | 5.3884 | 4.1204 | 1.433 | 1.431 | 1.429 | 1.492 | 1.443 | 1.368 | Over-range | 60 | 1091 | 746 | 1464 | 3302 | - - - | - - - | - - - | - - - | 1091 | 746 | 1464 | 3302 | 725 | 727 | 14 | 1466 | - - - | - - - | - - - | - - - | 725 | 727 | 14 | 1466 | 1320 | 1060 | 1491 | 3871 | # # # | # # # | # # # | # # # | 0.827 | 0.704 | 0.982 | 0.853 | # # # | # # # | # # # | - - - | 0.833 | 0.713 | 0.999 | 0.864 | - - - | 0.444 | 1.61 | 1.58 | 1.5 | 1.47 | 1.51 | 1.52 | 10.53 | 16.04 | 18.17 | 0 | - - - | - - - | - - - | - - - | 1320 | 1060 | 1491 | 3871 | Over-range | 742 | 748 | 279 | 2019 | 155 | 175 | 273 | 1388 | 1094 | 745 | 1464 | 3303 | 1094 | 745 | 1464 | 3303 | - - - | - - - | - - - | - - -
5/10/2026 | 11:30:00 AM | 280.58 | 277.65 | 276.48 | 484.79 | 478.11 | 482.84 | 4.915 | 4.0031 | 5.4678 | 4.118 | 1.433 | 1.432 | 1.429 | 1.489 | 1.436 | 1.357 | Over-range | 59.99 | 1133 | 824 | 1484 | 3441 | - - - | - - - | - - - | - - - | 1133 | 824 | 1484 | 3441 | 766 | 723 | 1 | 1490 | - - - | - - - | - - - | - - - | 766 | 723 | 1 | 1490 | 1377 | 1111 | 1512 | 3999 | # # # | # # # | # # # | # # # | 0.823 | 0.742 | 0.982 | 0.86 | # # # | # # # | # # # | - - - | 0.821 | 0.744 | 0.983 | 0.861 | - - - | 0.433 | 1.6 | 1.57 | 1.48 | 1.46 | 1.51 | 1.5 | 10.04 | 15.2 | 17.86 | 0 | - - - | - - - | - - - | - - - | 1377 | 1111 | 1512 | 3999 | Over-range | 782 | 744 | 284 | 2039 | 157 | 176 | 272 | 1386 | 1145 | 827 | 1501 | 3473 | 1145 | 827 | 1501 | 3473 | - - - | - - - | - - - | - - -
5/10/2026 | 11:45:00 AM | 280.05 | 277.05 | 275.97 | 483.74 | 477.21 | 481.97 | 5.2078 | 4.6731 | 5.6615 | 4.1121 | 1.432 | 1.431 | 1.429 | 1.494 | 1.43 | 1.318 | Over-range | 60 | 1170 | 1054 | 1531 | 3755 | - - - | - - - | - - - | - - - | 1170 | 1054 | 1531 | 3755 | 853 | 712 | -128 | 1436 | - - - | - - - | - - - | - - - | 853 | 712 | -128 | 1436 | 1457 | 1289 | 1562 | 4307 | # # # | # # # | # # # | # # # | 0.803 | 0.818 | 0.98 | 0.872 | # # # | # # # | # # # | - - - | 0.809 | 0.826 | 0.995 | 0.881 | - - - | 0.383 | 1.59 | 1.56 | 1.5 | 1.45 | 1.5 | 1.49 | 9.43 | 13.74 | 17.42 | 0 | - - - | - - - | - - - | - - - | 1457 | 1289 | 1562 | 4307 | Over-range | 867 | 735 | 308 | 2108 | 156 | 182 | 273 | 1541 | 1174 | 1052 | 1531 | 3757 | 1174 | 1052 | 1531 | 3757 | - - - | - - - | - - - | - - -
5/10/2026 | 12:00:00 PM | 281.64 | 278.68 | 277.54 | 486.58 | 479.94 | 484.69 | 5.7336 | 5.6259 | 5.987 | 4.1053 | 1.432 | 1.431 | 1.429 | 1.5 | 1.456 | 1.312 | Over-range | 60.01 | 1255 | 1371 | 1617 | 4243 | - - - | - - - | - - - | - - - | 1255 | 1371 | 1617 | 4243 | 1002 | 731 | -255 | 1477 | - - - | - - - | - - - | - - - | 1002 | 731 | -255 | 1477 | 1614 | 1566 | 1661 | 4842 | # # # | # # # | # # # | # # # | 0.777 | 0.875 | 0.973 | 0.876 | # # # | # # # | # # # | - - - | 0.782 | 0.881 | 0.987 | 0.884 | - - - | 0.348 | 1.57 | 1.55 | 1.46 | 1.44 | 1.47 | 1.46 | 8.68 | 11.98 | 16.91 | 0 | - - - | - - - | - - - | - - - | 1614 | 1566 | 1661 | 4842 | Over-range | 1015 | 756 | 380 | 2332 | 165 | 193 | 280 | 1805 | 1258 | 1368 | 1618 | 4245 | 1258 | 1368 | 1618 | 4245 | - - - | - - - | - - - | - - -
5/10/2026 | 12:15:00 PM | 282.35 | 279.37 | 278.24 | 487.8 | 481.13 | 485.91 | 5.5281 | 5.2436 | 5.8656 | 4.1137 | 1.433 | 1.432 | 1.429 | 1.499 | 1.437 | 1.288 | Over-range | 60 | 1224 | 1244 | 1595 | 4063 | - - - | - - - | - - - | - - - | 1224 | 1244 | 1595 | 4063 | 954 | 742 | -192 | 1503 | - - - | - - - | - - - | - - - | 954 | 742 | -192 | 1503 | 1560 | 1462 | 1632 | 4654 | # # # | # # # | # # # | # # # | 0.784 | 0.851 | 0.978 | 0.873 | # # # | # # # | # # # | - - - | 0.789 | 0.858 | 0.992 | 0.881 | - - - | 0.37 | 1.57 | 1.55 | 1.45 | 1.45 | 1.45 | 1.46 | 9.04 | 12.79 | 17.26 | 0 | - - - | - - - | - - - | - - - | 1560 | 1462 | 1632 | 4654 | Over-range | 968 | 767 | 343 | 2271 | 160 | 193 | 281 | 1701 | 1227 | 1243 | 1594 | 4065 | 1227 | 1243 | 1594 | 4065 | - - - | - - - | - - - | - - -
5/10/2026 | 12:30:00 PM | 282.17 | 279.3 | 278.14 | 487.55 | 481.05 | 485.64 | 5.0026 | 4.3125 | 5.5514 | 4.1184 | 1.432 | 1.431 | 1.428 | 1.494 | 1.43 | 1.33 | Over-range | 59.99 | 1141 | 928 | 1518 | 3586 | - - - | - - - | - - - | - - - | 1141 | 928 | 1518 | 3586 | 817 | 746 | -54 | 1508 | - - - | - - - | - - - | - - - | 817 | 746 | -54 | 1508 | 1411 | 1204 | 1544 | 4159 | # # # | # # # | # # # | # # # | 0.808 | 0.77 | 0.983 | 0.862 | # # # | # # # | # # # | - - - | 0.814 | 0.78 | 0.999 | 0.872 | - - - | 0.42 | 1.56 | 1.53 | 1.41 | 1.43 | 1.42 | 1.43 | 9.91 | 14.72 | 17.85 | 0 | - - - | - - - | - - - | - - - | 1411 | 1204 | 1544 | 4159 | Over-range | 831 | 767 | 281 | 2107 | 156 | 180 | 275 | 1472 | 1143 | 929 | 1516 | 3587 | 1143 | 929 | 1516 | 3587 | - - - | - - - | - - - | - - -
5/10/2026 | 12:45:00 PM | 281.92 | 279.08 | 277.89 | 487.15 | 480.65 | 485.19 | 5.5011 | 5.2054 | 5.8496 | 4.1145 | 1.433 | 1.432 | 1.429 | 1.499 | 1.441 | 1.285 | Over-range | 60 | 1218 | 1228 | 1589 | 4034 | - - - | - - - | - - - | - - - | 1218 | 1228 | 1589 | 4034 | 944 | 739 | -188 | 1494 | - - - | - - - | - - - | - - - | 944 | 739 | -188 | 1494 | 1549 | 1448 | 1625 | 4622 | # # # | # # # | # # # | # # # | 0.786 | 0.848 | 0.978 | 0.873 | # # # | # # # | # # # | - - - | 0.791 | 0.856 | 0.992 | 0.881 | - - - | 0.37 | 1.6 | 1.52 | 1.44 | 1.44 | 1.45 | 1.47 | 9.01 | 12.92 | 17.24 | 0 | - - - | - - - | - - - | - - - | 1549 | 1448 | 1625 | 4622 | Over-range | 957 | 763 | 341 | 2256 | 158 | 190 | 279 | 1688 | 1220 | 1229 | 1585 | 4034 | 1220 | 1229 | 1585 | 4034 | - - - | - - - | - - - | - - -
5/10/2026 | 1:00:00 PM | 281.67 | 278.81 | 277.66 | 486.7 | 480.2 | 484.78 | 5.6375 | 5.2161 | 5.8503 | 4.1081 | 1.433 | 1.432 | 1.43 | 1.495 | 1.44 | 1.289 | Over-range | 60 | 1250 | 1236 | 1590 | 4076 | - - - | - - - | - - - | - - - | 1250 | 1236 | 1590 | 4076 | 959 | 735 | -160 | 1533 | - - - | - - - | - - - | - - - | 959 | 735 | -160 | 1533 | 1585 | 1451 | 1624 | 4660 | # # # | # # # | # # # | # # # | 0.789 | 0.852 | 0.979 | 0.875 | # # # | # # # | # # # | - - - | 0.785 | 0.852 | 0.972 | 0.872 | - - - | 0.376 | 1.62 | 1.56 | 1.46 | 1.46 | 1.48 | 1.49 | 8.92 | 12.83 | 17.26 | 0 | - - - | - - - | - - - | - - - | 1585 | 1451 | 1624 | 4660 | Over-range | 974 | 759 | 330 | 2259 | 163 | 185 | 278 | 1654 | 1262 | 1245 | 1617 | 4124 | 1262 | 1245 | 1617 | 4124 | - - - | - - - | - - - | - - -
5/10/2026 | 1:15:00 PM | 281.62 | 278.8 | 277.58 | 486.67 | 480.12 | 484.67 | 4.6591 | 3.7518 | 5.3392 | 4.1186 | 1.434 | 1.433 | 1.431 | 1.488 | 1.457 | 1.395 | Over-range | 60.01 | 1085 | 677 | 1451 | 3213 | - - - | - - - | - - - | - - - | 1085 | 677 | 1451 | 3213 | 710 | 740 | 64 | 1514 | - - - | - - - | - - - | - - - | 710 | 740 | 64 | 1514 | 1308 | 1034 | 1481 | 3823 | # # # | # # # | # # # | # # # | 0.83 | 0.655 | 0.979 | 0.84 | # # # | # # # | # # # | - - - | 0.836 | 0.664 | 0.997 | 0.852 | - - - | 0.471 | 1.61 | 1.6 | 1.48 | 1.46 | 1.49 | 1.5 | 10.76 | 16.6 | 18.16 | 0 | - - - | - - - | - - - | - - - | 1308 | 1034 | 1481 | 3823 | Over-range | 728 | 761 | 297 | 2065 | 159 | 176 | 271 | 1403 | 1086 | 676 | 1453 | 3214 | 1086 | 676 | 1453 | 3214 | - - - | - - - | - - - | - - -
5/10/2026 | 1:30:00 PM | 281.38 | 278.64 | 277.4 | 486.27 | 479.9 | 484.27 | 4.7853 | 3.9587 | 5.406 | 4.1195 | 1.434 | 1.433 | 1.431 | 1.49 | 1.45 | 1.377 | Over-range | 60 | 1104 | 751 | 1467 | 3322 | - - - | - - - | - - - | - - - | 1104 | 751 | 1467 | 3322 | 741 | 738 | 30 | 1509 | - - - | - - - | - - - | - - - | 741 | 738 | 30 | 1509 | 1341 | 1087 | 1498 | 3926 | # # # | # # # | # # # | # # # | 0.824 | 0.691 | 0.979 | 0.846 | # # # | # # # | # # # | - - - | 0.829 | 0.701 | 0.996 | 0.857 | - - - | 0.454 | 1.62 | 1.61 | 1.52 | 1.49 | 1.52 | 1.53 | 10.55 | 16.21 | 18.14 | 0 | - - - | - - - | - - - | - - - | 1341 | 1087 | 1498 | 3926 | Over-range | 758 | 758 | 300 | 2083 | 159 | 176 | 274 | 1434 | 1104 | 752 | 1466 | 3322 | 1104 | 752 | 1466 | 3322 | - - - | - - - | - - - | - - -
5/10/2026 | 1:45:00 PM | 280.94 | 278.19 | 276.95 | 485.57 | 479.05 | 483.51 | 4.9362 | 4.1478 | 5.4777 | 4.1124 | 1.434 | 1.433 | 1.431 | 1.49 | 1.434 | 1.351 | Over-range | 59.99 | 1130 | 857 | 1489 | 3476 | - - - | - - - | - - - | - - - | 1130 | 857 | 1489 | 3476 | 783 | 731 | -19 | 1494 | - - - | - - - | - - - | - - - | 783 | 731 | -19 | 1494 | 1384 | 1146 | 1516 | 4047 | # # # | # # # | # # # | # # # | 0.816 | 0.747 | 0.982 | 0.859 | # # # | # # # | # # # | - - - | 0.822 | 0.756 | 0.999 | 0.869 | - - - | 0.43 | 1.64 | 1.62 | 1.52 | 1.5 | 1.53 | 1.54 | 10.05 | 15.32 | 18 | 0 | - - - | - - - | - - - | - - - | 1384 | 1146 | 1516 | 4047 | Over-range | 799 | 752 | 286 | 2071 | 161 | 178 | 274 | 1433 | 1130 | 857 | 1489 | 3476 | 1130 | 857 | 1489 | 3476 | - - - | - - - | - - - | - - -
5/10/2026 | 2:00:00 PM | 280.54 | 277.79 | 276.55 | 484.86 | 478.35 | 482.83 | 5.2923 | 4.7297 | 5.6777 | 4.1069 | 1.435 | 1.434 | 1.431 | 1.492 | 1.422 | 1.296 | Over-range | 60 | 1188 | 1081 | 1541 | 3810 | - - - | - - - | - - - | - - - | 1188 | 1081 | 1541 | 3810 | 876 | 725 | -120 | 1479 | - - - | - - - | - - - | - - - | 876 | 725 | -120 | 1479 | 1485 | 1314 | 1570 | 4369 | # # # | # # # | # # # | # # # | 0.8 | 0.823 | 0.982 | 0.872 | # # # | # # # | # # # | - - - | 0.805 | 0.831 | 0.997 | 0.881 | - - - | 0.388 | 1.61 | 1.61 | 1.5 | 1.48 | 1.51 | 1.53 | 9.26 | 13.59 | 17.44 | 0 | - - - | - - - | - - - | - - - | 1485 | 1314 | 1570 | 4369 | Over-range | 891 | 747 | 300 | 2137 | 160 | 180 | 274 | 1542 | 1188 | 1083 | 1539 | 3810 | 1188 | 1083 | 1539 | 3810 | - - - | - - - | - - - | - - -
5/10/2026 | 2:15:00 PM | 280.67 | 277.88 | 276.74 | 484.96 | 478.63 | 483.16 | 4.6566 | 3.7372 | 5.3342 | 4.1157 | 1.434 | 1.433 | 1.431 | 1.49 | 1.452 | 1.391 | Over-range | 60 | 1083 | 679 | 1445 | 3208 | - - - | - - - | - - - | - - - | 1083 | 679 | 1445 | 3208 | 704 | 729 | 57 | 1490 | - - - | - - - | - - - | - - - | 704 | 729 | 57 | 1490 | 1303 | 1027 | 1475 | 3805 | # # # | # # # | # # # | # # # | 0.832 | 0.661 | 0.98 | 0.843 | # # # | # # # | # # # | - - - | 0.838 | 0.671 | 0.997 | 0.854 | - - - | 0.465 | 1.58 | 1.58 | 1.47 | 1.45 | 1.48 | 1.49 | 10.65 | 16.54 | 18.09 | 0 | - - - | - - - | - - - | - - - | 1303 | 1027 | 1475 | 3805 | Over-range | 722 | 749 | 293 | 2038 | 154 | 173 | 269 | 1390 | 1086 | 678 | 1445 | 3210 | 1086 | 678 | 1445 | 3210 | - - - | - - - | - - - | - - -
5/10/2026 | 2:30:00 PM | 280.66 | 277.9 | 276.7 | 485.02 | 478.61 | 483.08 | 4.7284 | 3.8043 | 5.3599 | 4.1133 | 1.434 | 1.433 | 1.43 | 1.489 | 1.465 | 1.401 | Over-range | 59.99 | 1098 | 670 | 1446 | 3213 | - - - | - - - | - - - | - - - | 1098 | 670 | 1446 | 3213 | 706 | 730 | 78 | 1514 | - - - | - - - | - - - | - - - | 706 | 730 | 78 | 1514 | 1317 | 1035 | 1481 | 3832 | # # # | # # # | # # # | # # # | 0.834 | 0.648 | 0.976 | 0.839 | # # # | # # # | # # # | - - - | 0.831 | 0.652 | 0.979 | 0.84 | - - - | 0.471 | 1.6 | 1.57 | 1.47 | 1.46 | 1.48 | 1.48 | 10.65 | 16.56 | 17.93 | 0 | - - - | - - - | - - - | - - - | 1317 | 1035 | 1481 | 3832 | Over-range | 724 | 750 | 319 | 2076 | 157 | 172 | 268 | 1415 | 1107 | 675 | 1459 | 3241 | 1107 | 675 | 1459 | 3241 | - - - | - - - | - - - | - - -
5/10/2026 | 2:45:00 PM | 280.44 | 277.62 | 276.48 | 484.59 | 478.15 | 482.73 | 4.9231 | 4.1366 | 5.4681 | 4.1059 | 1.434 | 1.433 | 1.43 | 1.493 | 1.444 | 1.353 | Over-range | 59.99 | 1127 | 850 | 1484 | 3461 | - - - | - - - | - - - | - - - | 1127 | 850 | 1484 | 3461 | 776 | 724 | -19 | 1480 | - - - | - - - | - - - | - - - | 776 | 724 | -19 | 1480 | 1377 | 1138 | 1511 | 4026 | # # # | # # # | # # # | # # # | 0.818 | 0.747 | 0.982 | 0.86 | # # # | # # # | # # # | - - - | 0.824 | 0.756 | 0.999 | 0.87 | - - - | 0.428 | 1.55 | 1.54 | 1.43 | 1.43 | 1.43 | 1.45 | 9.87 | 15.09 | 17.66 | 0 | - - - | - - - | - - - | - - - | 1377 | 1138 | 1511 | 4026 | Over-range | 791 | 745 | 282 | 2055 | 154 | 176 | 268 | 1423 | 1129 | 849 | 1485 | 3462 | 1129 | 849 | 1485 | 3462 | - - - | - - - | - - - | - - -
5/10/2026 | 3:00:00 PM | 280.72 | 277.83 | 276.74 | 484.99 | 478.52 | 483.24 | 5.3121 | 4.7642 | 5.6854 | 4.1021 | 1.435 | 1.434 | 1.43 | 1.494 | 1.424 | 1.294 | Over-range | 59.99 | 1191 | 1092 | 1545 | 3828 | - - - | - - - | - - - | - - - | 1191 | 1092 | 1545 | 3828 | 884 | 724 | -123 | 1484 | - - - | - - - | - - - | - - - | 884 | 724 | -123 | 1484 | 1491 | 1323 | 1573 | 4388 | # # # | # # # | # # # | # # # | 0.799 | 0.826 | 0.982 | 0.873 | # # # | # # # | # # # | - - - | 0.803 | 0.833 | 0.997 | 0.881 | - - - | 0.388 | 1.59 | 1.56 | 1.45 | 1.44 | 1.46 | 1.47 | 9.14 | 13.34 | 17.21 | 0 | - - - | - - - | - - - | - - - | 1491 | 1323 | 1573 | 4388 | Over-range | 897 | 747 | 298 | 2144 | 153 | 181 | 271 | 1547 | 1194 | 1093 | 1542 | 3829 | 1194 | 1093 | 1542 | 3829 | - - - | - - - | - - - | - - -
5/10/2026 | 3:15:00 PM | 280.73 | 277.88 | 276.69 | 485.05 | 478.56 | 483.15 | 4.7007 | 3.8616 | 5.373 | 4.1125 | 1.435 | 1.434 | 1.431 | 1.492 | 1.451 | 1.377 | Over-range | 60.01 | 1088 | 723 | 1456 | 3268 | - - - | - - - | - - - | - - - | 1088 | 723 | 1456 | 3268 | 717 | 728 | 27 | 1473 | - - - | - - - | - - - | - - - | 717 | 728 | 27 | 1473 | 1314 | 1059 | 1485 | 3858 | # # # | # # # | # # # | # # # | 0.828 | 0.683 | 0.981 | 0.847 | # # # | # # # | # # # | - - - | 0.834 | 0.693 | 0.997 | 0.858 | - - - | 0.451 | 1.56 | 1.54 | 1.45 | 1.43 | 1.44 | 1.45 | 10.5 | 16.09 | 17.88 | 0 | - - - | - - - | - - - | - - - | 1314 | 1059 | 1485 | 3858 | Over-range | 734 | 748 | 290 | 2042 | 154 | 168 | 267 | 1413 | 1089 | 725 | 1454 | 3268 | 1089 | 725 | 1454 | 3268 | - - - | - - - | - - - | - - -
5/10/2026 | 3:30:00 PM | 280.54 | 277.65 | 276.59 | 484.67 | 478.25 | 482.97 | 4.7895 | 3.9529 | 5.4256 | 4.1085 | 1.434 | 1.434 | 1.431 | 1.493 | 1.449 | 1.372 | Over-range | 60 | 1107 | 753 | 1466 | 3325 | - - - | - - - | - - - | - - - | 1107 | 753 | 1466 | 3325 | 732 | 726 | 25 | 1482 | - - - | - - - | - - - | - - - | 732 | 726 | 25 | 1482 | 1338 | 1080 | 1499 | 3917 | # # # | # # # | # # # | # # # | 0.828 | 0.697 | 0.978 | 0.849 | # # # | # # # | # # # | - - - | 0.826 | 0.701 | 0.984 | 0.852 | - - - | 0.446 | 1.55 | 1.54 | 1.44 | 1.42 | 1.44 | 1.45 | 10.3 | 15.97 | 17.89 | 0 | - - - | - - - | - - - | - - - | 1338 | 1080 | 1499 | 3917 | Over-range | 748 | 746 | 309 | 2062 | 153 | 171 | 270 | 1429 | 1119 | 757 | 1473 | 3348 | 1119 | 757 | 1473 | 3348 | - - - | - - - | - - - | - - -
5/10/2026 | 3:45:00 PM | 280.22 | 277.3 | 276.18 | 484.1 | 477.56 | 482.33 | 4.8934 | 4.1609 | 5.4835 | 4.1035 | 1.434 | 1.434 | 1.431 | 1.492 | 1.438 | 1.338 | Over-range | 60.01 | 1119 | 863 | 1487 | 3469 | - - - | - - - | - - - | - - - | 1119 | 863 | 1487 | 3469 | 771 | 719 | -41 | 1448 | - - - | - - - | - - - | - - - | 771 | 719 | -41 | 1448 | 1368 | 1144 | 1514 | 4026 | # # # | # # # | # # # | # # # | 0.818 | 0.755 | 0.982 | 0.862 | # # # | # # # | # # # | - - - | 0.824 | 0.764 | 0.998 | 0.872 | - - - | 0.417 | 1.56 | 1.52 | 1.47 | 1.42 | 1.46 | 1.46 | 9.95 | 14.85 | 17.65 | 0 | - - - | - - - | - - - | - - - | 1368 | 1144 | 1514 | 4026 | Over-range | 786 | 740 | 284 | 2041 | 151 | 173 | 268 | 1436 | 1122 | 864 | 1484 | 3470 | 1122 | 864 | 1484 | 3470 | - - - | - - - | - - - | - - -
5/10/2026 | 4:00:00 PM | 280.51 | 277.62 | 276.54 | 484.61 | 478.22 | 482.86 | 5.2138 | 4.6806 | 5.6691 | 4.1022 | 1.435 | 1.434 | 1.431 | 1.493 | 1.423 | 1.291 | Over-range | 60 | 1172 | 1064 | 1538 | 3775 | - - - | - - - | - - - | - - - | 1172 | 1064 | 1538 | 3775 | 861 | 721 | -126 | 1454 | - - - | - - - | - - - | - - - | 861 | 721 | -126 | 1454 | 1462 | 1299 | 1568 | 4329 | # # # | # # # | # # # | # # # | 0.802 | 0.82 | 0.981 | 0.872 | # # # | # # # | # # # | - - - | 0.807 | 0.828 | 0.996 | 0.881 | - - - | 0.385 | 1.59 | 1.55 | 1.48 | 1.45 | 1.47 | 1.48 | 9.3 | 13.49 | 17.33 | 0 | - - - | - - - | - - - | - - - | 1462 | 1299 | 1568 | 4329 | Over-range | 874 | 743 | 301 | 2118 | 153 | 182 | 272 | 1540 | 1176 | 1064 | 1537 | 3777 | 1176 | 1064 | 1537 | 3777 | - - - | - - - | - - - | - - -
5/10/2026 | 4:15:00 PM | 280.58 | 277.74 | 276.66 | 484.73 | 478.46 | 483.03 | 4.9542 | 4.2406 | 5.5205 | 4.1055 | 1.435 | 1.435 | 1.431 | 1.493 | 1.429 | 1.331 | Over-range | 60 | 1130 | 905 | 1501 | 3536 | - - - | - - - | - - - | - - - | 1130 | 905 | 1501 | 3536 | 792 | 725 | -55 | 1461 | - - - | - - - | - - - | - - - | 792 | 725 | -55 | 1461 | 1389 | 1175 | 1527 | 4091 | # # # | # # # | # # # | # # # | 0.814 | 0.77 | 0.983 | 0.864 | # # # | # # # | # # # | - - - | 0.819 | 0.779 | 0.999 | 0.874 | - - - | 0.413 | 1.59 | 1.57 | 1.47 | 1.46 | 1.47 | 1.48 | 9.77 | 14.66 | 17.67 | 0 | - - - | - - - | - - - | - - - | 1389 | 1175 | 1527 | 4091 | Over-range | 807 | 746 | 280 | 2057 | 154 | 178 | 270 | 1446 | 1133 | 904 | 1501 | 3538 | 1133 | 904 | 1501 | 3538 | - - - | - - - | - - - | - - -
5/10/2026 | 4:30:00 PM | 280.4 | 277.67 | 276.51 | 484.56 | 478.27 | 482.69 | 5.5277 | 5.2543 | 5.8633 | 4.0965 | 1.435 | 1.435 | 1.431 | 1.496 | 1.452 | 1.276 | Over-range | 60 | 1221 | 1255 | 1584 | 4059 | - - - | - - - | - - - | - - - | 1221 | 1255 | 1584 | 4059 | 941 | 719 | -211 | 1448 | - - - | - - - | - - - | - - - | 941 | 719 | -211 | 1448 | 1550 | 1458 | 1621 | 4629 | # # # | # # # | # # # | # # # | 0.788 | 0.861 | 0.977 | 0.877 | # # # | # # # | # # # | - - - | 0.792 | 0.867 | 0.991 | 0.885 | - - - | 0.357 | 1.6 | 1.59 | 1.48 | 1.47 | 1.48 | 1.49 | 8.78 | 12.33 | 16.91 | 0 | - - - | - - - | - - - | - - - | 1550 | 1458 | 1621 | 4629 | Over-range | 954 | 742 | 346 | 2224 | 162 | 182 | 273 | 1689 | 1221 | 1256 | 1582 | 4059 | 1221 | 1256 | 1582 | 4059 | - - - | - - - | - - - | - - -
5/10/2026 | 4:45:00 PM | 280.17 | 277.36 | 276.21 | 484.12 | 477.68 | 482.28 | 5.6342 | 5.3425 | 5.8976 | 4.0893 | 1.435 | 1.434 | 1.431 | 1.495 | 1.457 | 1.281 | Over-range | 59.99 | 1242 | 1284 | 1591 | 4118 | - - - | - - - | - - - | - - - | 1242 | 1284 | 1591 | 4118 | 956 | 714 | -210 | 1459 | - - - | - - - | - - - | - - - | 956 | 714 | -210 | 1459 | 1577 | 1481 | 1629 | 4687 | # # # | # # # | # # # | # # # | 0.788 | 0.867 | 0.977 | 0.878 | # # # | # # # | # # # | - - - | 0.785 | 0.866 | 0.979 | 0.878 | - - - | 0.355 | 1.58 | 1.55 | 1.45 | 1.44 | 1.45 | 1.46 | 8.68 | 12.18 | 16.77 | 0 | - - - | - - - | - - - | - - - | 1577 | 1481 | 1629 | 4687 | Over-range | 971 | 737 | 350 | 2239 | 162 | 181 | 271 | 1694 | 1255 | 1291 | 1620 | 4166 | 1255 | 1291 | 1620 | 4166 | - - - | - - - | - - - | - - -
5/10/2026 | 5:00:00 PM | 280.2 | 277.4 | 276.24 | 484.11 | 477.8 | 482.34 | 5.3951 | 5.0109 | 5.779 | 4.0958 | 1.434 | 1.434 | 1.431 | 1.494 | 1.44 | 1.269 | Over-range | 59.99 | 1200 | 1178 | 1563 | 3940 | - - - | - - - | - - - | - - - | 1200 | 1178 | 1563 | 3940 | 905 | 716 | -179 | 1441 | - - - | - - - | - - - | - - - | 905 | 716 | -179 | 1441 | 1512 | 1390 | 1596 | 4498 | # # # | # # # | # # # | # # # | 0.794 | 0.847 | 0.979 | 0.876 | # # # | # # # | # # # | - - - | 0.799 | 0.854 | 0.994 | 0.885 | - - - | 0.366 | 1.57 | 1.55 | 1.39 | 1.42 | 1.42 | 1.44 | 8.9 | 12.73 | 16.97 | 0 | - - - | - - - | - - - | - - - | 1512 | 1390 | 1596 | 4498 | Over-range | 920 | 739 | 325 | 2169 | 162 | 181 | 270 | 1622 | 1201 | 1176 | 1565 | 3942 | 1201 | 1176 | 1565 | 3942 | - - - | - - - | - - - | - - -
5/10/2026 | 5:15:00 PM | 280.38 | 277.99 | 276.7 | 484.79 | 478.84 | 482.73 | 5.0158 | 4.3702 | 5.5594 | 4.1019 | 1.434 | 1.434 | 1.431 | 1.492 | 1.434 | 1.323 | Over-range | 60.01 | 1139 | 943 | 1510 | 3592 | - - - | - - - | - - - | - - - | 1139 | 943 | 1510 | 3592 | 805 | 726 | -73 | 1457 | - - - | - - - | - - - | - - - | 805 | 726 | -73 | 1457 | 1404 | 1208 | 1538 | 4149 | # # # | # # # | # # # | # # # | 0.811 | 0.781 | 0.982 | 0.866 | # # # | # # # | # # # | - - - | 0.816 | 0.789 | 0.998 | 0.875 | - - - | 0.406 | 1.57 | 1.5 | 1.39 | 1.42 | 1.41 | 1.43 | 9.68 | 14.25 | 17.53 | 0 | - - - | - - - | - - - | - - - | 1404 | 1208 | 1538 | 4149 | Over-range | 821 | 746 | 288 | 2075 | 160 | 174 | 270 | 1476 | 1138 | 944 | 1511 | 3593 | 1138 | 944 | 1511 | 3593 | - - - | - - - | - - - | - - -
5/10/2026 | 5:30:00 PM | 280.11 | 277.61 | 276.38 | 484.23 | 478.19 | 482.26 | 5.0932 | 4.4863 | 5.6001 | 4.1001 | 1.434 | 1.434 | 1.431 | 1.492 | 1.425 | 1.309 | Over-range | 60 | 1151 | 993 | 1519 | 3664 | - - - | - - - | - - - | - - - | 1151 | 993 | 1519 | 3664 | 825 | 720 | -97 | 1448 | - - - | - - - | - - - | - - - | 825 | 720 | -97 | 1448 | 1426 | 1242 | 1547 | 4215 | # # # | # # # | # # # | # # # | 0.808 | 0.8 | 0.982 | 0.869 | # # # | # # # | # # # | - - - | 0.812 | 0.808 | 0.997 | 0.879 | - - - | 0.395 | 1.55 | 1.52 | 1.41 | 1.42 | 1.42 | 1.44 | 9.47 | 14.13 | 17.54 | 0 | - - - | - - - | - - - | - - - | 1426 | 1242 | 1547 | 4215 | Over-range | 841 | 742 | 292 | 2083 | 159 | 180 | 271 | 1497 | 1152 | 992 | 1521 | 3666 | 1152 | 992 | 1521 | 3666 | - - - | - - - | - - - | - - -
5/10/2026 | 5:45:00 PM | 280.02 | 277.59 | 276.34 | 484.12 | 478.21 | 482.11 | 5.4833 | 5.0722 | 5.8124 | 4.0981 | 1.434 | 1.434 | 1.431 | 1.493 | 1.44 | 1.283 | Over-range | 60 | 1218 | 1195 | 1572 | 3985 | - - - | - - - | - - - | - - - | 1218 | 1195 | 1572 | 3985 | 917 | 718 | -170 | 1464 | - - - | - - - | - - - | - - - | 917 | 718 | -170 | 1464 | 1533 | 1406 | 1606 | 4546 | # # # | # # # | # # # | # # # | 0.794 | 0.85 | 0.979 | 0.877 | # # # | # # # | # # # | - - - | 0.792 | 0.85 | 0.974 | 0.874 | - - - | 0.367 | 1.55 | 1.5 | 1.41 | 1.42 | 1.41 | 1.43 | 8.91 | 12.71 | 17.06 | 0 | - - - | - - - | - - - | - - - | 1533 | 1406 | 1606 | 4546 | Over-range | 931 | 741 | 328 | 2187 | 159 | 180 | 272 | 1621 | 1230 | 1203 | 1597 | 4030 | 1230 | 1203 | 1597 | 4030 | - - - | - - - | - - - | - - -
5/10/2026 | 6:00:00 PM | 280 | 277.71 | 276.41 | 484.21 | 478.42 | 482.09 | 5.3262 | 4.8896 | 5.7439 | 4.1073 | 1.434 | 1.434 | 1.431 | 1.494 | 1.43 | 1.279 | Over-range | 60.01 | 1188 | 1136 | 1556 | 3879 | - - - | - - - | - - - | - - - | 1188 | 1136 | 1556 | 3879 | 888 | 719 | -159 | 1447 | - - - | - - - | - - - | - - - | 888 | 719 | -159 | 1447 | 1491 | 1357 | 1588 | 4435 | # # # | # # # | # # # | # # # | 0.797 | 0.837 | 0.98 | 0.875 | # # # | # # # | # # # | - - - | 0.802 | 0.844 | 0.995 | 0.884 | - - - | 0.373 | 1.56 | 1.5 | 1.38 | 1.41 | 1.39 | 1.42 | 9.02 | 13.04 | 17.15 | 0 | - - - | - - - | - - - | - - - | 1491 | 1357 | 1588 | 4435 | Over-range | 901 | 742 | 316 | 2150 | 153 | 184 | 272 | 1591 | 1192 | 1134 | 1555 | 3881 | 1192 | 1134 | 1555 | 3881 | - - - | - - - | - - - | - - -
5/10/2026 | 6:15:00 PM | 280.25 | 278.04 | 276.82 | 484.67 | 479.13 | 482.65 | 5.4156 | 5.0545 | 5.8035 | 4.1057 | 1.435 | 1.434 | 1.432 | 1.495 | 1.435 | 1.273 | Over-range | 60.01 | 1202 | 1190 | 1572 | 3965 | - - - | - - - | - - - | - - - | 1202 | 1190 | 1572 | 3965 | 913 | 723 | -179 | 1456 | - - - | - - - | - - - | - - - | 913 | 723 | -179 | 1456 | 1518 | 1405 | 1606 | 4529 | # # # | # # # | # # # | # # # | 0.792 | 0.847 | 0.979 | 0.875 | # # # | # # # | # # # | - - - | 0.797 | 0.854 | 0.994 | 0.884 | - - - | 0.367 | 1.59 | 1.53 | 1.45 | 1.45 | 1.44 | 1.46 | 8.98 | 12.82 | 17.2 | 0 | - - - | - - - | - - - | - - - | 1518 | 1405 | 1606 | 4529 | Over-range | 926 | 747 | 330 | 2190 | 155 | 188 | 276 | 1636 | 1206 | 1189 | 1571 | 3966 | 1206 | 1189 | 1571 | 3966 | - - - | - - - | - - - | - - -
5/10/2026 | 6:30:00 PM | 280.29 | 278.06 | 276.86 | 484.74 | 479.16 | 482.72 | 5.3317 | 4.8988 | 5.7494 | 4.1073 | 1.434 | 1.434 | 1.431 | 1.495 | 1.427 | 1.278 | Over-range | 59.99 | 1189 | 1138 | 1560 | 3887 | - - - | - - - | - - - | - - - | 1189 | 1138 | 1560 | 3887 | 892 | 725 | -156 | 1460 | - - - | - - - | - - - | - - - | 892 | 725 | -156 | 1460 | 1494 | 1362 | 1592 | 4448 | # # # | # # # | # # # | # # # | 0.796 | 0.836 | 0.98 | 0.874 | # # # | # # # | # # # | - - - | 0.801 | 0.843 | 0.995 | 0.883 | - - - | 0.376 | 1.57 | 1.51 | 1.4 | 1.42 | 1.41 | 1.43 | 9.11 | 13.17 | 17.31 | 0 | - - - | - - - | - - - | - - - | 1494 | 1362 | 1592 | 4448 | Over-range | 905 | 748 | 317 | 2163 | 153 | 185 | 275 | 1595 | 1193 | 1138 | 1557 | 3888 | 1193 | 1138 | 1557 | 3888 | - - - | - - - | - - - | - - -
5/10/2026 | 6:45:00 PM | 280.59 | 278.39 | 277.11 | 485.26 | 479.74 | 483.14 | 5.3876 | 4.9107 | 5.7652 | 4.1042 | 1.434 | 1.434 | 1.431 | 1.493 | 1.429 | 1.285 | Over-range | 59.99 | 1202 | 1142 | 1566 | 3909 | - - - | - - - | - - - | - - - | 1202 | 1142 | 1566 | 3909 | 900 | 729 | -140 | 1488 | - - - | - - - | - - - | - - - | 900 | 729 | -140 | 1488 | 1510 | 1367 | 1598 | 4475 | # # # | # # # | # # # | # # # | 0.796 | 0.835 | 0.98 | 0.874 | # # # | # # # | # # # | - - - | 0.793 | 0.836 | 0.977 | 0.872 | - - - | 0.381 | 1.58 | 1.5 | 1.43 | 1.43 | 1.41 | 1.44 | 9.07 | 13.42 | 17.37 | 0 | - - - | - - - | - - - | - - - | 1510 | 1367 | 1598 | 4475 | Over-range | 914 | 752 | 318 | 2178 | 157 | 186 | 277 | 1587 | 1215 | 1148 | 1589 | 3953 | 1215 | 1148 | 1589 | 3953 | - - - | - - - | - - - | - - -
5/10/2026 | 7:00:00 PM | 281.12 | 279.08 | 277.82 | 486.31 | 480.97 | 484.19 | 4.8894 | 4.2714 | 5.5156 | 4.1095 | 1.434 | 1.433 | 1.431 | 1.493 | 1.449 | 1.351 | Over-range | 60 | 1113 | 849 | 1497 | 3458 | - - - | - - - | - - - | - - - | 1113 | 849 | 1497 | 3458 | 773 | 742 | -21 | 1492 | - - - | - - - | - - - | - - - | 773 | 742 | -21 | 1492 | 1366 | 1169 | 1530 | 4065 | # # # | # # # | # # # | # # # | 0.815 | 0.726 | 0.978 | 0.851 | # # # | # # # | # # # | - - - | 0.82 | 0.735 | 0.995 | 0.861 | - - - | 0.431 | 1.57 | 1.53 | 1.41 | 1.44 | 1.41 | 1.44 | 10.25 | 15.6 | 18.01 | 0 | - - - | - - - | - - - | - - - | 1366 | 1169 | 1530 | 4065 | Over-range | 790 | 764 | 315 | 2125 | 160 | 182 | 276 | 1510 | 1113 | 848 | 1499 | 3460 | 1113 | 848 | 1499 | 3460 | - - - | - - - | - - - | - - -
5/10/2026 | 7:15:00 PM | 281.44 | 279.54 | 278.21 | 487.01 | 481.76 | 484.73 | 4.7669 | 3.9709 | 5.4375 | 4.1213 | 1.434 | 1.433 | 1.431 | 1.493 | 1.438 | 1.367 | Over-range | 60 | 1099 | 785 | 1485 | 3369 | - - - | - - - | - - - | - - - | 1099 | 785 | 1485 | 3369 | 749 | 750 | 9 | 1507 | - - - | - - - | - - - | - - - | 749 | 750 | 9 | 1507 | 1340 | 1105 | 1512 | 3957 | # # # | # # # | # # # | # # # | 0.821 | 0.71 | 0.982 | 0.852 | # # # | # # # | # # # | - - - | 0.826 | 0.72 | 0.999 | 0.862 | - - - | 0.447 | 1.6 | 1.54 | 1.41 | 1.45 | 1.41 | 1.45 | 10.38 | 16.12 | 18.38 | 0 | - - - | - - - | - - - | - - - | 1340 | 1105 | 1512 | 3957 | Over-range | 765 | 771 | 286 | 2074 | 159 | 179 | 278 | 1423 | 1099 | 786 | 1484 | 3369 | 1099 | 786 | 1484 | 3369 | - - - | - - - | - - - | - - -
5/10/2026 | 7:30:00 PM | 281.63 | 279.7 | 278.38 | 487.32 | 482.03 | 485.07 | 4.8351 | 4.0932 | 5.4859 | 4.1084 | 1.434 | 1.433 | 1.431 | 1.492 | 1.432 | 1.352 | Over-range | 60 | 1108 | 843 | 1501 | 3452 | - - - | - - - | - - - | - - - | 1108 | 843 | 1501 | 3452 | 775 | 751 | -15 | 1510 | - - - | - - - | - - - | - - - | 775 | 751 | -15 | 1510 | 1362 | 1144 | 1527 | 4033 | # # # | # # # | # # # | # # # | 0.814 | 0.737 | 0.983 | 0.856 | # # # | # # # | # # # | - - - | 0.82 | 0.747 | 1 | 0.867 | - - - | 0.438 | 1.6 | 1.53 | 1.41 | 1.45 | 1.41 | 1.45 | 10.16 | 15.58 | 18.28 | 0 | - - - | - - - | - - - | - - - | 1362 | 1144 | 1527 | 4033 | Over-range | 792 | 773 | 281 | 2085 | 160 | 182 | 279 | 1437 | 1108 | 843 | 1502 | 3453 | 1108 | 843 | 1502 | 3453 | - - - | - - - | - - - | - - -
5/10/2026 | 7:45:00 PM | 282.13 | 280.35 | 278.89 | 488.33 | 483.13 | 485.83 | 5.4249 | 5.0862 | 5.8239 | 4.1239 | 1.434 | 1.433 | 1.431 | 1.495 | 1.431 | 1.294 | Over-range | 60 | 1204 | 1185 | 1589 | 3979 | - - - | - - - | - - - | - - - | 1204 | 1185 | 1589 | 3979 | 927 | 756 | -159 | 1523 | - - - | - - - | - - - | - - - | 927 | 756 | -159 | 1523 | 1529 | 1421 | 1624 | 4574 | # # # | # # # | # # # | # # # | 0.788 | 0.834 | 0.979 | 0.87 | # # # | # # # | # # # | - - - | 0.793 | 0.842 | 0.994 | 0.879 | - - - | 0.383 | 1.58 | 1.54 | 1.42 | 1.45 | 1.41 | 1.45 | 9.21 | 13.48 | 17.74 | 0 | - - - | - - - | - - - | - - - | 1529 | 1421 | 1624 | 4574 | Over-range | 942 | 781 | 332 | 2257 | 167 | 195 | 286 | 1664 | 1206 | 1184 | 1590 | 3980 | 1206 | 1184 | 1590 | 3980 | - - - | - - - | - - - | - - -
5/10/2026 | 8:00:00 PM | 282.54 | 280.66 | 279.22 | 488.98 | 483.61 | 486.54 | 5.7174 | 6.5004 | 5.9739 | 2.9363 | 1.434 | 1.433 | 1.431 | 1.496 | 1.475 | 1.291 | Over-range | 60.01 | 1259 | 1690 | 1629 | 4579 | - - - | - - - | - - - | - - - | 1259 | 1690 | 1629 | 4579 | 993 | 647 | -208 | 1431 | - - - | - - - | - - - | - - - | 993 | 647 | -208 | 1431 | 1614 | 1820 | 1668 | 5102 | # # # | # # # | # # # | # # # | 0.78 | 0.929 | 0.977 | 0.897 | # # # | # # # | # # # | - - - | 0.776 | 0.923 | 0.971 | 0.892 | - - - | 0.313 | 1.59 | 1.51 | 1.42 | 1.45 | 1.4 | 1.45 | 10.14 | 9.85 | 18.06 | 0 | - - - | - - - | - - - | - - - | 1614 | 1820 | 1668 | 5102 | Over-range | 1010 | 666 | 357 | 2248 | 151 | 135 | 280 | 1730 | 1270 | 1701 | 1657 | 4628 | 1270 | 1701 | 1657 | 4628 | - - - | - - - | - - - | - - -
5/10/2026 | 8:15:00 PM | 282.46 | 280.51 | 279.11 | 488.76 | 483.35 | 486.4 | 5.3904 | 6.1126 | 5.8011 | 2.7197 | 1.434 | 1.433 | 1.43 | 1.495 | 1.469 | 1.281 | Over-range | 60 | 1199 | 1582 | 1586 | 4368 | - - - | - - - | - - - | - - - | 1199 | 1582 | 1586 | 4368 | 922 | 637 | -150 | 1407 | - - - | - - - | - - - | - - - | 922 | 637 | -150 | 1407 | 1522 | 1713 | 1619 | 4854 | # # # | # # # | # # # | # # # | 0.788 | 0.924 | 0.98 | 0.9 | # # # | # # # | # # # | - - - | 0.793 | 0.927 | 0.996 | 0.908 | - - - | 0.322 | 1.58 | 1.49 | 1.38 | 1.44 | 1.39 | 1.42 | 9.25 | 8.81 | 17.7 | 0 | - - - | - - - | - - - | - - - | 1522 | 1713 | 1619 | 4854 | Over-range | 937 | 655 | 324 | 2118 | 168 | 155 | 285 | 1581 | 1200 | 1582 | 1587 | 4369 | 1200 | 1582 | 1587 | 4369 | - - - | - - - | - - - | - - -
5/10/2026 | 8:30:00 PM | 282.71 | 280.82 | 279.36 | 489.26 | 483.89 | 486.77 | 4.8172 | 4.9651 | 5.4754 | 2.7446 | 1.434 | 1.432 | 1.43 | 1.491 | 1.431 | 1.362 | Over-range | 60 | 1109 | 1225 | 1503 | 3837 | - - - | - - - | - - - | - - - | 1109 | 1225 | 1503 | 3837 | 774 | 645 | 7 | 1426 | - - - | - - - | - - - | - - - | 774 | 645 | 7 | 1426 | 1362 | 1393 | 1530 | 4284 | # # # | # # # | # # # | # # # | 0.815 | 0.879 | 0.983 | 0.896 | # # # | # # # | # # # | - - - | 0.821 | 0.884 | 1 | 0.905 | - - - | 0.372 | 1.59 | 1.5 | 1.35 | 1.43 | 1.37 | 1.41 | 10.38 | 10.39 | 18.45 | 0 | - - - | - - - | - - - | - - - | 1362 | 1393 | 1530 | 4284 | Over-range | 790 | 663 | 283 | 1906 | 158 | 152 | 282 | 1264 | 1111 | 1226 | 1501 | 3838 | 1111 | 1226 | 1501 | 3838 | - - - | - - - | - - - | - - -
5/10/2026 | 8:45:00 PM | 282.81 | 280.79 | 279.38 | 489.36 | 483.81 | 486.91 | 5.1372 | 5.5961 | 5.6509 | 2.7398 | 1.433 | 1.432 | 1.429 | 1.496 | 1.456 | 1.316 | Over-range | 60 | 1159 | 1418 | 1549 | 4127 | - - - | - - - | - - - | - - - | 1159 | 1418 | 1549 | 4127 | 857 | 642 | -77 | 1422 | - - - | - - - | - - - | - - - | 857 | 642 | -77 | 1422 | 1451 | 1566 | 1578 | 4596 | # # # | # # # | # # # | # # # | 0.799 | 0.906 | 0.982 | 0.898 | # # # | # # # | # # # | - - - | 0.804 | 0.91 | 0.998 | 0.906 | - - - | 0.344 | 1.57 | 1.48 | 1.36 | 1.42 | 1.37 | 1.4 | 9.74 | 9.64 | 18.09 | 0 | - - - | - - - | - - - | - - - | 1451 | 1566 | 1578 | 4596 | Over-range | 873 | 661 | 301 | 2022 | 163 | 159 | 285 | 1435 | 1162 | 1415 | 1551 | 4128 | 1162 | 1415 | 1551 | 4128 | - - - | - - - | - - - | - - -
5/10/2026 | 9:00:00 PM | 283.07 | 281.02 | 279.51 | 489.85 | 484.08 | 487.23 | 5.385 | 5.9556 | 5.7698 | 2.7413 | 1.433 | 1.432 | 1.429 | 1.497 | 1.468 | 1.295 | Over-range | 60.01 | 1205 | 1535 | 1581 | 4322 | - - - | - - - | - - - | - - - | 1205 | 1535 | 1581 | 4322 | 915 | 644 | -112 | 1445 | - - - | - - - | - - - | - - - | 915 | 644 | -112 | 1445 | 1523 | 1673 | 1613 | 4808 | # # # | # # # | # # # | # # # | 0.792 | 0.918 | 0.98 | 0.899 | # # # | # # # | # # # | - - - | 0.789 | 0.914 | 0.982 | 0.897 | - - - | 0.335 | 1.59 | 1.5 | 1.35 | 1.43 | 1.37 | 1.41 | 9.35 | 9.1 | 17.84 | 0 | - - - | - - - | - - - | - - - | 1523 | 1673 | 1613 | 4808 | Over-range | 930 | 664 | 317 | 2107 | 169 | 159 | 287 | 1528 | 1217 | 1543 | 1600 | 4360 | 1217 | 1543 | 1600 | 4360 | - - - | - - - | - - - | - - -
5/10/2026 | 9:15:00 PM | 283.36 | 281.33 | 279.84 | 490.32 | 484.7 | 487.74 | 5.0701 | 5.4767 | 5.6185 | 2.7462 | 1.433 | 1.432 | 1.429 | 1.496 | 1.472 | 1.329 | Over-range | 59.99 | 1147 | 1366 | 1541 | 4054 | - - - | - - - | - - - | - - - | 1147 | 1366 | 1541 | 4054 | 840 | 651 | -50 | 1441 | - - - | - - - | - - - | - - - | 840 | 651 | -50 | 1441 | 1433 | 1527 | 1571 | 4531 | # # # | # # # | # # # | # # # | 0.801 | 0.895 | 0.981 | 0.895 | # # # | # # # | # # # | - - - | 0.807 | 0.899 | 0.997 | 0.904 | - - - | 0.355 | 1.63 | 1.5 | 1.4 | 1.46 | 1.39 | 1.44 | 10.11 | 10.07 | 18.18 | 0 | - - - | - - - | - - - | - - - | 1433 | 1527 | 1571 | 4531 | Over-range | 857 | 670 | 307 | 2022 | 167 | 157 | 285 | 1413 | 1148 | 1365 | 1543 | 4056 | 1148 | 1365 | 1543 | 4056 | - - - | - - - | - - - | - - -
5/10/2026 | 9:30:00 PM | 283.74 | 281.65 | 280.18 | 490.9 | 485.29 | 488.38 | 4.5839 | 4.5194 | 5.3629 | 2.7561 | 1.433 | 1.431 | 1.428 | 1.492 | 1.446 | 1.401 | Over-range | 60.02 | 1072 | 1070 | 1472 | 3613 | - - - | - - - | - - - | - - - | 1072 | 1070 | 1472 | 3613 | 715 | 658 | 81 | 1455 | - - - | - - - | - - - | - - - | 715 | 658 | 81 | 1455 | 1299 | 1268 | 1502 | 4069 | # # # | # # # | # # # | # # # | 0.825 | 0.844 | 0.98 | 0.888 | # # # | # # # | # # # | - - - | 0.832 | 0.85 | 0.997 | 0.898 | - - - | 0.403 | 1.6 | 1.49 | 1.37 | 1.45 | 1.38 | 1.42 | 11.17 | 11.79 | 18.92 | 0 | - - - | - - - | - - - | - - - | 1299 | 1268 | 1502 | 4069 | Over-range | 734 | 676 | 301 | 1871 | 163 | 152 | 285 | 1174 | 1071 | 1071 | 1471 | 3614 | 1071 | 1071 | 1471 | 3614 | - - - | - - - | - - - | - - -
5/10/2026 | 9:45:00 PM | 283.76 | 281.77 | 280.26 | 491.07 | 485.42 | 488.44 | 4.9336 | 5.1799 | 5.5436 | 2.7541 | 1.433 | 1.431 | 1.427 | 1.496 | 1.443 | 1.351 | Over-range | 60 | 1128 | 1289 | 1526 | 3943 | - - - | - - - | - - - | - - - | 1128 | 1289 | 1526 | 3943 | 811 | 658 | -11 | 1458 | - - - | - - - | - - - | - - - | 811 | 658 | -11 | 1458 | 1399 | 1457 | 1553 | 4409 | # # # | # # # | # # # | # # # | 0.806 | 0.885 | 0.982 | 0.894 | # # # | # # # | # # # | - - - | 0.812 | 0.889 | 1 | 0.904 | - - - | 0.37 | 1.6 | 1.5 | 1.37 | 1.46 | 1.37 | 1.42 | 10.33 | 10.38 | 18.59 | 0 | - - - | - - - | - - - | - - - | 1399 | 1457 | 1553 | 4409 | Over-range | 828 | 677 | 291 | 1974 | 163 | 157 | 287 | 1329 | 1130 | 1288 | 1526 | 3944 | 1130 | 1288 | 1526 | 3944 | - - - | - - - | - - - | - - -
5/10/2026 | 10:00:00 PM | 284.22 | 282.1 | 280.65 | 491.74 | 486.02 | 489.23 | 5.4838 | 6.2449 | 5.8579 | 2.7529 | 1.432 | 1.43 | 1.427 | 1.505 | 1.473 | 1.28 | Over-range | 60.02 | 1216 | 1621 | 1609 | 4447 | - - - | - - - | - - - | - - - | 1216 | 1621 | 1609 | 4447 | 959 | 658 | -154 | 1461 | - - - | - - - | - - - | - - - | 959 | 658 | -154 | 1461 | 1558 | 1758 | 1644 | 4959 | # # # | # # # | # # # | # # # | 0.781 | 0.922 | 0.979 | 0.897 | # # # | # # # | # # # | - - - | 0.786 | 0.926 | 0.995 | 0.905 | - - - | 0.329 | 1.63 | 1.49 | 1.35 | 1.46 | 1.38 | 1.42 | 9.33 | 9.07 | 17.96 | 0 | - - - | - - - | - - - | - - - | 1558 | 1758 | 1644 | 4959 | Over-range | 972 | 678 | 335 | 2196 | 162 | 167 | 293 | 1637 | 1219 | 1622 | 1606 | 4447 | 1219 | 1622 | 1606 | 4447 | - - - | - - - | - - - | - - -
5/10/2026 | 10:15:00 PM | 283.54 | 281.36 | 280 | 490.44 | 484.83 | 488.12 | 5.2936 | 5.8721 | 5.7415 | 2.7499 | 1.431 | 1.429 | 1.426 | 1.505 | 1.466 | 1.298 | Over-range | 60 | 1186 | 1509 | 1577 | 4272 | - - - | - - - | - - - | - - - | 1186 | 1509 | 1577 | 4272 | 905 | 650 | -110 | 1444 | - - - | - - - | - - - | - - - | 905 | 650 | -110 | 1444 | 1501 | 1651 | 1607 | 4759 | # # # | # # # | # # # | # # # | 0.79 | 0.914 | 0.981 | 0.898 | # # # | # # # | # # # | - - - | 0.795 | 0.918 | 0.997 | 0.906 | - - - | 0.338 | 1.61 | 1.52 | 1.36 | 1.45 | 1.39 | 1.42 | 9.55 | 9.31 | 18.04 | 0 | - - - | - - - | - - - | - - - | 1501 | 1651 | 1607 | 4759 | Over-range | 919 | 670 | 310 | 2097 | 160 | 160 | 288 | 1520 | 1188 | 1510 | 1574 | 4273 | 1188 | 1510 | 1574 | 4273 | - - - | - - - | - - - | - - -
5/10/2026 | 10:30:00 PM | 283.55 | 281.37 | 279.89 | 490.57 | 484.68 | 488 | 5.3212 | 5.8036 | 5.7299 | 2.7467 | 1.431 | 1.429 | 1.426 | 1.502 | 1.468 | 1.311 | Over-range | 60.01 | 1197 | 1490 | 1573 | 4260 | - - - | - - - | - - - | - - - | 1197 | 1490 | 1573 | 4260 | 900 | 650 | -87 | 1462 | - - - | - - - | - - - | - - - | 900 | 650 | -87 | 1462 | 1507 | 1633 | 1604 | 4744 | # # # | # # # | # # # | # # # | 0.794 | 0.912 | 0.981 | 0.898 | # # # | # # # | # # # | - - - | 0.791 | 0.909 | 0.983 | 0.897 | - - - | 0.343 | 1.6 | 1.52 | 1.39 | 1.46 | 1.4 | 1.44 | 9.54 | 9.44 | 18.15 | 0 | - - - | - - - | - - - | - - - | 1507 | 1633 | 1604 | 4744 | Over-range | 916 | 669 | 310 | 2088 | 170 | 158 | 289 | 1486 | 1207 | 1499 | 1591 | 4297 | 1207 | 1499 | 1591 | 4297 | - - - | - - - | - - - | - - -
5/10/2026 | 10:45:00 PM | 284.15 | 281.81 | 280.41 | 491.47 | 485.43 | 489.04 | 5.2658 | 5.8073 | 5.722 | 2.7518 | 1.431 | 1.43 | 1.426 | 1.506 | 1.466 | 1.303 | Over-range | 60.01 | 1183 | 1491 | 1575 | 4248 | - - - | - - - | - - - | - - - | 1183 | 1491 | 1575 | 4248 | 901 | 655 | -99 | 1456 | - - - | - - - | - - - | - - - | 901 | 655 | -99 | 1456 | 1496 | 1637 | 1604 | 4737 | # # # | # # # | # # # | # # # | 0.79 | 0.911 | 0.982 | 0.897 | # # # | # # # | # # # | - - - | 0.796 | 0.915 | 0.998 | 0.905 | - - - | 0.343 | 1.65 | 1.52 | 1.4 | 1.48 | 1.43 | 1.46 | 9.7 | 9.55 | 18.21 | 0 | - - - | - - - | - - - | - - - | 1496 | 1637 | 1604 | 4737 | Over-range | 917 | 675 | 307 | 2096 | 165 | 164 | 290 | 1507 | 1186 | 1488 | 1576 | 4250 | 1186 | 1488 | 1576 | 4250 | - - - | - - - | - - - | - - -
5/10/2026 | 11:00:00 PM | 284.48 | 282.18 | 280.69 | 492.08 | 486.03 | 489.53 | 5.262 | 5.7923 | 5.7221 | 2.7582 | 1.432 | 1.43 | 1.426 | 1.505 | 1.464 | 1.305 | Over-range | 60.02 | 1183 | 1487 | 1577 | 4246 | - - - | - - - | - - - | - - - | 1183 | 1487 | 1577 | 4246 | 903 | 658 | -95 | 1466 | - - - | - - - | - - - | - - - | 903 | 658 | -95 | 1466 | 1497 | 1634 | 1606 | 4738 | # # # | # # # | # # # | # # # | 0.79 | 0.91 | 0.982 | 0.896 | # # # | # # # | # # # | - - - | 0.795 | 0.914 | 0.998 | 0.905 | - - - | 0.345 | 1.64 | 1.53 | 1.45 | 1.49 | 1.43 | 1.48 | 9.77 | 9.61 | 18.3 | 0 | - - - | - - - | - - - | - - - | 1497 | 1634 | 1606 | 4738 | Over-range | 918 | 679 | 307 | 2101 | 163 | 165 | 291 | 1505 | 1186 | 1486 | 1575 | 4247 | 1186 | 1486 | 1575 | 4247 | - - - | - - - | - - - | - - -
5/10/2026 | 11:15:00 PM | 284.66 | 282.25 | 280.79 | 492.34 | 486.1 | 489.81 | 5.2617 | 5.7863 | 5.7181 | 2.7581 | 1.432 | 1.43 | 1.426 | 1.505 | 1.463 | 1.305 | Over-range | 60.02 | 1183 | 1485 | 1576 | 4244 | - - - | - - - | - - - | - - - | 1183 | 1485 | 1576 | 4244 | 904 | 660 | -93 | 1469 | - - - | - - - | - - - | - - - | 904 | 660 | -93 | 1469 | 1498 | 1633 | 1606 | 4737 | # # # | # # # | # # # | # # # | 0.79 | 0.909 | 0.982 | 0.896 | # # # | # # # | # # # | - - - | 0.796 | 0.914 | 0.998 | 0.905 | - - - | 0.346 | 1.67 | 1.55 | 1.45 | 1.51 | 1.45 | 1.5 | 9.82 | 9.65 | 18.31 | 0 | - - - | - - - | - - - | - - - | 1498 | 1633 | 1606 | 4737 | Over-range | 918 | 680 | 306 | 2103 | 162 | 165 | 292 | 1504 | 1187 | 1485 | 1573 | 4245 | 1187 | 1485 | 1573 | 4245 | - - - | - - - | - - - | - - -
5/10/2026 | 11:30:00 PM | 285.11 | 282.69 | 281.27 | 493.1 | 486.89 | 490.62 | 4.6537 | 4.66 | 5.4067 | 2.7677 | 1.433 | 1.431 | 1.427 | 1.494 | 1.469 | 1.397 | Over-range | 60.01 | 1082 | 1095 | 1486 | 3663 | - - - | - - - | - - - | - - - | 1082 | 1095 | 1486 | 3663 | 741 | 673 | 82 | 1496 | - - - | - - - | - - - | - - - | 741 | 673 | 82 | 1496 | 1322 | 1302 | 1520 | 4144 | # # # | # # # | # # # | # # # | 0.818 | 0.841 | 0.978 | 0.884 | # # # | # # # | # # # | - - - | 0.825 | 0.847 | 0.996 | 0.894 | - - - | 0.408 | 1.71 | 1.57 | 1.48 | 1.54 | 1.48 | 1.53 | 11.45 | 12.01 | 18.98 | 0 | - - - | - - - | - - - | - - - | 1322 | 1302 | 1520 | 4144 | Over-range | 759 | 692 | 316 | 1936 | 165 | 161 | 288 | 1222 | 1084 | 1093 | 1488 | 3665 | 1084 | 1093 | 1488 | 3665 | - - - | - - - | - - - | - - -
5/10/2026 | 11:45:00 PM | 285.42 | 283 | 281.48 | 493.68 | 487.33 | 491.04 | 4.7387 | 4.7795 | 5.4452 | 2.7712 | 1.433 | 1.431 | 1.427 | 1.496 | 1.431 | 1.383 | Over-range | 60.02 | 1099 | 1158 | 1503 | 3760 | - - - | - - - | - - - | - - - | 1099 | 1158 | 1503 | 3760 | 771 | 676 | 56 | 1503 | - - - | - - - | - - - | - - - | 771 | 676 | 56 | 1503 | 1352 | 1351 | 1533 | 4236 | # # # | # # # | # # # | # # # | 0.813 | 0.857 | 0.981 | 0.888 | # # # | # # # | # # # | - - - | 0.819 | 0.863 | 0.999 | 0.898 | - - - | 0.4 | 1.71 | 1.59 | 1.49 | 1.55 | 1.49 | 1.54 | 11.13 | 11.5 | 19.09 | 0 | - - - | - - - | - - - | - - - | 1352 | 1351 | 1533 | 4236 | Over-range | 788 | 695 | 298 | 1951 | 165 | 161 | 291 | 1243 | 1101 | 1157 | 1502 | 3761 | 1101 | 1157 | 1502 | 3761 | - - - | - - - | - - - | - - -
5/11/2026 | 12:00:00 AM | 285.05 | 282.58 | 281.12 | 492.99 | 486.67 | 490.43 | 4.8691 | 4.8838 | 5.4887 | 2.7681 | 1.433 | 1.431 | 1.427 | 1.497 | 1.425 | 1.381 | Over-range | 60.01 | 1126 | 1195 | 1512 | 3834 | - - - | - - - | - - - | - - - | 1126 | 1195 | 1512 | 3834 | 790 | 671 | 55 | 1516 | - - - | - - - | - - - | - - - | 790 | 671 | 55 | 1516 | 1386 | 1380 | 1543 | 4309 | # # # | # # # | # # # | # # # | 0.813 | 0.866 | 0.98 | 0.89 | # # # | # # # | # # # | - - - | 0.811 | 0.866 | 0.99 | 0.892 | - - - | 0.395 | 1.72 | 1.58 | 1.5 | 1.55 | 1.49 | 1.55 | 10.82 | 11.15 | 18.92 | 0 | - - - | - - - | - - - | - - - | 1386 | 1380 | 1543 | 4309 | Over-range | 808 | 689 | 304 | 1967 | 167 | 156 | 291 | 1247 | 1136 | 1205 | 1521 | 3862 | 1136 | 1205 | 1521 | 3862 | - - - | - - - | - - - | - - -
5/11/2026 | 12:15:00 AM | 283.8 | 281.27 | 279.85 | 490.78 | 484.38 | 488.28 | 5.2082 | 5.7076 | 5.6849 | 2.7474 | 1.432 | 1.43 | 1.426 | 1.504 | 1.458 | 1.313 | Over-range | 60 | 1172 | 1451 | 1560 | 4184 | - - - | - - - | - - - | - - - | 1172 | 1451 | 1560 | 4184 | 882 | 648 | -85 | 1444 | - - - | - - - | - - - | - - - | 882 | 648 | -85 | 1444 | 1476 | 1599 | 1590 | 4665 | # # # | # # # | # # # | # # # | 0.794 | 0.908 | 0.981 | 0.897 | # # # | # # # | # # # | - - - | 0.8 | 0.912 | 0.997 | 0.905 | - - - | 0.345 | 1.68 | 1.57 | 1.47 | 1.53 | 1.48 | 1.52 | 9.85 | 9.61 | 18.15 | 0 | - - - | - - - | - - - | - - - | 1476 | 1599 | 1590 | 4665 | Over-range | 896 | 668 | 307 | 2064 | 161 | 160 | 286 | 1470 | 1176 | 1449 | 1559 | 4184 | 1176 | 1449 | 1559 | 4184 | - - - | - - - | - - - | - - -
5/11/2026 | 12:30:00 AM | 284.06 | 281.58 | 280.18 | 491.26 | 484.98 | 488.75 | 5.4618 | 6.1983 | 5.8371 | 2.7491 | 1.432 | 1.429 | 1.425 | 1.506 | 1.468 | 1.287 | Over-range | 60 | 1213 | 1606 | 1602 | 4421 | - - - | - - - | - - - | - - - | 1213 | 1606 | 1602 | 4421 | 951 | 652 | -150 | 1451 | - - - | - - - | - - - | - - - | 951 | 652 | -150 | 1451 | 1550 | 1742 | 1635 | 4927 | # # # | # # # | # # # | # # # | 0.782 | 0.922 | 0.98 | 0.897 | # # # | # # # | # # # | - - - | 0.788 | 0.926 | 0.995 | 0.905 | - - - | 0.328 | 1.69 | 1.55 | 1.46 | 1.52 | 1.47 | 1.51 | 9.42 | 8.91 | 17.75 | 0 | - - - | - - - | - - - | - - - | 1550 | 1742 | 1635 | 4927 | Over-range | 965 | 672 | 328 | 2175 | 167 | 162 | 288 | 1618 | 1216 | 1603 | 1603 | 4423 | 1216 | 1603 | 1603 | 4423 | - - - | - - - | - - - | - - -
5/11/2026 | 12:45:00 AM | 284.29 | 281.88 | 280.38 | 491.72 | 485.46 | 489.06 | 5.2188 | 5.7107 | 5.6954 | 2.7572 | 1.432 | 1.429 | 1.426 | 1.504 | 1.457 | 1.31 | Over-range | 60 | 1175 | 1458 | 1568 | 4201 | - - - | - - - | - - - | - - - | 1175 | 1458 | 1568 | 4201 | 889 | 657 | -84 | 1462 | - - - | - - - | - - - | - - - | 889 | 657 | -84 | 1462 | 1483 | 1608 | 1597 | 4688 | # # # | # # # | # # # | # # # | 0.793 | 0.907 | 0.982 | 0.896 | # # # | # # # | # # # | - - - | 0.798 | 0.911 | 0.999 | 0.905 | - - - | 0.348 | 1.67 | 1.57 | 1.49 | 1.53 | 1.48 | 1.53 | 9.91 | 9.59 | 18.23 | 0 | - - - | - - - | - - - | - - - | 1483 | 1608 | 1597 | 4688 | Over-range | 904 | 676 | 303 | 2079 | 166 | 159 | 289 | 1478 | 1177 | 1458 | 1567 | 4202 | 1177 | 1458 | 1567 | 4202 | - - - | - - - | - - - | - - -
5/11/2026 | 1:00:00 AM | 284.52 | 282.09 | 280.58 | 492.16 | 485.76 | 489.45 | 4.5033 | 4.3623 | 5.3243 | 2.7628 | 1.432 | 1.43 | 1.426 | 1.49 | 1.468 | 1.416 | Over-range | 60.02 | 1059 | 1010 | 1460 | 3529 | - - - | - - - | - - - | - - - | 1059 | 1010 | 1460 | 3529 | 697 | 665 | 113 | 1475 | - - - | - - - | - - - | - - - | 697 | 665 | 113 | 1475 | 1279 | 1223 | 1493 | 3995 | # # # | # # # | # # # | # # # | 0.828 | 0.826 | 0.978 | 0.883 | # # # | # # # | # # # | - - - | 0.834 | 0.833 | 0.996 | 0.894 | - - - | 0.418 | 1.7 | 1.57 | 1.47 | 1.54 | 1.49 | 1.53 | 11.7 | 12.25 | 18.98 | 0 | - - - | - - - | - - - | - - - | 1279 | 1223 | 1493 | 3995 | Over-range | 716 | 682 | 313 | 1871 | 166 | 152 | 283 | 1149 | 1058 | 1011 | 1461 | 3530 | 1058 | 1011 | 1461 | 3530 | - - - | - - - | - - - | - - -
5/11/2026 | 1:15:00 AM | 284.46 | 281.99 | 280.64 | 491.93 | 485.76 | 489.5 | 4.8256 | 4.9537 | 5.4833 | 2.7566 | 1.432 | 1.429 | 1.426 | 1.498 | 1.432 | 1.369 | Over-range | 60.01 | 1113 | 1217 | 1511 | 3841 | - - - | - - - | - - - | - - - | 1113 | 1217 | 1511 | 3841 | 786 | 662 | 23 | 1471 | - - - | - - - | - - - | - - - | 786 | 662 | 23 | 1471 | 1372 | 1395 | 1539 | 4306 | # # # | # # # | # # # | # # # | 0.811 | 0.873 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.817 | 0.878 | 1 | 0.902 | - - - | 0.383 | 1.69 | 1.58 | 1.49 | 1.54 | 1.49 | 1.54 | 10.76 | 10.9 | 18.8 | 0 | - - - | - - - | - - - | - - - | 1372 | 1395 | 1539 | 4306 | Over-range | 803 | 680 | 291 | 1947 | 166 | 158 | 288 | 1274 | 1114 | 1215 | 1513 | 3842 | 1114 | 1215 | 1513 | 3842 | - - - | - - - | - - - | - - -
5/11/2026 | 1:30:00 AM | 284.57 | 282.11 | 280.72 | 492.12 | 485.98 | 489.63 | 4.906 | 5.0997 | 5.5264 | 2.7622 | 1.432 | 1.429 | 1.426 | 1.5 | 1.432 | 1.357 | Over-range | 60.01 | 1126 | 1266 | 1524 | 3916 | - - - | - - - | - - - | - - - | 1126 | 1266 | 1524 | 3916 | 808 | 662 | 3 | 1473 | - - - | - - - | - - - | - - - | 808 | 662 | 3 | 1473 | 1396 | 1438 | 1551 | 4385 | # # # | # # # | # # # | # # # | 0.807 | 0.881 | 0.982 | 0.893 | # # # | # # # | # # # | - - - | 0.813 | 0.886 | 0.999 | 0.902 | - - - | 0.376 | 1.7 | 1.56 | 1.5 | 1.54 | 1.49 | 1.53 | 10.61 | 10.63 | 18.7 | 0 | - - - | - - - | - - - | - - - | 1396 | 1438 | 1551 | 4385 | Over-range | 825 | 681 | 290 | 1973 | 166 | 159 | 289 | 1313 | 1128 | 1263 | 1525 | 3917 | 1128 | 1263 | 1525 | 3917 | - - - | - - - | - - - | - - -
5/11/2026 | 1:45:00 AM | 284.77 | 282.21 | 280.97 | 492.37 | 486.24 | 490.07 | 5.538 | 6.36 | 5.9143 | 2.756 | 1.432 | 1.429 | 1.426 | 1.509 | 1.465 | 1.278 | Over-range | 60.01 | 1227 | 1655 | 1626 | 4507 | - - - | - - - | - - - | - - - | 1227 | 1655 | 1626 | 4507 | 976 | 665 | -166 | 1474 | - - - | - - - | - - - | - - - | 976 | 665 | -166 | 1474 | 1576 | 1792 | 1661 | 5030 | # # # | # # # | # # # | # # # | 0.778 | 0.924 | 0.979 | 0.896 | # # # | # # # | # # # | - - - | 0.783 | 0.928 | 0.994 | 0.904 | - - - | 0.327 | 1.7 | 1.59 | 1.48 | 1.54 | 1.5 | 1.53 | 9.4 | 8.96 | 17.95 | 0 | - - - | - - - | - - - | - - - | 1576 | 1792 | 1661 | 5030 | Over-range | 990 | 686 | 342 | 2232 | 164 | 171 | 296 | 1675 | 1230 | 1655 | 1623 | 4508 | 1230 | 1655 | 1623 | 4508 | - - - | - - - | - - - | - - -
5/11/2026 | 2:00:00 AM | 284.97 | 282.44 | 281.09 | 492.8 | 486.5 | 490.34 | 5.6001 | 6.2869 | 5.886 | 2.758 | 1.432 | 1.429 | 1.426 | 1.504 | 1.464 | 1.287 | Over-range | 60.01 | 1245 | 1637 | 1619 | 4501 | - - - | - - - | - - - | - - - | 1245 | 1637 | 1619 | 4501 | 980 | 663 | -135 | 1507 | - - - | - - - | - - - | - - - | 980 | 663 | -135 | 1507 | 1594 | 1774 | 1654 | 5022 | # # # | # # # | # # # | # # # | 0.781 | 0.923 | 0.979 | 0.896 | # # # | # # # | # # # | - - - | 0.779 | 0.92 | 0.985 | 0.896 | - - - | 0.335 | 1.71 | 1.57 | 1.48 | 1.54 | 1.49 | 1.54 | 9.42 | 9.04 | 17.98 | 0 | - - - | - - - | - - - | - - - | 1594 | 1774 | 1654 | 5022 | Over-range | 995 | 683 | 338 | 2228 | 169 | 162 | 294 | 1633 | 1259 | 1648 | 1630 | 4536 | 1259 | 1648 | 1630 | 4536 | - - - | - - - | - - - | - - -
5/11/2026 | 2:15:00 AM | 284.97 | 282.43 | 281.1 | 492.72 | 486.57 | 490.34 | 5.3032 | 5.8593 | 5.7476 | 2.7668 | 1.432 | 1.429 | 1.426 | 1.505 | 1.452 | 1.298 | Over-range | 60 | 1189 | 1506 | 1586 | 4281 | - - - | - - - | - - - | - - - | 1189 | 1506 | 1586 | 4281 | 917 | 664 | -98 | 1482 | - - - | - - - | - - - | - - - | 917 | 664 | -98 | 1482 | 1511 | 1654 | 1616 | 4781 | # # # | # # # | # # # | # # # | 0.787 | 0.91 | 0.982 | 0.895 | # # # | # # # | # # # | - - - | 0.793 | 0.914 | 0.998 | 0.904 | - - - | 0.346 | 1.72 | 1.58 | 1.52 | 1.56 | 1.51 | 1.56 | 9.87 | 9.51 | 18.24 | 0 | - - - | - - - | - - - | - - - | 1511 | 1654 | 1616 | 4781 | Over-range | 932 | 685 | 310 | 2129 | 165 | 166 | 292 | 1528 | 1193 | 1503 | 1585 | 4282 | 1193 | 1503 | 1585 | 4282 | - - - | - - - | - - - | - - -
5/11/2026 | 2:30:00 AM | 285.16 | 282.66 | 281.29 | 493.13 | 486.9 | 490.65 | 4.9465 | 5.1696 | 5.551 | 2.7668 | 1.432 | 1.429 | 1.426 | 1.498 | 1.426 | 1.351 | Over-range | 60.02 | 1133 | 1288 | 1534 | 3955 | - - - | - - - | - - - | - - - | 1133 | 1288 | 1534 | 3955 | 824 | 670 | -1 | 1493 | - - - | - - - | - - - | - - - | 824 | 670 | -1 | 1493 | 1411 | 1461 | 1561 | 4433 | # # # | # # # | # # # | # # # | 0.803 | 0.882 | 0.983 | 0.892 | # # # | # # # | # # # | - - - | 0.809 | 0.887 | 1 | 0.902 | - - - | 0.378 | 1.73 | 1.59 | 1.52 | 1.56 | 1.52 | 1.57 | 10.63 | 10.53 | 18.7 | 0 | - - - | - - - | - - - | - - - | 1411 | 1461 | 1561 | 4433 | Over-range | 841 | 689 | 291 | 2002 | 164 | 162 | 290 | 1334 | 1136 | 1286 | 1534 | 3956 | 1136 | 1286 | 1534 | 3956 | - - - | - - - | - - - | - - -
5/11/2026 | 2:45:00 AM | 285.22 | 282.63 | 281.22 | 493.21 | 486.72 | 490.67 | 5.2545 | 5.774 | 5.7189 | 2.7627 | 1.432 | 1.429 | 1.426 | 1.504 | 1.45 | 1.309 | Over-range | 60.01 | 1181 | 1473 | 1577 | 4232 | - - - | - - - | - - - | - - - | 1181 | 1473 | 1577 | 4232 | 904 | 667 | -83 | 1487 | - - - | - - - | - - - | - - - | 904 | 667 | -83 | 1487 | 1497 | 1627 | 1608 | 4732 | # # # | # # # | # # # | # # # | 0.789 | 0.906 | 0.981 | 0.894 | # # # | # # # | # # # | - - - | 0.795 | 0.91 | 0.998 | 0.903 | - - - | 0.351 | 1.74 | 1.62 | 1.54 | 1.58 | 1.54 | 1.59 | 10.03 | 9.81 | 18.37 | 0 | - - - | - - - | - - - | - - - | 1497 | 1627 | 1608 | 4732 | Over-range | 920 | 687 | 311 | 2117 | 171 | 164 | 293 | 1503 | 1184 | 1470 | 1579 | 4233 | 1184 | 1470 | 1579 | 4233 | - - - | - - - | - - - | - - -
5/11/2026 | 3:00:00 AM | 285.15 | 282.56 | 281.19 | 493.04 | 486.72 | 490.57 | 5.0589 | 5.4375 | 5.6017 | 2.7609 | 1.432 | 1.429 | 1.426 | 1.499 | 1.478 | 1.34 | Over-range | 60.01 | 1146 | 1337 | 1540 | 4023 | - - - | - - - | - - - | - - - | 1146 | 1337 | 1540 | 4023 | 846 | 668 | -24 | 1488 | - - - | - - - | - - - | - - - | 846 | 668 | -24 | 1488 | 1435 | 1513 | 1574 | 4522 | # # # | # # # | # # # | # # # | 0.798 | 0.884 | 0.979 | 0.89 | # # # | # # # | # # # | - - - | 0.805 | 0.889 | 0.996 | 0.899 | - - - | 0.37 | 1.73 | 1.61 | 1.55 | 1.57 | 1.54 | 1.58 | 10.63 | 10.63 | 18.57 | 0 | - - - | - - - | - - - | - - - | 1435 | 1513 | 1574 | 4522 | Over-range | 862 | 687 | 322 | 2062 | 168 | 163 | 291 | 1418 | 1149 | 1335 | 1541 | 4024 | 1149 | 1335 | 1541 | 4024 | - - - | - - - | - - - | - - -
5/11/2026 | 3:15:00 AM | 285.27 | 282.77 | 281.3 | 493.37 | 486.99 | 490.74 | 4.6593 | 4.6376 | 5.4089 | 2.77 | 1.432 | 1.429 | 1.426 | 1.494 | 1.444 | 1.395 | Over-range | 59.99 | 1085 | 1105 | 1490 | 3680 | - - - | - - - | - - - | - - - | 1085 | 1105 | 1490 | 3680 | 747 | 675 | 80 | 1502 | - - - | - - - | - - - | - - - | 747 | 675 | 80 | 1502 | 1328 | 1307 | 1521 | 4156 | # # # | # # # | # # # | # # # | 0.817 | 0.846 | 0.979 | 0.885 | # # # | # # # | # # # | - - - | 0.824 | 0.852 | 0.998 | 0.896 | - - - | 0.408 | 1.75 | 1.62 | 1.54 | 1.58 | 1.54 | 1.59 | 11.42 | 11.93 | 19.18 | 0 | - - - | - - - | - - - | - - - | 1328 | 1307 | 1521 | 4156 | Over-range | 766 | 694 | 307 | 1931 | 169 | 159 | 291 | 1211 | 1085 | 1104 | 1491 | 3680 | 1085 | 1104 | 1491 | 3680 | - - - | - - - | - - - | - - -
5/11/2026 | 3:30:00 AM | 285.14 | 282.63 | 281.22 | 493.11 | 486.77 | 490.58 | 4.8043 | 4.9002 | 5.4764 | 2.7655 | 1.431 | 1.429 | 1.425 | 1.495 | 1.425 | 1.373 | Over-range | 60 | 1109 | 1197 | 1512 | 3818 | - - - | - - - | - - - | - - - | 1109 | 1197 | 1512 | 3818 | 786 | 672 | 40 | 1498 | - - - | - - - | - - - | - - - | 786 | 672 | 40 | 1498 | 1369 | 1383 | 1540 | 4292 | # # # | # # # | # # # | # # # | 0.81 | 0.866 | 0.982 | 0.889 | # # # | # # # | # # # | - - - | 0.816 | 0.871 | 0.999 | 0.899 | - - - | 0.393 | 1.76 | 1.61 | 1.56 | 1.58 | 1.55 | 1.6 | 10.99 | 11.1 | 18.83 | 0 | - - - | - - - | - - - | - - - | 1369 | 1383 | 1540 | 4292 | Over-range | 803 | 691 | 294 | 1961 | 164 | 158 | 289 | 1264 | 1112 | 1197 | 1509 | 3818 | 1112 | 1197 | 1509 | 3818 | - - - | - - - | - - - | - - -
5/11/2026 | 3:45:00 AM | 285.1 | 282.68 | 281.18 | 493.12 | 486.86 | 490.45 | 4.9517 | 5.1869 | 5.5567 | 2.7637 | 1.431 | 1.429 | 1.425 | 1.499 | 1.432 | 1.351 | Over-range | 60.02 | 1133 | 1291 | 1534 | 3958 | - - - | - - - | - - - | - - - | 1133 | 1291 | 1534 | 3958 | 823 | 671 | -2 | 1491 | - - - | - - - | - - - | - - - | 823 | 671 | -2 | 1491 | 1411 | 1464 | 1562 | 4437 | # # # | # # # | # # # | # # # | 0.803 | 0.882 | 0.982 | 0.892 | # # # | # # # | # # # | - - - | 0.809 | 0.887 | 1 | 0.902 | - - - | 0.377 | 1.73 | 1.65 | 1.57 | 1.59 | 1.56 | 1.6 | 10.62 | 10.7 | 18.8 | 0 | - - - | - - - | - - - | - - - | 1411 | 1464 | 1562 | 4437 | Over-range | 841 | 689 | 295 | 2006 | 172 | 159 | 292 | 1340 | 1133 | 1290 | 1536 | 3959 | 1133 | 1290 | 1536 | 3959 | - - - | - - - | - - - | - - -
5/11/2026 | 4:00:00 AM | 285.08 | 282.6 | 281.18 | 493.01 | 486.77 | 490.49 | 5.5032 | 6.2539 | 5.8496 | 2.7502 | 1.431 | 1.428 | 1.425 | 1.506 | 1.466 | 1.274 | Over-range | 60.01 | 1221 | 1628 | 1611 | 4460 | - - - | - - - | - - - | - - - | 1221 | 1628 | 1611 | 4460 | 969 | 667 | -150 | 1485 | - - - | - - - | - - - | - - - | 969 | 667 | -150 | 1485 | 1569 | 1767 | 1645 | 4980 | # # # | # # # | # # # | # # # | 0.779 | 0.921 | 0.979 | 0.896 | # # # | # # # | # # # | - - - | 0.783 | 0.926 | 0.996 | 0.904 | - - - | 0.333 | 1.76 | 1.62 | 1.57 | 1.58 | 1.56 | 1.6 | 9.52 | 9.17 | 18.17 | 0 | - - - | - - - | - - - | - - - | 1569 | 1767 | 1645 | 4980 | Over-range | 985 | 687 | 333 | 2217 | 174 | 163 | 296 | 1646 | 1221 | 1630 | 1609 | 4459 | 1221 | 1630 | 1609 | 4459 | - - - | - - - | - - - | - - -
5/11/2026 | 4:15:00 AM | 284.88 | 282.48 | 281.03 | 492.74 | 486.54 | 490.16 | 5.3435 | 5.8498 | 5.7527 | 2.7582 | 1.432 | 1.429 | 1.426 | 1.499 | 1.457 | 1.306 | Over-range | 60.02 | 1200 | 1503 | 1586 | 4289 | - - - | - - - | - - - | - - - | 1200 | 1503 | 1586 | 4289 | 919 | 666 | -83 | 1500 | - - - | - - - | - - - | - - - | 919 | 666 | -83 | 1500 | 1521 | 1652 | 1617 | 4789 | # # # | # # # | # # # | # # # | 0.789 | 0.91 | 0.981 | 0.896 | # # # | # # # | # # # | - - - | 0.787 | 0.907 | 0.985 | 0.895 | - - - | 0.35 | 1.77 | 1.64 | 1.61 | 1.6 | 1.58 | 1.63 | 9.78 | 9.61 | 18.22 | 0 | - - - | - - - | - - - | - - - | 1521 | 1652 | 1617 | 4789 | Over-range | 934 | 685 | 312 | 2132 | 168 | 162 | 293 | 1510 | 1211 | 1514 | 1599 | 4324 | 1211 | 1514 | 1599 | 4324 | - - - | - - - | - - - | - - -
5/11/2026 | 4:30:00 AM | 284.58 | 282.26 | 280.88 | 492.23 | 486.27 | 489.76 | 5.2863 | 5.7438 | 5.7231 | 2.757 | 1.432 | 1.43 | 1.426 | 1.498 | 1.459 | 1.314 | Over-range | 60.01 | 1190 | 1470 | 1578 | 4238 | - - - | - - - | - - - | - - - | 1190 | 1470 | 1578 | 4238 | 902 | 664 | -70 | 1496 | - - - | - - - | - - - | - - - | 902 | 664 | -70 | 1496 | 1503 | 1621 | 1607 | 4732 | # # # | # # # | # # # | # # # | 0.792 | 0.907 | 0.982 | 0.896 | # # # | # # # | # # # | - - - | 0.797 | 0.911 | 0.998 | 0.904 | - - - | 0.353 | 1.78 | 1.66 | 1.64 | 1.61 | 1.6 | 1.65 | 9.85 | 9.77 | 18.31 | 0 | - - - | - - - | - - - | - - - | 1503 | 1621 | 1607 | 4732 | Over-range | 918 | 683 | 307 | 2105 | 169 | 160 | 292 | 1477 | 1190 | 1472 | 1575 | 4237 | 1190 | 1472 | 1575 | 4237 | - - - | - - - | - - - | - - -
5/11/2026 | 4:45:00 AM | 284.65 | 282.25 | 280.77 | 492.34 | 486.13 | 489.73 | 4.7535 | 4.8439 | 5.4414 | 2.7758 | 1.431 | 1.429 | 1.426 | 1.492 | 1.479 | 1.383 | Over-range | 60.01 | 1096 | 1143 | 1491 | 3731 | - - - | - - - | - - - | - - - | 1096 | 1143 | 1491 | 3731 | 761 | 667 | 56 | 1484 | - - - | - - - | - - - | - - - | 761 | 667 | 56 | 1484 | 1346 | 1342 | 1526 | 4214 | # # # | # # # | # # # | # # # | 0.814 | 0.852 | 0.977 | 0.885 | # # # | # # # | # # # | - - - | 0.82 | 0.858 | 0.995 | 0.895 | - - - | 0.398 | 1.8 | 1.71 | 1.65 | 1.64 | 1.63 | 1.68 | 11.28 | 11.83 | 18.92 | 0 | - - - | - - - | - - - | - - - | 1346 | 1342 | 1526 | 4214 | Over-range | 779 | 685 | 321 | 1958 | 167 | 155 | 289 | 1266 | 1096 | 1145 | 1490 | 3731 | 1096 | 1145 | 1490 | 3731 | - - - | - - - | - - - | - - -
5/11/2026 | 5:00:00 AM | 284.41 | 282.01 | 280.48 | 491.98 | 485.62 | 489.25 | 4.7512 | 4.7778 | 5.4441 | 2.7888 | 1.431 | 1.429 | 1.426 | 1.491 | 1.435 | 1.377 | Over-range | 60.01 | 1100 | 1155 | 1497 | 3752 | - - - | - - - | - - - | - - - | 1100 | 1155 | 1497 | 3752 | 764 | 663 | 49 | 1477 | - - - | - - - | - - - | - - - | 764 | 663 | 49 | 1477 | 1350 | 1343 | 1527 | 4219 | # # # | # # # | # # # | # # # | 0.815 | 0.86 | 0.981 | 0.889 | # # # | # # # | # # # | - - - | 0.822 | 0.866 | 0.999 | 0.899 | - - - | 0.394 | 1.84 | 1.74 | 1.69 | 1.67 | 1.68 | 1.72 | 11.07 | 11.44 | 18.8 | 0 | - - - | - - - | - - - | - - - | 1350 | 1343 | 1527 | 4219 | Over-range | 782 | 681 | 298 | 1929 | 165 | 155 | 288 | 1239 | 1101 | 1156 | 1495 | 3752 | 1101 | 1156 | 1495 | 3752 | - - - | - - - | - - - | - - -
5/11/2026 | 5:15:00 AM | 283.73 | 281.27 | 279.77 | 490.73 | 484.37 | 488.09 | 4.7414 | 4.7485 | 5.4131 | 2.7743 | 1.43 | 1.43 | 1.426 | 1.49 | 1.423 | 1.376 | Over-range | 60 | 1099 | 1154 | 1487 | 3739 | - - - | - - - | - - - | - - - | 1099 | 1154 | 1487 | 3739 | 759 | 654 | 43 | 1457 | - - - | - - - | - - - | - - - | 759 | 654 | 43 | 1457 | 1345 | 1335 | 1514 | 4195 | # # # | # # # | # # # | # # # | 0.817 | 0.864 | 0.982 | 0.891 | # # # | # # # | # # # | - - - | 0.822 | 0.87 | 0.999 | 0.901 | - - - | 0.39 | 1.86 | 1.82 | 1.75 | 1.71 | 1.73 | 1.77 | 10.97 | 11.26 | 18.8 | 0 | - - - | - - - | - - - | - - - | 1345 | 1335 | 1514 | 4195 | Over-range | 776 | 672 | 289 | 1902 | 165 | 151 | 285 | 1223 | 1098 | 1156 | 1484 | 3739 | 1098 | 1156 | 1484 | 3739 | - - - | - - - | - - - | - - -
5/11/2026 | 5:30:00 AM | 283.38 | 280.98 | 279.46 | 490.19 | 483.87 | 487.46 | 5.1653 | 5.5829 | 5.6603 | 2.7754 | 1.43 | 1.43 | 1.426 | 1.495 | 1.458 | 1.32 | Over-range | 60.01 | 1166 | 1414 | 1552 | 4132 | - - - | - - - | - - - | - - - | 1166 | 1414 | 1552 | 4132 | 866 | 646 | -72 | 1439 | - - - | - - - | - - - | - - - | 866 | 646 | -72 | 1439 | 1462 | 1564 | 1581 | 4607 | # # # | # # # | # # # | # # # | 0.797 | 0.904 | 0.981 | 0.897 | # # # | # # # | # # # | - - - | 0.802 | 0.909 | 0.998 | 0.905 | - - - | 0.348 | 1.91 | 1.85 | 1.81 | 1.75 | 1.78 | 1.83 | 10.05 | 10.02 | 18.22 | 0 | - - - | - - - | - - - | - - - | 1462 | 1564 | 1581 | 4607 | Over-range | 883 | 665 | 303 | 2039 | 170 | 157 | 288 | 1441 | 1166 | 1414 | 1552 | 4131 | 1166 | 1414 | 1552 | 4131 | - - - | - - - | - - - | - - -
5/11/2026 | 5:45:00 AM | 282.96 | 280.53 | 279.12 | 489.41 | 483.15 | 486.87 | 5.4446 | 6.1237 | 5.7979 | 2.7596 | 1.431 | 1.43 | 1.427 | 1.496 | 1.476 | 1.297 | Over-range | 60 | 1210 | 1586 | 1585 | 4381 | - - - | - - - | - - - | - - - | 1210 | 1586 | 1585 | 4381 | 940 | 637 | -149 | 1426 | - - - | - - - | - - - | - - - | 940 | 637 | -149 | 1426 | 1540 | 1717 | 1618 | 4876 | # # # | # # # | # # # | # # # | 0.785 | 0.924 | 0.98 | 0.899 | # # # | # # # | # # # | - - - | 0.79 | 0.928 | 0.995 | 0.906 | - - - | 0.326 | 2.01 | 1.97 | 1.94 | 1.86 | 1.89 | 1.94 | 9.48 | 9.22 | 17.82 | 0 | - - - | - - - | - - - | - - - | 1540 | 1717 | 1618 | 4876 | Over-range | 954 | 657 | 326 | 2141 | 165 | 164 | 288 | 1596 | 1213 | 1585 | 1583 | 4381 | 1213 | 1585 | 1583 | 4381 | - - - | - - - | - - - | - - -
5/11/2026 | 6:00:00 AM | 282.7 | 280.29 | 278.83 | 489 | 482.68 | 486.37 | 5.0707 | 5.4177 | 5.604 | 2.769 | 1.432 | 1.43 | 1.427 | 1.49 | 1.473 | 1.329 | Over-range | 60.01 | 1148 | 1351 | 1532 | 4031 | - - - | - - - | - - - | - - - | 1148 | 1351 | 1532 | 4031 | 836 | 637 | -47 | 1424 | - - - | - - - | - - - | - - - | 836 | 637 | -47 | 1424 | 1430 | 1506 | 1562 | 4498 | # # # | # # # | # # # | # # # | 0.803 | 0.897 | 0.981 | 0.896 | # # # | # # # | # # # | - - - | 0.809 | 0.902 | 0.997 | 0.905 | - - - | 0.353 | 2.04 | 1.97 | 1.94 | 1.86 | 1.91 | 1.96 | 10.28 | 10.28 | 18.05 | 0 | - - - | - - - | - - - | - - - | 1430 | 1506 | 1562 | 4498 | Over-range | 852 | 656 | 302 | 1995 | 163 | 158 | 283 | 1392 | 1151 | 1350 | 1530 | 4032 | 1151 | 1350 | 1530 | 4032 | - - - | - - - | - - - | - - -
5/11/2026 | 6:15:00 AM | 282.28 | 279.96 | 278.47 | 488.28 | 482.2 | 485.66 | 4.5126 | 4.3363 | 5.296 | 2.7665 | 1.432 | 1.431 | 1.428 | 1.484 | 1.456 | 1.401 | Over-range | 59.99 | 1059 | 1013 | 1443 | 3515 | - - - | - - - | - - - | - - - | 1059 | 1013 | 1443 | 3515 | 686 | 638 | 97 | 1420 | - - - | - - - | - - - | - - - | 686 | 638 | 97 | 1420 | 1272 | 1209 | 1474 | 3956 | # # # | # # # | # # # | # # # | 0.832 | 0.838 | 0.979 | 0.888 | # # # | # # # | # # # | - - - | 0.839 | 0.844 | 0.997 | 0.899 | - - - | 0.404 | 2.04 | 2.02 | 1.98 | 1.88 | 1.93 | 1.99 | 11.53 | 12.28 | 18.81 | 0 | - - - | - - - | - - - | - - - | 1272 | 1209 | 1474 | 3956 | Over-range | 706 | 655 | 302 | 1815 | 166 | 150 | 280 | 1128 | 1058 | 1012 | 1444 | 3515 | 1058 | 1012 | 1444 | 3515 | - - - | - - - | - - - | - - -

## Energy and Cost
Energy and Cost
Date | Time | Ep (15 min) | Ep+ (15 min) | Ep- (15 min) | Eq (15 min) | Eq/q1 (15 min) | Eq/q2 (15 min) | Eq/q3 (15 min) | Eq/q4 (15 min) | Es (15 min) | Es+ (15 min) | Es- (15 min)
|  | kWh | kWh | kWh | kvarh | kvarh | kvarh | kvarh | kvarh | kVAh | kVAh | kVAh
5/1/2026 | 11:30:00 AM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5/1/2026 | 11:45:00 AM | 0.851 | 0.851 | 0 | 0.379 | 0.379 | 0 | 0 | 0 | 0.997 | 0.997 | 0
5/1/2026 | 12:00:00 PM | 1.842 | 1.842 | 0 | 0.754 | 0.754 | 0 | 0 | 0 | 2.133 | 2.133 | 0
5/1/2026 | 12:15:00 PM | 2.783 | 2.783 | 0 | 1.135 | 1.135 | 0 | 0 | 0 | 3.22 | 3.22 | 0
5/1/2026 | 12:30:00 PM | 3.544 | 3.544 | 0 | 1.516 | 1.516 | 0 | 0 | 0 | 4.139 | 4.139 | 0
5/1/2026 | 12:45:00 PM | 4.396 | 4.396 | 0 | 1.894 | 1.894 | 0 | 0 | 0 | 5.137 | 5.137 | 0
5/1/2026 | 1:00:00 PM | 5.246 | 5.246 | 0 | 2.272 | 2.272 | 0 | 0 | 0 | 6.131 | 6.131 | 0
5/1/2026 | 1:15:00 PM | 6.231 | 6.231 | 0 | 2.658 | 2.658 | 0 | 0 | 0 | 7.263 | 7.263 | 0
5/1/2026 | 1:30:00 PM | 7.228 | 7.228 | 0 | 3.036 | 3.036 | 0 | 0 | 0 | 8.406 | 8.406 | 0
5/1/2026 | 1:45:00 PM | 8.185 | 8.185 | 0 | 3.413 | 3.413 | 0 | 0 | 0 | 9.506 | 9.506 | 0
5/1/2026 | 2:00:00 PM | 8.989 | 8.989 | 0 | 3.793 | 3.793 | 0 | 0 | 0 | 10.466 | 10.466 | 0
5/1/2026 | 2:15:00 PM | 9.828 | 9.828 | 0 | 4.174 | 4.174 | 0 | 0 | 0 | 11.453 | 11.453 | 0
5/1/2026 | 2:30:00 PM | 10.668 | 10.668 | 0 | 4.554 | 4.554 | 0 | 0 | 0 | 12.44 | 12.44 | 0
5/1/2026 | 2:45:00 PM | 11.61 | 11.61 | 0 | 4.934 | 4.934 | 0 | 0 | 0 | 13.527 | 13.527 | 0
5/1/2026 | 3:00:00 PM | 12.631 | 12.631 | 0 | 5.311 | 5.311 | 0 | 0 | 0 | 14.697 | 14.697 | 0
5/1/2026 | 3:15:00 PM | 13.522 | 13.522 | 0 | 5.692 | 5.692 | 0 | 0 | 0 | 15.736 | 15.736 | 0
5/1/2026 | 3:30:00 PM | 14.31 | 14.31 | 0 | 6.082 | 6.082 | 0 | 0 | 0 | 16.682 | 16.682 | 0
5/1/2026 | 3:45:00 PM | 15.165 | 15.165 | 0 | 6.463 | 6.463 | 0 | 0 | 0 | 17.683 | 17.683 | 0
5/1/2026 | 4:00:00 PM | 16.124 | 16.124 | 0 | 6.843 | 6.843 | 0 | 0 | 0 | 18.788 | 18.788 | 0
5/1/2026 | 4:15:00 PM | 17.124 | 17.124 | 0 | 7.223 | 7.223 | 0 | 0 | 0 | 19.936 | 19.936 | 0
5/1/2026 | 4:30:00 PM | 17.985 | 17.985 | 0 | 7.607 | 7.607 | 0 | 0 | 0 | 20.953 | 20.953 | 0
5/1/2026 | 4:45:00 PM | 18.806 | 18.806 | 0 | 7.992 | 7.992 | 0 | 0 | 0 | 21.926 | 21.926 | 0
5/1/2026 | 5:00:00 PM | 19.673 | 19.673 | 0 | 8.375 | 8.375 | 0 | 0 | 0 | 22.94 | 22.94 | 0
5/1/2026 | 5:15:00 PM | 20.696 | 20.696 | 0 | 8.765 | 8.765 | 0 | 0 | 0 | 24.113 | 24.113 | 0
5/1/2026 | 5:30:00 PM | 21.625 | 21.625 | 0 | 9.149 | 9.149 | 0 | 0 | 0 | 25.188 | 25.188 | 0
5/1/2026 | 5:45:00 PM | 22.549 | 22.549 | 0 | 9.532 | 9.532 | 0 | 0 | 0 | 26.262 | 26.262 | 0
5/1/2026 | 6:00:00 PM | 23.327 | 23.327 | 0 | 9.918 | 9.918 | 0 | 0 | 0 | 27.198 | 27.198 | 0
5/1/2026 | 6:15:00 PM | 24.173 | 24.173 | 0 | 10.309 | 10.309 | 0 | 0 | 0 | 28.197 | 28.197 | 0
5/1/2026 | 6:30:00 PM | 25.026 | 25.026 | 0 | 10.701 | 10.701 | 0 | 0 | 0 | 29.202 | 29.202 | 0
5/1/2026 | 6:45:00 PM | 25.993 | 25.993 | 0 | 11.091 | 11.091 | 0 | 0 | 0 | 30.32 | 30.32 | 0
5/1/2026 | 7:00:00 PM | 27.037 | 27.037 | 0 | 11.462 | 11.462 | 0 | 0 | 0 | 31.499 | 31.499 | 0
5/1/2026 | 7:15:00 PM | 28.037 | 28.037 | 0 | 11.822 | 11.822 | 0 | 0 | 0 | 32.614 | 32.614 | 0
5/1/2026 | 7:30:00 PM | 29.098 | 29.098 | 0 | 12.192 | 12.192 | 0 | 0 | 0 | 33.797 | 33.797 | 0
5/1/2026 | 7:45:00 PM | 30.192 | 30.192 | 0 | 12.553 | 12.553 | 0 | 0 | 0 | 35.016 | 35.016 | 0
5/1/2026 | 8:00:00 PM | 31.075 | 31.075 | 0 | 12.918 | 12.918 | 0 | 0 | 0 | 36.013 | 36.013 | 0
5/1/2026 | 8:15:00 PM | 32.025 | 32.025 | 0 | 13.282 | 13.282 | 0 | 0 | 0 | 37.078 | 37.078 | 0
5/1/2026 | 8:30:00 PM | 32.971 | 32.971 | 0 | 13.646 | 13.646 | 0 | 0 | 0 | 38.137 | 38.137 | 0
5/1/2026 | 8:45:00 PM | 34.004 | 34.004 | 0 | 14.006 | 14.006 | 0 | 0 | 0 | 39.289 | 39.289 | 0
5/1/2026 | 9:00:00 PM | 35.103 | 35.103 | 0 | 14.37 | 14.37 | 0 | 0 | 0 | 40.515 | 40.515 | 0
5/1/2026 | 9:15:00 PM | 36.126 | 36.126 | 0 | 14.735 | 14.735 | 0 | 0 | 0 | 41.657 | 41.657 | 0
5/1/2026 | 9:30:00 PM | 37.112 | 37.112 | 0 | 15.105 | 15.105 | 0 | 0 | 0 | 42.76 | 42.76 | 0
5/1/2026 | 9:45:00 PM | 38.181 | 38.181 | 0 | 15.483 | 15.483 | 0 | 0 | 0 | 43.954 | 43.954 | 0
5/1/2026 | 10:00:00 PM | 39.257 | 39.257 | 0 | 15.855 | 15.855 | 0 | 0 | 0 | 45.156 | 45.156 | 0
5/1/2026 | 10:15:00 PM | 40.244 | 40.244 | 0 | 16.227 | 16.227 | 0 | 0 | 0 | 46.267 | 46.267 | 0
5/1/2026 | 10:30:00 PM | 41.161 | 41.161 | 0 | 16.596 | 16.596 | 0 | 0 | 0 | 47.3 | 47.3 | 0
5/1/2026 | 10:45:00 PM | 42.095 | 42.095 | 0 | 16.964 | 16.964 | 0 | 0 | 0 | 48.349 | 48.349 | 0
5/1/2026 | 11:00:00 PM | 43.099 | 43.099 | 0 | 17.334 | 17.334 | 0 | 0 | 0 | 49.472 | 49.472 | 0
5/1/2026 | 11:15:00 PM | 44.179 | 44.179 | 0 | 17.704 | 17.704 | 0 | 0 | 0 | 50.679 | 50.679 | 0
5/1/2026 | 11:30:00 PM | 45.082 | 45.082 | 0 | 18.08 | 18.08 | 0 | 0 | 0 | 51.701 | 51.701 | 0
5/1/2026 | 11:45:00 PM | 46.017 | 46.017 | 0 | 18.458 | 18.458 | 0 | 0 | 0 | 52.756 | 52.756 | 0
5/2/2026 | 12:00:00 AM | 46.962 | 46.962 | 0 | 18.846 | 18.846 | 0 | 0 | 0 | 53.822 | 53.822 | 0
5/2/2026 | 12:15:00 AM | 47.933 | 47.933 | 0 | 19.226 | 19.226 | 0 | 0 | 0 | 54.915 | 54.915 | 0
5/2/2026 | 12:30:00 AM | 49.025 | 49.025 | 0 | 19.606 | 19.606 | 0 | 0 | 0 | 56.137 | 56.137 | 0
5/2/2026 | 12:45:00 AM | 50.067 | 50.067 | 0 | 19.988 | 19.988 | 0 | 0 | 0 | 57.306 | 57.306 | 0
5/2/2026 | 1:00:00 AM | 50.95 | 50.95 | 0 | 20.374 | 20.374 | 0 | 0 | 0 | 58.314 | 58.314 | 0
5/2/2026 | 1:15:00 AM | 51.898 | 51.898 | 0 | 20.764 | 20.764 | 0 | 0 | 0 | 59.386 | 59.386 | 0
5/2/2026 | 1:30:00 AM | 52.834 | 52.834 | 0 | 21.134 | 21.134 | 0 | 0 | 0 | 60.439 | 60.439 | 0
5/2/2026 | 1:45:00 AM | 53.773 | 53.773 | 0 | 21.507 | 21.507 | 0 | 0 | 0 | 61.495 | 61.495 | 0
5/2/2026 | 2:00:00 AM | 54.794 | 54.794 | 0 | 21.878 | 21.878 | 0 | 0 | 0 | 62.637 | 62.637 | 0
5/2/2026 | 2:15:00 AM | 55.842 | 55.842 | 0 | 22.255 | 22.255 | 0 | 0 | 0 | 63.807 | 63.807 | 0
5/2/2026 | 2:30:00 AM | 56.792 | 56.792 | 0 | 22.624 | 22.624 | 0 | 0 | 0 | 64.877 | 64.877 | 0
5/2/2026 | 2:45:00 AM | 57.697 | 57.697 | 0 | 22.996 | 22.996 | 0 | 0 | 0 | 65.897 | 65.897 | 0
5/2/2026 | 3:00:00 AM | 58.623 | 58.623 | 0 | 23.369 | 23.369 | 0 | 0 | 0 | 66.94 | 66.94 | 0
5/2/2026 | 3:15:00 AM | 59.604 | 59.604 | 0 | 23.741 | 23.741 | 0 | 0 | 0 | 68.041 | 68.041 | 0
5/2/2026 | 3:30:00 AM | 60.664 | 60.664 | 0 | 24.113 | 24.113 | 0 | 0 | 0 | 69.225 | 69.225 | 0
5/2/2026 | 3:45:00 AM | 61.714 | 61.714 | 0 | 24.485 | 24.485 | 0 | 0 | 0 | 70.398 | 70.398 | 0
5/2/2026 | 4:00:00 AM | 62.608 | 62.608 | 0 | 24.862 | 24.862 | 0 | 0 | 0 | 71.412 | 71.412 | 0
5/2/2026 | 4:15:00 AM | 63.551 | 63.551 | 0 | 25.24 | 25.24 | 0 | 0 | 0 | 72.475 | 72.475 | 0
5/2/2026 | 4:30:00 AM | 64.557 | 64.557 | 0 | 25.624 | 25.624 | 0 | 0 | 0 | 73.603 | 73.603 | 0
5/2/2026 | 4:45:00 AM | 65.606 | 65.606 | 0 | 25.997 | 25.997 | 0 | 0 | 0 | 74.775 | 74.775 | 0
5/2/2026 | 5:00:00 AM | 66.638 | 66.638 | 0 | 26.372 | 26.372 | 0 | 0 | 0 | 75.932 | 75.932 | 0
5/2/2026 | 5:15:00 AM | 67.519 | 67.519 | 0 | 26.752 | 26.752 | 0 | 0 | 0 | 76.933 | 76.933 | 0
5/2/2026 | 5:30:00 AM | 68.454 | 68.454 | 0 | 27.13 | 27.13 | 0 | 0 | 0 | 77.987 | 77.987 | 0
5/2/2026 | 5:45:00 AM | 69.378 | 69.378 | 0 | 27.507 | 27.507 | 0 | 0 | 0 | 79.028 | 79.028 | 0
5/2/2026 | 6:00:00 AM | 70.361 | 70.361 | 0 | 27.879 | 27.879 | 0 | 0 | 0 | 80.131 | 80.131 | 0
5/2/2026 | 6:15:00 AM | 71.4 | 71.4 | 0 | 28.251 | 28.251 | 0 | 0 | 0 | 81.292 | 81.292 | 0
5/2/2026 | 6:30:00 AM | 72.36 | 72.36 | 0 | 28.622 | 28.622 | 0 | 0 | 0 | 82.371 | 82.371 | 0
5/2/2026 | 6:45:00 AM | 73.266 | 73.266 | 0 | 29.001 | 29.001 | 0 | 0 | 0 | 83.394 | 83.394 | 0
5/2/2026 | 7:00:00 AM | 74.188 | 74.188 | 0 | 29.371 | 29.371 | 0 | 0 | 0 | 84.431 | 84.431 | 0
5/2/2026 | 7:15:00 AM | 75.112 | 75.112 | 0 | 29.74 | 29.74 | 0 | 0 | 0 | 85.47 | 85.47 | 0
5/2/2026 | 7:30:00 AM | 76.137 | 76.137 | 0 | 30.107 | 30.107 | 0 | 0 | 0 | 86.614 | 86.614 | 0
5/2/2026 | 7:45:00 AM | 77.14 | 77.14 | 0 | 30.474 | 30.474 | 0 | 0 | 0 | 87.734 | 87.734 | 0
5/2/2026 | 8:00:00 AM | 78.007 | 78.007 | 0 | 30.84 | 30.84 | 0 | 0 | 0 | 88.715 | 88.715 | 0
5/2/2026 | 8:15:00 AM | 78.922 | 78.922 | 0 | 31.203 | 31.203 | 0 | 0 | 0 | 89.742 | 89.742 | 0
5/2/2026 | 8:30:00 AM | 79.831 | 79.831 | 0 | 31.56 | 31.56 | 0 | 0 | 0 | 90.759 | 90.759 | 0
5/2/2026 | 8:45:00 AM | 80.757 | 80.757 | 0 | 31.915 | 31.915 | 0 | 0 | 0 | 91.795 | 91.795 | 0
5/2/2026 | 9:00:00 AM | 81.789 | 81.789 | 0 | 32.276 | 32.276 | 0 | 0 | 0 | 92.942 | 92.942 | 0
5/2/2026 | 9:15:00 AM | 82.775 | 82.775 | 0 | 32.629 | 32.629 | 0 | 0 | 0 | 94.039 | 94.039 | 0
5/2/2026 | 9:30:00 AM | 83.679 | 83.679 | 0 | 32.98 | 32.98 | 0 | 0 | 0 | 95.05 | 95.05 | 0
5/2/2026 | 9:45:00 AM | 84.544 | 84.544 | 0 | 33.336 | 33.336 | 0 | 0 | 0 | 96.034 | 96.034 | 0
5/2/2026 | 10:00:00 AM | 85.339 | 85.339 | 0 | 33.716 | 33.716 | 0 | 0 | 0 | 96.979 | 96.979 | 0
5/2/2026 | 10:15:00 AM | 86.15 | 86.15 | 0 | 34.094 | 34.094 | 0 | 0 | 0 | 97.936 | 97.936 | 0
5/2/2026 | 10:30:00 AM | 87.044 | 87.044 | 0 | 34.469 | 34.469 | 0 | 0 | 0 | 98.972 | 98.972 | 0
5/2/2026 | 10:45:00 AM | 87.981 | 87.981 | 0 | 34.84 | 34.84 | 0 | 0 | 0 | 100.049 | 100.049 | 0
5/2/2026 | 11:00:00 AM | 88.828 | 88.828 | 0 | 35.212 | 35.212 | 0 | 0 | 0 | 101.043 | 101.043 | 0
5/2/2026 | 11:15:00 AM | 89.607 | 89.607 | 0 | 35.59 | 35.59 | 0 | 0 | 0 | 101.971 | 101.971 | 0
5/2/2026 | 11:30:00 AM | 90.417 | 90.417 | 0 | 35.956 | 35.956 | 0 | 0 | 0 | 102.921 | 102.921 | 0
5/2/2026 | 11:45:00 AM | 91.245 | 91.245 | 0 | 36.322 | 36.322 | 0 | 0 | 0 | 103.888 | 103.888 | 0
5/2/2026 | 12:00:00 PM | 92.193 | 92.193 | 0 | 36.688 | 36.688 | 0 | 0 | 0 | 104.977 | 104.977 | 0
5/2/2026 | 12:15:00 PM | 93.169 | 93.169 | 0 | 37.065 | 37.065 | 0 | 0 | 0 | 106.098 | 106.098 | 0
5/2/2026 | 12:30:00 PM | 94.084 | 94.084 | 0 | 37.442 | 37.442 | 0 | 0 | 0 | 107.157 | 107.157 | 0
5/2/2026 | 12:45:00 PM | 94.962 | 94.962 | 0 | 37.819 | 37.819 | 0 | 0 | 0 | 108.178 | 108.178 | 0
5/2/2026 | 1:00:00 PM | 95.918 | 95.918 | 0 | 38.196 | 38.196 | 0 | 0 | 0 | 109.28 | 109.28 | 0
5/2/2026 | 1:15:00 PM | 96.912 | 96.912 | 0 | 38.58 | 38.58 | 0 | 0 | 0 | 110.419 | 110.419 | 0
5/2/2026 | 1:30:00 PM | 97.778 | 97.778 | 0 | 38.959 | 38.959 | 0 | 0 | 0 | 111.438 | 111.438 | 0
5/2/2026 | 1:45:00 PM | 98.587 | 98.587 | 0 | 39.339 | 39.339 | 0 | 0 | 0 | 112.397 | 112.397 | 0
5/2/2026 | 2:00:00 PM | 99.421 | 99.421 | 0 | 39.716 | 39.716 | 0 | 0 | 0 | 113.377 | 113.377 | 0
5/2/2026 | 2:15:00 PM | 100.325 | 100.325 | 0 | 40.094 | 40.094 | 0 | 0 | 0 | 114.425 | 114.425 | 0
5/2/2026 | 2:30:00 PM | 101.313 | 101.313 | 0 | 40.47 | 40.47 | 0 | 0 | 0 | 115.559 | 115.559 | 0
5/2/2026 | 2:45:00 PM | 102.165 | 102.165 | 0 | 40.846 | 40.846 | 0 | 0 | 0 | 116.562 | 116.562 | 0
5/2/2026 | 3:00:00 PM | 102.994 | 102.994 | 0 | 41.231 | 41.231 | 0 | 0 | 0 | 117.54 | 117.54 | 0
5/2/2026 | 3:15:00 PM | 103.83 | 103.83 | 0 | 41.607 | 41.607 | 0 | 0 | 0 | 118.521 | 118.521 | 0
5/2/2026 | 3:30:00 PM | 104.743 | 104.743 | 0 | 41.982 | 41.982 | 0 | 0 | 0 | 119.579 | 119.579 | 0
5/2/2026 | 3:45:00 PM | 105.757 | 105.757 | 0 | 42.357 | 42.357 | 0 | 0 | 0 | 120.739 | 120.739 | 0
5/2/2026 | 4:00:00 PM | 106.659 | 106.659 | 0 | 42.733 | 42.733 | 0 | 0 | 0 | 121.784 | 121.784 | 0
5/2/2026 | 4:15:00 PM | 107.539 | 107.539 | 0 | 43.108 | 43.108 | 0 | 0 | 0 | 122.808 | 122.808 | 0
5/2/2026 | 4:30:00 PM | 108.51 | 108.51 | 0 | 43.482 | 43.482 | 0 | 0 | 0 | 123.923 | 123.923 | 0
5/2/2026 | 4:45:00 PM | 109.451 | 109.451 | 0 | 43.862 | 43.862 | 0 | 0 | 0 | 125.011 | 125.011 | 0
5/2/2026 | 5:00:00 PM | 110.229 | 110.229 | 0 | 44.239 | 44.239 | 0 | 0 | 0 | 125.941 | 125.941 | 0
5/2/2026 | 5:15:00 PM | 111.074 | 111.074 | 0 | 44.615 | 44.615 | 0 | 0 | 0 | 126.932 | 126.932 | 0
5/2/2026 | 5:30:00 PM | 112.022 | 112.022 | 0 | 44.991 | 44.991 | 0 | 0 | 0 | 128.025 | 128.025 | 0
5/2/2026 | 5:45:00 PM | 112.963 | 112.963 | 0 | 45.368 | 45.368 | 0 | 0 | 0 | 129.11 | 129.11 | 0
5/2/2026 | 6:00:00 PM | 113.723 | 113.723 | 0 | 45.745 | 45.745 | 0 | 0 | 0 | 130.026 | 130.026 | 0
5/2/2026 | 6:15:00 PM | 114.562 | 114.562 | 0 | 46.123 | 46.123 | 0 | 0 | 0 | 131.011 | 131.011 | 0
5/2/2026 | 6:30:00 PM | 115.495 | 115.495 | 0 | 46.508 | 46.508 | 0 | 0 | 0 | 132.09 | 132.09 | 0
5/2/2026 | 6:45:00 PM | 116.456 | 116.456 | 0 | 46.888 | 46.888 | 0 | 0 | 0 | 133.197 | 133.197 | 0
5/2/2026 | 7:00:00 PM | 117.236 | 117.236 | 0 | 47.272 | 47.272 | 0 | 0 | 0 | 134.136 | 134.136 | 0
5/2/2026 | 7:15:00 PM | 118.051 | 118.051 | 0 | 47.66 | 47.66 | 0 | 0 | 0 | 135.105 | 135.105 | 0
5/2/2026 | 7:30:00 PM | 118.893 | 118.893 | 0 | 48.048 | 48.048 | 0 | 0 | 0 | 136.098 | 136.098 | 0
5/2/2026 | 7:45:00 PM | 119.907 | 119.907 | 0 | 48.42 | 48.42 | 0 | 0 | 0 | 137.249 | 137.249 | 0
5/2/2026 | 8:00:00 PM | 120.932 | 120.932 | 0 | 48.779 | 48.779 | 0 | 0 | 0 | 138.391 | 138.391 | 0
5/2/2026 | 8:15:00 PM | 121.808 | 121.808 | 0 | 49.144 | 49.144 | 0 | 0 | 0 | 139.381 | 139.381 | 0
5/2/2026 | 8:30:00 PM | 122.756 | 122.756 | 0 | 49.517 | 49.517 | 0 | 0 | 0 | 140.445 | 140.445 | 0
5/2/2026 | 8:45:00 PM | 123.704 | 123.704 | 0 | 49.88 | 49.88 | 0 | 0 | 0 | 141.507 | 141.507 | 0
5/2/2026 | 9:00:00 PM | 124.754 | 124.754 | 0 | 50.243 | 50.243 | 0 | 0 | 0 | 142.678 | 142.678 | 0
5/2/2026 | 9:15:00 PM | 125.792 | 125.792 | 0 | 50.609 | 50.609 | 0 | 0 | 0 | 143.836 | 143.836 | 0
5/2/2026 | 9:30:00 PM | 126.661 | 126.661 | 0 | 50.978 | 50.978 | 0 | 0 | 0 | 144.821 | 144.821 | 0
5/2/2026 | 9:45:00 PM | 127.599 | 127.599 | 0 | 51.352 | 51.352 | 0 | 0 | 0 | 145.876 | 145.876 | 0
5/2/2026 | 10:00:00 PM | 128.537 | 128.537 | 0 | 51.726 | 51.726 | 0 | 0 | 0 | 146.931 | 146.931 | 0
5/2/2026 | 10:15:00 PM | 129.584 | 129.584 | 0 | 52.102 | 52.102 | 0 | 0 | 0 | 148.103 | 148.103 | 0
5/2/2026 | 10:30:00 PM | 130.608 | 130.608 | 0 | 52.476 | 52.476 | 0 | 0 | 0 | 149.249 | 149.249 | 0
5/2/2026 | 10:45:00 PM | 131.526 | 131.526 | 0 | 52.854 | 52.854 | 0 | 0 | 0 | 150.289 | 150.289 | 0
5/2/2026 | 11:00:00 PM | 132.451 | 132.451 | 0 | 53.245 | 53.245 | 0 | 0 | 0 | 151.336 | 151.336 | 0
5/2/2026 | 11:15:00 PM | 133.373 | 133.373 | 0 | 53.626 | 53.626 | 0 | 0 | 0 | 152.378 | 152.378 | 0
5/2/2026 | 11:30:00 PM | 134.33 | 134.33 | 0 | 54.01 | 54.01 | 0 | 0 | 0 | 153.458 | 153.458 | 0
5/2/2026 | 11:45:00 PM | 135.391 | 135.391 | 0 | 54.397 | 54.397 | 0 | 0 | 0 | 154.648 | 154.648 | 0
5/3/2026 | 12:00:00 AM | 136.398 | 136.398 | 0 | 54.787 | 54.787 | 0 | 0 | 0 | 155.782 | 155.782 | 0
5/3/2026 | 12:15:00 AM | 137.306 | 137.306 | 0 | 55.182 | 55.182 | 0 | 0 | 0 | 156.819 | 156.819 | 0
5/3/2026 | 12:30:00 AM | 138.231 | 138.231 | 0 | 55.57 | 55.57 | 0 | 0 | 0 | 157.867 | 157.867 | 0
5/3/2026 | 12:45:00 AM | 139.154 | 139.154 | 0 | 55.948 | 55.948 | 0 | 0 | 0 | 158.909 | 158.909 | 0
5/3/2026 | 1:00:00 AM | 140.117 | 140.117 | 0 | 56.329 | 56.329 | 0 | 0 | 0 | 159.993 | 159.993 | 0
5/3/2026 | 1:15:00 AM | 141.141 | 141.141 | 0 | 56.718 | 56.718 | 0 | 0 | 0 | 161.141 | 161.141 | 0
5/3/2026 | 1:30:00 AM | 142.043 | 142.043 | 0 | 57.098 | 57.098 | 0 | 0 | 0 | 162.165 | 162.165 | 0
5/3/2026 | 1:45:00 AM | 142.962 | 142.962 | 0 | 57.481 | 57.481 | 0 | 0 | 0 | 163.205 | 163.205 | 0
5/3/2026 | 2:00:00 AM | 143.881 | 143.881 | 0 | 57.865 | 57.865 | 0 | 0 | 0 | 164.244 | 164.244 | 0
5/3/2026 | 2:15:00 AM | 144.805 | 144.805 | 0 | 58.25 | 58.25 | 0 | 0 | 0 | 165.291 | 165.291 | 0
5/3/2026 | 2:30:00 AM | 145.855 | 145.855 | 0 | 58.637 | 58.637 | 0 | 0 | 0 | 166.47 | 166.47 | 0
5/3/2026 | 2:45:00 AM | 146.904 | 146.904 | 0 | 59.026 | 59.026 | 0 | 0 | 0 | 167.647 | 167.647 | 0
5/3/2026 | 3:00:00 AM | 147.804 | 147.804 | 0 | 59.417 | 59.417 | 0 | 0 | 0 | 168.674 | 168.674 | 0
5/3/2026 | 3:15:00 AM | 148.738 | 148.738 | 0 | 59.81 | 59.81 | 0 | 0 | 0 | 169.734 | 169.734 | 0
5/3/2026 | 3:30:00 AM | 149.676 | 149.676 | 0 | 60.211 | 60.211 | 0 | 0 | 0 | 170.797 | 170.797 | 0
5/3/2026 | 3:45:00 AM | 150.674 | 150.674 | 0 | 60.604 | 60.604 | 0 | 0 | 0 | 171.923 | 171.923 | 0
5/3/2026 | 4:00:00 AM | 151.726 | 151.726 | 0 | 60.997 | 60.997 | 0 | 0 | 0 | 173.107 | 173.107 | 0
5/3/2026 | 4:15:00 AM | 152.696 | 152.696 | 0 | 61.391 | 61.391 | 0 | 0 | 0 | 174.207 | 174.207 | 0
5/3/2026 | 4:30:00 AM | 153.607 | 153.607 | 0 | 61.784 | 61.784 | 0 | 0 | 0 | 175.244 | 175.244 | 0
5/3/2026 | 4:45:00 AM | 154.534 | 154.534 | 0 | 62.179 | 62.179 | 0 | 0 | 0 | 176.296 | 176.296 | 0
5/3/2026 | 5:00:00 AM | 155.466 | 155.466 | 0 | 62.573 | 62.573 | 0 | 0 | 0 | 177.354 | 177.354 | 0
5/3/2026 | 5:15:00 AM | 156.492 | 156.492 | 0 | 62.963 | 62.963 | 0 | 0 | 0 | 178.508 | 178.508 | 0
5/3/2026 | 5:30:00 AM | 157.535 | 157.535 | 0 | 63.353 | 63.353 | 0 | 0 | 0 | 179.681 | 179.681 | 0
5/3/2026 | 5:45:00 AM | 158.413 | 158.413 | 0 | 63.753 | 63.753 | 0 | 0 | 0 | 180.686 | 180.686 | 0
5/3/2026 | 6:00:00 AM | 159.342 | 159.342 | 0 | 64.143 | 64.143 | 0 | 0 | 0 | 181.738 | 181.738 | 0
5/3/2026 | 6:15:00 AM | 160.275 | 160.275 | 0 | 64.528 | 64.528 | 0 | 0 | 0 | 182.793 | 182.793 | 0
5/3/2026 | 6:30:00 AM | 161.232 | 161.232 | 0 | 64.912 | 64.912 | 0 | 0 | 0 | 183.872 | 183.872 | 0
5/3/2026 | 6:45:00 AM | 162.33 | 162.33 | 0 | 65.325 | 65.325 | 0 | 0 | 0 | 185.095 | 185.095 | 0
5/3/2026 | 7:00:00 AM | 163.405 | 163.405 | 0 | 65.745 | 65.745 | 0 | 0 | 0 | 186.28 | 186.28 | 0
5/3/2026 | 7:15:00 AM | 164.486 | 164.486 | 0 | 66.159 | 66.159 | 0 | 0 | 0 | 187.467 | 187.467 | 0
5/3/2026 | 7:30:00 AM | 165.568 | 165.568 | 0 | 66.571 | 66.571 | 0 | 0 | 0 | 188.655 | 188.655 | 0
5/3/2026 | 7:45:00 AM | 166.684 | 166.684 | 0 | 66.998 | 66.998 | 0 | 0 | 0 | 189.891 | 189.891 | 0
5/3/2026 | 8:00:00 AM | 167.752 | 167.752 | 0 | 67.447 | 67.447 | 0 | 0 | 0 | 191.102 | 191.102 | 0
5/3/2026 | 8:15:00 AM | 168.671 | 168.671 | 0 | 67.889 | 67.889 | 0 | 0 | 0 | 192.19 | 192.19 | 0
5/3/2026 | 8:30:00 AM | 169.666 | 169.666 | 0 | 68.327 | 68.327 | 0 | 0 | 0 | 193.333 | 193.333 | 0
5/3/2026 | 8:45:00 AM | 170.659 | 170.659 | 0 | 68.762 | 68.762 | 0 | 0 | 0 | 194.472 | 194.472 | 0
5/3/2026 | 9:00:00 AM | 171.677 | 171.677 | 0 | 69.183 | 69.183 | 0 | 0 | 0 | 195.627 | 195.627 | 0
5/3/2026 | 9:15:00 AM | 172.793 | 172.793 | 0 | 69.578 | 69.578 | 0 | 0 | 0 | 196.859 | 196.859 | 0
5/3/2026 | 9:30:00 AM | 173.796 | 173.796 | 0 | 69.973 | 69.973 | 0 | 0 | 0 | 197.991 | 197.991 | 0
5/3/2026 | 9:45:00 AM | 174.724 | 174.724 | 0 | 70.37 | 70.37 | 0 | 0 | 0 | 199.059 | 199.059 | 0
5/3/2026 | 10:00:00 AM | 175.711 | 175.711 | 0 | 70.766 | 70.766 | 0 | 0 | 0 | 200.173 | 200.173 | 0
5/3/2026 | 10:15:00 AM | 176.801 | 176.801 | 0 | 71.159 | 71.159 | 0 | 0 | 0 | 201.377 | 201.377 | 0
5/3/2026 | 10:30:00 AM | 177.888 | 177.888 | 0 | 71.541 | 71.541 | 0 | 0 | 0 | 202.576 | 202.576 | 0
5/3/2026 | 10:45:00 AM | 178.723 | 178.723 | 0 | 71.928 | 71.928 | 0 | 0 | 0 | 203.561 | 203.561 | 0
5/3/2026 | 11:00:00 AM | 179.552 | 179.552 | 0 | 72.312 | 72.312 | 0 | 0 | 0 | 204.54 | 204.54 | 0
5/3/2026 | 11:15:00 AM | 180.388 | 180.388 | 0 | 72.694 | 72.694 | 0 | 0 | 0 | 205.524 | 205.524 | 0
5/3/2026 | 11:30:00 AM | 181.349 | 181.349 | 0 | 73.075 | 73.075 | 0 | 0 | 0 | 206.632 | 206.632 | 0
5/3/2026 | 11:45:00 AM | 182.32 | 182.32 | 0 | 73.454 | 73.454 | 0 | 0 | 0 | 207.748 | 207.748 | 0
5/3/2026 | 12:00:00 PM | 183.13 | 183.13 | 0 | 73.833 | 73.833 | 0 | 0 | 0 | 208.712 | 208.712 | 0
5/3/2026 | 12:15:00 PM | 183.961 | 183.961 | 0 | 74.221 | 74.221 | 0 | 0 | 0 | 209.693 | 209.693 | 0
5/3/2026 | 12:30:00 PM | 184.795 | 184.795 | 0 | 74.599 | 74.599 | 0 | 0 | 0 | 210.672 | 210.672 | 0
5/3/2026 | 12:45:00 PM | 185.676 | 185.676 | 0 | 74.976 | 74.976 | 0 | 0 | 0 | 211.697 | 211.697 | 0
5/3/2026 | 1:00:00 PM | 186.679 | 186.679 | 0 | 75.349 | 75.349 | 0 | 0 | 0 | 212.846 | 212.846 | 0
5/3/2026 | 1:15:00 PM | 187.531 | 187.531 | 0 | 75.726 | 75.726 | 0 | 0 | 0 | 213.85 | 213.85 | 0
5/3/2026 | 1:30:00 PM | 188.337 | 188.337 | 0 | 76.103 | 76.103 | 0 | 0 | 0 | 214.805 | 214.805 | 0
5/3/2026 | 1:45:00 PM | 189.214 | 189.214 | 0 | 76.476 | 76.476 | 0 | 0 | 0 | 215.823 | 215.823 | 0
5/3/2026 | 2:00:00 PM | 190.229 | 190.229 | 0 | 76.847 | 76.847 | 0 | 0 | 0 | 216.985 | 216.985 | 0
5/3/2026 | 2:15:00 PM | 191.088 | 191.088 | 0 | 77.23 | 77.23 | 0 | 0 | 0 | 217.995 | 217.995 | 0
5/3/2026 | 2:30:00 PM | 191.897 | 191.897 | 0 | 77.607 | 77.607 | 0 | 0 | 0 | 218.953 | 218.953 | 0
5/3/2026 | 2:45:00 PM | 192.741 | 192.741 | 0 | 77.982 | 77.982 | 0 | 0 | 0 | 219.941 | 219.941 | 0
5/3/2026 | 3:00:00 PM | 193.615 | 193.615 | 0 | 78.357 | 78.357 | 0 | 0 | 0 | 220.958 | 220.958 | 0
5/3/2026 | 3:15:00 PM | 194.62 | 194.62 | 0 | 78.726 | 78.726 | 0 | 0 | 0 | 222.107 | 222.107 | 0
5/3/2026 | 3:30:00 PM | 195.625 | 195.625 | 0 | 79.095 | 79.095 | 0 | 0 | 0 | 223.256 | 223.256 | 0
5/3/2026 | 3:45:00 PM | 196.439 | 196.439 | 0 | 79.466 | 79.466 | 0 | 0 | 0 | 224.22 | 224.22 | 0
5/3/2026 | 4:00:00 PM | 197.276 | 197.276 | 0 | 79.843 | 79.843 | 0 | 0 | 0 | 225.202 | 225.202 | 0
5/3/2026 | 4:15:00 PM | 198.126 | 198.126 | 0 | 80.212 | 80.212 | 0 | 0 | 0 | 226.193 | 226.193 | 0
5/3/2026 | 4:30:00 PM | 199.089 | 199.089 | 0 | 80.58 | 80.58 | 0 | 0 | 0 | 227.297 | 227.297 | 0
5/3/2026 | 4:45:00 PM | 200.077 | 200.077 | 0 | 80.945 | 80.945 | 0 | 0 | 0 | 228.427 | 228.427 | 0
5/3/2026 | 5:00:00 PM | 200.947 | 200.947 | 0 | 81.31 | 81.31 | 0 | 0 | 0 | 229.443 | 229.443 | 0
5/3/2026 | 5:15:00 PM | 201.762 | 201.762 | 0 | 81.677 | 81.677 | 0 | 0 | 0 | 230.401 | 230.401 | 0
5/3/2026 | 5:30:00 PM | 202.623 | 202.623 | 0 | 82.041 | 82.041 | 0 | 0 | 0 | 231.401 | 231.401 | 0
5/3/2026 | 5:45:00 PM | 203.62 | 203.62 | 0 | 82.411 | 82.411 | 0 | 0 | 0 | 232.539 | 232.539 | 0
5/3/2026 | 6:00:00 PM | 204.561 | 204.561 | 0 | 82.772 | 82.772 | 0 | 0 | 0 | 233.618 | 233.618 | 0
5/3/2026 | 6:15:00 PM | 205.43 | 205.43 | 0 | 83.135 | 83.135 | 0 | 0 | 0 | 234.624 | 234.624 | 0
5/3/2026 | 6:30:00 PM | 206.377 | 206.377 | 0 | 83.497 | 83.497 | 0 | 0 | 0 | 235.71 | 235.71 | 0
5/3/2026 | 6:45:00 PM | 207.329 | 207.329 | 0 | 83.86 | 83.86 | 0 | 0 | 0 | 236.8 | 236.8 | 0
5/3/2026 | 7:00:00 PM | 208.093 | 208.093 | 0 | 84.228 | 84.228 | 0 | 0 | 0 | 237.715 | 237.715 | 0
5/3/2026 | 7:15:00 PM | 208.941 | 208.941 | 0 | 84.594 | 84.594 | 0 | 0 | 0 | 238.704 | 238.704 | 0
5/3/2026 | 7:30:00 PM | 209.802 | 209.802 | 0 | 84.969 | 84.969 | 0 | 0 | 0 | 239.705 | 239.705 | 0
5/3/2026 | 7:45:00 PM | 210.843 | 210.843 | 0 | 85.318 | 85.318 | 0 | 0 | 0 | 240.873 | 240.873 | 0
5/3/2026 | 8:00:00 PM | 211.868 | 211.868 | 0 | 85.658 | 85.658 | 0 | 0 | 0 | 242.008 | 242.008 | 0
5/3/2026 | 8:15:00 PM | 212.849 | 212.849 | 0 | 86.001 | 86.001 | 0 | 0 | 0 | 243.097 | 243.097 | 0
5/3/2026 | 8:30:00 PM | 213.916 | 213.916 | 0 | 86.343 | 86.343 | 0 | 0 | 0 | 244.279 | 244.279 | 0
5/3/2026 | 8:45:00 PM | 214.923 | 214.923 | 0 | 86.684 | 86.684 | 0 | 0 | 0 | 245.398 | 245.398 | 0
5/3/2026 | 9:00:00 PM | 215.807 | 215.807 | 0 | 87.028 | 87.028 | 0 | 0 | 0 | 246.387 | 246.387 | 0
5/3/2026 | 9:15:00 PM | 216.736 | 216.736 | 0 | 87.373 | 87.373 | 0 | 0 | 0 | 247.421 | 247.421 | 0
5/3/2026 | 9:30:00 PM | 217.682 | 217.682 | 0 | 87.72 | 87.72 | 0 | 0 | 0 | 248.475 | 248.475 | 0
5/3/2026 | 9:45:00 PM | 218.746 | 218.746 | 0 | 88.069 | 88.069 | 0 | 0 | 0 | 249.655 | 249.655 | 0
5/3/2026 | 10:00:00 PM | 219.764 | 219.764 | 0 | 88.429 | 88.429 | 0 | 0 | 0 | 250.787 | 250.787 | 0
5/3/2026 | 10:15:00 PM | 220.634 | 220.634 | 0 | 88.786 | 88.786 | 0 | 0 | 0 | 251.767 | 251.767 | 0
5/3/2026 | 10:30:00 PM | 221.555 | 221.555 | 0 | 89.142 | 89.142 | 0 | 0 | 0 | 252.799 | 252.799 | 0
5/3/2026 | 10:45:00 PM | 222.483 | 222.483 | 0 | 89.502 | 89.502 | 0 | 0 | 0 | 253.838 | 253.838 | 0
5/3/2026 | 11:00:00 PM | 223.454 | 223.454 | 0 | 89.862 | 89.862 | 0 | 0 | 0 | 254.923 | 254.923 | 0
5/3/2026 | 11:15:00 PM | 224.499 | 224.499 | 0 | 90.221 | 90.221 | 0 | 0 | 0 | 256.086 | 256.086 | 0
5/3/2026 | 11:30:00 PM | 225.396 | 225.396 | 0 | 90.583 | 90.583 | 0 | 0 | 0 | 257.098 | 257.098 | 0
5/3/2026 | 11:45:00 PM | 226.307 | 226.307 | 0 | 90.949 | 90.949 | 0 | 0 | 0 | 258.122 | 258.122 | 0
5/4/2026 | 12:00:00 AM | 227.223 | 227.223 | 0 | 91.318 | 91.318 | 0 | 0 | 0 | 259.153 | 259.153 | 0
5/4/2026 | 12:15:00 AM | 228.189 | 228.189 | 0 | 91.686 | 91.686 | 0 | 0 | 0 | 260.235 | 260.235 | 0
5/4/2026 | 12:30:00 AM | 229.208 | 229.208 | 0 | 92.063 | 92.063 | 0 | 0 | 0 | 261.375 | 261.375 | 0
5/4/2026 | 12:45:00 AM | 230.094 | 230.094 | 0 | 92.435 | 92.435 | 0 | 0 | 0 | 262.379 | 262.379 | 0
5/4/2026 | 1:00:00 AM | 231.007 | 231.007 | 0 | 92.807 | 92.807 | 0 | 0 | 0 | 263.408 | 263.408 | 0
5/4/2026 | 1:15:00 AM | 231.915 | 231.915 | 0 | 93.179 | 93.179 | 0 | 0 | 0 | 264.432 | 264.432 | 0
5/4/2026 | 1:30:00 AM | 232.84 | 232.84 | 0 | 93.547 | 93.547 | 0 | 0 | 0 | 265.472 | 265.472 | 0
5/4/2026 | 1:45:00 AM | 233.856 | 233.856 | 0 | 93.917 | 93.917 | 0 | 0 | 0 | 266.608 | 266.608 | 0
5/4/2026 | 2:00:00 AM | 234.815 | 234.815 | 0 | 94.29 | 94.29 | 0 | 0 | 0 | 267.685 | 267.685 | 0
5/4/2026 | 2:15:00 AM | 235.688 | 235.688 | 0 | 94.664 | 94.664 | 0 | 0 | 0 | 268.675 | 268.675 | 0
5/4/2026 | 2:30:00 AM | 236.613 | 236.613 | 0 | 95.037 | 95.037 | 0 | 0 | 0 | 269.717 | 269.717 | 0
5/4/2026 | 2:45:00 AM | 237.532 | 237.532 | 0 | 95.412 | 95.412 | 0 | 0 | 0 | 270.753 | 270.753 | 0
5/4/2026 | 3:00:00 AM | 238.46 | 238.46 | 0 | 95.788 | 95.788 | 0 | 0 | 0 | 271.798 | 271.798 | 0
5/4/2026 | 3:15:00 AM | 239.485 | 239.485 | 0 | 96.173 | 96.173 | 0 | 0 | 0 | 272.947 | 272.947 | 0
5/4/2026 | 3:30:00 AM | 240.457 | 240.457 | 0 | 96.55 | 96.55 | 0 | 0 | 0 | 274.04 | 274.04 | 0
5/4/2026 | 3:45:00 AM | 241.335 | 241.335 | 0 | 96.93 | 96.93 | 0 | 0 | 0 | 275.038 | 275.038 | 0
5/4/2026 | 4:00:00 AM | 242.257 | 242.257 | 0 | 97.307 | 97.307 | 0 | 0 | 0 | 276.078 | 276.078 | 0
5/4/2026 | 4:15:00 AM | 243.174 | 243.174 | 0 | 97.688 | 97.688 | 0 | 0 | 0 | 277.115 | 277.115 | 0
5/4/2026 | 4:30:00 AM | 244.176 | 244.176 | 0 | 98.066 | 98.066 | 0 | 0 | 0 | 278.238 | 278.238 | 0
5/4/2026 | 4:45:00 AM | 245.175 | 245.175 | 0 | 98.442 | 98.442 | 0 | 0 | 0 | 279.358 | 279.358 | 0
5/4/2026 | 5:00:00 AM | 246.095 | 246.095 | 0 | 98.817 | 98.817 | 0 | 0 | 0 | 280.399 | 280.399 | 0
5/4/2026 | 5:15:00 AM | 247.001 | 247.001 | 0 | 99.191 | 99.191 | 0 | 0 | 0 | 281.421 | 281.421 | 0
5/4/2026 | 5:30:00 AM | 247.902 | 247.902 | 0 | 99.566 | 99.566 | 0 | 0 | 0 | 282.438 | 282.438 | 0
5/4/2026 | 5:45:00 AM | 248.817 | 248.817 | 0 | 99.937 | 99.937 | 0 | 0 | 0 | 283.467 | 283.467 | 0
5/4/2026 | 6:00:00 AM | 249.817 | 249.817 | 0 | 100.31 | 100.31 | 0 | 0 | 0 | 284.585 | 284.585 | 0
5/4/2026 | 6:15:00 AM | 250.742 | 250.742 | 0 | 100.668 | 100.668 | 0 | 0 | 0 | 285.621 | 285.621 | 0
5/4/2026 | 6:30:00 AM | 251.64 | 251.64 | 0 | 101.019 | 101.019 | 0 | 0 | 0 | 286.626 | 286.626 | 0
5/4/2026 | 6:45:00 AM | 252.536 | 252.536 | 0 | 101.369 | 101.369 | 0 | 0 | 0 | 287.627 | 287.627 | 0
5/4/2026 | 7:00:00 AM | 253.443 | 253.443 | 0 | 101.723 | 101.723 | 0 | 0 | 0 | 288.641 | 288.641 | 0
5/4/2026 | 7:15:00 AM | 254.45 | 254.45 | 0 | 102.071 | 102.071 | 0 | 0 | 0 | 289.759 | 289.759 | 0
5/4/2026 | 7:30:00 AM | 255.371 | 255.371 | 0 | 102.42 | 102.42 | 0 | 0 | 0 | 290.788 | 290.788 | 0
5/4/2026 | 7:45:00 AM | 256.209 | 256.209 | 0 | 102.786 | 102.786 | 0 | 0 | 0 | 291.754 | 291.754 | 0
5/4/2026 | 8:00:00 AM | 257.007 | 257.007 | 0 | 103.166 | 103.166 | 0 | 0 | 0 | 292.7 | 292.7 | 0
5/4/2026 | 8:15:00 AM | 257.835 | 257.835 | 0 | 103.542 | 103.542 | 0 | 0 | 0 | 293.672 | 293.672 | 0
5/4/2026 | 8:30:00 AM | 258.771 | 258.771 | 0 | 103.913 | 103.913 | 0 | 0 | 0 | 294.749 | 294.749 | 0
5/4/2026 | 8:45:00 AM | 259.749 | 259.749 | 0 | 104.286 | 104.286 | 0 | 0 | 0 | 295.866 | 295.866 | 0
5/4/2026 | 9:00:00 AM | 260.598 | 260.598 | 0 | 104.65 | 104.65 | 0 | 0 | 0 | 296.854 | 296.854 | 0
5/4/2026 | 9:15:00 AM | 261.364 | 261.364 | 0 | 105.013 | 105.013 | 0 | 0 | 0 | 297.765 | 297.765 | 0
5/4/2026 | 9:30:00 AM | 262.191 | 262.191 | 0 | 105.372 | 105.372 | 0 | 0 | 0 | 298.729 | 298.729 | 0
5/4/2026 | 9:45:00 AM | 263.036 | 263.036 | 0 | 105.735 | 105.735 | 0 | 0 | 0 | 299.711 | 299.711 | 0
5/4/2026 | 10:00:00 AM | 264.025 | 264.025 | 0 | 106.104 | 106.104 | 0 | 0 | 0 | 300.842 | 300.842 | 0
5/4/2026 | 10:15:00 AM | 265.052 | 265.052 | 0 | 106.468 | 106.468 | 0 | 0 | 0 | 302.013 | 302.013 | 0
5/4/2026 | 10:30:00 AM | 266.013 | 266.013 | 0 | 106.833 | 106.833 | 0 | 0 | 0 | 303.112 | 303.112 | 0
5/4/2026 | 10:45:00 AM | 266.881 | 266.881 | 0 | 107.199 | 107.199 | 0 | 0 | 0 | 304.118 | 304.118 | 0
5/4/2026 | 11:00:00 AM | 267.815 | 267.815 | 0 | 107.573 | 107.573 | 0 | 0 | 0 | 305.192 | 305.192 | 0
5/4/2026 | 11:15:00 AM | 268.777 | 268.777 | 0 | 107.939 | 107.939 | 0 | 0 | 0 | 306.294 | 306.294 | 0
5/4/2026 | 11:30:00 AM | 269.55 | 269.55 | 0 | 108.305 | 108.305 | 0 | 0 | 0 | 307.215 | 307.215 | 0
5/4/2026 | 11:45:00 AM | 270.408 | 270.408 | 0 | 108.668 | 108.668 | 0 | 0 | 0 | 308.21 | 308.21 | 0
5/4/2026 | 12:00:00 PM | 271.297 | 271.297 | 0 | 109.031 | 109.031 | 0 | 0 | 0 | 309.236 | 309.236 | 0
5/4/2026 | 12:15:00 PM | 272.297 | 272.297 | 0 | 109.391 | 109.391 | 0 | 0 | 0 | 310.377 | 310.377 | 0
5/4/2026 | 12:30:00 PM | 273.147 | 273.147 | 0 | 109.753 | 109.753 | 0 | 0 | 0 | 311.373 | 311.373 | 0
5/4/2026 | 12:45:00 PM | 273.986 | 273.986 | 0 | 110.117 | 110.117 | 0 | 0 | 0 | 312.352 | 312.352 | 0
5/4/2026 | 1:00:00 PM | 274.742 | 274.742 | 0 | 110.477 | 110.477 | 0 | 0 | 0 | 313.257 | 313.257 | 0
5/4/2026 | 1:15:00 PM | 275.539 | 275.539 | 0 | 110.836 | 110.836 | 0 | 0 | 0 | 314.202 | 314.202 | 0
5/4/2026 | 1:30:00 PM | 276.427 | 276.427 | 0 | 111.193 | 111.193 | 0 | 0 | 0 | 315.228 | 315.228 | 0
5/4/2026 | 1:45:00 PM | 277.339 | 277.339 | 0 | 111.549 | 111.549 | 0 | 0 | 0 | 316.277 | 316.277 | 0
5/4/2026 | 2:00:00 PM | 278.208 | 278.208 | 0 | 111.906 | 111.906 | 0 | 0 | 0 | 317.283 | 317.283 | 0
5/4/2026 | 2:15:00 PM | 279.235 | 279.235 | 0 | 112.265 | 112.265 | 0 | 0 | 0 | 318.451 | 318.451 | 0
5/4/2026 | 2:30:00 PM | 280.185 | 280.185 | 0 | 112.62 | 112.62 | 0 | 0 | 0 | 319.54 | 319.54 | 0
5/4/2026 | 2:45:00 PM | 281.093 | 281.093 | 0 | 112.978 | 112.978 | 0 | 0 | 0 | 320.586 | 320.586 | 0
5/4/2026 | 3:00:00 PM | 282.103 | 282.103 | 0 | 113.335 | 113.335 | 0 | 0 | 0 | 321.74 | 321.74 | 0
5/4/2026 | 3:15:00 PM | 283.023 | 283.023 | 0 | 113.691 | 113.691 | 0 | 0 | 0 | 322.803 | 322.803 | 0
5/4/2026 | 3:30:00 PM | 283.819 | 283.819 | 0 | 114.047 | 114.047 | 0 | 0 | 0 | 323.741 | 323.741 | 0
5/4/2026 | 3:45:00 PM | 284.614 | 284.614 | 0 | 114.41 | 114.41 | 0 | 0 | 0 | 324.683 | 324.683 | 0
5/4/2026 | 4:00:00 PM | 285.416 | 285.416 | 0 | 114.766 | 114.766 | 0 | 0 | 0 | 325.63 | 325.63 | 0
5/4/2026 | 4:15:00 PM | 286.236 | 286.236 | 0 | 115.119 | 115.119 | 0 | 0 | 0 | 326.592 | 326.592 | 0
5/4/2026 | 4:30:00 PM | 287.041 | 287.041 | 0 | 115.473 | 115.473 | 0 | 0 | 0 | 327.538 | 327.538 | 0
5/4/2026 | 4:45:00 PM | 288.033 | 288.033 | 0 | 115.84 | 115.84 | 0 | 0 | 0 | 328.676 | 328.676 | 0
5/4/2026 | 5:00:00 PM | 288.936 | 288.936 | 0 | 116.221 | 116.221 | 0 | 0 | 0 | 329.724 | 329.724 | 0
5/4/2026 | 5:15:00 PM | 289.974 | 289.974 | 0 | 116.599 | 116.599 | 0 | 0 | 0 | 330.915 | 330.915 | 0
5/4/2026 | 5:30:00 PM | 290.958 | 290.958 | 0 | 116.975 | 116.975 | 0 | 0 | 0 | 332.047 | 332.047 | 0
5/4/2026 | 5:45:00 PM | 291.848 | 291.848 | 0 | 117.353 | 117.353 | 0 | 0 | 0 | 333.083 | 333.083 | 0
5/4/2026 | 6:00:00 PM | 292.858 | 292.858 | 0 | 117.732 | 117.732 | 0 | 0 | 0 | 334.244 | 334.244 | 0
5/4/2026 | 6:15:00 PM | 293.85 | 293.85 | 0 | 118.122 | 118.122 | 0 | 0 | 0 | 335.388 | 335.388 | 0
5/4/2026 | 6:30:00 PM | 294.625 | 294.625 | 0 | 118.513 | 118.513 | 0 | 0 | 0 | 336.328 | 336.328 | 0
5/4/2026 | 6:45:00 PM | 295.499 | 295.499 | 0 | 118.902 | 118.902 | 0 | 0 | 0 | 337.354 | 337.354 | 0
5/4/2026 | 7:00:00 PM | 296.392 | 296.392 | 0 | 119.29 | 119.29 | 0 | 0 | 0 | 338.4 | 338.4 | 0
5/4/2026 | 7:15:00 PM | 297.413 | 297.413 | 0 | 119.682 | 119.682 | 0 | 0 | 0 | 339.577 | 339.577 | 0
5/4/2026 | 7:30:00 PM | 298.431 | 298.431 | 0 | 120.082 | 120.082 | 0 | 0 | 0 | 340.753 | 340.753 | 0
5/4/2026 | 7:45:00 PM | 299.4 | 299.4 | 0 | 120.465 | 120.465 | 0 | 0 | 0 | 341.861 | 341.861 | 0
5/4/2026 | 8:00:00 PM | 300.366 | 300.366 | 0 | 120.836 | 120.836 | 0 | 0 | 0 | 342.947 | 342.947 | 0
5/4/2026 | 8:15:00 PM | 301.431 | 301.431 | 0 | 121.211 | 121.211 | 0 | 0 | 0 | 344.14 | 344.14 | 0
5/4/2026 | 8:30:00 PM | 302.501 | 302.501 | 0 | 121.582 | 121.582 | 0 | 0 | 0 | 345.338 | 345.338 | 0
5/4/2026 | 8:45:00 PM | 303.571 | 303.571 | 0 | 121.959 | 121.959 | 0 | 0 | 0 | 346.536 | 346.536 | 0
5/4/2026 | 9:00:00 PM | 304.541 | 304.541 | 0 | 122.334 | 122.334 | 0 | 0 | 0 | 347.632 | 347.632 | 0
5/4/2026 | 9:15:00 PM | 305.482 | 305.482 | 0 | 122.713 | 122.713 | 0 | 0 | 0 | 348.697 | 348.697 | 0
5/4/2026 | 9:30:00 PM | 306.451 | 306.451 | 0 | 123.095 | 123.095 | 0 | 0 | 0 | 349.791 | 349.791 | 0
5/4/2026 | 9:45:00 PM | 307.529 | 307.529 | 0 | 123.469 | 123.469 | 0 | 0 | 0 | 350.999 | 350.999 | 0
5/4/2026 | 10:00:00 PM | 308.525 | 308.525 | 0 | 123.837 | 123.837 | 0 | 0 | 0 | 352.119 | 352.119 | 0
5/4/2026 | 10:15:00 PM | 309.44 | 309.44 | 0 | 124.203 | 124.203 | 0 | 0 | 0 | 353.148 | 353.148 | 0
5/4/2026 | 10:30:00 PM | 310.39 | 310.39 | 0 | 124.563 | 124.563 | 0 | 0 | 0 | 354.21 | 354.21 | 0
5/4/2026 | 10:45:00 PM | 311.345 | 311.345 | 0 | 124.925 | 124.925 | 0 | 0 | 0 | 355.279 | 355.279 | 0
5/4/2026 | 11:00:00 PM | 312.428 | 312.428 | 0 | 125.294 | 125.294 | 0 | 0 | 0 | 356.486 | 356.486 | 0
5/4/2026 | 11:15:00 PM | 313.499 | 313.499 | 0 | 125.664 | 125.664 | 0 | 0 | 0 | 357.681 | 357.681 | 0
5/4/2026 | 11:30:00 PM | 314.454 | 314.454 | 0 | 126.037 | 126.037 | 0 | 0 | 0 | 358.753 | 358.753 | 0
5/4/2026 | 11:45:00 PM | 315.42 | 315.42 | 0 | 126.414 | 126.414 | 0 | 0 | 0 | 359.837 | 359.837 | 0
5/5/2026 | 12:00:00 AM | 316.503 | 316.503 | 0 | 126.79 | 126.79 | 0 | 0 | 0 | 361.047 | 361.047 | 0
5/5/2026 | 12:15:00 AM | 317.525 | 317.525 | 0 | 127.168 | 127.168 | 0 | 0 | 0 | 362.193 | 362.193 | 0
5/5/2026 | 12:30:00 AM | 318.418 | 318.418 | 0 | 127.556 | 127.556 | 0 | 0 | 0 | 363.208 | 363.208 | 0
5/5/2026 | 12:45:00 AM | 319.362 | 319.362 | 0 | 127.938 | 127.938 | 0 | 0 | 0 | 364.271 | 364.271 | 0
5/5/2026 | 1:00:00 AM | 320.306 | 320.306 | 0 | 128.323 | 128.323 | 0 | 0 | 0 | 365.336 | 365.336 | 0
5/5/2026 | 1:15:00 AM | 321.302 | 321.302 | 0 | 128.701 | 128.701 | 0 | 0 | 0 | 366.454 | 366.454 | 0
5/5/2026 | 1:30:00 AM | 322.375 | 322.375 | 0 | 129.079 | 129.079 | 0 | 0 | 0 | 367.652 | 367.652 | 0
5/5/2026 | 1:45:00 AM | 323.359 | 323.359 | 0 | 129.463 | 129.463 | 0 | 0 | 0 | 368.762 | 368.762 | 0
5/5/2026 | 2:00:00 AM | 324.259 | 324.259 | 0 | 129.853 | 129.853 | 0 | 0 | 0 | 369.784 | 369.784 | 0
5/5/2026 | 2:15:00 AM | 325.2 | 325.2 | 0 | 130.243 | 130.243 | 0 | 0 | 0 | 370.849 | 370.849 | 0
5/5/2026 | 2:30:00 AM | 326.16 | 326.16 | 0 | 130.632 | 130.632 | 0 | 0 | 0 | 371.932 | 371.932 | 0
5/5/2026 | 2:45:00 AM | 327.224 | 327.224 | 0 | 131.03 | 131.03 | 0 | 0 | 0 | 373.126 | 373.126 | 0
5/5/2026 | 3:00:00 AM | 328.257 | 328.257 | 0 | 131.421 | 131.421 | 0 | 0 | 0 | 374.286 | 374.286 | 0
5/5/2026 | 3:15:00 AM | 329.25 | 329.25 | 0 | 131.813 | 131.813 | 0 | 0 | 0 | 375.408 | 375.408 | 0
5/5/2026 | 3:30:00 AM | 330.161 | 330.161 | 0 | 132.207 | 132.207 | 0 | 0 | 0 | 376.445 | 376.445 | 0
5/5/2026 | 3:45:00 AM | 331.09 | 331.09 | 0 | 132.602 | 132.602 | 0 | 0 | 0 | 377.499 | 377.499 | 0
5/5/2026 | 4:00:00 AM | 332.02 | 332.02 | 0 | 132.996 | 132.996 | 0 | 0 | 0 | 378.553 | 378.553 | 0
5/5/2026 | 4:15:00 AM | 332.982 | 332.982 | 0 | 133.391 | 133.391 | 0 | 0 | 0 | 379.64 | 379.64 | 0
5/5/2026 | 4:30:00 AM | 334.019 | 334.019 | 0 | 133.782 | 133.782 | 0 | 0 | 0 | 380.806 | 380.806 | 0
5/5/2026 | 4:45:00 AM | 335.033 | 335.033 | 0 | 134.169 | 134.169 | 0 | 0 | 0 | 381.944 | 381.944 | 0
5/5/2026 | 5:00:00 AM | 335.934 | 335.934 | 0 | 134.558 | 134.558 | 0 | 0 | 0 | 382.97 | 382.97 | 0
5/5/2026 | 5:15:00 AM | 336.874 | 336.874 | 0 | 134.945 | 134.945 | 0 | 0 | 0 | 384.03 | 384.03 | 0
5/5/2026 | 5:30:00 AM | 337.815 | 337.815 | 0 | 135.314 | 135.314 | 0 | 0 | 0 | 385.086 | 385.086 | 0
5/5/2026 | 5:45:00 AM | 338.842 | 338.842 | 0 | 135.681 | 135.681 | 0 | 0 | 0 | 386.233 | 386.233 | 0
5/5/2026 | 6:00:00 AM | 339.913 | 339.913 | 0 | 136.047 | 136.047 | 0 | 0 | 0 | 387.427 | 387.427 | 0
5/5/2026 | 6:15:00 AM | 340.824 | 340.824 | 0 | 136.412 | 136.412 | 0 | 0 | 0 | 388.453 | 388.453 | 0
5/5/2026 | 6:30:00 AM | 341.753 | 341.753 | 0 | 136.773 | 136.773 | 0 | 0 | 0 | 389.494 | 389.494 | 0
5/5/2026 | 6:45:00 AM | 342.688 | 342.688 | 0 | 137.136 | 137.136 | 0 | 0 | 0 | 390.54 | 390.54 | 0
5/5/2026 | 7:00:00 AM | 343.717 | 343.717 | 0 | 137.496 | 137.496 | 0 | 0 | 0 | 391.688 | 391.688 | 0
5/5/2026 | 7:15:00 AM | 344.783 | 344.783 | 0 | 137.854 | 137.854 | 0 | 0 | 0 | 392.873 | 392.873 | 0
5/5/2026 | 7:30:00 AM | 345.707 | 345.707 | 0 | 138.212 | 138.212 | 0 | 0 | 0 | 393.91 | 393.91 | 0
5/5/2026 | 7:45:00 AM | 346.565 | 346.565 | 0 | 138.59 | 138.59 | 0 | 0 | 0 | 394.903 | 394.903 | 0
5/5/2026 | 8:00:00 AM | 347.412 | 347.412 | 0 | 138.986 | 138.986 | 0 | 0 | 0 | 395.9 | 395.9 | 0
5/5/2026 | 8:15:00 AM | 348.301 | 348.301 | 0 | 139.369 | 139.369 | 0 | 0 | 0 | 396.936 | 396.936 | 0
5/5/2026 | 8:30:00 AM | 349.261 | 349.261 | 0 | 139.752 | 139.752 | 0 | 0 | 0 | 398.042 | 398.042 | 0
5/5/2026 | 8:45:00 AM | 350.14 | 350.14 | 0 | 140.13 | 140.13 | 0 | 0 | 0 | 399.066 | 399.066 | 0
5/5/2026 | 9:00:00 AM | 350.908 | 350.908 | 0 | 140.508 | 140.508 | 0 | 0 | 0 | 399.988 | 399.988 | 0
5/5/2026 | 9:15:00 AM | 351.747 | 351.747 | 0 | 140.88 | 140.88 | 0 | 0 | 0 | 400.969 | 400.969 | 0
5/5/2026 | 9:30:00 AM | 352.626 | 352.626 | 0 | 141.253 | 141.253 | 0 | 0 | 0 | 401.989 | 401.989 | 0
5/5/2026 | 9:45:00 AM | 353.643 | 353.643 | 0 | 141.62 | 141.62 | 0 | 0 | 0 | 403.151 | 403.151 | 0
5/5/2026 | 10:00:00 AM | 354.582 | 354.582 | 0 | 141.988 | 141.988 | 0 | 0 | 0 | 404.229 | 404.229 | 0
5/5/2026 | 10:15:00 AM | 355.459 | 355.459 | 0 | 142.362 | 142.362 | 0 | 0 | 0 | 405.245 | 405.245 | 0
5/5/2026 | 10:30:00 AM | 356.385 | 356.385 | 0 | 142.726 | 142.726 | 0 | 0 | 0 | 406.309 | 406.309 | 0
5/5/2026 | 10:45:00 AM | 357.382 | 357.382 | 0 | 143.086 | 143.086 | 0 | 0 | 0 | 407.446 | 407.446 | 0
5/5/2026 | 11:00:00 AM | 358.253 | 358.253 | 0 | 143.445 | 143.445 | 0 | 0 | 0 | 408.46 | 408.46 | 0
5/5/2026 | 11:15:00 AM | 359.091 | 359.091 | 0 | 143.803 | 143.803 | 0 | 0 | 0 | 409.438 | 409.438 | 0
5/5/2026 | 11:30:00 AM | 359.859 | 359.859 | 0 | 144.163 | 144.163 | 0 | 0 | 0 | 410.354 | 410.354 | 0
5/5/2026 | 11:45:00 AM | 360.796 | 360.796 | 0 | 144.52 | 144.52 | 0 | 0 | 0 | 411.43 | 411.43 | 0
5/5/2026 | 12:00:00 PM | 361.68 | 361.68 | 0 | 144.883 | 144.883 | 0 | 0 | 0 | 412.45 | 412.45 | 0
5/5/2026 | 12:15:00 PM | 362.637 | 362.637 | 0 | 145.237 | 145.237 | 0 | 0 | 0 | 413.545 | 413.545 | 0
5/5/2026 | 12:30:00 PM | 363.693 | 363.693 | 0 | 145.591 | 145.591 | 0 | 0 | 0 | 414.746 | 414.746 | 0
5/5/2026 | 12:45:00 PM | 364.675 | 364.675 | 0 | 145.956 | 145.956 | 0 | 0 | 0 | 415.872 | 415.872 | 0
5/5/2026 | 1:00:00 PM | 365.562 | 365.562 | 0 | 146.319 | 146.319 | 0 | 0 | 0 | 416.907 | 416.907 | 0
5/5/2026 | 1:15:00 PM | 366.411 | 366.411 | 0 | 146.69 | 146.69 | 0 | 0 | 0 | 417.901 | 417.901 | 0
5/5/2026 | 1:30:00 PM | 367.181 | 367.181 | 0 | 147.057 | 147.057 | 0 | 0 | 0 | 418.823 | 418.823 | 0
5/5/2026 | 1:45:00 PM | 368.137 | 368.137 | 0 | 147.423 | 147.423 | 0 | 0 | 0 | 419.92 | 419.92 | 0
5/5/2026 | 2:00:00 PM | 369.025 | 369.025 | 0 | 147.791 | 147.791 | 0 | 0 | 0 | 420.95 | 420.95 | 0
5/5/2026 | 2:15:00 PM | 369.981 | 369.981 | 0 | 148.157 | 148.157 | 0 | 0 | 0 | 422.05 | 422.05 | 0
5/5/2026 | 2:30:00 PM | 371.063 | 371.063 | 0 | 148.527 | 148.527 | 0 | 0 | 0 | 423.281 | 423.281 | 0
5/5/2026 | 2:45:00 PM | 372.108 | 372.108 | 0 | 148.892 | 148.892 | 0 | 0 | 0 | 424.472 | 424.472 | 0
5/5/2026 | 3:00:00 PM | 373.102 | 373.102 | 0 | 149.256 | 149.256 | 0 | 0 | 0 | 425.609 | 425.609 | 0
5/5/2026 | 3:15:00 PM | 373.972 | 373.972 | 0 | 149.621 | 149.621 | 0 | 0 | 0 | 426.619 | 426.619 | 0
5/5/2026 | 3:30:00 PM | 375.007 | 375.007 | 0 | 149.991 | 149.991 | 0 | 0 | 0 | 427.801 | 427.801 | 0
5/5/2026 | 3:45:00 PM | 375.993 | 375.993 | 0 | 150.356 | 150.356 | 0 | 0 | 0 | 428.933 | 428.933 | 0
5/5/2026 | 4:00:00 PM | 376.767 | 376.767 | 0 | 150.72 | 150.72 | 0 | 0 | 0 | 429.856 | 429.856 | 0
5/5/2026 | 4:15:00 PM | 377.578 | 377.578 | 0 | 151.084 | 151.084 | 0 | 0 | 0 | 430.816 | 430.816 | 0
5/5/2026 | 4:30:00 PM | 378.396 | 378.396 | 0 | 151.447 | 151.447 | 0 | 0 | 0 | 431.783 | 431.783 | 0
5/5/2026 | 4:45:00 PM | 379.26 | 379.26 | 0 | 151.811 | 151.811 | 0 | 0 | 0 | 432.788 | 432.788 | 0
5/5/2026 | 5:00:00 PM | 380.208 | 380.208 | 0 | 152.168 | 152.168 | 0 | 0 | 0 | 433.874 | 433.874 | 0
5/5/2026 | 5:15:00 PM | 381.114 | 381.114 | 0 | 152.535 | 152.535 | 0 | 0 | 0 | 434.923 | 434.923 | 0
5/5/2026 | 5:30:00 PM | 382.173 | 382.173 | 0 | 152.9 | 152.9 | 0 | 0 | 0 | 436.132 | 436.132 | 0
5/5/2026 | 5:45:00 PM | 383.183 | 383.183 | 0 | 153.275 | 153.275 | 0 | 0 | 0 | 437.29 | 437.29 | 0
5/5/2026 | 6:00:00 PM | 384.071 | 384.071 | 0 | 153.649 | 153.649 | 0 | 0 | 0 | 438.322 | 438.322 | 0
5/5/2026 | 6:15:00 PM | 385.09 | 385.09 | 0 | 154.026 | 154.026 | 0 | 0 | 0 | 439.493 | 439.493 | 0
5/5/2026 | 6:30:00 PM | 386.132 | 386.132 | 0 | 154.404 | 154.404 | 0 | 0 | 0 | 440.687 | 440.687 | 0
5/5/2026 | 6:45:00 PM | 387.132 | 387.132 | 0 | 154.789 | 154.789 | 0 | 0 | 0 | 441.837 | 441.837 | 0
5/5/2026 | 7:00:00 PM | 387.959 | 387.959 | 0 | 155.174 | 155.174 | 0 | 0 | 0 | 442.824 | 442.824 | 0
5/5/2026 | 7:15:00 PM | 388.813 | 388.813 | 0 | 155.558 | 155.558 | 0 | 0 | 0 | 443.83 | 443.83 | 0
5/5/2026 | 7:30:00 PM | 389.698 | 389.698 | 0 | 155.945 | 155.945 | 0 | 0 | 0 | 444.868 | 444.868 | 0
5/5/2026 | 7:45:00 PM | 390.758 | 390.758 | 0 | 156.323 | 156.323 | 0 | 0 | 0 | 446.076 | 446.076 | 0
5/5/2026 | 8:00:00 PM | 391.913 | 391.913 | 0 | 156.684 | 156.684 | 0 | 0 | 0 | 447.363 | 447.363 | 0
5/5/2026 | 8:15:00 PM | 393.015 | 393.015 | 0 | 157.047 | 157.047 | 0 | 0 | 0 | 448.592 | 448.592 | 0
5/5/2026 | 8:30:00 PM | 393.985 | 393.985 | 0 | 157.407 | 157.407 | 0 | 0 | 0 | 449.684 | 449.684 | 0
5/5/2026 | 8:45:00 PM | 394.933 | 394.933 | 0 | 157.766 | 157.766 | 0 | 0 | 0 | 450.747 | 450.747 | 0
5/5/2026 | 9:00:00 PM | 395.816 | 395.816 | 0 | 158.133 | 158.133 | 0 | 0 | 0 | 451.747 | 451.747 | 0
5/5/2026 | 9:15:00 PM | 396.748 | 396.748 | 0 | 158.497 | 158.497 | 0 | 0 | 0 | 452.798 | 452.798 | 0
5/5/2026 | 9:30:00 PM | 397.676 | 397.676 | 0 | 158.863 | 158.863 | 0 | 0 | 0 | 453.847 | 453.847 | 0
5/5/2026 | 9:45:00 PM | 398.634 | 398.634 | 0 | 159.233 | 159.233 | 0 | 0 | 0 | 454.926 | 454.926 | 0
5/5/2026 | 10:00:00 PM | 399.707 | 399.707 | 0 | 159.606 | 159.606 | 0 | 0 | 0 | 456.127 | 456.127 | 0
5/5/2026 | 10:15:00 PM | 400.598 | 400.598 | 0 | 159.976 | 159.976 | 0 | 0 | 0 | 457.139 | 457.139 | 0
5/5/2026 | 10:30:00 PM | 401.657 | 401.657 | 0 | 160.345 | 160.345 | 0 | 0 | 0 | 458.324 | 458.324 | 0
5/5/2026 | 10:45:00 PM | 402.64 | 402.64 | 0 | 160.715 | 160.715 | 0 | 0 | 0 | 459.428 | 459.428 | 0
5/5/2026 | 11:00:00 PM | 403.728 | 403.728 | 0 | 161.088 | 161.088 | 0 | 0 | 0 | 460.647 | 460.647 | 0
5/5/2026 | 11:15:00 PM | 404.845 | 404.845 | 0 | 161.464 | 161.464 | 0 | 0 | 0 | 461.897 | 461.897 | 0
5/5/2026 | 11:30:00 PM | 405.859 | 405.859 | 0 | 161.837 | 161.837 | 0 | 0 | 0 | 463.037 | 463.037 | 0
5/5/2026 | 11:45:00 PM | 406.784 | 406.784 | 0 | 162.21 | 162.21 | 0 | 0 | 0 | 464.081 | 464.081 | 0
5/6/2026 | 12:00:00 AM | 407.688 | 407.688 | 0 | 162.581 | 162.581 | 0 | 0 | 0 | 465.104 | 465.104 | 0
5/6/2026 | 12:15:00 AM | 408.625 | 408.625 | 0 | 162.952 | 162.952 | 0 | 0 | 0 | 466.161 | 466.161 | 0
5/6/2026 | 12:30:00 AM | 409.64 | 409.64 | 0 | 163.329 | 163.329 | 0 | 0 | 0 | 467.301 | 467.301 | 0
5/6/2026 | 12:45:00 AM | 410.702 | 410.702 | 0 | 163.704 | 163.704 | 0 | 0 | 0 | 468.49 | 468.49 | 0
5/6/2026 | 1:00:00 AM | 411.586 | 411.586 | 0 | 164.081 | 164.081 | 0 | 0 | 0 | 469.494 | 469.494 | 0
5/6/2026 | 1:15:00 AM | 412.516 | 412.516 | 0 | 164.457 | 164.457 | 0 | 0 | 0 | 470.547 | 470.547 | 0
5/6/2026 | 1:30:00 AM | 413.527 | 413.527 | 0 | 164.83 | 164.83 | 0 | 0 | 0 | 471.681 | 471.681 | 0
5/6/2026 | 1:45:00 AM | 414.588 | 414.588 | 0 | 165.209 | 165.209 | 0 | 0 | 0 | 472.869 | 472.869 | 0
5/6/2026 | 2:00:00 AM | 415.596 | 415.596 | 0 | 165.584 | 165.584 | 0 | 0 | 0 | 474 | 474 | 0
5/6/2026 | 2:15:00 AM | 416.727 | 416.727 | 0 | 165.958 | 165.958 | 0 | 0 | 0 | 475.265 | 475.265 | 0
5/6/2026 | 2:30:00 AM | 417.841 | 417.841 | 0 | 166.333 | 166.333 | 0 | 0 | 0 | 476.511 | 476.511 | 0
5/6/2026 | 2:45:00 AM | 418.911 | 418.911 | 0 | 166.714 | 166.714 | 0 | 0 | 0 | 477.709 | 477.709 | 0
5/6/2026 | 3:00:00 AM | 420 | 420 | 0 | 167.089 | 167.089 | 0 | 0 | 0 | 478.926 | 478.926 | 0
5/6/2026 | 3:15:00 AM | 421.068 | 421.068 | 0 | 167.462 | 167.462 | 0 | 0 | 0 | 480.121 | 480.121 | 0
5/6/2026 | 3:30:00 AM | 422.128 | 422.128 | 0 | 167.838 | 167.838 | 0 | 0 | 0 | 481.308 | 481.308 | 0
5/6/2026 | 3:45:00 AM | 423.199 | 423.199 | 0 | 168.215 | 168.215 | 0 | 0 | 0 | 482.507 | 482.507 | 0
5/6/2026 | 4:00:00 AM | 424.28 | 424.28 | 0 | 168.592 | 168.592 | 0 | 0 | 0 | 483.717 | 483.717 | 0
5/6/2026 | 4:15:00 AM | 425.307 | 425.307 | 0 | 168.975 | 168.975 | 0 | 0 | 0 | 484.873 | 484.873 | 0
5/6/2026 | 4:30:00 AM | 426.228 | 426.228 | 0 | 169.351 | 169.351 | 0 | 0 | 0 | 485.914 | 485.914 | 0
5/6/2026 | 4:45:00 AM | 427.232 | 427.232 | 0 | 169.726 | 169.726 | 0 | 0 | 0 | 487.04 | 487.04 | 0
5/6/2026 | 5:00:00 AM | 428.351 | 428.351 | 0 | 170.1 | 170.1 | 0 | 0 | 0 | 488.292 | 488.292 | 0
5/6/2026 | 5:15:00 AM | 429.502 | 429.502 | 0 | 170.472 | 170.472 | 0 | 0 | 0 | 489.578 | 489.578 | 0
5/6/2026 | 5:30:00 AM | 430.578 | 430.578 | 0 | 170.848 | 170.848 | 0 | 0 | 0 | 490.782 | 490.782 | 0
5/6/2026 | 5:45:00 AM | 431.556 | 431.556 | 0 | 171.221 | 171.221 | 0 | 0 | 0 | 491.879 | 491.879 | 0
5/6/2026 | 6:00:00 AM | 432.681 | 432.681 | 0 | 171.588 | 171.588 | 0 | 0 | 0 | 493.134 | 493.134 | 0
5/6/2026 | 6:15:00 AM | 433.802 | 433.802 | 0 | 171.951 | 171.951 | 0 | 0 | 0 | 494.385 | 494.385 | 0
5/6/2026 | 6:30:00 AM | 434.723 | 434.723 | 0 | 172.319 | 172.319 | 0 | 0 | 0 | 495.423 | 495.423 | 0
5/6/2026 | 6:45:00 AM | 435.649 | 435.649 | 0 | 172.69 | 172.69 | 0 | 0 | 0 | 496.467 | 496.467 | 0
5/6/2026 | 7:00:00 AM | 436.59 | 436.59 | 0 | 173.056 | 173.056 | 0 | 0 | 0 | 497.525 | 497.525 | 0
5/6/2026 | 7:15:00 AM | 437.467 | 437.467 | 0 | 173.423 | 173.423 | 0 | 0 | 0 | 498.518 | 498.518 | 0
5/6/2026 | 7:30:00 AM | 438.547 | 438.547 | 0 | 173.784 | 173.784 | 0 | 0 | 0 | 499.722 | 499.722 | 0
5/6/2026 | 7:45:00 AM | 439.549 | 439.549 | 0 | 174.142 | 174.142 | 0 | 0 | 0 | 500.839 | 500.839 | 0
5/6/2026 | 8:00:00 AM | 440.571 | 440.571 | 0 | 174.495 | 174.495 | 0 | 0 | 0 | 501.977 | 501.977 | 0
5/6/2026 | 8:15:00 AM | 441.728 | 441.728 | 0 | 174.845 | 174.845 | 0 | 0 | 0 | 503.26 | 503.26 | 0
5/6/2026 | 8:30:00 AM | 442.878 | 442.878 | 0 | 175.191 | 175.191 | 0 | 0 | 0 | 504.539 | 504.539 | 0
5/6/2026 | 8:45:00 AM | 443.981 | 443.981 | 0 | 175.538 | 175.538 | 0 | 0 | 0 | 505.763 | 505.763 | 0
5/6/2026 | 9:00:00 AM | 445.064 | 445.064 | 0 | 175.882 | 175.882 | 0 | 0 | 0 | 506.965 | 506.965 | 0
5/6/2026 | 9:15:00 AM | 446.078 | 446.078 | 0 | 176.242 | 176.242 | 0 | 0 | 0 | 508.113 | 508.113 | 0
5/6/2026 | 9:30:00 AM | 447.04 | 447.04 | 0 | 176.614 | 176.614 | 0 | 0 | 0 | 509.216 | 509.216 | 0
5/6/2026 | 9:45:00 AM | 447.876 | 447.876 | 0 | 176.972 | 176.972 | 0 | 0 | 0 | 510.191 | 510.191 | 0
5/6/2026 | 10:00:00 AM | 448.888 | 448.888 | 0 | 177.332 | 177.332 | 0 | 0 | 0 | 511.347 | 511.347 | 0
5/6/2026 | 10:15:00 AM | 449.88 | 449.88 | 0 | 177.695 | 177.695 | 0 | 0 | 0 | 512.484 | 512.484 | 0
5/6/2026 | 10:30:00 AM | 450.828 | 450.828 | 0 | 178.066 | 178.066 | 0 | 0 | 0 | 513.577 | 513.577 | 0
5/6/2026 | 10:45:00 AM | 451.791 | 451.791 | 0 | 178.451 | 178.451 | 0 | 0 | 0 | 514.688 | 514.688 | 0
5/6/2026 | 11:00:00 AM | 452.749 | 452.749 | 0 | 178.83 | 178.83 | 0 | 0 | 0 | 515.795 | 515.795 | 0
5/6/2026 | 11:15:00 AM | 453.705 | 453.705 | 0 | 179.212 | 179.212 | 0 | 0 | 0 | 516.901 | 516.901 | 0
5/6/2026 | 11:30:00 AM | 454.661 | 454.661 | 0 | 179.593 | 179.593 | 0 | 0 | 0 | 518.007 | 518.007 | 0
5/6/2026 | 11:45:00 AM | 455.627 | 455.627 | 0 | 179.97 | 179.97 | 0 | 0 | 0 | 519.12 | 519.12 | 0
5/6/2026 | 12:00:00 PM | 456.603 | 456.603 | 0 | 180.348 | 180.348 | 0 | 0 | 0 | 520.243 | 520.243 | 0
5/6/2026 | 12:15:00 PM | 457.395 | 457.395 | 0 | 180.723 | 180.723 | 0 | 0 | 0 | 521.192 | 521.192 | 0
5/6/2026 | 12:30:00 PM | 458.206 | 458.206 | 0 | 181.092 | 181.092 | 0 | 0 | 0 | 522.157 | 522.157 | 0
5/6/2026 | 12:45:00 PM | 459.022 | 459.022 | 0 | 181.464 | 181.464 | 0 | 0 | 0 | 523.126 | 523.126 | 0
5/6/2026 | 1:00:00 PM | 459.852 | 459.852 | 0 | 181.842 | 181.842 | 0 | 0 | 0 | 524.107 | 524.107 | 0
5/6/2026 | 1:15:00 PM | 460.862 | 460.862 | 0 | 182.208 | 182.208 | 0 | 0 | 0 | 525.265 | 525.265 | 0
5/6/2026 | 1:30:00 PM | 461.721 | 461.721 | 0 | 182.573 | 182.573 | 0 | 0 | 0 | 526.275 | 526.275 | 0
5/6/2026 | 1:45:00 PM | 462.544 | 462.544 | 0 | 182.936 | 182.936 | 0 | 0 | 0 | 527.248 | 527.248 | 0
5/6/2026 | 2:00:00 PM | 463.313 | 463.313 | 0 | 183.305 | 183.305 | 0 | 0 | 0 | 528.17 | 528.17 | 0
5/6/2026 | 2:15:00 PM | 464.374 | 464.374 | 0 | 183.666 | 183.666 | 0 | 0 | 0 | 529.382 | 529.382 | 0
5/6/2026 | 2:30:00 PM | 465.4 | 465.4 | 0 | 184.03 | 184.03 | 0 | 0 | 0 | 530.555 | 530.555 | 0
5/6/2026 | 2:45:00 PM | 466.405 | 466.405 | 0 | 184.393 | 184.393 | 0 | 0 | 0 | 531.706 | 531.706 | 0
5/6/2026 | 3:00:00 PM | 467.323 | 467.323 | 0 | 184.763 | 184.763 | 0 | 0 | 0 | 532.769 | 532.769 | 0
5/6/2026 | 3:15:00 PM | 468.323 | 468.323 | 0 | 185.128 | 185.128 | 0 | 0 | 0 | 533.915 | 533.915 | 0
5/6/2026 | 3:30:00 PM | 469.404 | 469.404 | 0 | 185.491 | 185.491 | 0 | 0 | 0 | 535.149 | 535.149 | 0
5/6/2026 | 3:45:00 PM | 470.433 | 470.433 | 0 | 185.852 | 185.852 | 0 | 0 | 0 | 536.327 | 536.327 | 0
5/6/2026 | 4:00:00 PM | 471.443 | 471.443 | 0 | 186.22 | 186.22 | 0 | 0 | 0 | 537.485 | 537.485 | 0
5/6/2026 | 4:15:00 PM | 472.218 | 472.218 | 0 | 186.588 | 186.588 | 0 | 0 | 0 | 538.413 | 538.413 | 0
5/6/2026 | 4:30:00 PM | 473.031 | 473.031 | 0 | 186.955 | 186.955 | 0 | 0 | 0 | 539.38 | 539.38 | 0
5/6/2026 | 4:45:00 PM | 473.988 | 473.988 | 0 | 187.328 | 187.328 | 0 | 0 | 0 | 540.485 | 540.485 | 0
5/6/2026 | 5:00:00 PM | 474.902 | 474.902 | 0 | 187.696 | 187.696 | 0 | 0 | 0 | 541.552 | 541.552 | 0
5/6/2026 | 5:15:00 PM | 475.736 | 475.736 | 0 | 188.068 | 188.068 | 0 | 0 | 0 | 542.537 | 542.537 | 0
5/6/2026 | 5:30:00 PM | 476.74 | 476.74 | 0 | 188.438 | 188.438 | 0 | 0 | 0 | 543.69 | 543.69 | 0
5/6/2026 | 5:45:00 PM | 477.551 | 477.551 | 0 | 188.814 | 188.814 | 0 | 0 | 0 | 544.659 | 544.659 | 0
5/6/2026 | 6:00:00 PM | 478.378 | 478.378 | 0 | 189.187 | 189.187 | 0 | 0 | 0 | 545.642 | 545.642 | 0
5/6/2026 | 6:15:00 PM | 479.32 | 479.32 | 0 | 189.559 | 189.559 | 0 | 0 | 0 | 546.734 | 546.734 | 0
5/6/2026 | 6:30:00 PM | 480.456 | 480.456 | 0 | 189.911 | 189.911 | 0 | 0 | 0 | 547.999 | 547.999 | 0
5/6/2026 | 6:45:00 PM | 481.458 | 481.458 | 0 | 190.263 | 190.263 | 0 | 0 | 0 | 549.123 | 549.123 | 0
5/6/2026 | 7:00:00 PM | 482.419 | 482.419 | 0 | 190.616 | 190.616 | 0 | 0 | 0 | 550.202 | 550.202 | 0
5/6/2026 | 7:15:00 PM | 483.512 | 483.512 | 0 | 190.97 | 190.97 | 0 | 0 | 0 | 551.422 | 551.422 | 0
5/6/2026 | 7:30:00 PM | 484.652 | 484.652 | 0 | 191.329 | 191.329 | 0 | 0 | 0 | 552.694 | 552.694 | 0
5/6/2026 | 7:45:00 PM | 485.756 | 485.756 | 0 | 191.685 | 191.685 | 0 | 0 | 0 | 553.928 | 553.928 | 0
5/6/2026 | 8:00:00 PM | 486.8 | 486.8 | 0 | 192.041 | 192.041 | 0 | 0 | 0 | 555.094 | 555.094 | 0
5/6/2026 | 8:15:00 PM | 487.876 | 487.876 | 0 | 192.398 | 192.398 | 0 | 0 | 0 | 556.297 | 556.297 | 0
5/6/2026 | 8:30:00 PM | 488.908 | 488.908 | 0 | 192.76 | 192.76 | 0 | 0 | 0 | 557.452 | 557.452 | 0
5/6/2026 | 8:45:00 PM | 489.802 | 489.802 | 0 | 193.124 | 193.124 | 0 | 0 | 0 | 558.466 | 558.466 | 0
5/6/2026 | 9:00:00 PM | 490.715 | 490.715 | 0 | 193.478 | 193.478 | 0 | 0 | 0 | 559.496 | 559.496 | 0
5/6/2026 | 9:15:00 PM | 491.758 | 491.758 | 0 | 193.832 | 193.832 | 0 | 0 | 0 | 560.663 | 560.663 | 0
5/6/2026 | 9:30:00 PM | 492.875 | 492.875 | 0 | 194.19 | 194.19 | 0 | 0 | 0 | 561.909 | 561.909 | 0
5/6/2026 | 9:45:00 PM | 493.96 | 493.96 | 0 | 194.543 | 194.543 | 0 | 0 | 0 | 563.12 | 563.12 | 0
5/6/2026 | 10:00:00 PM | 495.037 | 495.037 | 0 | 194.899 | 194.899 | 0 | 0 | 0 | 564.322 | 564.322 | 0
5/6/2026 | 10:15:00 PM | 495.991 | 495.991 | 0 | 195.253 | 195.253 | 0 | 0 | 0 | 565.396 | 565.396 | 0
5/6/2026 | 10:30:00 PM | 496.94 | 496.94 | 0 | 195.604 | 195.604 | 0 | 0 | 0 | 566.46 | 566.46 | 0
5/6/2026 | 10:45:00 PM | 497.973 | 497.973 | 0 | 195.963 | 195.963 | 0 | 0 | 0 | 567.613 | 567.613 | 0
5/6/2026 | 11:00:00 PM | 498.884 | 498.884 | 0 | 196.321 | 196.321 | 0 | 0 | 0 | 568.64 | 568.64 | 0
5/6/2026 | 11:15:00 PM | 499.906 | 499.906 | 0 | 196.678 | 196.678 | 0 | 0 | 0 | 569.785 | 569.785 | 0
5/6/2026 | 11:30:00 PM | 500.962 | 500.962 | 0 | 197.039 | 197.039 | 0 | 0 | 0 | 570.964 | 570.964 | 0
5/6/2026 | 11:45:00 PM | 501.835 | 501.835 | 0 | 197.402 | 197.402 | 0 | 0 | 0 | 571.955 | 571.955 | 0
5/7/2026 | 12:00:00 AM | 502.809 | 502.809 | 0 | 197.774 | 197.774 | 0 | 0 | 0 | 573.05 | 573.05 | 0
5/7/2026 | 12:15:00 AM | 503.869 | 503.869 | 0 | 198.141 | 198.141 | 0 | 0 | 0 | 574.237 | 574.237 | 0
5/7/2026 | 12:30:00 AM | 504.974 | 504.974 | 0 | 198.511 | 198.511 | 0 | 0 | 0 | 575.473 | 575.473 | 0
5/7/2026 | 12:45:00 AM | 506.125 | 506.125 | 0 | 198.882 | 198.882 | 0 | 0 | 0 | 576.761 | 576.761 | 0
5/7/2026 | 1:00:00 AM | 507.194 | 507.194 | 0 | 199.255 | 199.255 | 0 | 0 | 0 | 577.961 | 577.961 | 0
5/7/2026 | 1:15:00 AM | 508.287 | 508.287 | 0 | 199.627 | 199.627 | 0 | 0 | 0 | 579.184 | 579.184 | 0
5/7/2026 | 1:30:00 AM | 509.361 | 509.361 | 0 | 200.006 | 200.006 | 0 | 0 | 0 | 580.387 | 580.387 | 0
5/7/2026 | 1:45:00 AM | 510.435 | 510.435 | 0 | 200.378 | 200.378 | 0 | 0 | 0 | 581.588 | 581.588 | 0
5/7/2026 | 2:00:00 AM | 511.505 | 511.505 | 0 | 200.75 | 200.75 | 0 | 0 | 0 | 582.784 | 582.784 | 0
5/7/2026 | 2:15:00 AM | 512.576 | 512.576 | 0 | 201.124 | 201.124 | 0 | 0 | 0 | 583.982 | 583.982 | 0
5/7/2026 | 2:30:00 AM | 513.645 | 513.645 | 0 | 201.5 | 201.5 | 0 | 0 | 0 | 585.178 | 585.178 | 0
5/7/2026 | 2:45:00 AM | 514.715 | 514.715 | 0 | 201.881 | 201.881 | 0 | 0 | 0 | 586.376 | 586.376 | 0
5/7/2026 | 3:00:00 AM | 515.786 | 515.786 | 0 | 202.263 | 202.263 | 0 | 0 | 0 | 587.574 | 587.574 | 0
5/7/2026 | 3:15:00 AM | 516.859 | 516.859 | 0 | 202.649 | 202.649 | 0 | 0 | 0 | 588.777 | 588.777 | 0
5/7/2026 | 3:30:00 AM | 517.924 | 517.924 | 0 | 203.019 | 203.019 | 0 | 0 | 0 | 589.968 | 589.968 | 0
5/7/2026 | 3:45:00 AM | 518.989 | 518.989 | 0 | 203.392 | 203.392 | 0 | 0 | 0 | 591.16 | 591.16 | 0
5/7/2026 | 4:00:00 AM | 520.058 | 520.058 | 0 | 203.766 | 203.766 | 0 | 0 | 0 | 592.356 | 592.356 | 0
5/7/2026 | 4:15:00 AM | 521.128 | 521.128 | 0 | 204.145 | 204.145 | 0 | 0 | 0 | 593.554 | 593.554 | 0
5/7/2026 | 4:30:00 AM | 522.198 | 522.198 | 0 | 204.524 | 204.524 | 0 | 0 | 0 | 594.752 | 594.752 | 0
5/7/2026 | 4:45:00 AM | 523.267 | 523.267 | 0 | 204.902 | 204.902 | 0 | 0 | 0 | 595.947 | 595.947 | 0
5/7/2026 | 5:00:00 AM | 524.342 | 524.342 | 0 | 205.29 | 205.29 | 0 | 0 | 0 | 597.15 | 597.15 | 0
5/7/2026 | 5:15:00 AM | 525.411 | 525.411 | 0 | 205.667 | 205.667 | 0 | 0 | 0 | 598.346 | 598.346 | 0
5/7/2026 | 5:30:00 AM | 526.48 | 526.48 | 0 | 206.043 | 206.043 | 0 | 0 | 0 | 599.54 | 599.54 | 0
5/7/2026 | 5:45:00 AM | 527.545 | 527.545 | 0 | 206.413 | 206.413 | 0 | 0 | 0 | 600.73 | 600.73 | 0
5/7/2026 | 6:00:00 AM | 528.609 | 528.609 | 0 | 206.779 | 206.779 | 0 | 0 | 0 | 601.915 | 601.915 | 0
5/7/2026 | 6:15:00 AM | 529.669 | 529.669 | 0 | 207.14 | 207.14 | 0 | 0 | 0 | 603.095 | 603.095 | 0
5/7/2026 | 6:30:00 AM | 530.728 | 530.728 | 0 | 207.495 | 207.495 | 0 | 0 | 0 | 604.272 | 604.272 | 0
5/7/2026 | 6:45:00 AM | 531.792 | 531.792 | 0 | 207.854 | 207.854 | 0 | 0 | 0 | 605.453 | 605.453 | 0
5/7/2026 | 7:00:00 AM | 532.852 | 532.852 | 0 | 208.206 | 208.206 | 0 | 0 | 0 | 606.629 | 606.629 | 0
5/7/2026 | 7:15:00 AM | 533.74 | 533.74 | 0 | 208.566 | 208.566 | 0 | 0 | 0 | 607.63 | 607.63 | 0
5/7/2026 | 7:30:00 AM | 534.679 | 534.679 | 0 | 208.928 | 208.928 | 0 | 0 | 0 | 608.681 | 608.681 | 0
5/7/2026 | 7:45:00 AM | 535.634 | 535.634 | 0 | 209.286 | 209.286 | 0 | 0 | 0 | 609.747 | 609.747 | 0
5/7/2026 | 8:00:00 AM | 536.701 | 536.701 | 0 | 209.641 | 209.641 | 0 | 0 | 0 | 610.933 | 610.933 | 0
5/7/2026 | 8:15:00 AM | 537.779 | 537.779 | 0 | 209.993 | 209.993 | 0 | 0 | 0 | 612.13 | 612.13 | 0
5/7/2026 | 8:30:00 AM | 538.846 | 538.846 | 0 | 210.35 | 210.35 | 0 | 0 | 0 | 613.313 | 613.313 | 0
5/7/2026 | 8:45:00 AM | 539.867 | 539.867 | 0 | 210.706 | 210.706 | 0 | 0 | 0 | 614.452 | 614.452 | 0
5/7/2026 | 9:00:00 AM | 540.767 | 540.767 | 0 | 211.061 | 211.061 | 0 | 0 | 0 | 615.461 | 615.461 | 0
5/7/2026 | 9:15:00 AM | 541.661 | 541.661 | 0 | 211.414 | 211.414 | 0 | 0 | 0 | 616.465 | 616.465 | 0
5/7/2026 | 9:30:00 AM | 542.633 | 542.633 | 0 | 211.756 | 211.756 | 0 | 0 | 0 | 617.551 | 617.551 | 0
5/7/2026 | 9:45:00 AM | 543.599 | 543.599 | 0 | 212.1 | 212.1 | 0 | 0 | 0 | 618.627 | 618.627 | 0
5/7/2026 | 10:00:00 AM | 544.493 | 544.493 | 0 | 212.45 | 212.45 | 0 | 0 | 0 | 619.636 | 619.636 | 0
5/7/2026 | 10:15:00 AM | 545.34 | 545.34 | 0 | 212.822 | 212.822 | 0 | 0 | 0 | 620.626 | 620.626 | 0
5/7/2026 | 10:30:00 AM | 546.257 | 546.257 | 0 | 213.2 | 213.2 | 0 | 0 | 0 | 621.686 | 621.686 | 0
5/7/2026 | 10:45:00 AM | 547.278 | 547.278 | 0 | 213.568 | 213.568 | 0 | 0 | 0 | 622.853 | 622.853 | 0
5/7/2026 | 11:00:00 AM | 548.264 | 548.264 | 0 | 213.937 | 213.937 | 0 | 0 | 0 | 623.982 | 623.982 | 0
5/7/2026 | 11:15:00 AM | 549.281 | 549.281 | 0 | 214.307 | 214.307 | 0 | 0 | 0 | 625.145 | 625.145 | 0
5/7/2026 | 11:30:00 AM | 550.247 | 550.247 | 0 | 214.682 | 214.682 | 0 | 0 | 0 | 626.257 | 626.257 | 0
5/7/2026 | 11:45:00 AM | 551.28 | 551.28 | 0 | 215.06 | 215.06 | 0 | 0 | 0 | 627.44 | 627.44 | 0
5/7/2026 | 12:00:00 PM | 552.125 | 552.125 | 0 | 215.439 | 215.439 | 0 | 0 | 0 | 628.44 | 628.44 | 0
5/7/2026 | 12:15:00 PM | 552.944 | 552.944 | 0 | 215.823 | 215.823 | 0 | 0 | 0 | 629.414 | 629.414 | 0
5/7/2026 | 12:30:00 PM | 553.741 | 553.741 | 0 | 216.2 | 216.2 | 0 | 0 | 0 | 630.362 | 630.362 | 0
5/7/2026 | 12:45:00 PM | 554.541 | 554.541 | 0 | 216.577 | 216.577 | 0 | 0 | 0 | 631.318 | 631.318 | 0
5/7/2026 | 1:00:00 PM | 555.479 | 555.479 | 0 | 216.956 | 216.956 | 0 | 0 | 0 | 632.402 | 632.402 | 0
5/7/2026 | 1:15:00 PM | 556.428 | 556.428 | 0 | 217.333 | 217.333 | 0 | 0 | 0 | 633.495 | 633.495 | 0
5/7/2026 | 1:30:00 PM | 557.313 | 557.313 | 0 | 217.708 | 217.708 | 0 | 0 | 0 | 634.522 | 634.522 | 0
5/7/2026 | 1:45:00 PM | 558.266 | 558.266 | 0 | 218.09 | 218.09 | 0 | 0 | 0 | 635.619 | 635.619 | 0
5/7/2026 | 2:00:00 PM | 559.289 | 559.289 | 0 | 218.464 | 218.464 | 0 | 0 | 0 | 636.789 | 636.789 | 0
5/7/2026 | 2:15:00 PM | 560.278 | 560.278 | 0 | 218.843 | 218.843 | 0 | 0 | 0 | 637.923 | 637.923 | 0
5/7/2026 | 2:30:00 PM | 561.254 | 561.254 | 0 | 219.223 | 219.223 | 0 | 0 | 0 | 639.043 | 639.043 | 0
5/7/2026 | 2:45:00 PM | 562.087 | 562.087 | 0 | 219.605 | 219.605 | 0 | 0 | 0 | 640.029 | 640.029 | 0
5/7/2026 | 3:00:00 PM | 562.92 | 562.92 | 0 | 219.986 | 219.986 | 0 | 0 | 0 | 641.011 | 641.011 | 0
5/7/2026 | 3:15:00 PM | 563.781 | 563.781 | 0 | 220.367 | 220.367 | 0 | 0 | 0 | 642.016 | 642.016 | 0
5/7/2026 | 3:30:00 PM | 564.695 | 564.695 | 0 | 220.754 | 220.754 | 0 | 0 | 0 | 643.075 | 643.075 | 0
5/7/2026 | 3:45:00 PM | 565.708 | 565.708 | 0 | 221.135 | 221.135 | 0 | 0 | 0 | 644.235 | 644.235 | 0
5/7/2026 | 4:00:00 PM | 566.548 | 566.548 | 0 | 221.517 | 221.517 | 0 | 0 | 0 | 645.228 | 645.228 | 0
5/7/2026 | 4:15:00 PM | 567.383 | 567.383 | 0 | 221.902 | 221.902 | 0 | 0 | 0 | 646.213 | 646.213 | 0
5/7/2026 | 4:30:00 PM | 568.237 | 568.237 | 0 | 222.286 | 222.286 | 0 | 0 | 0 | 647.213 | 647.213 | 0
5/7/2026 | 4:45:00 PM | 569.106 | 569.106 | 0 | 222.672 | 222.672 | 0 | 0 | 0 | 648.228 | 648.228 | 0
5/7/2026 | 5:00:00 PM | 570.127 | 570.127 | 0 | 223.063 | 223.063 | 0 | 0 | 0 | 649.398 | 649.398 | 0
5/7/2026 | 5:15:00 PM | 571.156 | 571.156 | 0 | 223.451 | 223.451 | 0 | 0 | 0 | 650.578 | 650.578 | 0
5/7/2026 | 5:30:00 PM | 572.156 | 572.156 | 0 | 223.84 | 223.84 | 0 | 0 | 0 | 651.727 | 651.727 | 0
5/7/2026 | 5:45:00 PM | 573.127 | 573.127 | 0 | 224.232 | 224.232 | 0 | 0 | 0 | 652.847 | 652.847 | 0
5/7/2026 | 6:00:00 PM | 574.002 | 574.002 | 0 | 224.626 | 224.626 | 0 | 0 | 0 | 653.874 | 653.874 | 0
5/7/2026 | 6:15:00 PM | 574.884 | 574.884 | 0 | 225.025 | 225.025 | 0 | 0 | 0 | 654.908 | 654.908 | 0
5/7/2026 | 6:30:00 PM | 575.904 | 575.904 | 0 | 225.425 | 225.425 | 0 | 0 | 0 | 656.083 | 656.083 | 0
5/7/2026 | 6:45:00 PM | 576.881 | 576.881 | 0 | 225.832 | 225.832 | 0 | 0 | 0 | 657.214 | 657.214 | 0
5/7/2026 | 7:00:00 PM | 577.85 | 577.85 | 0 | 226.234 | 226.234 | 0 | 0 | 0 | 658.337 | 658.337 | 0
5/7/2026 | 7:15:00 PM | 578.82 | 578.82 | 0 | 226.642 | 226.642 | 0 | 0 | 0 | 659.463 | 659.463 | 0
5/7/2026 | 7:30:00 PM | 580.816 | 580.816 | 0 | 228.572 | 228.572 | 0 | 0 | 0 | 662.366 | 662.366 | 0
5/7/2026 | 7:45:00 PM | 581.762 | 581.762 | 0 | 228.953 | 228.953 | 0 | 0 | 0 | 663.437 | 663.437 | 0
5/7/2026 | 8:00:00 PM | 582.702 | 582.702 | 0 | 229.326 | 229.326 | 0 | 0 | 0 | 664.493 | 664.493 | 0
5/7/2026 | 8:15:00 PM | 583.655 | 583.655 | 0 | 229.696 | 229.696 | 0 | 0 | 0 | 665.562 | 665.562 | 0
5/7/2026 | 8:30:00 PM | 584.703 | 584.703 | 0 | 230.074 | 230.074 | 0 | 0 | 0 | 666.734 | 666.734 | 0
5/7/2026 | 8:45:00 PM | 585.837 | 585.837 | 0 | 230.442 | 230.442 | 0 | 0 | 0 | 667.998 | 667.998 | 0
5/7/2026 | 9:00:00 PM | 586.771 | 586.771 | 0 | 230.815 | 230.815 | 0 | 0 | 0 | 669.052 | 669.052 | 0
5/7/2026 | 9:15:00 PM | 587.689 | 587.689 | 0 | 231.193 | 231.193 | 0 | 0 | 0 | 670.091 | 670.091 | 0
5/7/2026 | 9:30:00 PM | 588.613 | 588.613 | 0 | 231.573 | 231.573 | 0 | 0 | 0 | 671.136 | 671.136 | 0
5/7/2026 | 9:45:00 PM | 589.576 | 589.576 | 0 | 231.956 | 231.956 | 0 | 0 | 0 | 672.221 | 672.221 | 0
5/7/2026 | 10:00:00 PM | 590.537 | 590.537 | 0 | 232.338 | 232.338 | 0 | 0 | 0 | 673.304 | 673.304 | 0
5/7/2026 | 10:15:00 PM | 591.621 | 591.621 | 0 | 232.712 | 232.712 | 0 | 0 | 0 | 674.515 | 674.515 | 0
5/7/2026 | 10:30:00 PM | 592.739 | 592.739 | 0 | 233.093 | 233.093 | 0 | 0 | 0 | 675.763 | 675.763 | 0
5/7/2026 | 10:45:00 PM | 593.73 | 593.73 | 0 | 233.472 | 233.472 | 0 | 0 | 0 | 676.878 | 676.878 | 0
5/7/2026 | 11:00:00 PM | 594.635 | 594.635 | 0 | 233.857 | 233.857 | 0 | 0 | 0 | 677.906 | 677.906 | 0
5/7/2026 | 11:15:00 PM | 595.581 | 595.581 | 0 | 234.241 | 234.241 | 0 | 0 | 0 | 678.973 | 678.973 | 0
5/7/2026 | 11:30:00 PM | 596.539 | 596.539 | 0 | 234.627 | 234.627 | 0 | 0 | 0 | 680.054 | 680.054 | 0
5/7/2026 | 11:45:00 PM | 597.585 | 597.585 | 0 | 235.015 | 235.015 | 0 | 0 | 0 | 681.229 | 681.229 | 0
5/8/2026 | 12:00:00 AM | 598.698 | 598.698 | 0 | 235.401 | 235.401 | 0 | 0 | 0 | 682.474 | 682.474 | 0
5/8/2026 | 12:15:00 AM | 599.627 | 599.627 | 0 | 235.777 | 235.777 | 0 | 0 | 0 | 683.523 | 683.523 | 0
5/8/2026 | 12:30:00 AM | 600.544 | 600.544 | 0 | 236.15 | 236.15 | 0 | 0 | 0 | 684.558 | 684.558 | 0
5/8/2026 | 12:45:00 AM | 601.494 | 601.494 | 0 | 236.534 | 236.534 | 0 | 0 | 0 | 685.626 | 685.626 | 0
5/8/2026 | 1:00:00 AM | 602.556 | 602.556 | 0 | 236.908 | 236.908 | 0 | 0 | 0 | 686.813 | 686.813 | 0
5/8/2026 | 1:15:00 AM | 603.626 | 603.626 | 0 | 237.281 | 237.281 | 0 | 0 | 0 | 688.007 | 688.007 | 0
5/8/2026 | 1:30:00 AM | 604.508 | 604.508 | 0 | 237.656 | 237.656 | 0 | 0 | 0 | 689.008 | 689.008 | 0
5/8/2026 | 1:45:00 AM | 605.419 | 605.419 | 0 | 238.031 | 238.031 | 0 | 0 | 0 | 690.038 | 690.038 | 0
5/8/2026 | 2:00:00 AM | 606.358 | 606.358 | 0 | 238.407 | 238.407 | 0 | 0 | 0 | 691.096 | 691.096 | 0
5/8/2026 | 2:15:00 AM | 607.363 | 607.363 | 0 | 238.782 | 238.782 | 0 | 0 | 0 | 692.221 | 692.221 | 0
5/8/2026 | 2:30:00 AM | 608.349 | 608.349 | 0 | 239.159 | 239.159 | 0 | 0 | 0 | 693.326 | 693.326 | 0
5/8/2026 | 2:45:00 AM | 609.271 | 609.271 | 0 | 239.536 | 239.536 | 0 | 0 | 0 | 694.365 | 694.365 | 0
5/8/2026 | 3:00:00 AM | 610.22 | 610.22 | 0 | 239.915 | 239.915 | 0 | 0 | 0 | 695.433 | 695.433 | 0
5/8/2026 | 3:15:00 AM | 611.279 | 611.279 | 0 | 240.305 | 240.305 | 0 | 0 | 0 | 696.617 | 696.617 | 0
5/8/2026 | 3:30:00 AM | 612.213 | 612.213 | 0 | 240.689 | 240.689 | 0 | 0 | 0 | 697.675 | 697.675 | 0
5/8/2026 | 3:45:00 AM | 613.137 | 613.137 | 0 | 241.073 | 241.073 | 0 | 0 | 0 | 698.719 | 698.719 | 0
5/8/2026 | 4:00:00 AM | 614.058 | 614.058 | 0 | 241.457 | 241.457 | 0 | 0 | 0 | 699.76 | 699.76 | 0
5/8/2026 | 4:15:00 AM | 615.077 | 615.077 | 0 | 241.839 | 241.839 | 0 | 0 | 0 | 700.903 | 700.903 | 0
5/8/2026 | 4:30:00 AM | 616.133 | 616.133 | 0 | 242.221 | 242.221 | 0 | 0 | 0 | 702.085 | 702.085 | 0
5/8/2026 | 4:45:00 AM | 617.076 | 617.076 | 0 | 242.602 | 242.602 | 0 | 0 | 0 | 703.15 | 703.15 | 0
5/8/2026 | 5:00:00 AM | 617.996 | 617.996 | 0 | 242.983 | 242.983 | 0 | 0 | 0 | 704.189 | 704.189 | 0
5/8/2026 | 5:15:00 AM | 618.941 | 618.941 | 0 | 243.361 | 243.361 | 0 | 0 | 0 | 705.252 | 705.252 | 0
5/8/2026 | 5:30:00 AM | 619.897 | 619.897 | 0 | 243.74 | 243.74 | 0 | 0 | 0 | 706.326 | 706.326 | 0
5/8/2026 | 5:45:00 AM | 620.85 | 620.85 | 0 | 244.123 | 244.123 | 0 | 0 | 0 | 707.397 | 707.397 | 0
5/8/2026 | 6:00:00 AM | 621.928 | 621.928 | 0 | 244.499 | 244.499 | 0 | 0 | 0 | 708.6 | 708.6 | 0
5/8/2026 | 6:15:00 AM | 622.968 | 622.968 | 0 | 244.867 | 244.867 | 0 | 0 | 0 | 709.76 | 709.76 | 0
5/8/2026 | 6:30:00 AM | 623.943 | 623.943 | 0 | 245.237 | 245.237 | 0 | 0 | 0 | 710.851 | 710.851 | 0
5/8/2026 | 6:45:00 AM | 624.975 | 624.975 | 0 | 245.606 | 245.606 | 0 | 0 | 0 | 712.003 | 712.003 | 0
5/8/2026 | 7:00:00 AM | 626.041 | 626.041 | 0 | 245.973 | 245.973 | 0 | 0 | 0 | 713.19 | 713.19 | 0
5/8/2026 | 7:15:00 AM | 627.016 | 627.016 | 0 | 246.339 | 246.339 | 0 | 0 | 0 | 714.284 | 714.284 | 0
5/8/2026 | 7:30:00 AM | 627.918 | 627.918 | 0 | 246.707 | 246.707 | 0 | 0 | 0 | 715.298 | 715.298 | 0
5/8/2026 | 7:45:00 AM | 628.814 | 628.814 | 0 | 247.08 | 247.08 | 0 | 0 | 0 | 716.314 | 716.314 | 0
5/8/2026 | 8:00:00 AM | 629.631 | 629.631 | 0 | 247.475 | 247.475 | 0 | 0 | 0 | 717.285 | 717.285 | 0
5/8/2026 | 8:15:00 AM | 630.469 | 630.469 | 0 | 247.866 | 247.866 | 0 | 0 | 0 | 718.273 | 718.273 | 0
5/8/2026 | 8:30:00 AM | 631.459 | 631.459 | 0 | 248.263 | 248.263 | 0 | 0 | 0 | 719.411 | 719.411 | 0
5/8/2026 | 8:45:00 AM | 632.46 | 632.46 | 0 | 248.651 | 248.651 | 0 | 0 | 0 | 720.562 | 720.562 | 0
5/8/2026 | 9:00:00 AM | 633.33 | 633.33 | 0 | 249.038 | 249.038 | 0 | 0 | 0 | 721.584 | 721.584 | 0
5/8/2026 | 9:15:00 AM | 634.127 | 634.127 | 0 | 249.422 | 249.422 | 0 | 0 | 0 | 722.533 | 722.533 | 0
5/8/2026 | 9:30:00 AM | 634.971 | 634.971 | 0 | 249.805 | 249.805 | 0 | 0 | 0 | 723.522 | 723.522 | 0
5/8/2026 | 9:45:00 AM | 635.821 | 635.821 | 0 | 250.19 | 250.19 | 0 | 0 | 0 | 724.52 | 724.52 | 0
5/8/2026 | 10:00:00 AM | 636.751 | 636.751 | 0 | 250.571 | 250.571 | 0 | 0 | 0 | 725.595 | 725.595 | 0
5/8/2026 | 10:15:00 AM | 637.704 | 637.704 | 0 | 250.949 | 250.949 | 0 | 0 | 0 | 726.692 | 726.692 | 0
5/8/2026 | 10:30:00 AM | 638.654 | 638.654 | 0 | 251.326 | 251.326 | 0 | 0 | 0 | 727.787 | 727.787 | 0
5/8/2026 | 10:45:00 AM | 639.42 | 639.42 | 0 | 251.703 | 251.703 | 0 | 0 | 0 | 728.709 | 728.709 | 0
5/8/2026 | 11:00:00 AM | 640.269 | 640.269 | 0 | 252.079 | 252.079 | 0 | 0 | 0 | 729.701 | 729.701 | 0
5/8/2026 | 11:15:00 AM | 641.121 | 641.121 | 0 | 252.464 | 252.464 | 0 | 0 | 0 | 730.699 | 730.699 | 0
5/8/2026 | 11:30:00 AM | 642.08 | 642.08 | 0 | 252.837 | 252.837 | 0 | 0 | 0 | 731.801 | 731.801 | 0
5/8/2026 | 11:45:00 AM | 643.085 | 643.085 | 0 | 253.207 | 253.207 | 0 | 0 | 0 | 732.951 | 732.951 | 0
5/8/2026 | 12:00:00 PM | 644.009 | 644.009 | 0 | 253.576 | 253.576 | 0 | 0 | 0 | 734.014 | 734.014 | 0
5/8/2026 | 12:15:00 PM | 644.839 | 644.839 | 0 | 253.946 | 253.946 | 0 | 0 | 0 | 734.994 | 734.994 | 0
5/8/2026 | 12:30:00 PM | 645.671 | 645.671 | 0 | 254.318 | 254.318 | 0 | 0 | 0 | 735.971 | 735.971 | 0
5/8/2026 | 12:45:00 PM | 646.527 | 646.527 | 0 | 254.69 | 254.69 | 0 | 0 | 0 | 736.968 | 736.968 | 0
5/8/2026 | 1:00:00 PM | 647.52 | 647.52 | 0 | 255.066 | 255.066 | 0 | 0 | 0 | 738.106 | 738.106 | 0
5/8/2026 | 1:15:00 PM | 648.564 | 648.564 | 0 | 255.441 | 255.441 | 0 | 0 | 0 | 739.299 | 739.299 | 0
5/8/2026 | 1:30:00 PM | 649.539 | 649.539 | 0 | 255.823 | 255.823 | 0 | 0 | 0 | 740.416 | 740.416 | 0
5/8/2026 | 1:45:00 PM | 650.328 | 650.328 | 0 | 256.196 | 256.196 | 0 | 0 | 0 | 741.354 | 741.354 | 0
5/8/2026 | 2:00:00 PM | 651.179 | 651.179 | 0 | 256.567 | 256.567 | 0 | 0 | 0 | 742.346 | 742.346 | 0
5/8/2026 | 2:15:00 PM | 652.035 | 652.035 | 0 | 256.939 | 256.939 | 0 | 0 | 0 | 743.342 | 743.342 | 0
5/8/2026 | 2:30:00 PM | 653.016 | 653.016 | 0 | 257.309 | 257.309 | 0 | 0 | 0 | 744.465 | 744.465 | 0
5/8/2026 | 2:45:00 PM | 653.987 | 653.987 | 0 | 257.676 | 257.676 | 0 | 0 | 0 | 745.577 | 745.577 | 0
5/8/2026 | 3:00:00 PM | 654.818 | 654.818 | 0 | 258.046 | 258.046 | 0 | 0 | 0 | 746.553 | 746.553 | 0
5/8/2026 | 3:15:00 PM | 655.653 | 655.653 | 0 | 258.418 | 258.418 | 0 | 0 | 0 | 747.531 | 747.531 | 0
5/8/2026 | 3:30:00 PM | 656.513 | 656.513 | 0 | 258.795 | 258.795 | 0 | 0 | 0 | 748.531 | 748.531 | 0
5/8/2026 | 3:45:00 PM | 657.428 | 657.428 | 0 | 259.165 | 259.165 | 0 | 0 | 0 | 749.587 | 749.587 | 0
5/8/2026 | 4:00:00 PM | 658.453 | 658.453 | 0 | 259.534 | 259.534 | 0 | 0 | 0 | 750.756 | 750.756 | 0
5/8/2026 | 4:15:00 PM | 659.399 | 659.399 | 0 | 259.907 | 259.907 | 0 | 0 | 0 | 751.843 | 751.843 | 0
5/8/2026 | 4:30:00 PM | 660.203 | 660.203 | 0 | 260.282 | 260.282 | 0 | 0 | 0 | 752.797 | 752.797 | 0
5/8/2026 | 4:45:00 PM | 661.049 | 661.049 | 0 | 260.655 | 260.655 | 0 | 0 | 0 | 753.785 | 753.785 | 0
5/8/2026 | 5:00:00 PM | 661.899 | 661.899 | 0 | 261.027 | 261.027 | 0 | 0 | 0 | 754.776 | 754.776 | 0
5/8/2026 | 5:15:00 PM | 662.855 | 662.855 | 0 | 261.411 | 261.411 | 0 | 0 | 0 | 755.877 | 755.877 | 0
5/8/2026 | 5:30:00 PM | 663.848 | 663.848 | 0 | 261.789 | 261.789 | 0 | 0 | 0 | 757.015 | 757.015 | 0
5/8/2026 | 5:45:00 PM | 664.771 | 664.771 | 0 | 262.167 | 262.167 | 0 | 0 | 0 | 758.082 | 758.082 | 0
5/8/2026 | 6:00:00 PM | 665.541 | 665.541 | 0 | 262.549 | 262.549 | 0 | 0 | 0 | 759.009 | 759.009 | 0
5/8/2026 | 6:15:00 PM | 666.358 | 666.358 | 0 | 262.931 | 262.931 | 0 | 0 | 0 | 759.982 | 759.982 | 0
5/8/2026 | 6:30:00 PM | 667.202 | 667.202 | 0 | 263.311 | 263.311 | 0 | 0 | 0 | 760.972 | 760.972 | 0
5/8/2026 | 6:45:00 PM | 668.076 | 668.076 | 0 | 263.691 | 263.691 | 0 | 0 | 0 | 761.992 | 761.992 | 0
5/8/2026 | 7:00:00 PM | 669.147 | 669.147 | 0 | 264.059 | 264.059 | 0 | 0 | 0 | 763.197 | 763.197 | 0
5/8/2026 | 7:15:00 PM | 670.214 | 670.214 | 0 | 264.404 | 264.404 | 0 | 0 | 0 | 764.38 | 764.38 | 0
5/8/2026 | 7:30:00 PM | 671.247 | 671.247 | 0 | 264.751 | 264.751 | 0 | 0 | 0 | 765.528 | 765.528 | 0
5/8/2026 | 7:45:00 PM | 672.223 | 672.223 | 0 | 265.1 | 265.1 | 0 | 0 | 0 | 766.612 | 766.612 | 0
5/8/2026 | 8:00:00 PM | 673.294 | 673.294 | 0 | 265.449 | 265.449 | 0 | 0 | 0 | 767.802 | 767.802 | 0
5/8/2026 | 8:15:00 PM | 674.258 | 674.258 | 0 | 265.801 | 265.801 | 0 | 0 | 0 | 768.88 | 768.88 | 0
5/8/2026 | 8:30:00 PM | 675.194 | 675.194 | 0 | 266.153 | 266.153 | 0 | 0 | 0 | 769.925 | 769.925 | 0
5/8/2026 | 8:45:00 PM | 676.16 | 676.16 | 0 | 266.504 | 266.504 | 0 | 0 | 0 | 771.001 | 771.001 | 0
5/8/2026 | 9:00:00 PM | 677.167 | 677.167 | 0 | 266.863 | 266.863 | 0 | 0 | 0 | 772.12 | 772.12 | 0
5/8/2026 | 9:15:00 PM | 678.305 | 678.305 | 0 | 267.215 | 267.215 | 0 | 0 | 0 | 773.385 | 773.385 | 0
5/8/2026 | 9:30:00 PM | 679.408 | 679.408 | 0 | 267.57 | 267.57 | 0 | 0 | 0 | 774.61 | 774.61 | 0
5/8/2026 | 9:45:00 PM | 680.37 | 680.37 | 0 | 267.927 | 267.927 | 0 | 0 | 0 | 775.688 | 775.688 | 0
5/8/2026 | 10:00:00 PM | 681.293 | 681.293 | 0 | 268.284 | 268.284 | 0 | 0 | 0 | 776.722 | 776.722 | 0
5/8/2026 | 10:15:00 PM | 682.242 | 682.242 | 0 | 268.643 | 268.643 | 0 | 0 | 0 | 777.782 | 777.782 | 0
5/8/2026 | 10:30:00 PM | 683.245 | 683.245 | 0 | 269.003 | 269.003 | 0 | 0 | 0 | 778.9 | 778.9 | 0
5/8/2026 | 10:45:00 PM | 684.349 | 684.349 | 0 | 269.364 | 269.364 | 0 | 0 | 0 | 780.129 | 780.129 | 0
5/8/2026 | 11:00:00 PM | 685.389 | 685.389 | 0 | 269.734 | 269.734 | 0 | 0 | 0 | 781.288 | 781.288 | 0
5/8/2026 | 11:15:00 PM | 686.344 | 686.344 | 0 | 270.1 | 270.1 | 0 | 0 | 0 | 782.362 | 782.362 | 0
5/8/2026 | 11:30:00 PM | 687.27 | 687.27 | 0 | 270.466 | 270.466 | 0 | 0 | 0 | 783.401 | 783.401 | 0
5/8/2026 | 11:45:00 PM | 688.193 | 688.193 | 0 | 270.835 | 270.835 | 0 | 0 | 0 | 784.439 | 784.439 | 0
5/9/2026 | 12:00:00 AM | 689.134 | 689.134 | 0 | 271.205 | 271.205 | 0 | 0 | 0 | 785.496 | 785.496 | 0
5/9/2026 | 12:15:00 AM | 690.181 | 690.181 | 0 | 271.573 | 271.573 | 0 | 0 | 0 | 786.665 | 786.665 | 0
5/9/2026 | 12:30:00 AM | 691.259 | 691.259 | 0 | 271.944 | 271.944 | 0 | 0 | 0 | 787.868 | 787.868 | 0
5/9/2026 | 12:45:00 AM | 692.183 | 692.183 | 0 | 272.321 | 272.321 | 0 | 0 | 0 | 788.913 | 788.913 | 0
5/9/2026 | 1:00:00 AM | 693.11 | 693.11 | 0 | 272.7 | 272.7 | 0 | 0 | 0 | 789.959 | 789.959 | 0
5/9/2026 | 1:15:00 AM | 694.041 | 694.041 | 0 | 273.08 | 273.08 | 0 | 0 | 0 | 791.01 | 791.01 | 0
5/9/2026 | 1:30:00 AM | 695 | 695 | 0 | 273.459 | 273.459 | 0 | 0 | 0 | 792.089 | 792.089 | 0
5/9/2026 | 1:45:00 AM | 696.116 | 696.116 | 0 | 273.847 | 273.847 | 0 | 0 | 0 | 793.336 | 793.336 | 0
5/9/2026 | 2:00:00 AM | 697.191 | 697.191 | 0 | 274.227 | 274.227 | 0 | 0 | 0 | 794.54 | 794.54 | 0
5/9/2026 | 2:15:00 AM | 698.147 | 698.147 | 0 | 274.608 | 274.608 | 0 | 0 | 0 | 795.62 | 795.62 | 0
5/9/2026 | 2:30:00 AM | 699.072 | 699.072 | 0 | 274.99 | 274.99 | 0 | 0 | 0 | 796.666 | 796.666 | 0
5/9/2026 | 2:45:00 AM | 700.011 | 700.011 | 0 | 275.373 | 275.373 | 0 | 0 | 0 | 797.726 | 797.726 | 0
5/9/2026 | 3:00:00 AM | 700.958 | 700.958 | 0 | 275.755 | 275.755 | 0 | 0 | 0 | 798.793 | 798.793 | 0
5/9/2026 | 3:15:00 AM | 702.028 | 702.028 | 0 | 276.136 | 276.136 | 0 | 0 | 0 | 799.991 | 799.991 | 0
5/9/2026 | 3:30:00 AM | 703.105 | 703.105 | 0 | 276.519 | 276.519 | 0 | 0 | 0 | 801.198 | 801.198 | 0
5/9/2026 | 3:45:00 AM | 704.123 | 704.123 | 0 | 276.903 | 276.903 | 0 | 0 | 0 | 802.342 | 802.342 | 0
5/9/2026 | 4:00:00 AM | 705.011 | 705.011 | 0 | 277.289 | 277.289 | 0 | 0 | 0 | 803.354 | 803.354 | 0
5/9/2026 | 4:15:00 AM | 705.956 | 705.956 | 0 | 277.686 | 277.686 | 0 | 0 | 0 | 804.422 | 804.422 | 0
5/9/2026 | 4:30:00 AM | 706.893 | 706.893 | 0 | 278.075 | 278.075 | 0 | 0 | 0 | 805.483 | 805.483 | 0
5/9/2026 | 4:45:00 AM | 707.842 | 707.842 | 0 | 278.462 | 278.462 | 0 | 0 | 0 | 806.555 | 806.555 | 0
5/9/2026 | 5:00:00 AM | 708.919 | 708.919 | 0 | 278.845 | 278.845 | 0 | 0 | 0 | 807.761 | 807.761 | 0
5/9/2026 | 5:15:00 AM | 709.982 | 709.982 | 0 | 279.227 | 279.227 | 0 | 0 | 0 | 808.952 | 808.952 | 0
5/9/2026 | 5:30:00 AM | 710.928 | 710.928 | 0 | 279.61 | 279.61 | 0 | 0 | 0 | 810.023 | 810.023 | 0
5/9/2026 | 5:45:00 AM | 711.856 | 711.856 | 0 | 279.991 | 279.991 | 0 | 0 | 0 | 811.072 | 811.072 | 0
5/9/2026 | 6:00:00 AM | 712.793 | 712.793 | 0 | 280.373 | 280.373 | 0 | 0 | 0 | 812.129 | 812.129 | 0
5/9/2026 | 6:15:00 AM | 713.735 | 713.735 | 0 | 280.753 | 280.753 | 0 | 0 | 0 | 813.191 | 813.191 | 0
5/9/2026 | 6:30:00 AM | 714.757 | 714.757 | 0 | 281.13 | 281.13 | 0 | 0 | 0 | 814.335 | 814.335 | 0
5/9/2026 | 6:45:00 AM | 715.85 | 715.85 | 0 | 281.507 | 281.507 | 0 | 0 | 0 | 815.557 | 815.557 | 0
5/9/2026 | 7:00:00 AM | 716.773 | 716.773 | 0 | 281.896 | 281.896 | 0 | 0 | 0 | 816.604 | 816.604 | 0
5/9/2026 | 7:15:00 AM | 717.712 | 717.712 | 0 | 282.273 | 282.273 | 0 | 0 | 0 | 817.661 | 817.661 | 0
5/9/2026 | 7:30:00 AM | 718.654 | 718.654 | 0 | 282.647 | 282.647 | 0 | 0 | 0 | 818.72 | 818.72 | 0
5/9/2026 | 7:45:00 AM | 719.656 | 719.656 | 0 | 283.017 | 283.017 | 0 | 0 | 0 | 819.841 | 819.841 | 0
5/9/2026 | 8:00:00 AM | 720.747 | 720.747 | 0 | 283.383 | 283.383 | 0 | 0 | 0 | 821.057 | 821.057 | 0
5/9/2026 | 8:15:00 AM | 721.662 | 721.662 | 0 | 283.749 | 283.749 | 0 | 0 | 0 | 822.087 | 822.087 | 0
5/9/2026 | 8:30:00 AM | 722.592 | 722.592 | 0 | 284.113 | 284.113 | 0 | 0 | 0 | 823.131 | 823.131 | 0
5/9/2026 | 8:45:00 AM | 723.522 | 723.522 | 0 | 284.473 | 284.473 | 0 | 0 | 0 | 824.172 | 824.172 | 0
5/9/2026 | 9:00:00 AM | 724.568 | 724.568 | 0 | 284.83 | 284.83 | 0 | 0 | 0 | 825.336 | 825.336 | 0
5/9/2026 | 9:15:00 AM | 725.694 | 725.694 | 0 | 285.191 | 285.191 | 0 | 0 | 0 | 826.59 | 826.59 | 0
5/9/2026 | 9:30:00 AM | 726.775 | 726.775 | 0 | 285.557 | 285.557 | 0 | 0 | 0 | 827.79 | 827.79 | 0
5/9/2026 | 9:45:00 AM | 727.692 | 727.692 | 0 | 285.911 | 285.911 | 0 | 0 | 0 | 828.819 | 828.819 | 0
5/9/2026 | 10:00:00 AM | 728.623 | 728.623 | 0 | 286.263 | 286.263 | 0 | 0 | 0 | 829.861 | 829.861 | 0
5/9/2026 | 10:15:00 AM | 729.568 | 729.568 | 0 | 286.614 | 286.614 | 0 | 0 | 0 | 830.915 | 830.915 | 0
5/9/2026 | 10:30:00 AM | 730.593 | 730.593 | 0 | 286.962 | 286.962 | 0 | 0 | 0 | 832.055 | 832.055 | 0
5/9/2026 | 10:45:00 AM | 731.685 | 731.685 | 0 | 287.307 | 287.307 | 0 | 0 | 0 | 833.267 | 833.267 | 0
5/9/2026 | 11:00:00 AM | 732.728 | 732.728 | 0 | 287.652 | 287.652 | 0 | 0 | 0 | 834.425 | 834.425 | 0
5/9/2026 | 11:15:00 AM | 733.609 | 733.609 | 0 | 287.999 | 287.999 | 0 | 0 | 0 | 835.415 | 835.415 | 0
5/9/2026 | 11:30:00 AM | 734.511 | 734.511 | 0 | 288.357 | 288.357 | 0 | 0 | 0 | 836.441 | 836.441 | 0
5/9/2026 | 11:45:00 AM | 735.358 | 735.358 | 0 | 288.731 | 288.731 | 0 | 0 | 0 | 837.433 | 837.433 | 0
5/9/2026 | 12:00:00 PM | 736.354 | 736.354 | 0 | 289.111 | 289.111 | 0 | 0 | 0 | 838.574 | 838.574 | 0
5/9/2026 | 12:15:00 PM | 737.383 | 737.383 | 0 | 289.482 | 289.482 | 0 | 0 | 0 | 839.751 | 839.751 | 0
5/9/2026 | 12:30:00 PM | 738.295 | 738.295 | 0 | 289.855 | 289.855 | 0 | 0 | 0 | 840.807 | 840.807 | 0
5/9/2026 | 12:45:00 PM | 739.167 | 739.167 | 0 | 290.229 | 290.229 | 0 | 0 | 0 | 841.822 | 841.822 | 0
5/9/2026 | 1:00:00 PM | 740.149 | 740.149 | 0 | 290.605 | 290.605 | 0 | 0 | 0 | 842.95 | 842.95 | 0
5/9/2026 | 1:15:00 PM | 741.105 | 741.105 | 0 | 290.985 | 290.985 | 0 | 0 | 0 | 844.05 | 844.05 | 0
5/9/2026 | 1:30:00 PM | 741.872 | 741.872 | 0 | 291.366 | 291.366 | 0 | 0 | 0 | 844.976 | 844.976 | 0
5/9/2026 | 1:45:00 PM | 742.738 | 742.738 | 0 | 291.747 | 291.747 | 0 | 0 | 0 | 845.988 | 845.988 | 0
5/9/2026 | 2:00:00 PM | 743.618 | 743.618 | 0 | 292.127 | 292.127 | 0 | 0 | 0 | 847.013 | 847.013 | 0
5/9/2026 | 2:15:00 PM | 744.609 | 744.609 | 0 | 292.514 | 292.514 | 0 | 0 | 0 | 848.151 | 848.151 | 0
5/9/2026 | 2:30:00 PM | 745.583 | 745.583 | 0 | 292.891 | 292.891 | 0 | 0 | 0 | 849.27 | 849.27 | 0
5/9/2026 | 2:45:00 PM | 746.515 | 746.515 | 0 | 293.266 | 293.266 | 0 | 0 | 0 | 850.345 | 850.345 | 0
5/9/2026 | 3:00:00 PM | 747.321 | 747.321 | 0 | 293.643 | 293.643 | 0 | 0 | 0 | 851.305 | 851.305 | 0
5/9/2026 | 3:15:00 PM | 748.173 | 748.173 | 0 | 294.019 | 294.019 | 0 | 0 | 0 | 852.301 | 852.301 | 0
5/9/2026 | 3:30:00 PM | 749.039 | 749.039 | 0 | 294.393 | 294.393 | 0 | 0 | 0 | 853.309 | 853.309 | 0
5/9/2026 | 3:45:00 PM | 750.02 | 750.02 | 0 | 294.765 | 294.765 | 0 | 0 | 0 | 854.434 | 854.434 | 0
5/9/2026 | 4:00:00 PM | 750.973 | 750.973 | 0 | 295.145 | 295.145 | 0 | 0 | 0 | 855.53 | 855.53 | 0
5/9/2026 | 4:15:00 PM | 751.742 | 751.742 | 0 | 295.52 | 295.52 | 0 | 0 | 0 | 856.453 | 856.453 | 0
5/9/2026 | 4:30:00 PM | 752.611 | 752.611 | 0 | 295.892 | 295.892 | 0 | 0 | 0 | 857.464 | 857.464 | 0
5/9/2026 | 4:45:00 PM | 753.527 | 753.527 | 0 | 296.264 | 296.264 | 0 | 0 | 0 | 858.521 | 858.521 | 0
5/9/2026 | 5:00:00 PM | 754.549 | 754.549 | 0 | 296.632 | 296.632 | 0 | 0 | 0 | 859.688 | 859.688 | 0
5/9/2026 | 5:15:00 PM | 755.499 | 755.499 | 0 | 297.004 | 297.004 | 0 | 0 | 0 | 860.78 | 860.78 | 0
5/9/2026 | 5:30:00 PM | 756.29 | 756.29 | 0 | 297.378 | 297.378 | 0 | 0 | 0 | 861.724 | 861.724 | 0
5/9/2026 | 5:45:00 PM | 757.109 | 757.109 | 0 | 297.761 | 297.761 | 0 | 0 | 0 | 862.697 | 862.697 | 0
5/9/2026 | 6:00:00 PM | 757.93 | 757.93 | 0 | 298.136 | 298.136 | 0 | 0 | 0 | 863.669 | 863.669 | 0
5/9/2026 | 6:15:00 PM | 758.729 | 758.729 | 0 | 298.513 | 298.513 | 0 | 0 | 0 | 864.62 | 864.62 | 0
5/9/2026 | 6:30:00 PM | 759.693 | 759.693 | 0 | 298.889 | 298.889 | 0 | 0 | 0 | 865.727 | 865.727 | 0
5/9/2026 | 6:45:00 PM | 760.593 | 760.593 | 0 | 299.265 | 299.265 | 0 | 0 | 0 | 866.771 | 866.771 | 0
5/9/2026 | 7:00:00 PM | 761.369 | 761.369 | 0 | 299.645 | 299.645 | 0 | 0 | 0 | 867.703 | 867.703 | 0
5/9/2026 | 7:15:00 PM | 762.186 | 762.186 | 0 | 300.022 | 300.022 | 0 | 0 | 0 | 868.674 | 868.674 | 0
5/9/2026 | 7:30:00 PM | 763.076 | 763.076 | 0 | 300.388 | 300.388 | 0 | 0 | 0 | 869.693 | 869.693 | 0
5/9/2026 | 7:45:00 PM | 764 | 764 | 0 | 300.736 | 300.736 | 0 | 0 | 0 | 870.725 | 870.725 | 0
5/9/2026 | 8:00:00 PM | 765.074 | 765.074 | 0 | 301.077 | 301.077 | 0 | 0 | 0 | 871.915 | 871.915 | 0
5/9/2026 | 8:15:00 PM | 766.103 | 766.103 | 0 | 301.422 | 301.422 | 0 | 0 | 0 | 873.058 | 873.058 | 0
5/9/2026 | 8:30:00 PM | 766.977 | 766.977 | 0 | 301.771 | 301.771 | 0 | 0 | 0 | 874.039 | 874.039 | 0
5/9/2026 | 8:45:00 PM | 768.044 | 768.044 | 0 | 302.117 | 302.117 | 0 | 0 | 0 | 875.223 | 875.223 | 0
5/9/2026 | 9:00:00 PM | 768.913 | 768.913 | 0 | 302.465 | 302.465 | 0 | 0 | 0 | 876.197 | 876.197 | 0
5/9/2026 | 9:15:00 PM | 769.832 | 769.832 | 0 | 302.815 | 302.815 | 0 | 0 | 0 | 877.226 | 877.226 | 0
5/9/2026 | 9:30:00 PM | 770.843 | 770.843 | 0 | 303.171 | 303.171 | 0 | 0 | 0 | 878.352 | 878.352 | 0
5/9/2026 | 9:45:00 PM | 771.946 | 771.946 | 0 | 303.522 | 303.522 | 0 | 0 | 0 | 879.575 | 879.575 | 0
5/9/2026 | 10:00:00 PM | 772.941 | 772.941 | 0 | 303.877 | 303.877 | 0 | 0 | 0 | 880.686 | 880.686 | 0
5/9/2026 | 10:15:00 PM | 773.861 | 773.861 | 0 | 304.231 | 304.231 | 0 | 0 | 0 | 881.714 | 881.714 | 0
5/9/2026 | 10:30:00 PM | 774.818 | 774.818 | 0 | 304.587 | 304.587 | 0 | 0 | 0 | 882.782 | 882.782 | 0
5/9/2026 | 10:45:00 PM | 775.816 | 775.816 | 0 | 304.942 | 304.942 | 0 | 0 | 0 | 883.892 | 883.892 | 0
5/9/2026 | 11:00:00 PM | 776.961 | 776.961 | 0 | 305.297 | 305.297 | 0 | 0 | 0 | 885.165 | 885.165 | 0
5/9/2026 | 11:15:00 PM | 778.025 | 778.025 | 0 | 305.658 | 305.658 | 0 | 0 | 0 | 886.35 | 886.35 | 0
5/9/2026 | 11:30:00 PM | 779.072 | 779.072 | 0 | 306.028 | 306.028 | 0 | 0 | 0 | 887.516 | 887.516 | 0
5/9/2026 | 11:45:00 PM | 780.136 | 780.136 | 0 | 306.392 | 306.392 | 0 | 0 | 0 | 888.701 | 888.701 | 0
5/10/2026 | 12:00:00 AM | 781.074 | 781.074 | 0 | 306.76 | 306.76 | 0 | 0 | 0 | 889.757 | 889.757 | 0
5/10/2026 | 12:15:00 AM | 782.911 | 782.911 | 0 | 308.46 | 308.46 | 0 | 0 | 0 | 892.362 | 892.362 | 0
5/10/2026 | 12:30:00 AM | 783.906 | 783.906 | 0 | 308.896 | 308.896 | 0 | 0 | 0 | 893.504 | 893.504 | 0
5/10/2026 | 12:45:00 AM | 784.941 | 784.941 | 0 | 309.272 | 309.272 | 0 | 0 | 0 | 894.662 | 894.662 | 0
5/10/2026 | 1:00:00 AM | 786.049 | 786.049 | 0 | 309.646 | 309.646 | 0 | 0 | 0 | 895.9 | 895.9 | 0
5/10/2026 | 1:15:00 AM | 787.044 | 787.044 | 0 | 310.021 | 310.021 | 0 | 0 | 0 | 897.014 | 897.014 | 0
5/10/2026 | 1:30:00 AM | 788.103 | 788.103 | 0 | 310.396 | 310.396 | 0 | 0 | 0 | 898.198 | 898.198 | 0
5/10/2026 | 1:45:00 AM | 789.202 | 789.202 | 0 | 310.773 | 310.773 | 0 | 0 | 0 | 899.426 | 899.426 | 0
5/10/2026 | 2:00:00 AM | 790.289 | 790.289 | 0 | 311.16 | 311.16 | 0 | 0 | 0 | 900.641 | 900.641 | 0
5/10/2026 | 2:15:00 AM | 791.232 | 791.232 | 0 | 311.539 | 311.539 | 0 | 0 | 0 | 901.707 | 901.707 | 0
5/10/2026 | 2:30:00 AM | 792.177 | 792.177 | 0 | 311.916 | 311.916 | 0 | 0 | 0 | 902.771 | 902.771 | 0
5/10/2026 | 2:45:00 AM | 793.156 | 793.156 | 0 | 312.296 | 312.296 | 0 | 0 | 0 | 903.872 | 903.872 | 0
5/10/2026 | 3:00:00 AM | 794.294 | 794.294 | 0 | 312.676 | 312.676 | 0 | 0 | 0 | 905.145 | 905.145 | 0
5/10/2026 | 3:15:00 AM | 795.382 | 795.382 | 0 | 313.056 | 313.056 | 0 | 0 | 0 | 906.362 | 906.362 | 0
5/10/2026 | 3:30:00 AM | 796.414 | 796.414 | 0 | 313.435 | 313.435 | 0 | 0 | 0 | 907.519 | 907.519 | 0
5/10/2026 | 3:45:00 AM | 797.405 | 797.405 | 0 | 313.815 | 313.815 | 0 | 0 | 0 | 908.632 | 908.632 | 0
5/10/2026 | 4:00:00 AM | 798.494 | 798.494 | 0 | 314.196 | 314.196 | 0 | 0 | 0 | 909.851 | 909.851 | 0
5/10/2026 | 4:15:00 AM | 799.563 | 799.563 | 0 | 314.578 | 314.578 | 0 | 0 | 0 | 911.048 | 911.048 | 0
5/10/2026 | 4:30:00 AM | 800.639 | 800.639 | 0 | 314.967 | 314.967 | 0 | 0 | 0 | 912.252 | 912.252 | 0
5/10/2026 | 4:45:00 AM | 801.712 | 801.712 | 0 | 315.348 | 315.348 | 0 | 0 | 0 | 913.454 | 913.454 | 0
5/10/2026 | 5:00:00 AM | 802.779 | 802.779 | 0 | 315.724 | 315.724 | 0 | 0 | 0 | 914.647 | 914.647 | 0
5/10/2026 | 5:15:00 AM | 803.847 | 803.847 | 0 | 316.107 | 316.107 | 0 | 0 | 0 | 915.843 | 915.843 | 0
5/10/2026 | 5:30:00 AM | 804.791 | 804.791 | 0 | 316.49 | 316.49 | 0 | 0 | 0 | 916.913 | 916.913 | 0
5/10/2026 | 5:45:00 AM | 805.708 | 805.708 | 0 | 316.874 | 316.874 | 0 | 0 | 0 | 917.95 | 917.95 | 0
5/10/2026 | 6:00:00 AM | 806.637 | 806.637 | 0 | 317.258 | 317.258 | 0 | 0 | 0 | 919 | 919 | 0
5/10/2026 | 6:15:00 AM | 807.603 | 807.603 | 0 | 317.642 | 317.642 | 0 | 0 | 0 | 920.087 | 920.087 | 0
5/10/2026 | 6:30:00 AM | 808.709 | 808.709 | 0 | 318.02 | 318.02 | 0 | 0 | 0 | 921.324 | 921.324 | 0
5/10/2026 | 6:45:00 AM | 809.773 | 809.773 | 0 | 318.401 | 318.401 | 0 | 0 | 0 | 922.514 | 922.514 | 0
5/10/2026 | 7:00:00 AM | 810.796 | 810.796 | 0 | 318.792 | 318.792 | 0 | 0 | 0 | 923.666 | 923.666 | 0
5/10/2026 | 7:15:00 AM | 811.698 | 811.698 | 0 | 319.176 | 319.176 | 0 | 0 | 0 | 924.689 | 924.689 | 0
5/10/2026 | 7:30:00 AM | 812.641 | 812.641 | 0 | 319.558 | 319.558 | 0 | 0 | 0 | 925.752 | 925.752 | 0
5/10/2026 | 7:45:00 AM | 813.59 | 813.59 | 0 | 319.937 | 319.937 | 0 | 0 | 0 | 926.819 | 926.819 | 0
5/10/2026 | 8:00:00 AM | 814.635 | 814.635 | 0 | 320.313 | 320.313 | 0 | 0 | 0 | 927.989 | 927.989 | 0
5/10/2026 | 8:15:00 AM | 815.684 | 815.684 | 0 | 320.702 | 320.702 | 0 | 0 | 0 | 929.182 | 929.182 | 0
5/10/2026 | 8:30:00 AM | 816.64 | 816.64 | 0 | 321.105 | 321.105 | 0 | 0 | 0 | 930.292 | 930.292 | 0
5/10/2026 | 8:45:00 AM | 817.484 | 817.484 | 0 | 321.509 | 321.509 | 0 | 0 | 0 | 931.302 | 931.302 | 0
5/10/2026 | 9:00:00 AM | 818.322 | 818.322 | 0 | 321.909 | 321.909 | 0 | 0 | 0 | 932.298 | 932.298 | 0
5/10/2026 | 9:15:00 AM | 819.188 | 819.188 | 0 | 322.306 | 322.306 | 0 | 0 | 0 | 933.317 | 933.317 | 0
5/10/2026 | 9:30:00 AM | 820.157 | 820.157 | 0 | 322.705 | 322.705 | 0 | 0 | 0 | 934.436 | 934.436 | 0
5/10/2026 | 9:45:00 AM | 821.167 | 821.167 | 0 | 323.09 | 323.09 | 0 | 0 | 0 | 935.596 | 935.596 | 0
5/10/2026 | 10:00:00 AM | 822.133 | 822.133 | 0 | 323.47 | 323.47 | 0 | 0 | 0 | 936.708 | 936.708 | 0
5/10/2026 | 10:15:00 AM | 823.033 | 823.033 | 0 | 323.847 | 323.847 | 0 | 0 | 0 | 937.751 | 937.751 | 0
5/10/2026 | 10:30:00 AM | 823.942 | 823.942 | 0 | 324.22 | 324.22 | 0 | 0 | 0 | 938.803 | 938.803 | 0
5/10/2026 | 10:45:00 AM | 824.95 | 824.95 | 0 | 324.59 | 324.59 | 0 | 0 | 0 | 939.956 | 939.956 | 0
5/10/2026 | 11:00:00 AM | 825.832 | 825.832 | 0 | 324.958 | 324.958 | 0 | 0 | 0 | 940.987 | 940.987 | 0
5/10/2026 | 11:15:00 AM | 826.658 | 826.658 | 0 | 325.324 | 325.324 | 0 | 0 | 0 | 941.954 | 941.954 | 0
5/10/2026 | 11:30:00 AM | 827.518 | 827.518 | 0 | 325.697 | 325.697 | 0 | 0 | 0 | 942.954 | 942.954 | 0
5/10/2026 | 11:45:00 AM | 828.457 | 828.457 | 0 | 326.056 | 326.056 | 0 | 0 | 0 | 944.031 | 944.031 | 0
5/10/2026 | 12:00:00 PM | 829.517 | 829.517 | 0 | 326.425 | 326.425 | 0 | 0 | 0 | 945.241 | 945.241 | 0
5/10/2026 | 12:15:00 PM | 830.533 | 830.533 | 0 | 326.801 | 326.801 | 0 | 0 | 0 | 946.405 | 946.405 | 0
5/10/2026 | 12:30:00 PM | 831.43 | 831.43 | 0 | 327.178 | 327.178 | 0 | 0 | 0 | 947.444 | 947.444 | 0
5/10/2026 | 12:45:00 PM | 832.438 | 832.438 | 0 | 327.551 | 327.551 | 0 | 0 | 0 | 948.6 | 948.6 | 0
5/10/2026 | 1:00:00 PM | 833.457 | 833.457 | 0 | 327.935 | 327.935 | 0 | 0 | 0 | 949.765 | 949.765 | 0
5/10/2026 | 1:15:00 PM | 834.26 | 834.26 | 0 | 328.313 | 328.313 | 0 | 0 | 0 | 950.721 | 950.721 | 0
5/10/2026 | 1:30:00 PM | 835.091 | 835.091 | 0 | 328.69 | 328.69 | 0 | 0 | 0 | 951.702 | 951.702 | 0
5/10/2026 | 1:45:00 PM | 835.96 | 835.96 | 0 | 329.064 | 329.064 | 0 | 0 | 0 | 952.714 | 952.714 | 0
5/10/2026 | 2:00:00 PM | 836.912 | 836.912 | 0 | 329.434 | 329.434 | 0 | 0 | 0 | 953.806 | 953.806 | 0
5/10/2026 | 2:15:00 PM | 837.714 | 837.714 | 0 | 329.806 | 329.806 | 0 | 0 | 0 | 954.758 | 954.758 | 0
5/10/2026 | 2:30:00 PM | 838.518 | 838.518 | 0 | 330.185 | 330.185 | 0 | 0 | 0 | 955.716 | 955.716 | 0
5/10/2026 | 2:45:00 PM | 839.383 | 839.383 | 0 | 330.555 | 330.555 | 0 | 0 | 0 | 956.722 | 956.722 | 0
5/10/2026 | 3:00:00 PM | 840.34 | 840.34 | 0 | 330.926 | 330.926 | 0 | 0 | 0 | 957.819 | 957.819 | 0
5/10/2026 | 3:15:00 PM | 841.157 | 841.157 | 0 | 331.294 | 331.294 | 0 | 0 | 0 | 958.784 | 958.784 | 0
5/10/2026 | 3:30:00 PM | 841.988 | 841.988 | 0 | 331.664 | 331.664 | 0 | 0 | 0 | 959.763 | 959.763 | 0
5/10/2026 | 3:45:00 PM | 842.855 | 842.855 | 0 | 332.026 | 332.026 | 0 | 0 | 0 | 960.769 | 960.769 | 0
5/10/2026 | 4:00:00 PM | 843.799 | 843.799 | 0 | 332.39 | 332.39 | 0 | 0 | 0 | 961.852 | 961.852 | 0
5/10/2026 | 4:15:00 PM | 844.683 | 844.683 | 0 | 332.755 | 332.755 | 0 | 0 | 0 | 962.874 | 962.874 | 0
5/10/2026 | 4:30:00 PM | 845.698 | 845.698 | 0 | 333.117 | 333.117 | 0 | 0 | 0 | 964.032 | 964.032 | 0
5/10/2026 | 4:45:00 PM | 846.727 | 846.727 | 0 | 333.482 | 333.482 | 0 | 0 | 0 | 965.203 | 965.203 | 0
5/10/2026 | 5:00:00 PM | 847.712 | 847.712 | 0 | 333.842 | 333.842 | 0 | 0 | 0 | 966.328 | 966.328 | 0
5/10/2026 | 5:15:00 PM | 848.61 | 848.61 | 0 | 334.206 | 334.206 | 0 | 0 | 0 | 967.365 | 967.365 | 0
5/10/2026 | 5:30:00 PM | 849.526 | 849.526 | 0 | 334.568 | 334.568 | 0 | 0 | 0 | 968.419 | 968.419 | 0
5/10/2026 | 5:45:00 PM | 850.523 | 850.523 | 0 | 334.934 | 334.934 | 0 | 0 | 0 | 969.555 | 969.555 | 0
5/10/2026 | 6:00:00 PM | 851.492 | 851.492 | 0 | 335.296 | 335.296 | 0 | 0 | 0 | 970.664 | 970.664 | 0
5/10/2026 | 6:15:00 PM | 852.484 | 852.484 | 0 | 335.66 | 335.66 | 0 | 0 | 0 | 971.796 | 971.796 | 0
5/10/2026 | 6:30:00 PM | 853.455 | 853.455 | 0 | 336.025 | 336.025 | 0 | 0 | 0 | 972.908 | 972.908 | 0
5/10/2026 | 6:45:00 PM | 854.433 | 854.433 | 0 | 336.397 | 336.397 | 0 | 0 | 0 | 974.027 | 974.027 | 0
5/10/2026 | 7:00:00 PM | 855.297 | 855.297 | 0 | 336.77 | 336.77 | 0 | 0 | 0 | 975.043 | 975.043 | 0
5/10/2026 | 7:15:00 PM | 856.139 | 856.139 | 0 | 337.147 | 337.147 | 0 | 0 | 0 | 976.033 | 976.033 | 0
5/10/2026 | 7:30:00 PM | 857.002 | 857.002 | 0 | 337.524 | 337.524 | 0 | 0 | 0 | 977.041 | 977.041 | 0
5/10/2026 | 7:45:00 PM | 857.997 | 857.997 | 0 | 337.905 | 337.905 | 0 | 0 | 0 | 978.184 | 978.184 | 0
5/10/2026 | 8:00:00 PM | 859.142 | 859.142 | 0 | 338.263 | 338.263 | 0 | 0 | 0 | 979.46 | 979.46 | 0
5/10/2026 | 8:15:00 PM | 860.234 | 860.234 | 0 | 338.615 | 338.615 | 0 | 0 | 0 | 980.673 | 980.673 | 0
5/10/2026 | 8:30:00 PM | 861.193 | 861.193 | 0 | 338.971 | 338.971 | 0 | 0 | 0 | 981.744 | 981.744 | 0
5/10/2026 | 8:45:00 PM | 862.225 | 862.225 | 0 | 339.327 | 339.327 | 0 | 0 | 0 | 982.893 | 982.893 | 0
5/10/2026 | 9:00:00 PM | 863.305 | 863.305 | 0 | 339.688 | 339.688 | 0 | 0 | 0 | 984.095 | 984.095 | 0
5/10/2026 | 9:15:00 PM | 864.319 | 864.319 | 0 | 340.048 | 340.048 | 0 | 0 | 0 | 985.228 | 985.228 | 0
5/10/2026 | 9:30:00 PM | 865.222 | 865.222 | 0 | 340.412 | 340.412 | 0 | 0 | 0 | 986.245 | 986.245 | 0
5/10/2026 | 9:45:00 PM | 866.208 | 866.208 | 0 | 340.776 | 340.776 | 0 | 0 | 0 | 987.348 | 987.348 | 0
5/10/2026 | 10:00:00 PM | 867.319 | 867.319 | 0 | 341.142 | 341.142 | 0 | 0 | 0 | 988.587 | 988.587 | 0
5/10/2026 | 10:15:00 PM | 868.388 | 868.388 | 0 | 341.503 | 341.503 | 0 | 0 | 0 | 989.777 | 989.777 | 0
5/10/2026 | 10:30:00 PM | 869.453 | 869.453 | 0 | 341.868 | 341.868 | 0 | 0 | 0 | 990.963 | 990.963 | 0
5/10/2026 | 10:45:00 PM | 870.515 | 870.515 | 0 | 342.232 | 342.232 | 0 | 0 | 0 | 992.147 | 992.147 | 0
5/10/2026 | 11:00:00 PM | 871.576 | 871.576 | 0 | 342.599 | 342.599 | 0 | 0 | 0 | 993.332 | 993.332 | 0
5/10/2026 | 11:15:00 PM | 872.637 | 872.637 | 0 | 342.966 | 342.966 | 0 | 0 | 0 | 994.516 | 994.516 | 0
5/10/2026 | 11:30:00 PM | 873.553 | 873.553 | 0 | 343.34 | 343.34 | 0 | 0 | 0 | 995.552 | 995.552 | 0
5/10/2026 | 11:45:00 PM | 874.493 | 874.493 | 0 | 343.716 | 343.716 | 0 | 0 | 0 | 996.611 | 996.611 | 0
5/11/2026 | 12:00:00 AM | 875.451 | 875.451 | 0 | 344.095 | 344.095 | 0 | 0 | 0 | 997.688 | 997.688 | 0
5/11/2026 | 12:15:00 AM | 876.497 | 876.497 | 0 | 344.455 | 344.455 | 0 | 0 | 0 | 998.855 | 998.855 | 0
5/11/2026 | 12:30:00 AM | 877.603 | 877.603 | 0 | 344.818 | 344.818 | 0 | 0 | 0 | 1000.086 | 1000.086 | 0
5/11/2026 | 12:45:00 AM | 878.653 | 878.653 | 0 | 345.184 | 345.184 | 0 | 0 | 0 | 1001.258 | 1001.258 | 0
5/11/2026 | 1:00:00 AM | 879.535 | 879.535 | 0 | 345.553 | 345.553 | 0 | 0 | 0 | 1002.257 | 1002.257 | 0
5/11/2026 | 1:15:00 AM | 880.495 | 880.495 | 0 | 345.92 | 345.92 | 0 | 0 | 0 | 1003.333 | 1003.333 | 0
5/11/2026 | 1:30:00 AM | 881.474 | 881.474 | 0 | 346.289 | 346.289 | 0 | 0 | 0 | 1004.43 | 1004.43 | 0
5/11/2026 | 1:45:00 AM | 882.601 | 882.601 | 0 | 346.657 | 346.657 | 0 | 0 | 0 | 1005.687 | 1005.687 | 0
5/11/2026 | 2:00:00 AM | 883.726 | 883.726 | 0 | 347.034 | 347.034 | 0 | 0 | 0 | 1006.943 | 1006.943 | 0
5/11/2026 | 2:15:00 AM | 884.797 | 884.797 | 0 | 347.404 | 347.404 | 0 | 0 | 0 | 1008.138 | 1008.138 | 0
5/11/2026 | 2:30:00 AM | 885.785 | 885.785 | 0 | 347.777 | 347.777 | 0 | 0 | 0 | 1009.246 | 1009.246 | 0
5/11/2026 | 2:45:00 AM | 886.843 | 886.843 | 0 | 348.149 | 348.149 | 0 | 0 | 0 | 1010.429 | 1010.429 | 0
5/11/2026 | 3:00:00 AM | 887.849 | 887.849 | 0 | 348.521 | 348.521 | 0 | 0 | 0 | 1011.56 | 1011.56 | 0
5/11/2026 | 3:15:00 AM | 888.769 | 888.769 | 0 | 348.897 | 348.897 | 0 | 0 | 0 | 1012.599 | 1012.599 | 0
5/11/2026 | 3:30:00 AM | 889.723 | 889.723 | 0 | 349.271 | 349.271 | 0 | 0 | 0 | 1013.672 | 1013.672 | 0
5/11/2026 | 3:45:00 AM | 890.713 | 890.713 | 0 | 349.644 | 349.644 | 0 | 0 | 0 | 1014.781 | 1014.781 | 0
5/11/2026 | 4:00:00 AM | 891.828 | 891.828 | 0 | 350.015 | 350.015 | 0 | 0 | 0 | 1016.026 | 1016.026 | 0
5/11/2026 | 4:15:00 AM | 892.9 | 892.9 | 0 | 350.39 | 350.39 | 0 | 0 | 0 | 1017.223 | 1017.223 | 0
5/11/2026 | 4:30:00 AM | 893.96 | 893.96 | 0 | 350.764 | 350.764 | 0 | 0 | 0 | 1018.406 | 1018.406 | 0
5/11/2026 | 4:45:00 AM | 894.893 | 894.893 | 0 | 351.135 | 351.135 | 0 | 0 | 0 | 1019.46 | 1019.46 | 0
5/11/2026 | 5:00:00 AM | 895.831 | 895.831 | 0 | 351.505 | 351.505 | 0 | 0 | 0 | 1020.515 | 1020.515 | 0
5/11/2026 | 5:15:00 AM | 896.765 | 896.765 | 0 | 351.869 | 351.869 | 0 | 0 | 0 | 1021.563 | 1021.563 | 0
5/11/2026 | 5:30:00 AM | 897.798 | 897.798 | 0 | 352.229 | 352.229 | 0 | 0 | 0 | 1022.715 | 1022.715 | 0
5/11/2026 | 5:45:00 AM | 898.894 | 898.894 | 0 | 352.585 | 352.585 | 0 | 0 | 0 | 1023.934 | 1023.934 | 0
5/11/2026 | 6:00:00 AM | 899.901 | 899.901 | 0 | 352.941 | 352.941 | 0 | 0 | 0 | 1025.059 | 1025.059 | 0
5/11/2026 | 6:15:00 AM | 900.78 | 900.78 | 0 | 353.296 | 353.296 | 0 | 0 | 0 | 1026.047 | 1026.047 | 0