## Configuration
Configuration
PEL Transfer, Version 2.8.15973
Recording status
Session name | EQHB
Report start | 5/1/2026 12:15:00 PM
Report end | 5/11/2026 6:30:00 AM
Report duration | 9 days, 18:15:00 (h:min:s)
Recording start | 5/1/2026 12:10:03 PM
Recording end | 5/11/2026 6:25:03 AM
Recording duration | 9 days, 18:15:00 (h:min:s)
1 s trend | No
200 ms trend | No
1 s harmonics | No
Aggregated harmonics | No
Instrument ID
PEL model | PEL113
PEL serial number | 107349AAH
PEL name | PEL113-107349AAH
PEL location | St Josephs
Firmware DSP version | 1.96
Firmware microprocessor version | 1.14
Hardware version
Measurement configuration and status
Aggregation period | 15 min
Electrical hook-up | 3-phase 4-wire Y
Nominal frequency | Auto
Primary nominal voltage | - - -
Secondary nominal voltage | - - -
Current sensor I1 | MA193/MA194/A193/A196
Current sensor I2 | MA193/MA194/A193/A196
Current sensor I3 | MA193/MA194/A193/A196
Line flexible sensor range | 400 A
Line flexible sensor wraps | 1

## Event Log
Event Log
Date | Time | Event
5/1/2026 | 12:10:03 PM | Start of recording

## Total Energies and Costs
Total Energies and Costs
Name | Value | Cost | Cost per kWh, kvarh or kVAh
Ep+ Total (Wh) | 12.464 MWh
Ep- Total (Wh) | 0 kWh
Ep Total (Wh) | 12.464 MWh
Eq/q1 Total (varh) | 7.429 Mvarh
Eq/q2 Total (varh) | 0 kvarh
Eq/q3 Total (varh) | 0 kvarh
Eq/q4 Total (varh) | 0 kvarh
Eq Total (varh) | 7.429 Mvarh
Es+ Total (VAh) | 14.907 MVAh
Es- Total (VAh) | 0 kVAh
Es Total (VAh) | 14.907 MVAh
Positive-sequence active energy Ep⁺ | 7.01 kWh
Unbalance active energy Epu | 12.474 MWh
Harmonic active energy EpH | -17.337 kWh
Reactive energy Net/Total Eq | 7.429 Mvarh
Distortion energy Net/Total Ed | 3.303 Mvarh
MAX 15 min Summary I1 | 88.1483 A |  |  | 5/6/2026 | 1:45:00 PM
MAX 15 min Summary I2 | 83.1784 A |  |  | 5/6/2026 | 1:45:00 PM
MAX 15 min Summary I3 | 79.5184 A |  |  | 5/7/2026 | 10:00:00 AM
MAX 15 min Summary IN | 1.0706 A |  |  | 5/6/2026 | 10:45:00 AM
MAX 15 min Summary PFT+ | 0.851 |  |  | 5/6/2026 | 1:45:00 PM
MAX 15 min Summary PFT- |  |  |  | - - - | - - -
MAX 15 min Summary PT | 58.763 kW |  |  | 5/6/2026 | 1:45:00 PM
MAX 15 min Summary QT | 35.225 kvar |  |  | 5/3/2026 | 8:15:00 AM
MAX 15 min Summary ST | 69.331 kVA |  |  | 5/7/2026 | 10:00:00 AM

## Summary
Summary
Date | Time | V1 (15 min) | V2 (15 min) | V3 (15 min) | U12 (15 min) | U23 (15 min) | U31 (15 min) | I1 (15 min) | I2 (15 min) | I3 (15 min) | IN (15 min) | V1ᴄꜰ (15 min) | V2ᴄꜰ (15 min) | V3ᴄꜰ (15 min) | I1ᴄꜰ (15 min) | I2ᴄꜰ (15 min) | I3ᴄꜰ (15 min) | u₂ (15 min) | F (Hz) (15 min) | P1 (15 min) | P2 (15 min) | P3 (15 min) | PT (15 min) | P1- (15 min) | P2- (15 min) | P3- (15 min) | PT- (15 min) | P1+ (15 min) | P2+ (15 min) | P3+ (15 min) | PT+ (15 min) | Q1 (15 min) | Q2 (15 min) | Q3 (15 min) | QT (15 min) | Q1- (15 min) | Q2- (15 min) | Q3- (15 min) | QT- (15 min) | Q1+ (15 min) | Q2+ (15 min) | Q3+ (15 min) | QT+ (15 min) | S1 (15 min) | S2 (15 min) | S3 (15 min) | ST (15 min) | PF1- (15 min) | PF2- (15 min) | PF3- (15 min) | PFT- (15 min) | PF1+ (15 min) | PF2+ (15 min) | PF3+ (15 min) | PFT+ (15 min) | Cos φ1- (15 min) | Cos φ2- (15 min) | Cos φ3- (15 min) | Cos φT- (15 min) | Cos φ1+ (15 min) | Cos φ2+ (15 min) | Cos φ3+ (15 min) | Cos φT+ (15 min) | Tan Φ- (15 min) | Tan Φ+ (15 min) | V1ᴛʜᴅ (15 min) | V2ᴛʜᴅ (15 min) | V3ᴛʜᴅ (15 min) | U12ᴛʜᴅ (15 min) | U23ᴛʜᴅ (15 min) | U31ᴛʜᴅ (15 min) | I1ᴛʜᴅ (15 min) | I2ᴛʜᴅ (15 min) | I3ᴛʜᴅ (15 min) | INᴛʜᴅ (15 min) | S1- (15 min) | S2- (15 min) | S3- (15 min) | ST- (15 min) | S1+ (15 min) | S2+ (15 min) | S3+ (15 min) | ST+ (15 min) | i₂ (15 min) | N1 (15 min) | N2 (15 min) | N3 (15 min) | NT (15 min) | D1 (15 min) | D2 (15 min) | D3 (15 min) | DT (15 min) | Pᵳ1 (15 min) | Pᵳ2 (15 min) | Pᵳ3 (15 min) | PᵳT (15 min) | Pᵳ1+ (15 min) | Pᵳ2+ (15 min) | Pᵳ3+ (15 min) | PᵳT+ (15 min) | Pᵳ1- (15 min) | Pᵳ2- (15 min) | Pᵳ3- (15 min) | PᵳT- (15 min)
|  | V | V | V | V | V | V | A | A | A | A | [6 empty] | % | Hz | W | W | W | W | W | W | W | W | W | W | W | W | var | var | var | var | var | var | var | var | var | var | var | var | VA | VA | VA | VA | [18 empty] | % | % | % | % | % | % | % | % | % | % | VA | VA | VA | VA | VA | VA | VA | VA | % | var | var | var | var | var | var | var | var | W | W | W | W | W | W | W | W | W | W | W | W
5/1/2026 | 12:30:00 PM | 282.29 | 279.41 | 278.09 | 487.84 | 481.04 | 485.67 | 80.1953 | 74.5384 | 72.0153 | 0.2547 | 1.427 | 1.428 | 1.424 | 1.867 | 1.878 | 1.966 | Over-range | 60.01 | 18773 | 18022 | 16244 | 53039 | - - - | - - - | - - - | - - - | 18773 | 18022 | 16244 | 53039 | 11585 | 9296 | 10710 | 31591 | - - - | - - - | - - - | - - - | 11585 | 9296 | 10710 | 31591 | 22537 | 20720 | 19925 | 63182 | # # # | # # # | # # # | # # # | 0.833 | 0.87 | 0.815 | 0.84 | # # # | # # # | # # # | - - - | 0.85 | 0.888 | 0.834 | 0.858 | - - - | 0.596 | 1.75 | 1.71 | 1.68 | 1.56 | 1.65 | 1.68 | 19.12 | 19.5 | 20.98 | 0 | - - - | - - - | - - - | - - - | 22537 | 20720 | 19925 | 63182 | Over-range | 12462 | 10210 | 11529 | 34307 | 4510 | 4145 | 4186 | 13143 | 18753 | 18076 | 16282 | 53111 | 18753 | 18076 | 16282 | 53111 | - - - | - - - | - - - | - - -
5/1/2026 | 12:45:00 PM | 282.04 | 279.11 | 277.84 | 487.38 | 480.47 | 485.32 | 82.211 | 76.4839 | 73.6465 | 0.2628 | 1.427 | 1.428 | 1.425 | 1.915 | 1.927 | 1.995 | Over-range | 60 | 19172 | 18410 | 16557 | 54139 | - - - | - - - | - - - | - - - | 19172 | 18410 | 16557 | 54139 | 11669 | 9246 | 10702 | 31617 | - - - | - - - | - - - | - - - | 11669 | 9246 | 10702 | 31617 | 23032 | 21183 | 20318 | 64532 | # # # | # # # | # # # | # # # | 0.832 | 0.869 | 0.815 | 0.839 | # # # | # # # | # # # | - - - | 0.853 | 0.892 | 0.839 | 0.861 | - - - | 0.584 | 1.77 | 1.74 | 1.72 | 1.58 | 1.69 | 1.71 | 21.16 | 22.04 | 23.36 | 0 | - - - | - - - | - - - | - - - | 23032 | 21183 | 20318 | 64532 | Over-range | 12746 | 10451 | 11756 | 35059 | 5017 | 4774 | 4763 | 14852 | 19215 | 18399 | 16616 | 54231 | 19215 | 18399 | 16616 | 54231 | - - - | - - - | - - - | - - -
5/1/2026 | 1:00:00 PM | 282.01 | 279.12 | 277.8 | 487.38 | 480.43 | 485.24 | 82.537 | 77.2655 | 74.2886 | 0.267 | 1.427 | 1.428 | 1.425 | 1.94 | 1.946 | 2.015 | Over-range | 60 | 19312 | 18627 | 16821 | 54761 | - - - | - - - | - - - | - - - | 19312 | 18627 | 16821 | 54761 | 11541 | 9227 | 10565 | 31332 | - - - | - - - | - - - | - - - | 11541 | 9227 | 10565 | 31332 | 23120 | 21398 | 20494 | 65012 | # # # | # # # | # # # | # # # | 0.835 | 0.871 | 0.821 | 0.842 | # # # | # # # | # # # | - - - | 0.858 | 0.895 | 0.847 | 0.867 | - - - | 0.572 | 1.79 | 1.76 | 1.71 | 1.59 | 1.68 | 1.71 | 22.3 | 23.1 | 24.44 | 0 | - - - | - - - | - - - | - - - | 23120 | 21398 | 20494 | 65012 | Over-range | 12705 | 10519 | 11697 | 35014 | 5238 | 4982 | 4951 | 15423 | 19349 | 18616 | 16891 | 54856 | 19349 | 18616 | 16891 | 54856 | - - - | - - - | - - - | - - -
5/1/2026 | 1:15:00 PM | 282.21 | 279.39 | 278.14 | 487.68 | 481.09 | 485.68 | 82.1883 | 76.6037 | 73.5958 | 0.2676 | 1.427 | 1.428 | 1.425 | 1.908 | 1.918 | 1.985 | Over-range | 60.01 | 19175 | 18483 | 16585 | 54244 | - - - | - - - | - - - | - - - | 19175 | 18483 | 16585 | 54244 | 11748 | 9321 | 10740 | 31809 | - - - | - - - | - - - | - - - | 11748 | 9321 | 10740 | 31809 | 23055 | 21257 | 20337 | 64650 | # # # | # # # | # # # | # # # | 0.832 | 0.87 | 0.816 | 0.839 | # # # | # # # | # # # | - - - | 0.852 | 0.891 | 0.838 | 0.861 | - - - | 0.586 | 1.8 | 1.75 | 1.7 | 1.6 | 1.68 | 1.73 | 20.85 | 21.76 | 23.03 | 0 | - - - | - - - | - - - | - - - | 23055 | 21257 | 20337 | 64650 | Over-range | 12792 | 10486 | 11759 | 35143 | 4963 | 4719 | 4696 | 14675 | 19208 | 18494 | 16628 | 54330 | 19208 | 18494 | 16628 | 54330 | - - - | - - - | - - - | - - -
5/1/2026 | 1:30:00 PM | 282.12 | 279.29 | 278.02 | 487.59 | 480.84 | 485.48 | 80.2013 | 74.9478 | 72.2913 | 0.2655 | 1.427 | 1.428 | 1.425 | 1.928 | 1.931 | 2.003 | Over-range | 60 | 18691 | 18001 | 16281 | 52973 | - - - | - - - | - - - | - - - | 18691 | 18001 | 16281 | 52973 | 11407 | 9187 | 10467 | 31061 | - - - | - - - | - - - | - - - | 11407 | 9187 | 10467 | 31061 | 22478 | 20779 | 19964 | 63221 | # # # | # # # | # # # | # # # | 0.832 | 0.866 | 0.816 | 0.838 | # # # | # # # | # # # | - - - | 0.853 | 0.889 | 0.84 | 0.861 | - - - | 0.586 | 1.81 | 1.77 | 1.74 | 1.61 | 1.7 | 1.74 | 21.67 | 22.48 | 23.79 | 0 | - - - | - - - | - - - | - - - | 22478 | 20779 | 19964 | 63221 | Over-range | 12479 | 10364 | 11540 | 34473 | 4966 | 4716 | 4777 | 14704 | 18784 | 17991 | 16290 | 53065 | 18784 | 17991 | 16290 | 53065 | - - - | - - - | - - - | - - -
5/1/2026 | 1:45:00 PM | 282.06 | 279.26 | 278.02 | 487.48 | 480.84 | 485.45 | 83.2661 | 77.7981 | 74.3304 | 0.2709 | 1.427 | 1.428 | 1.425 | 1.915 | 1.92 | 1.991 | Over-range | 60.01 | 19464 | 18836 | 16828 | 55127 | - - - | - - - | - - - | - - - | 19464 | 18836 | 16828 | 55127 | 11797 | 9318 | 10703 | 31819 | - - - | - - - | - - - | - - - | 11797 | 9318 | 10703 | 31819 | 23356 | 21585 | 20540 | 65481 | # # # | # # # | # # # | # # # | 0.833 | 0.873 | 0.819 | 0.842 | # # # | # # # | # # # | - - - | 0.854 | 0.895 | 0.842 | 0.864 | - - - | 0.577 | 1.8 | 1.76 | 1.74 | 1.61 | 1.7 | 1.73 | 21.08 | 21.87 | 23.27 | 0 | - - - | - - - | - - - | - - - | 23356 | 21585 | 20540 | 65481 | Over-range | 12895 | 10521 | 11763 | 35289 | 5123 | 4806 | 4799 | 15031 | 19473 | 18902 | 16841 | 55215 | 19473 | 18902 | 16841 | 55215 | - - - | - - - | - - - | - - -
5/1/2026 | 2:00:00 PM | 282.07 | 279.22 | 277.96 | 487.5 | 480.71 | 485.4 | 79.6357 | 74.3012 | 71.6968 | 0.2661 | 1.427 | 1.428 | 1.425 | 1.942 | 1.948 | 2.022 | Over-range | 60 | 18575 | 17860 | 16138 | 52572 | - - - | - - - | - - - | - - - | 18575 | 17860 | 16138 | 52572 | 11229 | 9033 | 10365 | 30628 | - - - | - - - | - - - | - - - | 11229 | 9033 | 10365 | 30628 | 22335 | 20609 | 19806 | 62750 | # # # | # # # | # # # | # # # | 0.832 | 0.867 | 0.815 | 0.838 | # # # | # # # | # # # | - - - | 0.855 | 0.892 | 0.84 | 0.862 | - - - | 0.583 | 1.81 | 1.79 | 1.73 | 1.62 | 1.71 | 1.74 | 22.46 | 23.2 | 24.68 | 0 | - - - | - - - | - - - | - - - | 22335 | 20609 | 19806 | 62750 | Over-range | 12394 | 10270 | 11469 | 34225 | 5164 | 4812 | 4834 | 15051 | 18577 | 17941 | 16152 | 52670 | 18577 | 17941 | 16152 | 52670 | - - - | - - - | - - - | - - -
5/1/2026 | 2:15:00 PM | 282.35 | 279.59 | 278.3 | 488.03 | 481.41 | 485.89 | 83.1097 | 77.2886 | 74.4364 | 0.2731 | 1.427 | 1.428 | 1.424 | 1.909 | 1.91 | 1.99 | Over-range | 60.01 | 19465 | 18698 | 16817 | 54981 | - - - | - - - | - - - | - - - | 19465 | 18698 | 16817 | 54981 | 11794 | 9402 | 10857 | 32052 | - - - | - - - | - - - | - - - | 11794 | 9402 | 10857 | 32052 | 23319 | 21454 | 20577 | 65351 | # # # | # # # | # # # | # # # | 0.835 | 0.872 | 0.817 | 0.841 | # # # | # # # | # # # | - - - | 0.855 | 0.893 | 0.839 | 0.862 | - - - | 0.583 | 1.84 | 1.8 | 1.72 | 1.63 | 1.71 | 1.75 | 20.62 | 21.38 | 22.71 | 0 | - - - | - - - | - - - | - - - | 23319 | 21454 | 20577 | 65351 | Over-range | 12834 | 10507 | 11847 | 35296 | 4979 | 4613 | 4663 | 14552 | 19487 | 18784 | 16798 | 55068 | 19487 | 18784 | 16798 | 55068 | - - - | - - - | - - - | - - -
5/1/2026 | 2:30:00 PM | 282.15 | 279.35 | 278.08 | 487.67 | 480.94 | 485.58 | 79.8334 | 74.1451 | 71.8872 | 0.2641 | 1.427 | 1.428 | 1.425 | 1.917 | 1.92 | 2.003 | Over-range | 60 | 18632 | 17828 | 16148 | 52607 | - - - | - - - | - - - | - - - | 18632 | 17828 | 16148 | 52607 | 11406 | 9178 | 10614 | 31198 | - - - | - - - | - - - | - - - | 11406 | 9178 | 10614 | 31198 | 22407 | 20587 | 19878 | 62872 | # # # | # # # | # # # | # # # | 0.832 | 0.866 | 0.812 | 0.837 | # # # | # # # | # # # | - - - | 0.852 | 0.888 | 0.835 | 0.858 | - - - | 0.593 | 1.83 | 1.74 | 1.74 | 1.62 | 1.7 | 1.74 | 21.05 | 21.76 | 23.01 | 0 | - - - | - - - | - - - | - - - | 22407 | 20587 | 19878 | 62872 | Over-range | 12439 | 10282 | 11583 | 34400 | 4879 | 4561 | 4557 | 14262 | 18625 | 17867 | 16201 | 52692 | 18625 | 17867 | 16201 | 52692 | - - - | - - - | - - - | - - -
5/1/2026 | 2:45:00 PM | 282.2 | 279.42 | 278.06 | 487.82 | 480.98 | 485.55 | 83.5822 | 78.015 | 74.5696 | 0.271 | 1.426 | 1.428 | 1.424 | 1.907 | 1.898 | 1.989 | Over-range | 60 | 19510 | 18876 | 16851 | 55237 | - - - | - - - | - - - | - - - | 19510 | 18876 | 16851 | 55237 | 11951 | 9428 | 10818 | 32197 | - - - | - - - | - - - | - - - | 11951 | 9428 | 10818 | 32197 | 23441 | 21645 | 20595 | 65682 | # # # | # # # | # # # | # # # | 0.832 | 0.872 | 0.818 | 0.841 | # # # | # # # | # # # | - - - | 0.852 | 0.892 | 0.84 | 0.862 | - - - | 0.583 | 1.79 | 1.76 | 1.69 | 1.6 | 1.67 | 1.71 | 20.5 | 21.12 | 22.49 | 0 | - - - | - - - | - - - | - - - | 23441 | 21645 | 20595 | 65682 | Over-range | 12979 | 10571 | 11823 | 35485 | 4971 | 4699 | 4685 | 14673 | 19569 | 18864 | 16889 | 55322 | 19569 | 18864 | 16889 | 55322 | - - - | - - - | - - - | - - -
5/1/2026 | 3:00:00 PM | 282.17 | 279.47 | 278.13 | 487.79 | 481.18 | 485.53 | 80.3026 | 74.9081 | 72.0685 | 0.2661 | 1.426 | 1.428 | 1.424 | 1.887 | 1.887 | 1.975 | Over-range | 60.01 | 18656 | 18010 | 16175 | 52841 | - - - | - - - | - - - | - - - | 18656 | 18010 | 16175 | 52841 | 11737 | 9433 | 10724 | 31893 | - - - | - - - | - - - | - - - | 11737 | 9433 | 10724 | 31893 | 22528 | 20793 | 19916 | 63238 | # # # | # # # | # # # | # # # | 0.828 | 0.866 | 0.812 | 0.836 | # # # | # # # | # # # | - - - | 0.846 | 0.885 | 0.832 | 0.854 | - - - | 0.604 | 1.8 | 1.75 | 1.7 | 1.6 | 1.67 | 1.71 | 19.61 | 20.16 | 21.59 | 0 | - - - | - - - | - - - | - - - | 22528 | 20793 | 19916 | 63238 | Over-range | 12620 | 10380 | 11609 | 34710 | 4547 | 4253 | 4365 | 13454 | 18743 | 18022 | 16154 | 52918 | 18743 | 18022 | 16154 | 52918 | - - - | - - - | - - - | - - -
5/1/2026 | 3:15:00 PM | 282.34 | 279.72 | 278.23 | 488.24 | 481.42 | 485.75 | 81.4738 | 76.0258 | 72.6563 | 0.2666 | 1.427 | 1.428 | 1.425 | 1.88 | 1.876 | 1.966 | Over-range | 60.01 | 18990 | 18396 | 16396 | 53782 | - - - | - - - | - - - | - - - | 18990 | 18396 | 16396 | 53782 | 11816 | 9412 | 10726 | 31954 | - - - | - - - | - - - | - - - | 11816 | 9412 | 10726 | 31954 | 22871 | 21127 | 20093 | 64091 | # # # | # # # | # # # | # # # | 0.83 | 0.871 | 0.816 | 0.839 | # # # | # # # | # # # | - - - | 0.848 | 0.89 | 0.835 | 0.858 | - - - | 0.594 | 1.79 | 1.72 | 1.68 | 1.58 | 1.64 | 1.7 | 19.54 | 19.98 | 21.36 | 0 | - - - | - - - | - - - | - - - | 22871 | 21127 | 20093 | 64091 | Over-range | 12739 | 10377 | 11603 | 34830 | 4667 | 4283 | 4334 | 13600 | 19010 | 18474 | 16376 | 53859 | 19010 | 18474 | 16376 | 53859 | - - - | - - - | - - - | - - -
5/1/2026 | 3:30:00 PM | 282.31 | 279.66 | 278.12 | 488.16 | 481.25 | 485.65 | 79.9676 | 74.7736 | 71.592 | 0.2641 | 1.427 | 1.428 | 1.424 | 1.917 | 1.914 | 2.004 | Over-range | 60.01 | 18617 | 18038 | 16134 | 52789 | - - - | - - - | - - - | - - - | 18617 | 18038 | 16134 | 52789 | 11535 | 9242 | 10487 | 31263 | - - - | - - - | - - - | - - - | 11535 | 9242 | 10487 | 31263 | 22472 | 20798 | 19811 | 63081 | # # # | # # # | # # # | # # # | 0.829 | 0.867 | 0.814 | 0.837 | # # # | # # # | # # # | - - - | 0.849 | 0.89 | 0.837 | 0.859 | - - - | 0.592 | 1.76 | 1.72 | 1.68 | 1.58 | 1.64 | 1.69 | 21.29 | 21.79 | 23.27 | 0 | - - - | - - - | - - - | - - - | 22472 | 20798 | 19811 | 63081 | Over-range | 12579 | 10342 | 11487 | 34508 | 4942 | 4573 | 4620 | 14401 | 18647 | 18111 | 16114 | 52872 | 18647 | 18111 | 16114 | 52872 | - - - | - - - | - - - | - - -
5/1/2026 | 3:45:00 PM | 282.3 | 279.56 | 278.08 | 488.01 | 481.17 | 485.63 | 83.2905 | 78.2613 | 74.5131 | 0.2702 | 1.427 | 1.428 | 1.425 | 1.93 | 1.926 | 2.003 | Over-range | 60.01 | 19420 | 18902 | 16872 | 55194 | - - - | - - - | - - - | - - - | 19420 | 18902 | 16872 | 55194 | 11769 | 9360 | 10608 | 31737 | - - - | - - - | - - - | - - - | 11769 | 9360 | 10608 | 31737 | 23347 | 21702 | 20566 | 65615 | # # # | # # # | # # # | # # # | 0.832 | 0.871 | 0.82 | 0.841 | # # # | # # # | # # # | - - - | 0.854 | 0.895 | 0.845 | 0.865 | - - - | 0.575 | 1.77 | 1.74 | 1.68 | 1.59 | 1.65 | 1.7 | 21.88 | 22.55 | 24.01 | 0 | - - - | - - - | - - - | - - - | 23347 | 21702 | 20566 | 65615 | Over-range | 12943 | 10637 | 11743 | 35426 | 5270 | 4943 | 4933 | 15427 | 19443 | 18975 | 16873 | 55291 | 19443 | 18975 | 16873 | 55291 | - - - | - - - | - - - | - - -
5/1/2026 | 4:00:00 PM | 282.33 | 279.64 | 278.12 | 488.13 | 481.24 | 485.69 | 81.9028 | 76.7006 | 73.607 | 0.2663 | 1.427 | 1.428 | 1.425 | 1.94 | 1.942 | 2.018 | Over-range | 59.99 | 19084 | 18471 | 16596 | 54150 | - - - | - - - | - - - | - - - | 19084 | 18471 | 16596 | 54150 | 11686 | 9383 | 10670 | 31740 | - - - | - - - | - - - | - - - | 11686 | 9383 | 10670 | 31740 | 23006 | 21326 | 20360 | 64692 | # # # | # # # | # # # | # # # | 0.83 | 0.866 | 0.815 | 0.837 | # # # | # # # | # # # | - - - | 0.852 | 0.891 | 0.84 | 0.861 | - - - | 0.586 | 1.76 | 1.74 | 1.69 | 1.58 | 1.65 | 1.69 | 22.29 | 23.08 | 24.44 | 0 | - - - | - - - | - - - | - - - | 23006 | 21326 | 20360 | 64692 | Over-range | 12843 | 10648 | 11785 | 35370 | 5246 | 4961 | 4930 | 15391 | 19100 | 18512 | 16627 | 54239 | 19100 | 18512 | 16627 | 54239 | - - - | - - - | - - - | - - -
5/1/2026 | 4:15:00 PM | 282.52 | 279.8 | 278.28 | 488.45 | 481.49 | 486 | 83.8019 | 78.334 | 75.1702 | 0.269 | 1.427 | 1.428 | 1.425 | 1.916 | 1.922 | 2.001 | Over-range | 60.01 | 19633 | 18966 | 17034 | 55633 | - - - | - - - | - - - | - - - | 19633 | 18966 | 17034 | 55633 | 11935 | 9507 | 10873 | 32315 | - - - | - - - | - - - | - - - | 11935 | 9507 | 10873 | 32315 | 23556 | 21790 | 20806 | 66151 | # # # | # # # | # # # | # # # | 0.834 | 0.87 | 0.819 | 0.841 | # # # | # # # | # # # | - - - | 0.854 | 0.892 | 0.842 | 0.863 | - - - | 0.581 | 1.76 | 1.73 | 1.67 | 1.58 | 1.64 | 1.68 | 21.12 | 21.91 | 23.22 | 0 | - - - | - - - | - - - | - - - | 23556 | 21790 | 20806 | 66151 | Over-range | 13009 | 10714 | 11936 | 35761 | 5097 | 4871 | 4850 | 15104 | 19699 | 18940 | 17082 | 55720 | 19699 | 18940 | 17082 | 55720 | - - - | - - - | - - - | - - -
5/1/2026 | 4:30:00 PM | 282.58 | 280.04 | 278.45 | 488.68 | 481.95 | 486.13 | 81.0996 | 75.9602 | 72.981 | 0.2657 | 1.429 | 1.429 | 1.426 | 1.916 | 1.921 | 2.001 | Over-range | 59.99 | 18911 | 18316 | 16468 | 53695 | - - - | - - - | - - - | - - - | 18911 | 18316 | 16468 | 53695 | 11738 | 9464 | 10700 | 31901 | - - - | - - - | - - - | - - - | 11738 | 9464 | 10700 | 31901 | 22813 | 21159 | 20218 | 64190 | # # # | # # # | # # # | # # # | 0.829 | 0.866 | 0.815 | 0.837 | # # # | # # # | # # # | - - - | 0.85 | 0.887 | 0.837 | 0.858 | - - - | 0.594 | 1.8 | 1.74 | 1.67 | 1.6 | 1.65 | 1.71 | 21.04 | 21.8 | 23.11 | 0 | - - - | - - - | - - - | - - - | 22813 | 21159 | 20218 | 64190 | Over-range | 12754 | 10584 | 11721 | 35152 | 4920 | 4675 | 4718 | 14570 | 19003 | 18316 | 16465 | 53784 | 19003 | 18316 | 16465 | 53784 | - - - | - - - | - - - | - - -
5/1/2026 | 4:45:00 PM | 282.76 | 280.22 | 278.64 | 488.98 | 482.28 | 486.46 | 82.6867 | 77.7397 | 74.407 | 0.2685 | 1.428 | 1.428 | 1.425 | 1.916 | 1.917 | 1.994 | Over-range | 60.02 | 19294 | 18762 | 16850 | 54906 | - - - | - - - | - - - | - - - | 19294 | 18762 | 16850 | 54906 | 11869 | 9587 | 10789 | 32245 | - - - | - - - | - - - | - - - | 11869 | 9587 | 10789 | 32245 | 23254 | 21648 | 20614 | 65516 | # # # | # # # | # # # | # # # | 0.83 | 0.867 | 0.817 | 0.838 | # # # | # # # | # # # | - - - | 0.851 | 0.889 | 0.841 | 0.861 | - - - | 0.587 | 1.8 | 1.72 | 1.68 | 1.59 | 1.64 | 1.69 | 21.24 | 21.97 | 23.27 | 0 | - - - | - - - | - - - | - - - | 23254 | 21648 | 20614 | 65516 | Over-range | 12966 | 10775 | 11859 | 35694 | 5107 | 4819 | 4829 | 15016 | 19342 | 18817 | 16841 | 55000 | 19342 | 18817 | 16841 | 55000 | - - - | - - - | - - - | - - -
5/1/2026 | 5:00:00 PM | 282.57 | 279.92 | 278.32 | 488.61 | 481.65 | 486.05 | 82.6142 | 77.6238 | 74.0305 | 0.2658 | 1.428 | 1.429 | 1.425 | 1.928 | 1.921 | 2.006 | Over-range | 60.01 | 19256 | 18749 | 16753 | 54758 | - - - | - - - | - - - | - - - | 19256 | 18749 | 16753 | 54758 | 11839 | 9466 | 10709 | 32014 | - - - | - - - | - - - | - - - | 11839 | 9466 | 10709 | 32014 | 23211 | 21583 | 20478 | 65271 | # # # | # # # | # # # | # # # | 0.83 | 0.869 | 0.818 | 0.839 | # # # | # # # | # # # | - - - | 0.851 | 0.892 | 0.842 | 0.862 | - - - | 0.585 | 1.75 | 1.71 | 1.67 | 1.57 | 1.63 | 1.68 | 21.62 | 22.19 | 23.59 | 0 | - - - | - - - | - - - | - - - | 23211 | 21583 | 20478 | 65271 | Over-range | 12952 | 10677 | 11762 | 35489 | 5170 | 4866 | 4788 | 15095 | 19252 | 18788 | 16813 | 54853 | 19252 | 18788 | 16813 | 54853 | - - - | - - - | - - - | - - -
5/1/2026 | 5:15:00 PM | 282.94 | 280.38 | 278.74 | 489.34 | 482.51 | 486.65 | 80.1948 | 75.5006 | 72.2416 | 0.2618 | 1.428 | 1.429 | 1.427 | 1.897 | 1.899 | 1.979 | Over-range | 60.03 | 18708 | 18221 | 16364 | 53294 | - - - | - - - | - - - | - - - | 18708 | 18221 | 16364 | 53294 | 11617 | 9409 | 10559 | 31584 | - - - | - - - | - - - | - - - | 11617 | 9409 | 10559 | 31584 | 22539 | 21010 | 19998 | 63547 | # # # | # # # | # # # | # # # | 0.83 | 0.867 | 0.818 | 0.839 | # # # | # # # | # # # | - - - | 0.849 | 0.887 | 0.84 | 0.859 | - - - | 0.593 | 1.73 | 1.67 | 1.62 | 1.55 | 1.59 | 1.64 | 20.44 | 20.98 | 22.34 | 0 | - - - | - - - | - - - | - - - | 22539 | 21010 | 19998 | 63547 | Over-range | 12564 | 10447 | 11483 | 34584 | 4708 | 4469 | 4444 | 13876 | 18732 | 18233 | 16417 | 53382 | 18732 | 18233 | 16417 | 53382 | - - - | - - - | - - - | - - -
5/1/2026 | 5:30:00 PM | 282.74 | 280.14 | 278.59 | 488.9 | 482.22 | 486.34 | 81.5126 | 76.5889 | 73.2228 | 0.2663 | 1.428 | 1.428 | 1.427 | 1.891 | 1.894 | 1.967 | Over-range | 60.01 | 19017 | 18502 | 16572 | 54091 | - - - | - - - | - - - | - - - | 19017 | 18502 | 16572 | 54091 | 11830 | 9551 | 10726 | 32108 | - - - | - - - | - - - | - - - | 11830 | 9551 | 10726 | 32108 | 22916 | 21315 | 20275 | 64506 | # # # | # # # | # # # | # # # | 0.83 | 0.868 | 0.817 | 0.839 | # # # | # # # | # # # | - - - | 0.849 | 0.888 | 0.838 | 0.858 | - - - | 0.594 | 1.7 | 1.65 | 1.59 | 1.52 | 1.57 | 1.62 | 19.99 | 20.67 | 22.03 | 0 | - - - | - - - | - - - | - - - | 22916 | 21315 | 20275 | 64506 | Over-range | 12778 | 10569 | 11670 | 35114 | 4741 | 4446 | 4518 | 13976 | 19075 | 18558 | 16535 | 54169 | 19075 | 18558 | 16535 | 54169 | - - - | - - - | - - - | - - -
5/1/2026 | 5:45:00 PM | 282.68 | 280.13 | 278.5 | 488.93 | 482.09 | 486.17 | 80.662 | 75.9945 | 72.7903 | 0.263 | 1.428 | 1.429 | 1.428 | 1.907 | 1.915 | 1.988 | Over-range | 60 | 18789 | 18286 | 16448 | 53523 | - - - | - - - | - - - | - - - | 18789 | 18286 | 16448 | 53523 | 11600 | 9450 | 10572 | 31622 | - - - | - - - | - - - | - - - | 11600 | 9450 | 10572 | 31622 | 22657 | 21133 | 20136 | 63925 | # # # | # # # | # # # | # # # | 0.829 | 0.865 | 0.817 | 0.837 | # # # | # # # | # # # | - - - | 0.85 | 0.887 | 0.839 | 0.859 | - - - | 0.591 | 1.69 | 1.63 | 1.61 | 1.53 | 1.57 | 1.61 | 21.08 | 21.69 | 23.03 | 0 | - - - | - - - | - - - | - - - | 22657 | 21133 | 20136 | 63925 | Over-range | 12644 | 10567 | 11593 | 34892 | 4928 | 4630 | 4660 | 14457 | 18814 | 18351 | 16442 | 53607 | 18814 | 18351 | 16442 | 53607 | - - - | - - - | - - - | - - -
5/1/2026 | 6:00:00 PM | 282.85 | 280.3 | 278.74 | 489.17 | 482.49 | 486.53 | 82.4081 | 76.9719 | 73.8166 | 0.2668 | 1.427 | 1.427 | 1.426 | 1.859 | 1.88 | 1.964 | Over-range | 60.01 | 19228 | 18606 | 16645 | 54479 | - - - | - - - | - - - | - - - | 19228 | 18606 | 16645 | 54479 | 12040 | 9671 | 10999 | 32709 | - - - | - - - | - - - | - - - | 12040 | 9671 | 10999 | 32709 | 23179 | 21435 | 20457 | 65071 | # # # | # # # | # # # | # # # | 0.83 | 0.868 | 0.814 | 0.837 | # # # | # # # | # # # | - - - | 0.847 | 0.886 | 0.833 | 0.855 | - - - | 0.6 | 1.6 | 1.52 | 1.45 | 1.43 | 1.44 | 1.47 | 19.29 | 19.92 | 21.31 | 0 | - - - | - - - | - - - | - - - | 23179 | 21435 | 20457 | 65071 | Over-range | 12939 | 10631 | 11883 | 35559 | 4640 | 4328 | 4410 | 13688 | 19254 | 18660 | 16634 | 54548 | 19254 | 18660 | 16634 | 54548 | - - - | - - - | - - - | - - -
5/1/2026 | 6:15:00 PM | 283.74 | 281.23 | 279.67 | 490.71 | 484.17 | 488.07 | 80.2402 | 75.1205 | 72.6647 | 0.2662 | 1.428 | 1.426 | 1.425 | 1.882 | 1.904 | 1.986 | Over-range | 60.03 | 18735 | 18078 | 16373 | 53186 | - - - | - - - | - - - | - - - | 18735 | 18078 | 16373 | 53186 | 11769 | 9667 | 10893 | 32329 | - - - | - - - | - - - | - - - | 11769 | 9667 | 10893 | 32329 | 22638 | 20988 | 20203 | 63828 | # # # | # # # | # # # | # # # | 0.828 | 0.861 | 0.811 | 0.833 | # # # | # # # | # # # | - - - | 0.846 | 0.881 | 0.83 | 0.853 | - - - | 0.608 | 1.56 | 1.47 | 1.35 | 1.39 | 1.38 | 1.4 | 20.09 | 20.75 | 22.11 | 0 | - - - | - - - | - - - | - - - | 22638 | 20988 | 20203 | 63828 | Over-range | 12700 | 10649 | 11824 | 35260 | 4667 | 4374 | 4504 | 13791 | 18785 | 18120 | 16343 | 53249 | 18785 | 18120 | 16343 | 53249 | - - - | - - - | - - - | - - -
5/1/2026 | 6:30:00 PM | 283.63 | 281.13 | 279.46 | 490.63 | 483.83 | 487.78 | 82.3846 | 76.9377 | 73.4813 | 0.2684 | 1.428 | 1.426 | 1.424 | 1.858 | 1.87 | 1.968 | Over-range | 60 | 19215 | 18656 | 16569 | 54440 | - - - | - - - | - - - | - - - | 19215 | 18656 | 16569 | 54440 | 12250 | 9800 | 11125 | 33176 | - - - | - - - | - - - | - - - | 12250 | 9800 | 11125 | 33176 | 23259 | 21512 | 20429 | 65201 | # # # | # # # | # # # | # # # | 0.826 | 0.867 | 0.811 | 0.835 | # # # | # # # | # # # | - - - | 0.842 | 0.885 | 0.829 | 0.852 | - - - | 0.609 | 1.55 | 1.48 | 1.38 | 1.4 | 1.39 | 1.4 | 18.91 | 19.42 | 20.86 | 0 | - - - | - - - | - - - | - - - | 23259 | 21512 | 20429 | 65201 | Over-range | 13101 | 10702 | 11943 | 35860 | 4569 | 4226 | 4270 | 13399 | 19200 | 18729 | 16570 | 54498 | 19200 | 18729 | 16570 | 54498 | - - - | - - - | - - - | - - -
5/1/2026 | 6:45:00 PM | 283.66 | 281.09 | 279.48 | 490.58 | 483.77 | 487.89 | 80.1191 | 74.9505 | 72.1739 | 0.2635 | 1.429 | 1.427 | 1.425 | 1.875 | 1.891 | 1.981 | Over-range | 60 | 18627 | 18018 | 16199 | 52845 | - - - | - - - | - - - | - - - | 18627 | 18018 | 16199 | 52845 | 11877 | 9676 | 10925 | 32478 | - - - | - - - | - - - | - - - | 11877 | 9676 | 10925 | 32478 | 22606 | 20935 | 20055 | 63596 | # # # | # # # | # # # | # # # | 0.824 | 0.861 | 0.808 | 0.831 | # # # | # # # | # # # | - - - | 0.842 | 0.88 | 0.828 | 0.85 | - - - | 0.615 | 1.57 | 1.51 | 1.38 | 1.42 | 1.41 | 1.42 | 19.81 | 20.25 | 21.71 | 0 | - - - | - - - | - - - | - - - | 22606 | 20935 | 20055 | 63596 | Over-range | 12794 | 10637 | 11806 | 35331 | 4665 | 4334 | 4390 | 13661 | 18618 | 18076 | 16211 | 52905 | 18618 | 18076 | 16211 | 52905 | - - - | - - - | - - - | - - -
5/1/2026 | 7:00:00 PM | 283.75 | 281.18 | 279.5 | 490.78 | 483.86 | 487.94 | 80.3646 | 75.0697 | 71.5251 | 0.2609 | 1.428 | 1.426 | 1.424 | 1.863 | 1.869 | 1.979 | Over-range | 60 | 18684 | 18167 | 16091 | 52942 | - - - | - - - | - - - | - - - | 18684 | 18167 | 16091 | 52942 | 11999 | 9532 | 10834 | 32364 | - - - | - - - | - - - | - - - | 11999 | 9532 | 10834 | 32364 | 22656 | 20951 | 19857 | 63463 | # # # | # # # | # # # | # # # | 0.825 | 0.867 | 0.81 | 0.834 | # # # | # # # | # # # | - - - | 0.84 | 0.884 | 0.829 | 0.851 | - - - | 0.611 | 1.55 | 1.47 | 1.35 | 1.39 | 1.38 | 1.4 | 18.93 | 19.37 | 20.81 | 0 | - - - | - - - | - - - | - - - | 22656 | 20951 | 19857 | 63463 | Over-range | 12806 | 10420 | 11622 | 34964 | 4382 | 4124 | 4116 | 12969 | 18682 | 18166 | 16150 | 52998 | 18682 | 18166 | 16150 | 52998 | - - - | - - - | - - - | - - -
5/1/2026 | 7:15:00 PM | 283.75 | 281.25 | 279.62 | 490.81 | 484.09 | 488.02 | 78.8208 | 73.7494 | 70.7965 | 0.2603 | 1.427 | 1.425 | 1.423 | 1.873 | 1.876 | 1.985 | Over-range | 60 | 18295 | 17752 | 15884 | 51931 | - - - | - - - | - - - | - - - | 18295 | 17752 | 15884 | 51931 | 11845 | 9609 | 10794 | 32248 | - - - | - - - | - - - | - - - | 11845 | 9609 | 10794 | 32248 | 22244 | 20609 | 19679 | 62532 | # # # | # # # | # # # | # # # | 0.823 | 0.861 | 0.807 | 0.831 | # # # | # # # | # # # | - - - | 0.839 | 0.878 | 0.825 | 0.848 | - - - | 0.621 | 1.52 | 1.42 | 1.35 | 1.37 | 1.35 | 1.36 | 19.21 | 19.53 | 20.98 | 0 | - - - | - - - | - - - | - - - | 22244 | 20609 | 19679 | 62532 | Over-range | 12646 | 10458 | 11605 | 34807 | 4340 | 4050 | 4185 | 12862 | 18357 | 17754 | 15868 | 51979 | 18357 | 17754 | 15868 | 51979 | - - - | - - - | - - - | - - -
5/1/2026 | 7:30:00 PM | 283.94 | 281.54 | 279.87 | 491.23 | 484.57 | 488.39 | 81.0783 | 76.0464 | 72.538 | 0.2637 | 1.428 | 1.426 | 1.424 | 1.856 | 1.86 | 1.965 | Over-range | 60 | 18872 | 18410 | 16379 | 53661 | - - - | - - - | - - - | - - - | 18872 | 18410 | 16379 | 53661 | 12170 | 9817 | 10983 | 32970 | - - - | - - - | - - - | - - - | 12170 | 9817 | 10983 | 32970 | 22899 | 21279 | 20189 | 64367 | # # # | # # # | # # # | # # # | 0.824 | 0.865 | 0.811 | 0.834 | # # # | # # # | # # # | - - - | 0.84 | 0.881 | 0.829 | 0.85 | - - - | 0.614 | 1.53 | 1.42 | 1.34 | 1.38 | 1.35 | 1.37 | 18.58 | 18.9 | 20.36 | 0 | - - - | - - - | - - - | - - - | 22899 | 21279 | 20189 | 64367 | Over-range | 12962 | 10658 | 11792 | 35518 | 4357 | 4055 | 4197 | 12927 | 18935 | 18433 | 16339 | 53707 | 18935 | 18433 | 16339 | 53707 | - - - | - - - | - - - | - - -
5/1/2026 | 7:45:00 PM | 283.96 | 281.48 | 279.82 | 491.21 | 484.45 | 488.35 | 81.0984 | 75.9248 | 72.8749 | 0.2644 | 1.428 | 1.426 | 1.424 | 1.867 | 1.873 | 1.97 | Over-range | 60 | 18867 | 18297 | 16385 | 53549 | - - - | - - - | - - - | - - - | 18867 | 18297 | 16385 | 53549 | 12118 | 9853 | 11074 | 33045 | - - - | - - - | - - - | - - - | 12118 | 9853 | 11074 | 33045 | 22905 | 21233 | 20272 | 64410 | # # # | # # # | # # # | # # # | 0.824 | 0.862 | 0.808 | 0.831 | # # # | # # # | # # # | - - - | 0.84 | 0.879 | 0.826 | 0.849 | - - - | 0.617 | 1.53 | 1.42 | 1.35 | 1.38 | 1.35 | 1.37 | 19.11 | 19.56 | 20.88 | 0 | - - - | - - - | - - - | - - - | 22905 | 21233 | 20272 | 64410 | Over-range | 12974 | 10751 | 11919 | 35742 | 4533 | 4201 | 4315 | 13340 | 18899 | 18350 | 16351 | 53600 | 18899 | 18350 | 16351 | 53600 | - - - | - - - | - - - | - - -
5/1/2026 | 8:00:00 PM | 284.07 | 281.58 | 279.89 | 491.37 | 484.64 | 488.52 | 82.8593 | 77.7529 | 74.6622 | 0.2689 | 1.428 | 1.426 | 1.424 | 1.876 | 1.886 | 1.977 | Over-range | 60 | 19337 | 18773 | 16863 | 54973 | - - - | - - - | - - - | - - - | 19337 | 18773 | 16863 | 54973 | 12284 | 10025 | 11228 | 33537 | - - - | - - - | - - - | - - - | 12284 | 10025 | 11228 | 33537 | 23391 | 21740 | 20761 | 65892 | # # # | # # # | # # # | # # # | 0.827 | 0.864 | 0.812 | 0.834 | # # # | # # # | # # # | - - - | 0.844 | 0.881 | 0.831 | 0.852 | - - - | 0.61 | 1.51 | 1.44 | 1.33 | 1.37 | 1.34 | 1.36 | 19.37 | 19.9 | 21.2 | 0 | - - - | - - - | - - - | - - - | 23391 | 21740 | 20761 | 65892 | Over-range | 13155 | 10951 | 12101 | 36301 | 4615 | 4323 | 4427 | 13643 | 19378 | 18815 | 16827 | 55021 | 19378 | 18815 | 16827 | 55021 | - - - | - - - | - - - | - - -
5/1/2026 | 8:15:00 PM | 284.13 | 281.69 | 279.96 | 491.58 | 484.73 | 488.61 | 81.6856 | 76.5833 | 73.1947 | 0.266 | 1.428 | 1.426 | 1.424 | 1.884 | 1.891 | 1.992 | Over-range | 60 | 18996 | 18486 | 16479 | 53961 | - - - | - - - | - - - | - - - | 18996 | 18486 | 16479 | 53961 | 12167 | 9840 | 11050 | 33057 | - - - | - - - | - - - | - - - | 12167 | 9840 | 11050 | 33057 | 23064 | 21415 | 20353 | 64831 | # # # | # # # | # # # | # # # | 0.824 | 0.863 | 0.81 | 0.832 | # # # | # # # | # # # | - - - | 0.841 | 0.882 | 0.829 | 0.851 | - - - | 0.613 | 1.51 | 1.43 | 1.33 | 1.37 | 1.34 | 1.36 | 19.88 | 20.38 | 21.77 | 0 | - - - | - - - | - - - | - - - | 23064 | 21415 | 20353 | 64831 | Over-range | 13072 | 10797 | 11934 | 35905 | 4691 | 4362 | 4429 | 13776 | 19008 | 18540 | 16462 | 54011 | 19008 | 18540 | 16462 | 54011 | - - - | - - - | - - - | - - -
5/1/2026 | 8:30:00 PM | 283.96 | 281.49 | 279.79 | 491.24 | 484.42 | 488.33 | 82.2079 | 76.7801 | 73.8609 | 0.2648 | 1.429 | 1.427 | 1.424 | 1.867 | 1.879 | 1.978 | Over-range | 60 | 19233 | 18595 | 16680 | 54508 | - - - | - - - | - - - | - - - | 19233 | 18595 | 16680 | 54508 | 12186 | 9876 | 11167 | 33229 | - - - | - - - | - - - | - - - | 12186 | 9876 | 11167 | 33229 | 23233 | 21493 | 20559 | 65285 | # # # | # # # | # # # | # # # | 0.828 | 0.865 | 0.811 | 0.835 | # # # | # # # | # # # | - - - | 0.844 | 0.882 | 0.829 | 0.852 | - - - | 0.61 | 1.53 | 1.46 | 1.36 | 1.39 | 1.36 | 1.38 | 19.07 | 19.53 | 20.95 | 0 | - - - | - - - | - - - | - - - | 23233 | 21493 | 20559 | 65285 | Over-range | 13027 | 10767 | 12009 | 35905 | 4525 | 4215 | 4345 | 13384 | 19279 | 18626 | 16654 | 54559 | 19279 | 18626 | 16654 | 54559 | - - - | - - - | - - - | - - -
5/1/2026 | 8:45:00 PM | 283.76 | 281.36 | 279.53 | 490.98 | 484.13 | 487.86 | 82.193 | 76.8372 | 73.4136 | 0.2649 | 1.429 | 1.427 | 1.424 | 1.889 | 1.896 | 1.989 | Over-range | 60 | 19120 | 18552 | 16491 | 54163 | - - - | - - - | - - - | - - - | 19120 | 18552 | 16491 | 54163 | 12159 | 9714 | 11017 | 32889 | - - - | - - - | - - - | - - - | 12159 | 9714 | 11017 | 32889 | 23170 | 21450 | 20374 | 64994 | # # # | # # # | # # # | # # # | 0.825 | 0.865 | 0.809 | 0.833 | # # # | # # # | # # # | - - - | 0.843 | 0.884 | 0.829 | 0.852 | - - - | 0.607 | 1.54 | 1.45 | 1.35 | 1.4 | 1.36 | 1.38 | 19.78 | 20.62 | 21.77 | 0 | - - - | - - - | - - - | - - - | 23170 | 21450 | 20374 | 64994 | Over-range | 13073 | 10745 | 11948 | 35875 | 4687 | 4491 | 4522 | 14024 | 19193 | 18534 | 16486 | 54213 | 19193 | 18534 | 16486 | 54213 | - - - | - - - | - - - | - - -
5/1/2026 | 9:00:00 PM | 284.25 | 281.81 | 280.04 | 491.79 | 484.9 | 488.78 | 80.7395 | 75.6331 | 72.8268 | 0.2628 | 1.429 | 1.427 | 1.424 | 1.906 | 1.918 | 2.009 | Over-range | 59.99 | 18947 | 18328 | 16509 | 53784 | - - - | - - - | - - - | - - - | 18947 | 18328 | 16509 | 53784 | 11799 | 9592 | 10824 | 32215 | - - - | - - - | - - - | - - - | 11799 | 9592 | 10824 | 32215 | 22853 | 21208 | 20301 | 64361 | # # # | # # # | # # # | # # # | 0.829 | 0.864 | 0.813 | 0.836 | # # # | # # # | # # # | - - - | 0.849 | 0.885 | 0.835 | 0.856 | - - - | 0.599 | 1.57 | 1.48 | 1.36 | 1.41 | 1.38 | 1.4 | 20.84 | 21.53 | 22.8 | 0 | - - - | - - - | - - - | - - - | 22853 | 21208 | 20301 | 64361 | Over-range | 12770 | 10659 | 11805 | 35326 | 4811 | 4585 | 4646 | 14298 | 19013 | 18317 | 16514 | 53843 | 19013 | 18317 | 16514 | 53843 | - - - | - - - | - - - | - - -
5/1/2026 | 9:15:00 PM | 284.29 | 281.82 | 280.15 | 491.78 | 485.02 | 488.95 | 84.0797 | 78.6364 | 75.0707 | 0.2673 | 1.429 | 1.427 | 1.425 | 1.895 | 1.908 | 1.997 | Over-range | 60 | 19724 | 19150 | 17034 | 55908 | - - - | - - - | - - - | - - - | 19724 | 19150 | 17034 | 55908 | 12315 | 9830 | 11182 | 33328 | - - - | - - - | - - - | - - - | 12315 | 9830 | 11182 | 33328 | 23796 | 22042 | 20927 | 66765 | # # # | # # # | # # # | # # # | 0.829 | 0.869 | 0.814 | 0.837 | # # # | # # # | # # # | - - - | 0.847 | 0.889 | 0.835 | 0.857 | - - - | 0.596 | 1.58 | 1.47 | 1.41 | 1.42 | 1.4 | 1.42 | 20.28 | 21.01 | 22.33 | 0 | - - - | - - - | - - - | - - - | 23796 | 22042 | 20927 | 66765 | Over-range | 13306 | 10905 | 12146 | 36469 | 4956 | 4643 | 4666 | 14582 | 19713 | 19218 | 17029 | 55959 | 19713 | 19218 | 17029 | 55959 | - - - | - - - | - - - | - - -
5/1/2026 | 9:30:00 PM | 284.72 | 282.32 | 280.59 | 492.56 | 485.92 | 489.64 | 80.9462 | 75.7613 | 73.2399 | 0.2639 | 1.429 | 1.427 | 1.425 | 1.915 | 1.931 | 2.014 | Over-range | 59.99 | 18947 | 18276 | 16531 | 53754 | - - - | - - - | - - - | - - - | 18947 | 18276 | 16531 | 53754 | 11830 | 9698 | 10993 | 32521 | - - - | - - - | - - - | - - - | 11830 | 9698 | 10993 | 32521 | 22906 | 21240 | 20424 | 64569 | # # # | # # # | # # # | # # # | 0.827 | 0.86 | 0.809 | 0.833 | # # # | # # # | # # # | - - - | 0.847 | 0.882 | 0.832 | 0.854 | - - - | 0.605 | 1.61 | 1.48 | 1.39 | 1.44 | 1.41 | 1.43 | 21.26 | 22.12 | 23.16 | 0 | - - - | - - - | - - - | - - - | 22906 | 21240 | 20424 | 64569 | Over-range | 12865 | 10810 | 11984 | 35746 | 4967 | 4695 | 4689 | 14595 | 18928 | 18328 | 16560 | 53816 | 18928 | 18328 | 16560 | 53816 | - - - | - - - | - - - | - - -
5/1/2026 | 9:45:00 PM | 284.98 | 282.59 | 280.84 | 493.03 | 486.37 | 490.08 | 82.8855 | 77.3044 | 74.487 | 0.2658 | 1.429 | 1.427 | 1.425 | 1.887 | 1.904 | 1.997 | Over-range | 60.01 | 19421 | 18728 | 16807 | 54956 | - - - | - - - | - - - | - - - | 19421 | 18728 | 16807 | 54956 | 12233 | 9848 | 11271 | 33352 | - - - | - - - | - - - | - - - | 12233 | 9848 | 11271 | 33352 | 23469 | 21681 | 20775 | 65926 | # # # | # # # | # # # | # # # | 0.828 | 0.864 | 0.809 | 0.834 | # # # | # # # | # # # | - - - | 0.845 | 0.883 | 0.83 | 0.853 | - - - | 0.607 | 1.62 | 1.48 | 1.41 | 1.45 | 1.41 | 1.44 | 19.99 | 20.87 | 22.02 | 0 | - - - | - - - | - - - | - - - | 23469 | 21681 | 20775 | 65926 | Over-range | 13163 | 10903 | 12197 | 36368 | 4773 | 4603 | 4579 | 14266 | 19445 | 18700 | 16871 | 55016 | 19445 | 18700 | 16871 | 55016 | - - - | - - - | - - - | - - -
5/1/2026 | 10:00:00 PM | 285.25 | 282.87 | 281.08 | 493.55 | 486.77 | 490.53 | 82.0221 | 76.296 | 73.7211 | 0.2649 | 1.429 | 1.427 | 1.425 | 1.873 | 1.886 | 1.993 | Over-range | 60.01 | 19221 | 18503 | 16614 | 54338 | - - - | - - - | - - - | - - - | 19221 | 18503 | 16614 | 54338 | 12311 | 9983 | 11348 | 33642 | - - - | - - - | - - - | - - - | 12311 | 9983 | 11348 | 33642 | 23301 | 21478 | 20627 | 65406 | # # # | # # # | # # # | # # # | 0.825 | 0.862 | 0.805 | 0.831 | # # # | # # # | # # # | - - - | 0.842 | 0.879 | 0.824 | 0.849 | - - - | 0.619 | 1.63 | 1.5 | 1.41 | 1.45 | 1.42 | 1.45 | 19.31 | 19.9 | 21.25 | 0 | - - - | - - - | - - - | - - - | 23301 | 21478 | 20627 | 65406 | Over-range | 13166 | 10896 | 12218 | 36384 | 4593 | 4296 | 4458 | 13650 | 19292 | 18517 | 16575 | 54385 | 19292 | 18517 | 16575 | 54385 | - - - | - - - | - - - | - - -
5/1/2026 | 10:15:00 PM | 285.24 | 282.74 | 281.06 | 493.42 | 486.59 | 490.56 | 81.9075 | 75.9252 | 73.2496 | 0.2638 | 1.429 | 1.427 | 1.424 | 1.879 | 1.892 | 2.01 | Over-range | 60 | 19136 | 18378 | 16426 | 53939 | - - - | - - - | - - - | - - - | 19136 | 18378 | 16426 | 53939 | 12245 | 9790 | 11251 | 33286 | - - - | - - - | - - - | - - - | 12245 | 9790 | 11251 | 33286 | 23204 | 21293 | 20437 | 64934 | # # # | # # # | # # # | # # # | 0.825 | 0.863 | 0.804 | 0.831 | # # # | # # # | # # # | - - - | 0.842 | 0.881 | 0.823 | 0.849 | - - - | 0.617 | 1.6 | 1.49 | 1.41 | 1.45 | 1.42 | 1.45 | 19.64 | 20.19 | 21.72 | 0 | - - - | - - - | - - - | - - - | 23204 | 21293 | 20437 | 64934 | Over-range | 13117 | 10738 | 12145 | 36117 | 4605 | 4319 | 4481 | 13745 | 19205 | 18364 | 16415 | 53984 | 19205 | 18364 | 16415 | 53984 | - - - | - - - | - - - | - - -
5/1/2026 | 10:30:00 PM | 284.66 | 282.17 | 280.41 | 492.47 | 485.54 | 489.45 | 80.7062 | 74.9254 | 72.0395 | 0.2632 | 1.429 | 1.427 | 1.425 | 1.877 | 1.89 | 2.011 | Over-range | 60.01 | 18830 | 18144 | 16162 | 53135 | - - - | - - - | - - - | - - - | 18830 | 18144 | 16162 | 53135 | 12069 | 9653 | 11069 | 32791 | - - - | - - - | - - - | - - - | 12069 | 9653 | 11069 | 32791 | 22850 | 21006 | 20084 | 63940 | # # # | # # # | # # # | # # # | 0.824 | 0.864 | 0.805 | 0.831 | # # # | # # # | # # # | - - - | 0.841 | 0.882 | 0.824 | 0.849 | - - - | 0.617 | 1.61 | 1.49 | 1.42 | 1.46 | 1.43 | 1.46 | 19.67 | 20.1 | 21.63 | 0 | - - - | - - - | - - - | - - - | 22850 | 21006 | 20084 | 63940 | Over-range | 12939 | 10576 | 11915 | 35544 | 4582 | 4241 | 4333 | 13490 | 18833 | 18174 | 16176 | 53182 | 18833 | 18174 | 16176 | 53182 | - - - | - - - | - - - | - - -
5/1/2026 | 10:45:00 PM | 284.63 | 282.05 | 280.35 | 492.32 | 485.32 | 489.44 | 82.2991 | 76.5497 | 73.5222 | 0.2663 | 1.429 | 1.427 | 1.424 | 1.863 | 1.873 | 1.998 | Over-range | 60 | 19269 | 18595 | 16587 | 54451 | - - - | - - - | - - - | - - - | 19269 | 18595 | 16587 | 54451 | 12226 | 9795 | 11160 | 33181 | - - - | - - - | - - - | - - - | 12226 | 9795 | 11160 | 33181 | 23310 | 21463 | 20504 | 65277 | # # # | # # # | # # # | # # # | 0.827 | 0.866 | 0.809 | 0.834 | # # # | # # # | # # # | - - - | 0.844 | 0.883 | 0.828 | 0.852 | - - - | 0.609 | 1.63 | 1.49 | 1.42 | 1.46 | 1.43 | 1.47 | 19.22 | 19.39 | 21.12 | 0 | - - - | - - - | - - - | - - - | 23310 | 21463 | 20504 | 65277 | Over-range | 13103 | 10697 | 12038 | 35955 | 4612 | 4202 | 4422 | 13573 | 19315 | 18634 | 16546 | 54495 | 19315 | 18634 | 16546 | 54495 | - - - | - - - | - - - | - - -
5/1/2026 | 11:00:00 PM | 285.02 | 282.41 | 280.69 | 492.98 | 485.91 | 490.1 | 81.2271 | 75.1724 | 72.1 | 0.2628 | 1.429 | 1.427 | 1.424 | 1.871 | 1.88 | 2.011 | Over-range | 60 | 18955 | 18252 | 16166 | 53372 | - - - | - - - | - - - | - - - | 18955 | 18252 | 16166 | 53372 | 12209 | 9628 | 11087 | 32925 | - - - | - - - | - - - | - - - | 12209 | 9628 | 11087 | 32925 | 23019 | 21083 | 20113 | 64215 | # # # | # # # | # # # | # # # | 0.823 | 0.866 | 0.804 | 0.831 | # # # | # # # | # # # | - - - | 0.84 | 0.883 | 0.823 | 0.849 | - - - | 0.617 | 1.65 | 1.52 | 1.41 | 1.47 | 1.44 | 1.48 | 19.4 | 19.78 | 21.51 | 0 | - - - | - - - | - - - | - - - | 23019 | 21083 | 20113 | 64215 | Over-range | 13054 | 10541 | 11957 | 35681 | 4526 | 4208 | 4392 | 13500 | 19032 | 18228 | 16157 | 53417 | 19032 | 18228 | 16157 | 53417 | - - - | - - - | - - - | - - -
5/1/2026 | 11:15:00 PM | 285.11 | 282.47 | 280.68 | 493.13 | 485.94 | 490.13 | 80.0053 | 74.2547 | 71.5136 | 0.2635 | 1.429 | 1.428 | 1.425 | 1.876 | 1.882 | 2.014 | Over-range | 59.99 | 18693 | 17983 | 16058 | 52734 | - - - | - - - | - - - | - - - | 18693 | 17983 | 16058 | 52734 | 11934 | 9582 | 10945 | 32461 | - - - | - - - | - - - | - - - | 11934 | 9582 | 10945 | 32461 | 22662 | 20814 | 19936 | 63412 | # # # | # # # | # # # | # # # | 0.825 | 0.864 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.842 | 0.882 | 0.825 | 0.85 | - - - | 0.616 | 1.67 | 1.53 | 1.47 | 1.5 | 1.48 | 1.51 | 19.7 | 19.91 | 21.66 | 0 | - - - | - - - | - - - | - - - | 22662 | 20814 | 19936 | 63412 | Over-range | 12805 | 10467 | 11803 | 35186 | 4548 | 4125 | 4336 | 13329 | 18728 | 18032 | 16023 | 52783 | 18728 | 18032 | 16023 | 52783 | - - - | - - - | - - - | - - -
5/1/2026 | 11:30:00 PM | 285.44 | 282.81 | 281.06 | 493.74 | 486.52 | 490.78 | 83.2374 | 76.8271 | 73.7889 | 0.2671 | 1.429 | 1.427 | 1.424 | 1.859 | 1.864 | 1.999 | Over-range | 60 | 19484 | 18711 | 16567 | 54762 | - - - | - - - | - - - | - - - | 19484 | 18711 | 16567 | 54762 | 12517 | 9888 | 11449 | 33854 | - - - | - - - | - - - | - - - | 12517 | 9888 | 11449 | 33854 | 23631 | 21586 | 20615 | 65832 | # # # | # # # | # # # | # # # | 0.825 | 0.867 | 0.804 | 0.832 | # # # | # # # | # # # | - - - | 0.84 | 0.883 | 0.821 | 0.848 | - - - | 0.618 | 1.66 | 1.54 | 1.44 | 1.49 | 1.47 | 1.5 | 18.86 | 19.12 | 20.85 | 0 | - - - | - - - | - - - | - - - | 23631 | 21586 | 20615 | 65832 | Over-range | 13366 | 10754 | 12260 | 36515 | 4599 | 4145 | 4300 | 13441 | 19472 | 18776 | 16560 | 54808 | 19472 | 18776 | 16560 | 54808 | - - - | - - - | - - - | - - -
5/1/2026 | 11:45:00 PM | 285.88 | 283.3 | 281.44 | 494.58 | 487.28 | 491.44 | 81.4461 | 75.7311 | 73.0102 | 0.257 | 1.43 | 1.428 | 1.425 | 1.893 | 1.9 | 2.023 | Over-range | 60 | 18995 | 18280 | 16360 | 53635 | - - - | - - - | - - - | - - - | 18995 | 18280 | 16360 | 53635 | 12185 | 9845 | 11203 | 33233 | - - - | - - - | - - - | - - - | 12185 | 9845 | 11203 | 33233 | 23117 | 21272 | 20395 | 64785 | # # # | # # # | # # # | # # # | 0.822 | 0.859 | 0.802 | 0.828 | # # # | # # # | # # # | - - - | 0.841 | 0.879 | 0.823 | 0.848 | - - - | 0.62 | 1.7 | 1.55 | 1.5 | 1.52 | 1.51 | 1.54 | 20.5 | 20.92 | 22.47 | 0 | - - - | - - - | - - - | - - - | 23117 | 21272 | 20395 | 64785 | Over-range | 13160 | 10857 | 12161 | 36284 | 4843 | 4457 | 4616 | 14217 | 19026 | 18322 | 16337 | 53685 | 19026 | 18322 | 16337 | 53685 | - - - | - - - | - - - | - - -
5/2/2026 | 12:00:00 AM | 285.9 | 283.36 | 281.54 | 494.58 | 487.53 | 491.51 | 83.8337 | 78.0574 | 74.5507 | 0.2567 | 1.429 | 1.427 | 1.424 | 1.881 | 1.897 | 2.004 | Over-range | 60 | 19651 | 19040 | 16843 | 55535 | - - - | - - - | - - - | - - - | 19651 | 19040 | 16843 | 55535 | 12581 | 9977 | 11378 | 33937 | - - - | - - - | - - - | - - - | 12581 | 9977 | 11378 | 33937 | 23852 | 21991 | 20877 | 66720 | # # # | # # # | # # # | # # # | 0.824 | 0.866 | 0.807 | 0.832 | # # # | # # # | # # # | - - - | 0.842 | 0.885 | 0.827 | 0.851 | - - - | 0.611 | 1.69 | 1.55 | 1.48 | 1.51 | 1.49 | 1.52 | 19.91 | 20.58 | 22.17 | 0 | - - - | - - - | - - - | - - - | 23852 | 21991 | 20877 | 66720 | Over-range | 13512 | 10992 | 12325 | 36953 | 4844 | 4532 | 4661 | 14391 | 19699 | 19073 | 16812 | 55584 | 19699 | 19073 | 16812 | 55584 | - - - | - - - | - - - | - - -
5/2/2026 | 12:15:00 AM | 286.11 | 283.44 | 281.67 | 494.91 | 487.62 | 491.81 | 81.2404 | 75.4831 | 72.7474 | 0.264 | 1.428 | 1.425 | 1.423 | 1.905 | 1.919 | 2.038 | Over-range | 60.01 | 18975 | 18257 | 16319 | 53551 | - - - | - - - | - - - | - - - | 18975 | 18257 | 16319 | 53551 | 12150 | 9764 | 11174 | 33088 | - - - | - - - | - - - | - - - | 12150 | 9764 | 11174 | 33088 | 23094 | 21233 | 20352 | 64679 | # # # | # # # | # # # | # # # | 0.822 | 0.86 | 0.802 | 0.828 | # # # | # # # | # # # | - - - | 0.841 | 0.881 | 0.824 | 0.849 | - - - | 0.618 | 1.7 | 1.53 | 1.49 | 1.51 | 1.49 | 1.52 | 21.23 | 21.64 | 23.27 | 0 | - - - | - - - | - - - | - - - | 23094 | 21233 | 20352 | 64679 | Over-range | 13157 | 10828 | 12148 | 36242 | 4955 | 4593 | 4678 | 14529 | 18969 | 18274 | 16357 | 53600 | 18969 | 18274 | 16357 | 53600 | - - - | - - - | - - - | - - -
5/2/2026 | 12:30:00 AM | 286.34 | 283.52 | 281.86 | 495.17 | 487.85 | 492.2 | 83.4148 | 77.1382 | 74.1823 | 0.2524 | 1.426 | 1.424 | 1.422 | 1.894 | 1.907 | 2.03 | Over-range | 59.99 | 19586 | 18797 | 16704 | 55088 | - - - | - - - | - - - | - - - | 19586 | 18797 | 16704 | 55088 | 12474 | 9832 | 11396 | 33702 | - - - | - - - | - - - | - - - | 12474 | 9832 | 11396 | 33702 | 23762 | 21738 | 20797 | 66297 | # # # | # # # | # # # | # # # | 0.824 | 0.865 | 0.803 | 0.831 | # # # | # # # | # # # | - - - | 0.843 | 0.884 | 0.825 | 0.851 | - - - | 0.612 | 1.69 | 1.57 | 1.48 | 1.51 | 1.51 | 1.53 | 20.74 | 21.3 | 22.97 | 0 | - - - | - - - | - - - | - - - | 23762 | 21738 | 20797 | 66297 | Over-range | 13449 | 10906 | 12380 | 36863 | 4952 | 4654 | 4767 | 14734 | 19641 | 18756 | 16741 | 55137 | 19641 | 18756 | 16741 | 55137 | - - - | - - - | - - - | - - -
5/2/2026 | 12:45:00 AM | 286.58 | 283.71 | 282.08 | 495.5 | 488.22 | 492.62 | 83.3414 | 77.3425 | 74.6625 | 0.2688 | 1.427 | 1.425 | 1.422 | 1.912 | 1.931 | 2.046 | Over-range | 60 | 19575 | 18785 | 16821 | 55181 | - - - | - - - | - - - | - - - | 19575 | 18785 | 16821 | 55181 | 12365 | 9910 | 11395 | 33670 | - - - | - - - | - - - | - - - | 12365 | 9910 | 11395 | 33670 | 23772 | 21818 | 20951 | 66541 | # # # | # # # | # # # | # # # | 0.824 | 0.861 | 0.803 | 0.829 | # # # | # # # | # # # | - - - | 0.844 | 0.883 | 0.827 | 0.852 | - - - | 0.61 | 1.71 | 1.57 | 1.5 | 1.53 | 1.52 | 1.54 | 21.79 | 22.29 | 24.03 | 0 | - - - | - - - | - - - | - - - | 23772 | 21818 | 20951 | 66541 | Over-range | 13475 | 11080 | 12477 | 37145 | 5278 | 4881 | 5009 | 15471 | 19570 | 18821 | 16836 | 55228 | 19570 | 18821 | 16836 | 55228 | - - - | - - - | - - - | - - -
5/2/2026 | 1:00:00 AM | 286.83 | 284.05 | 282.34 | 496.04 | 488.75 | 493.02 | 83.3218 | 77.536 | 74.5324 | 0.2562 | 1.428 | 1.425 | 1.423 | 1.916 | 1.933 | 2.05 | Over-range | 60.01 | 19601 | 18884 | 16860 | 55344 | - - - | - - - | - - - | - - - | 19601 | 18884 | 16860 | 55344 | 12288 | 9815 | 11272 | 33375 | - - - | - - - | - - - | - - - | 12288 | 9815 | 11272 | 33375 | 23754 | 21867 | 20909 | 66529 | # # # | # # # | # # # | # # # | 0.825 | 0.864 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.846 | 0.886 | 0.83 | 0.854 | - - - | 0.603 | 1.72 | 1.58 | 1.51 | 1.54 | 1.53 | 1.56 | 21.98 | 22.53 | 24.18 | 0 | - - - | - - - | - - - | - - - | 23754 | 21867 | 20909 | 66529 | Over-range | 13411 | 11012 | 12354 | 36890 | 5278 | 4908 | 4971 | 15462 | 19579 | 18922 | 16900 | 55401 | 19579 | 18922 | 16900 | 55401 | - - - | - - - | - - - | - - -
5/2/2026 | 1:15:00 AM | 287.09 | 284.34 | 282.67 | 496.48 | 489.31 | 493.54 | 83.6474 | 77.6001 | 74.9481 | 0.2702 | 1.428 | 1.425 | 1.422 | 1.911 | 1.928 | 2.038 | Over-range | 59.99 | 19674 | 18872 | 16911 | 55456 | - - - | - - - | - - - | - - - | 19674 | 18872 | 16911 | 55456 | 12422 | 9981 | 11492 | 33895 | - - - | - - - | - - - | - - - | 12422 | 9981 | 11492 | 33895 | 23881 | 21921 | 21063 | 66865 | # # # | # # # | # # # | # # # | 0.824 | 0.861 | 0.803 | 0.829 | # # # | # # # | # # # | - - - | 0.844 | 0.883 | 0.826 | 0.851 | - - - | 0.611 | 1.74 | 1.58 | 1.52 | 1.54 | 1.53 | 1.57 | 21.73 | 22.29 | 23.84 | 0 | - - - | - - - | - - - | - - - | 23881 | 21921 | 21063 | 66865 | Over-range | 13530 | 11142 | 12547 | 37331 | 5275 | 4870 | 4956 | 15405 | 19646 | 18929 | 16929 | 55505 | 19646 | 18929 | 16929 | 55505 | - - - | - - - | - - - | - - -
5/2/2026 | 1:30:00 AM | 285.08 | 282.41 | 280.65 | 493.08 | 485.9 | 490.03 | 83.5234 | 77.9072 | 75.1145 | 0.256 | 1.427 | 1.425 | 1.422 | 1.924 | 1.935 | 2.044 | Over-range | 60.01 | 19664 | 18926 | 17026 | 55617 | - - - | - - - | - - - | - - - | 19664 | 18926 | 17026 | 55617 | 12062 | 9724 | 11142 | 32928 | - - - | - - - | - - - | - - - | 12062 | 9724 | 11142 | 32928 | 23687 | 21865 | 20969 | 66521 | # # # | # # # | # # # | # # # | 0.83 | 0.866 | 0.812 | 0.836 | # # # | # # # | # # # | - - - | 0.851 | 0.889 | 0.837 | 0.859 | - - - | 0.592 | 1.72 | 1.57 | 1.53 | 1.54 | 1.53 | 1.56 | 22.19 | 22.75 | 24.22 | 0 | - - - | - - - | - - - | - - - | 23687 | 21865 | 20969 | 66521 | Over-range | 13200 | 10938 | 12230 | 36471 | 5294 | 4945 | 4981 | 15494 | 19641 | 18959 | 17074 | 55675 | 19641 | 18959 | 17074 | 55675 | - - - | - - - | - - - | - - -
5/2/2026 | 1:45:00 AM | 285.24 | 282.6 | 280.84 | 493.36 | 486.26 | 490.32 | 83.4959 | 77.4942 | 74.6112 | 0.261 | 1.427 | 1.424 | 1.422 | 1.908 | 1.92 | 2.039 | Over-range | 60.02 | 19563 | 18801 | 16781 | 55146 | - - - | - - - | - - - | - - - | 19563 | 18801 | 16781 | 55146 | 12227 | 9736 | 11247 | 33211 | - - - | - - - | - - - | - - - | 12227 | 9736 | 11247 | 33211 | 23685 | 21754 | 20827 | 66266 | # # # | # # # | # # # | # # # | 0.826 | 0.864 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.846 | 0.886 | 0.829 | 0.854 | - - - | 0.602 | 1.74 | 1.58 | 1.52 | 1.55 | 1.53 | 1.57 | 21.64 | 22.2 | 23.79 | 0 | - - - | - - - | - - - | - - - | 23685 | 21754 | 20827 | 66266 | Over-range | 13336 | 10921 | 12317 | 36693 | 5221 | 4856 | 4929 | 15328 | 19556 | 18833 | 16808 | 55196 | 19556 | 18833 | 16808 | 55196 | - - - | - - - | - - - | - - -
5/2/2026 | 2:00:00 AM | 285.13 | 282.41 | 280.76 | 493.1 | 485.99 | 490.22 | 80.9525 | 74.9248 | 72.7377 | 0.2578 | 1.427 | 1.425 | 1.422 | 1.896 | 1.915 | 2.043 | Over-range | 60 | 18996 | 18148 | 16348 | 53491 | - - - | - - - | - - - | - - - | 18996 | 18148 | 16348 | 53491 | 11863 | 9556 | 11050 | 32469 | - - - | - - - | - - - | - - - | 11863 | 9556 | 11050 | 32469 | 22961 | 21030 | 20309 | 64300 | # # # | # # # | # # # | # # # | 0.827 | 0.863 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.847 | 0.884 | 0.827 | 0.853 | - - - | 0.607 | 1.74 | 1.58 | 1.54 | 1.55 | 1.55 | 1.58 | 21.25 | 21.51 | 23.35 | 0 | - - - | - - - | - - - | - - - | 22961 | 21030 | 20309 | 64300 | Over-range | 12892 | 10613 | 12041 | 35654 | 4962 | 4539 | 4706 | 14501 | 18986 | 18181 | 16375 | 53541 | 18986 | 18181 | 16375 | 53541 | - - - | - - - | - - - | - - -
5/2/2026 | 2:15:00 AM | 284.92 | 282.21 | 280.6 | 492.71 | 485.7 | 489.9 | 83.3604 | 76.9031 | 74.1711 | 0.2525 | 1.427 | 1.425 | 1.422 | 1.88 | 1.894 | 2.023 | Over-range | 60 | 19551 | 18713 | 16656 | 54920 | - - - | - - - | - - - | - - - | 19551 | 18713 | 16656 | 54920 | 12317 | 9728 | 11360 | 33406 | - - - | - - - | - - - | - - - | 12317 | 9728 | 11360 | 33406 | 23645 | 21584 | 20706 | 65935 | # # # | # # # | # # # | # # # | 0.827 | 0.867 | 0.804 | 0.833 | # # # | # # # | # # # | - - - | 0.845 | 0.886 | 0.825 | 0.852 | - - - | 0.608 | 1.74 | 1.6 | 1.54 | 1.56 | 1.55 | 1.58 | 20.29 | 20.67 | 22.47 | 0 | - - - | - - - | - - - | - - - | 23645 | 21584 | 20706 | 65935 | Over-range | 13291 | 10744 | 12289 | 36457 | 4915 | 4485 | 4610 | 14376 | 19519 | 18766 | 16683 | 54968 | 19519 | 18766 | 16683 | 54968 | - - - | - - - | - - - | - - -
5/2/2026 | 2:30:00 AM | 284.84 | 282.12 | 280.51 | 492.52 | 485.6 | 489.73 | 80.4105 | 74.533 | 72.2479 | 0.2598 | 1.428 | 1.425 | 1.422 | 1.891 | 1.91 | 2.035 | Over-range | 60.01 | 18820 | 18015 | 16214 | 53049 | - - - | - - - | - - - | - - - | 18820 | 18015 | 16214 | 53049 | 11801 | 9512 | 10987 | 32300 | - - - | - - - | - - - | - - - | 11801 | 9512 | 10987 | 32300 | 22765 | 20875 | 20138 | 63778 | # # # | # # # | # # # | # # # | 0.827 | 0.863 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.845 | 0.883 | 0.827 | 0.852 | - - - | 0.609 | 1.74 | 1.58 | 1.54 | 1.56 | 1.54 | 1.58 | 20.94 | 21.17 | 22.96 | 0 | - - - | - - - | - - - | - - - | 22765 | 20875 | 20138 | 63778 | Over-range | 12799 | 10532 | 11930 | 35370 | 4860 | 4433 | 4563 | 14153 | 18783 | 18058 | 16254 | 53095 | 18783 | 18058 | 16254 | 53095 | - - - | - - - | - - - | - - -
5/2/2026 | 2:45:00 AM | 285.2 | 282.53 | 280.89 | 493.24 | 486.26 | 490.34 | 81.7254 | 75.5667 | 72.7857 | 0.2542 | 1.427 | 1.425 | 1.422 | 1.869 | 1.88 | 2.019 | Over-range | 60.01 | 19138 | 18364 | 16346 | 53848 | - - - | - - - | - - - | - - - | 19138 | 18364 | 16346 | 53848 | 12123 | 9624 | 11163 | 32910 | - - - | - - - | - - - | - - - | 12123 | 9624 | 11163 | 32910 | 23183 | 21211 | 20325 | 64719 | # # # | # # # | # # # | # # # | 0.826 | 0.866 | 0.804 | 0.832 | # # # | # # # | # # # | - - - | 0.843 | 0.885 | 0.824 | 0.851 | - - - | 0.611 | 1.74 | 1.58 | 1.56 | 1.56 | 1.55 | 1.59 | 19.93 | 20.1 | 21.97 | 0 | - - - | - - - | - - - | - - - | 23183 | 21211 | 20325 | 64719 | Over-range | 13069 | 10591 | 12062 | 35849 | 4775 | 4318 | 4466 | 13919 | 19109 | 18425 | 16360 | 53894 | 19109 | 18425 | 16360 | 53894 | - - - | - - - | - - - | - - -
5/2/2026 | 3:00:00 AM | 285.24 | 282.49 | 280.92 | 493.22 | 486.23 | 490.43 | 80.5872 | 74.3999 | 72.2525 | 0.2521 | 1.427 | 1.424 | 1.421 | 1.862 | 1.877 | 2.024 | Over-range | 60.01 | 18846 | 17990 | 16163 | 52999 | - - - | - - - | - - - | - - - | 18846 | 17990 | 16163 | 52999 | 11981 | 9623 | 11168 | 32772 | - - - | - - - | - - - | - - - | 11981 | 9623 | 11168 | 32772 | 22828 | 20844 | 20145 | 63817 | # # # | # # # | # # # | # # # | 0.826 | 0.863 | 0.802 | 0.831 | # # # | # # # | # # # | - - - | 0.842 | 0.881 | 0.822 | 0.849 | - - - | 0.618 | 1.72 | 1.56 | 1.53 | 1.54 | 1.53 | 1.57 | 19.81 | 19.73 | 21.72 | 0 | - - - | - - - | - - - | - - - | 22828 | 20844 | 20145 | 63817 | Over-range | 12873 | 10514 | 12010 | 35514 | 4607 | 4139 | 4324 | 13403 | 18812 | 18019 | 16204 | 53035 | 18812 | 18019 | 16204 | 53035 | - - - | - - - | - - - | - - -
5/2/2026 | 3:15:00 AM | 285.38 | 282.8 | 281.09 | 493.59 | 486.74 | 490.62 | 81.905 | 75.8167 | 73.255 | 0.2603 | 1.427 | 1.424 | 1.422 | 1.856 | 1.868 | 2.007 | Over-range | 60.01 | 19198 | 18406 | 16465 | 54069 | - - - | - - - | - - - | - - - | 19198 | 18406 | 16465 | 54069 | 12183 | 9721 | 11253 | 33157 | - - - | - - - | - - - | - - - | 12183 | 9721 | 11253 | 33157 | 23214 | 21268 | 20443 | 64926 | # # # | # # # | # # # | # # # | 0.827 | 0.865 | 0.805 | 0.833 | # # # | # # # | # # # | - - - | 0.843 | 0.882 | 0.825 | 0.85 | - - - | 0.613 | 1.71 | 1.59 | 1.53 | 1.54 | 1.53 | 1.57 | 19.35 | 19.61 | 21.31 | 0 | - - - | - - - | - - - | - - - | 23214 | 21268 | 20443 | 64926 | Over-range | 13044 | 10642 | 12105 | 35911 | 4552 | 4230 | 4357 | 13493 | 19218 | 18378 | 16513 | 54110 | 19218 | 18378 | 16513 | 54110 | - - - | - - - | - - - | - - -
5/2/2026 | 3:30:00 AM | 285.34 | 282.67 | 280.96 | 493.54 | 486.4 | 490.54 | 81.2041 | 75.1692 | 72.5557 | 0.2467 | 1.426 | 1.423 | 1.421 | 1.864 | 1.867 | 2.02 | Over-range | 60 | 19025 | 18260 | 16314 | 53600 | - - - | - - - | - - - | - - - | 19025 | 18260 | 16314 | 53600 | 12143 | 9692 | 11149 | 32984 | - - - | - - - | - - - | - - - | 12143 | 9692 | 11149 | 32984 | 23052 | 21114 | 20274 | 64440 | # # # | # # # | # # # | # # # | 0.825 | 0.865 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.843 | 0.882 | 0.825 | 0.85 | - - - | 0.615 | 1.71 | 1.58 | 1.52 | 1.54 | 1.52 | 1.56 | 19.79 | 19.71 | 21.72 | 0 | - - - | - - - | - - - | - - - | 23052 | 21114 | 20274 | 64440 | Over-range | 13011 | 10590 | 12026 | 35747 | 4591 | 4188 | 4432 | 13552 | 19088 | 18229 | 16318 | 53635 | 19088 | 18229 | 16318 | 53635 | - - - | - - - | - - - | - - -
5/2/2026 | 3:45:00 AM | 285.32 | 282.69 | 280.98 | 493.51 | 486.45 | 490.51 | 82.3424 | 76.5074 | 73.6092 | 0.2629 | 1.427 | 1.424 | 1.421 | 1.879 | 1.893 | 2.027 | Over-range | 60.01 | 19313 | 18602 | 16600 | 54514 | - - - | - - - | - - - | - - - | 19313 | 18602 | 16600 | 54514 | 12155 | 9706 | 11111 | 32971 | - - - | - - - | - - - | - - - | 12155 | 9706 | 11111 | 32971 | 23371 | 21493 | 20561 | 65425 | # # # | # # # | # # # | # # # | 0.826 | 0.866 | 0.807 | 0.833 | # # # | # # # | # # # | - - - | 0.846 | 0.885 | 0.829 | 0.853 | - - - | 0.605 | 1.73 | 1.58 | 1.53 | 1.55 | 1.54 | 1.57 | 20.58 | 20.83 | 22.76 | 0 | - - - | - - - | - - - | - - - | 23371 | 21493 | 20561 | 65425 | Over-range | 13146 | 10744 | 12116 | 36123 | 4907 | 4517 | 4741 | 14489 | 19375 | 18617 | 16570 | 54562 | 19375 | 18617 | 16570 | 54562 | - - - | - - - | - - - | - - -
5/2/2026 | 4:00:00 AM | 285.63 | 282.97 | 281.25 | 494.03 | 486.92 | 491.03 | 81.6394 | 75.6548 | 73.0261 | 0.2556 | 1.426 | 1.423 | 1.42 | 1.889 | 1.899 | 2.036 | Over-range | 60 | 19130 | 18366 | 16422 | 53917 | - - - | - - - | - - - | - - - | 19130 | 18366 | 16422 | 53917 | 12122 | 9721 | 11156 | 33000 | - - - | - - - | - - - | - - - | 12122 | 9721 | 11156 | 33000 | 23198 | 21278 | 20425 | 64901 | # # # | # # # | # # # | # # # | 0.825 | 0.863 | 0.804 | 0.831 | # # # | # # # | # # # | - - - | 0.844 | 0.883 | 0.825 | 0.851 | - - - | 0.612 | 1.71 | 1.58 | 1.53 | 1.54 | 1.53 | 1.56 | 20.93 | 21.12 | 23.01 | 0 | - - - | - - - | - - - | - - - | 23198 | 21278 | 20425 | 64901 | Over-range | 13117 | 10733 | 12136 | 36102 | 4921 | 4467 | 4699 | 14400 | 19164 | 18409 | 16385 | 53958 | 19164 | 18409 | 16385 | 53958 | - - - | - - - | - - - | - - -
5/2/2026 | 4:15:00 AM | 285.7 | 283.03 | 281.34 | 494.14 | 487.05 | 491.16 | 81.7821 | 75.8375 | 73.1752 | 0.2605 | 1.427 | 1.424 | 1.421 | 1.879 | 1.89 | 2.028 | Over-range | 60 | 19203 | 18444 | 16502 | 54149 | - - - | - - - | - - - | - - - | 19203 | 18444 | 16502 | 54149 | 12127 | 9718 | 11182 | 33027 | - - - | - - - | - - - | - - - | 12127 | 9718 | 11182 | 33027 | 23249 | 21339 | 20481 | 65069 | # # # | # # # | # # # | # # # | 0.826 | 0.864 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.844 | 0.883 | 0.827 | 0.852 | - - - | 0.61 | 1.71 | 1.59 | 1.54 | 1.55 | 1.54 | 1.58 | 20.5 | 20.58 | 22.47 | 0 | - - - | - - - | - - - | - - - | 23249 | 21339 | 20481 | 65069 | Over-range | 13100 | 10716 | 12120 | 36052 | 4858 | 4428 | 4585 | 14193 | 19192 | 18475 | 16522 | 54189 | 19192 | 18475 | 16522 | 54189 | - - - | - - - | - - - | - - -
5/2/2026 | 4:30:00 AM | 285.62 | 283 | 281.32 | 494.05 | 487.04 | 491.05 | 81.9371 | 75.9802 | 73.1593 | 0.2617 | 1.426 | 1.423 | 1.421 | 1.875 | 1.891 | 2.021 | Over-range | 60 | 19186 | 18455 | 16454 | 54096 | - - - | - - - | - - - | - - - | 19186 | 18455 | 16454 | 54096 | 12208 | 9764 | 11231 | 33203 | - - - | - - - | - - - | - - - | 12208 | 9764 | 11231 | 33203 | 23278 | 21365 | 20461 | 65104 | # # # | # # # | # # # | # # # | 0.824 | 0.864 | 0.804 | 0.831 | # # # | # # # | # # # | - - - | 0.842 | 0.883 | 0.824 | 0.85 | - - - | 0.614 | 1.72 | 1.56 | 1.54 | 1.54 | 1.53 | 1.56 | 20.31 | 20.55 | 22.34 | 0 | - - - | - - - | - - - | - - - | 23278 | 21365 | 20461 | 65104 | Over-range | 13174 | 10751 | 12151 | 36194 | 4846 | 4400 | 4540 | 14116 | 19162 | 18513 | 16460 | 54134 | 19162 | 18513 | 16460 | 54134 | - - - | - - - | - - - | - - -
5/2/2026 | 4:45:00 AM | 285.46 | 282.84 | 281.12 | 493.78 | 486.7 | 490.74 | 82.561 | 76.9801 | 74.1195 | 0.2603 | 1.426 | 1.423 | 1.421 | 1.895 | 1.913 | 2.037 | Over-range | 60.01 | 19363 | 18667 | 16737 | 54768 | - - - | - - - | - - - | - - - | 19363 | 18667 | 16737 | 54768 | 12052 | 9686 | 11087 | 32824 | - - - | - - - | - - - | - - - | 12052 | 9686 | 11087 | 32824 | 23407 | 21598 | 20686 | 65690 | # # # | # # # | # # # | # # # | 0.827 | 0.864 | 0.809 | 0.834 | # # # | # # # | # # # | - - - | 0.847 | 0.886 | 0.833 | 0.856 | - - - | 0.599 | 1.75 | 1.6 | 1.53 | 1.55 | 1.55 | 1.58 | 21.64 | 22.03 | 23.75 | 0 | - - - | - - - | - - - | - - - | 23407 | 21598 | 20686 | 65690 | Over-range | 13137 | 10839 | 12140 | 36223 | 5125 | 4765 | 4846 | 15030 | 19351 | 18678 | 16789 | 54818 | 19351 | 18678 | 16789 | 54818 | - - - | - - - | - - - | - - -
5/2/2026 | 5:00:00 AM | 285.63 | 282.97 | 281.34 | 494 | 487.02 | 491.1 | 82.9933 | 77.2219 | 74.5167 | 0.2552 | 1.427 | 1.424 | 1.421 | 1.899 | 1.922 | 2.035 | Over-range | 60.01 | 19535 | 18779 | 16859 | 55173 | - - - | - - - | - - - | - - - | 19535 | 18779 | 16859 | 55173 | 12123 | 9728 | 11167 | 33018 | - - - | - - - | - - - | - - - | 12123 | 9728 | 11167 | 33018 | 23582 | 21717 | 20846 | 66146 | # # # | # # # | # # # | # # # | 0.828 | 0.865 | 0.809 | 0.834 | # # # | # # # | # # # | - - - | 0.849 | 0.887 | 0.833 | 0.856 | - - - | 0.598 | 1.75 | 1.62 | 1.54 | 1.57 | 1.57 | 1.6 | 21.64 | 22.33 | 23.95 | 0 | - - - | - - - | - - - | - - - | 23582 | 21717 | 20846 | 66146 | Over-range | 13205 | 10897 | 12252 | 36462 | 5158 | 4841 | 4971 | 15261 | 19573 | 18786 | 16862 | 55221 | 19573 | 18786 | 16862 | 55221 | - - - | - - - | - - - | - - -
5/2/2026 | 5:15:00 AM | 285.76 | 283.19 | 281.52 | 494.3 | 487.39 | 491.34 | 82.4915 | 76.9649 | 74.5903 | 0.2635 | 1.427 | 1.424 | 1.422 | 1.897 | 1.916 | 2.021 | Over-range | 60.01 | 19441 | 18686 | 16908 | 55035 | - - - | - - - | - - - | - - - | 19441 | 18686 | 16908 | 55035 | 12041 | 9833 | 11190 | 33064 | - - - | - - - | - - - | - - - | 12041 | 9833 | 11190 | 33064 | 23451 | 21666 | 20882 | 65998 | # # # | # # # | # # # | # # # | 0.829 | 0.863 | 0.81 | 0.834 | # # # | # # # | # # # | - - - | 0.849 | 0.884 | 0.833 | 0.856 | - - - | 0.601 | 1.78 | 1.64 | 1.61 | 1.6 | 1.61 | 1.65 | 21.43 | 21.97 | 23.58 | 0 | - - - | - - - | - - - | - - - | 23451 | 21666 | 20882 | 65998 | Over-range | 13108 | 10953 | 12244 | 36400 | 5100 | 4751 | 4898 | 15003 | 19463 | 18727 | 16902 | 55092 | 19463 | 18727 | 16902 | 55092 | - - - | - - - | - - - | - - -
5/2/2026 | 5:30:00 AM | 285.57 | 283.06 | 281.36 | 494.05 | 487.15 | 491.02 | 82.7865 | 77.2394 | 74.1251 | 0.2575 | 1.426 | 1.424 | 1.422 | 1.892 | 1.906 | 2.014 | Over-range | 60.01 | 19459 | 18813 | 16800 | 55071 | - - - | - - - | - - - | - - - | 19459 | 18813 | 16800 | 55071 | 12207 | 9760 | 11132 | 33098 | - - - | - - - | - - - | - - - | 12207 | 9760 | 11132 | 33098 | 23527 | 21738 | 20748 | 66013 | # # # | # # # | # # # | # # # | 0.827 | 0.865 | 0.81 | 0.834 | # # # | # # # | # # # | - - - | 0.847 | 0.886 | 0.833 | 0.855 | - - - | 0.601 | 1.76 | 1.64 | 1.63 | 1.59 | 1.61 | 1.65 | 21.04 | 21.71 | 23.26 | 0 | - - - | - - - | - - - | - - - | 23527 | 21738 | 20748 | 66013 | Over-range | 13218 | 10881 | 12167 | 36375 | 4991 | 4740 | 4843 | 14879 | 19530 | 18785 | 16812 | 55127 | 19530 | 18785 | 16812 | 55127 | - - - | - - - | - - - | - - -
5/2/2026 | 5:45:00 AM | 285.53 | 282.95 | 281.24 | 493.91 | 486.91 | 490.91 | 82.6243 | 77.0987 | 74.2897 | 0.2567 | 1.425 | 1.423 | 1.421 | 1.883 | 1.9 | 2.007 | Over-range | 60 | 19333 | 18648 | 16746 | 54726 | - - - | - - - | - - - | - - - | 19333 | 18648 | 16746 | 54726 | 12219 | 9891 | 11225 | 33336 | - - - | - - - | - - - | - - - | 12219 | 9891 | 11225 | 33336 | 23426 | 21636 | 20747 | 65809 | # # # | # # # | # # # | # # # | 0.825 | 0.862 | 0.807 | 0.832 | # # # | # # # | # # # | - - - | 0.844 | 0.881 | 0.829 | 0.852 | - - - | 0.609 | 1.74 | 1.62 | 1.55 | 1.56 | 1.57 | 1.6 | 20.64 | 21.14 | 22.73 | 0 | - - - | - - - | - - - | - - - | 23426 | 21636 | 20747 | 65809 | Over-range | 13216 | 10949 | 12231 | 36498 | 4917 | 4590 | 4754 | 14551 | 19395 | 18645 | 16733 | 54773 | 19395 | 18645 | 16733 | 54773 | - - - | - - - | - - - | - - -
5/2/2026 | 6:00:00 AM | 285.13 | 282.52 | 280.83 | 493.21 | 486.17 | 490.22 | 83.01 | 76.971 | 73.8302 | 0.2585 | 1.425 | 1.423 | 1.421 | 1.867 | 1.878 | 2.003 | Over-range | 60 | 19480 | 18764 | 16657 | 54901 | - - - | - - - | - - - | - - - | 19480 | 18764 | 16657 | 54901 | 12316 | 9742 | 11208 | 33266 | - - - | - - - | - - - | - - - | 12316 | 9742 | 11208 | 33266 | 23546 | 21610 | 20614 | 65769 | # # # | # # # | # # # | # # # | 0.827 | 0.868 | 0.808 | 0.835 | # # # | # # # | # # # | - - - | 0.845 | 0.886 | 0.828 | 0.853 | - - - | 0.606 | 1.76 | 1.61 | 1.56 | 1.55 | 1.57 | 1.6 | 19.71 | 20.22 | 21.98 | 0 | - - - | - - - | - - - | - - - | 23546 | 21610 | 20614 | 65769 | Over-range | 13220 | 10707 | 12134 | 36188 | 4722 | 4364 | 4573 | 14020 | 19557 | 18777 | 16619 | 54953 | 19557 | 18777 | 16619 | 54953 | - - - | - - - | - - - | - - -
5/2/2026 | 6:15:00 AM | 285.03 | 282.44 | 280.73 | 493.03 | 486.08 | 490 | 79.896 | 74.2664 | 71.8472 | 0.2472 | 1.426 | 1.424 | 1.421 | 1.882 | 1.895 | 2.018 | Over-range | 59.99 | 18659 | 17923 | 16110 | 52691 | - - - | - - - | - - - | - - - | 18659 | 17923 | 16110 | 52691 | 11848 | 9566 | 10960 | 32374 | - - - | - - - | - - - | - - - | 11848 | 9566 | 10960 | 32374 | 22622 | 20812 | 20028 | 63462 | # # # | # # # | # # # | # # # | 0.825 | 0.861 | 0.804 | 0.83 | # # # | # # # | # # # | - - - | 0.843 | 0.88 | 0.826 | 0.85 | - - - | 0.614 | 1.73 | 1.62 | 1.56 | 1.55 | 1.56 | 1.6 | 20.5 | 20.9 | 22.54 | 0 | - - - | - - - | - - - | - - - | 22622 | 20812 | 20028 | 63462 | Over-range | 12782 | 10564 | 11885 | 35333 | 4684 | 4382 | 4494 | 13854 | 18692 | 17897 | 16147 | 52737 | 18692 | 17897 | 16147 | 52737 | - - - | - - - | - - - | - - -
5/2/2026 | 6:30:00 AM | 284.9 | 282.33 | 280.62 | 492.83 | 485.89 | 489.78 | 81.8537 | 76.085 | 73.054 | 0.255 | 1.425 | 1.423 | 1.421 | 1.867 | 1.879 | 1.999 | Over-range | 60 | 19195 | 18508 | 16486 | 54188 | - - - | - - - | - - - | - - - | 19195 | 18508 | 16486 | 54188 | 12105 | 9636 | 11103 | 32844 | - - - | - - - | - - - | - - - | 12105 | 9636 | 11103 | 32844 | 23198 | 21346 | 20385 | 64928 | # # # | # # # | # # # | # # # | 0.827 | 0.867 | 0.809 | 0.835 | # # # | # # # | # # # | - - - | 0.844 | 0.886 | 0.829 | 0.853 | - - - | 0.606 | 1.71 | 1.56 | 1.53 | 1.52 | 1.53 | 1.56 | 19.72 | 20.18 | 21.68 | 0 | - - - | - - - | - - - | - - - | 23198 | 21346 | 20385 | 64928 | Over-range | 13018 | 10619 | 11977 | 35733 | 4690 | 4372 | 4397 | 13802 | 19170 | 18523 | 16543 | 54236 | 19170 | 18523 | 16543 | 54236 | - - - | - - - | - - - | - - -
5/2/2026 | 6:45:00 AM | 284.72 | 282.21 | 280.5 | 492.56 | 485.73 | 489.5 | 80.395 | 74.8661 | 72.2314 | 0.2554 | 1.425 | 1.423 | 1.421 | 1.858 | 1.86 | 1.985 | Over-range | 60.01 | 18781 | 18098 | 16236 | 53114 | - - - | - - - | - - - | - - - | 18781 | 18098 | 16236 | 53114 | 12009 | 9700 | 11082 | 32791 | - - - | - - - | - - - | - - - | 12009 | 9700 | 11082 | 32791 | 22757 | 20979 | 20129 | 63865 | # # # | # # # | # # # | # # # | 0.825 | 0.863 | 0.807 | 0.832 | # # # | # # # | # # # | - - - | 0.841 | 0.88 | 0.826 | 0.849 | - - - | 0.617 | 1.72 | 1.58 | 1.55 | 1.53 | 1.54 | 1.57 | 19.07 | 19.32 | 20.8 | 0 | - - - | - - - | - - - | - - - | 22757 | 20979 | 20129 | 63865 | Over-range | 12838 | 10592 | 11884 | 35419 | 4436 | 4161 | 4199 | 13113 | 18791 | 18070 | 16302 | 53163 | 18791 | 18070 | 16302 | 53163 | - - - | - - - | - - - | - - -
5/2/2026 | 7:00:00 AM | 284.67 | 282.16 | 280.46 | 492.46 | 485.63 | 489.44 | 81.2217 | 75.7363 | 72.7009 | 0.2513 | 1.426 | 1.424 | 1.422 | 1.821 | 1.82 | 1.944 | Over-range | 60.01 | 19056 | 18435 | 16462 | 53954 | - - - | - - - | - - - | - - - | 19056 | 18435 | 16462 | 53954 | 12151 | 9762 | 11106 | 33019 | - - - | - - - | - - - | - - - | 12151 | 9762 | 11106 | 33019 | 23007 | 21242 | 20281 | 64530 | # # # | # # # | # # # | # # # | 0.828 | 0.868 | 0.812 | 0.836 | # # # | # # # | # # # | - - - | 0.842 | 0.882 | 0.828 | 0.851 | - - - | 0.612 | 1.72 | 1.58 | 1.61 | 1.55 | 1.57 | 1.61 | 17.57 | 17.67 | 19.23 | 0 | - - - | - - - | - - - | - - - | 23007 | 21242 | 20281 | 64530 | Over-range | 12883 | 10540 | 11835 | 35370 | 4175 | 3874 | 3985 | 12386 | 19088 | 18418 | 16488 | 53994 | 19088 | 18418 | 16488 | 53994 | - - - | - - - | - - - | - - -
5/2/2026 | 7:15:00 AM | 284.54 | 282.05 | 280.27 | 492.28 | 485.38 | 489.12 | 79.5391 | 74.5192 | 71.3241 | 0.2541 | 1.425 | 1.424 | 1.422 | 1.824 | 1.822 | 1.944 | Over-range | 60 | 18514 | 18021 | 16065 | 52599 | - - - | - - - | - - - | - - - | 18514 | 18021 | 16065 | 52599 | 12097 | 9815 | 10966 | 32879 | - - - | - - - | - - - | - - - | 12097 | 9815 | 10966 | 32879 | 22514 | 20890 | 19880 | 63284 | # # # | # # # | # # # | # # # | 0.822 | 0.863 | 0.808 | 0.831 | # # # | # # # | # # # | - - - | 0.837 | 0.877 | 0.824 | 0.846 | - - - | 0.625 | 1.73 | 1.67 | 1.64 | 1.57 | 1.61 | 1.65 | 17.81 | 17.81 | 19.52 | 0 | - - - | - - - | - - - | - - - | 22514 | 20890 | 19880 | 63284 | Over-range | 12806 | 10555 | 11700 | 35164 | 4100 | 3792 | 3986 | 12198 | 18591 | 18013 | 16044 | 52648 | 18591 | 18013 | 16044 | 52648 | - - - | - - - | - - - | - - -
5/2/2026 | 7:30:00 AM | 284.45 | 281.92 | 280.12 | 492.12 | 485.12 | 488.92 | 79.6212 | 74.7841 | 71.3278 | 0.2569 | 1.425 | 1.424 | 1.422 | 1.825 | 1.82 | 1.945 | Over-range | 60.01 | 18570 | 18136 | 16131 | 52837 | - - - | - - - | - - - | - - - | 18570 | 18136 | 16131 | 52837 | 12017 | 9715 | 10826 | 32558 | - - - | - - - | - - - | - - - | 12017 | 9715 | 10826 | 32558 | 22527 | 20954 | 19863 | 63345 | # # # | # # # | # # # | # # # | 0.824 | 0.866 | 0.812 | 0.834 | # # # | # # # | # # # | - - - | 0.839 | 0.88 | 0.829 | 0.849 | - - - | 0.616 | 1.76 | 1.67 | 1.67 | 1.59 | 1.63 | 1.67 | 17.91 | 17.91 | 19.63 | 0 | - - - | - - - | - - - | - - - | 22527 | 20954 | 19863 | 63345 | Over-range | 12746 | 10485 | 11580 | 34913 | 4147 | 3849 | 4014 | 12328 | 18640 | 18124 | 16122 | 52886 | 18640 | 18124 | 16122 | 52886 | - - - | - - - | - - - | - - -
5/2/2026 | 7:45:00 AM | 284.38 | 281.83 | 280.07 | 491.94 | 485 | 488.86 | 80.6589 | 75.7772 | 72.2647 | 0.25 | 1.425 | 1.424 | 1.422 | 1.836 | 1.835 | 1.955 | Over-range | 60 | 18757 | 18315 | 16287 | 53359 | - - - | - - - | - - - | - - - | 18757 | 18315 | 16287 | 53359 | 12100 | 9788 | 10927 | 32816 | - - - | - - - | - - - | - - - | 12100 | 9788 | 10927 | 32816 | 22790 | 21192 | 20096 | 64078 | # # # | # # # | # # # | # # # | 0.823 | 0.864 | 0.811 | 0.833 | # # # | # # # | # # # | - - - | 0.839 | 0.88 | 0.828 | 0.849 | - - - | 0.615 | 1.77 | 1.7 | 1.7 | 1.62 | 1.66 | 1.7 | 18.72 | 18.77 | 20.58 | 0 | - - - | - - - | - - - | - - - | 22790 | 21192 | 20096 | 64078 | Over-range | 12928 | 10641 | 11756 | 35430 | 4442 | 4067 | 4232 | 13051 | 18789 | 18357 | 16265 | 53411 | 18789 | 18357 | 16265 | 53411 | - - - | - - - | - - - | - - -
5/2/2026 | 8:00:00 AM | 284.12 | 281.64 | 279.81 | 491.56 | 484.61 | 488.39 | 80.1811 | 75.5236 | 72.0846 | 0.2554 | 1.425 | 1.424 | 1.422 | 1.839 | 1.841 | 1.958 | Over-range | 60.01 | 18684 | 18264 | 16305 | 53254 | - - - | - - - | - - - | - - - | 18684 | 18264 | 16305 | 53254 | 11951 | 9735 | 10851 | 32537 | - - - | - - - | - - - | - - - | 11951 | 9735 | 10851 | 32537 | 22635 | 21112 | 20036 | 63783 | # # # | # # # | # # # | # # # | 0.826 | 0.865 | 0.814 | 0.835 | # # # | # # # | # # # | - - - | 0.841 | 0.882 | 0.832 | 0.852 | - - - | 0.611 | 1.82 | 1.7 | 1.7 | 1.64 | 1.68 | 1.73 | 18.93 | 19.01 | 20.66 | 0 | - - - | - - - | - - - | - - - | 22635 | 21112 | 20036 | 63783 | Over-range | 12771 | 10579 | 11632 | 35077 | 4418 | 4058 | 4109 | 12870 | 18651 | 18314 | 16346 | 53311 | 18651 | 18314 | 16346 | 53311 | - - - | - - - | - - - | - - -
5/2/2026 | 8:15:00 AM | 283.58 | 281.07 | 279.34 | 490.57 | 483.7 | 487.55 | 81.2546 | 76.4514 | 72.698 | 0.2499 | 1.425 | 1.425 | 1.422 | 1.823 | 1.83 | 1.933 | Over-range | 60 | 18926 | 18532 | 16452 | 53909 | - - - | - - - | - - - | - - - | 18926 | 18532 | 16452 | 53909 | 12168 | 9824 | 10952 | 32945 | - - - | - - - | - - - | - - - | 12168 | 9824 | 10952 | 32945 | 22932 | 21367 | 20203 | 64503 | # # # | # # # | # # # | # # # | 0.825 | 0.867 | 0.814 | 0.836 | # # # | # # # | # # # | - - - | 0.84 | 0.883 | 0.831 | 0.851 | - - - | 0.611 | 1.8 | 1.72 | 1.74 | 1.64 | 1.69 | 1.74 | 18.01 | 18.09 | 19.77 | 0 | - - - | - - - | - - - | - - - | 22932 | 21367 | 20203 | 64503 | Over-range | 12943 | 10624 | 11715 | 35388 | 4310 | 3947 | 4065 | 12646 | 18932 | 18581 | 16445 | 53959 | 18932 | 18581 | 16445 | 53959 | - - - | - - - | - - - | - - -
5/2/2026 | 8:30:00 AM | 283.11 | 280.45 | 278.72 | 489.65 | 482.52 | 486.68 | 80.2293 | 75.1001 | 72.2348 | 0.2565 | 1.425 | 1.425 | 1.422 | 1.822 | 1.843 | 1.942 | Over-range | 60.01 | 18772 | 18158 | 16327 | 53257 | - - - | - - - | - - - | - - - | 18772 | 18158 | 16327 | 53257 | 11749 | 9568 | 10766 | 32083 | - - - | - - - | - - - | - - - | 11749 | 9568 | 10766 | 32083 | 22586 | 20919 | 20015 | 63520 | # # # | # # # | # # # | # # # | 0.831 | 0.868 | 0.816 | 0.838 | # # # | # # # | # # # | - - - | 0.847 | 0.884 | 0.833 | 0.855 | - - - | 0.602 | 1.78 | 1.69 | 1.73 | 1.62 | 1.68 | 1.72 | 18.49 | 18.65 | 20.3 | 0 | - - - | - - - | - - - | - - - | 22586 | 20919 | 20015 | 63520 | Over-range | 12548 | 10374 | 11565 | 34589 | 4318 | 3929 | 4144 | 12686 | 18809 | 18214 | 16289 | 53311 | 18809 | 18214 | 16289 | 53311 | - - - | - - - | - - - | - - -
5/2/2026 | 8:45:00 AM | 282.87 | 280.19 | 278.49 | 489.19 | 482.13 | 486.28 | 82.5762 | 77.3094 | 74.2586 | 0.2576 | 1.425 | 1.426 | 1.422 | 1.846 | 1.862 | 1.951 | Over-range | 60.01 | 19330 | 18688 | 16791 | 54809 | - - - | - - - | - - - | - - - | 19330 | 18688 | 16791 | 54809 | 11958 | 9671 | 10984 | 32613 | - - - | - - - | - - - | - - - | 11958 | 9671 | 10984 | 32613 | 23223 | 21504 | 20555 | 65283 | # # # | # # # | # # # | # # # | 0.832 | 0.869 | 0.817 | 0.84 | # # # | # # # | # # # | - - - | 0.849 | 0.887 | 0.836 | 0.857 | - - - | 0.595 | 1.8 | 1.74 | 1.72 | 1.63 | 1.69 | 1.73 | 19.04 | 19.46 | 20.91 | 0 | - - - | - - - | - - - | - - - | 23223 | 21504 | 20555 | 65283 | Over-range | 12853 | 10618 | 11840 | 35416 | 4613 | 4291 | 4328 | 13541 | 19310 | 18731 | 16830 | 54871 | 19310 | 18731 | 16830 | 54871 | - - - | - - - | - - - | - - -
5/2/2026 | 9:00:00 AM | 282.94 | 280.25 | 278.56 | 489.29 | 482.28 | 486.38 | 80.2696 | 75.5891 | 72.4969 | 0.2518 | 1.425 | 1.426 | 1.423 | 1.871 | 1.891 | 1.97 | Over-range | 60 | 18673 | 18161 | 16340 | 53174 | - - - | - - - | - - - | - - - | 18673 | 18161 | 16340 | 53174 | 11711 | 9544 | 10691 | 31946 | - - - | - - - | - - - | - - - | 11711 | 9544 | 10691 | 31946 | 22533 | 20995 | 20033 | 63562 | # # # | # # # | # # # | # # # | 0.829 | 0.865 | 0.816 | 0.837 | # # # | # # # | # # # | - - - | 0.846 | 0.884 | 0.836 | 0.856 | - - - | 0.601 | 1.81 | 1.74 | 1.74 | 1.64 | 1.7 | 1.74 | 19.88 | 20.34 | 21.78 | 0 | - - - | - - - | - - - | - - - | 22533 | 20995 | 20033 | 63562 | Over-range | 12604 | 10521 | 11578 | 34790 | 4552 | 4333 | 4348 | 13491 | 18682 | 18146 | 16403 | 53230 | 18682 | 18146 | 16403 | 53230 | - - - | - - - | - - - | - - -
5/2/2026 | 9:15:00 AM | 282.61 | 279.94 | 278.15 | 488.8 | 481.58 | 485.73 | 83.6596 | 78.5974 | 74.4371 | 0.263 | 1.423 | 1.424 | 1.421 | 1.84 | 1.854 | 1.946 | Over-range | 60 | 19515 | 19096 | 16865 | 55476 | - - - | - - - | - - - | - - - | 19515 | 19096 | 16865 | 55476 | 12330 | 9817 | 11018 | 33166 | - - - | - - - | - - - | - - - | 12330 | 9817 | 11018 | 33166 | 23536 | 21886 | 20601 | 66023 | # # # | # # # | # # # | # # # | 0.829 | 0.873 | 0.819 | 0.84 | # # # | # # # | # # # | - - - | 0.845 | 0.889 | 0.836 | 0.857 | - - - | 0.598 | 1.75 | 1.7 | 1.66 | 1.58 | 1.65 | 1.68 | 18.46 | 18.74 | 20.33 | 0 | - - - | - - - | - - - | - - - | 23536 | 21886 | 20601 | 66023 | Over-range | 13151 | 10684 | 11821 | 35773 | 4500 | 4146 | 4213 | 13207 | 19514 | 19155 | 16864 | 55533 | 19514 | 19155 | 16864 | 55533 | - - - | - - - | - - - | - - -
5/2/2026 | 9:30:00 AM | 282.38 | 279.57 | 277.89 | 488.27 | 480.97 | 485.4 | 78.9566 | 74.0462 | 70.7491 | 0.2463 | 1.424 | 1.425 | 1.421 | 1.856 | 1.87 | 1.969 | Over-range | 59.99 | 18315 | 17811 | 15891 | 52017 | - - - | - - - | - - - | - - - | 18315 | 17811 | 15891 | 52017 | 11625 | 9349 | 10524 | 31497 | - - - | - - - | - - - | - - - | 11625 | 9349 | 10524 | 31497 | 22156 | 20550 | 19530 | 62236 | # # # | # # # | # # # | # # # | 0.827 | 0.867 | 0.814 | 0.836 | # # # | # # # | # # # | - - - | 0.843 | 0.884 | 0.833 | 0.853 | - - - | 0.606 | 1.76 | 1.7 | 1.67 | 1.58 | 1.65 | 1.68 | 19.27 | 19.43 | 21.07 | 0 | - - - | - - - | - - - | - - - | 22156 | 20550 | 19530 | 62236 | Over-range | 12460 | 10237 | 11340 | 34137 | 4383 | 4078 | 4129 | 12885 | 18317 | 17807 | 15944 | 52069 | 18317 | 17807 | 15944 | 52069 | - - - | - - - | - - - | - - -
5/2/2026 | 9:45:00 AM | 282.06 | 279.14 | 277.42 | 487.65 | 480.14 | 484.72 | 81.1122 | 75.8454 | 71.8581 | 0.2554 | 1.423 | 1.425 | 1.421 | 1.858 | 1.865 | 1.969 | Over-range | 60.01 | 18823 | 18330 | 16146 | 53299 | - - - | - - - | - - - | - - - | 18823 | 18330 | 16146 | 53299 | 11898 | 9340 | 10601 | 31839 | - - - | - - - | - - - | - - - | 11898 | 9340 | 10601 | 31839 | 22737 | 21017 | 19801 | 63554 | # # # | # # # | # # # | # # # | 0.828 | 0.872 | 0.815 | 0.839 | # # # | # # # | # # # | - - - | 0.844 | 0.889 | 0.834 | 0.856 | - - - | 0.597 | 1.67 | 1.67 | 1.64 | 1.53 | 1.62 | 1.63 | 18.93 | 19.17 | 20.88 | 0 | - - - | - - - | - - - | - - - | 22737 | 21017 | 19801 | 63554 | Over-range | 12740 | 10256 | 11445 | 34565 | 4444 | 4142 | 4213 | 13167 | 18860 | 18317 | 16170 | 53347 | 18860 | 18317 | 16170 | 53347 | - - - | - - - | - - - | - - -
5/2/2026 | 10:00:00 AM | 282.21 | 279.43 | 277.67 | 488.03 | 480.67 | 485.01 | 80.8537 | 75.7792 | 71.9147 | 0.2544 | 1.424 | 1.425 | 1.422 | 1.841 | 1.85 | 1.947 | Over-range | 60 | 18785 | 18332 | 16204 | 53321 | - - - | - - - | - - - | - - - | 18785 | 18332 | 16204 | 53321 | 12003 | 9547 | 10725 | 32274 | - - - | - - - | - - - | - - - | 12003 | 9547 | 10725 | 32274 | 22716 | 21063 | 19874 | 63653 | # # # | # # # | # # # | # # # | 0.827 | 0.87 | 0.815 | 0.838 | # # # | # # # | # # # | - - - | 0.842 | 0.886 | 0.833 | 0.854 | - - - | 0.605 | 1.7 | 1.69 | 1.66 | 1.56 | 1.63 | 1.65 | 18.33 | 18.49 | 20.15 | 0 | - - - | - - - | - - - | - - - | 22716 | 21063 | 19874 | 63653 | Over-range | 12768 | 10362 | 11497 | 34741 | 4273 | 3957 | 4070 | 12645 | 18836 | 18334 | 16201 | 53371 | 18836 | 18334 | 16201 | 53371 | - - - | - - - | - - - | - - -
5/2/2026 | 10:15:00 AM | 281.98 | 279.12 | 277.51 | 487.53 | 480.25 | 484.73 | 80.7091 | 75.3461 | 71.8486 | 0.2506 | 1.424 | 1.425 | 1.422 | 1.836 | 1.846 | 1.956 | Over-range | 60 | 18754 | 18188 | 16142 | 53084 | - - - | - - - | - - - | - - - | 18754 | 18188 | 16142 | 53084 | 11825 | 9354 | 10639 | 31819 | - - - | - - - | - - - | - - - | 11825 | 9354 | 10639 | 31819 | 22596 | 20855 | 19787 | 63238 | # # # | # # # | # # # | # # # | 0.83 | 0.872 | 0.816 | 0.839 | # # # | # # # | # # # | - - - | 0.846 | 0.887 | 0.834 | 0.856 | - - - | 0.599 | 1.7 | 1.65 | 1.64 | 1.54 | 1.62 | 1.64 | 18.32 | 18.46 | 20.17 | 0 | - - - | - - - | - - - | - - - | 22596 | 20855 | 19787 | 63238 | Over-range | 12595 | 10189 | 11430 | 34332 | 4217 | 3930 | 4070 | 12574 | 18821 | 18151 | 16162 | 53134 | 18821 | 18151 | 16162 | 53134 | - - - | - - - | - - - | - - -
5/2/2026 | 10:30:00 AM | 281.78 | 278.94 | 277.31 | 487.22 | 479.92 | 484.38 | 81.164 | 75.7023 | 72.2699 | 0.2595 | 1.424 | 1.425 | 1.422 | 1.838 | 1.846 | 1.958 | Over-range | 60.01 | 18884 | 18295 | 16250 | 53429 | - - - | - - - | - - - | - - - | 18884 | 18295 | 16250 | 53429 | 11946 | 9466 | 10769 | 32181 | - - - | - - - | - - - | - - - | 11946 | 9466 | 10769 | 32181 | 22764 | 21000 | 19941 | 63706 | # # # | # # # | # # # | # # # | 0.83 | 0.871 | 0.815 | 0.839 | # # # | # # # | # # # | - - - | 0.845 | 0.886 | 0.833 | 0.855 | - - - | 0.602 | 1.67 | 1.64 | 1.6 | 1.52 | 1.6 | 1.6 | 18.34 | 18.53 | 20.16 | 0 | - - - | - - - | - - - | - - - | 22764 | 21000 | 19941 | 63706 | Over-range | 12707 | 10298 | 11548 | 34669 | 4243 | 3977 | 4092 | 12667 | 18949 | 18253 | 16276 | 53477 | 18949 | 18253 | 16276 | 53477 | - - - | - - - | - - - | - - -
5/2/2026 | 10:45:00 AM | 281.41 | 278.46 | 276.89 | 486.42 | 479.13 | 483.75 | 81.0564 | 75.3455 | 72.4411 | 0.2539 | 1.424 | 1.425 | 1.422 | 1.831 | 1.844 | 1.95 | Over-range | 60.01 | 18854 | 18137 | 16223 | 53214 | - - - | - - - | - - - | - - - | 18854 | 18137 | 16223 | 53214 | 11780 | 9408 | 10765 | 31954 | - - - | - - - | - - - | - - - | 11780 | 9408 | 10765 | 31954 | 22668 | 20828 | 19924 | 63420 | # # # | # # # | # # # | # # # | 0.832 | 0.871 | 0.814 | 0.839 | # # # | # # # | # # # | - - - | 0.847 | 0.886 | 0.831 | 0.855 | - - - | 0.601 | 1.65 | 1.67 | 1.61 | 1.52 | 1.6 | 1.61 | 18.15 | 18.24 | 19.96 | 0 | - - - | - - - | - - - | - - - | 22668 | 20828 | 19924 | 63420 | Over-range | 12568 | 10215 | 11546 | 34443 | 4261 | 3863 | 4066 | 12532 | 18893 | 18171 | 16201 | 53265 | 18893 | 18171 | 16201 | 53265 | - - - | - - - | - - - | - - -
5/2/2026 | 11:00:00 AM | 281.35 | 278.4 | 276.86 | 486.34 | 479.01 | 483.68 | 80.4987 | 74.8914 | 71.2781 | 0.2532 | 1.424 | 1.425 | 1.422 | 1.823 | 1.83 | 1.954 | Over-range | 60 | 18670 | 18090 | 15970 | 52729 | - - - | - - - | - - - | - - - | 18670 | 18090 | 15970 | 52729 | 11809 | 9284 | 10636 | 31729 | - - - | - - - | - - - | - - - | 11809 | 9284 | 10636 | 31729 | 22507 | 20697 | 19598 | 62802 | # # # | # # # | # # # | # # # | 0.83 | 0.874 | 0.815 | 0.84 | # # # | # # # | # # # | - - - | 0.844 | 0.889 | 0.831 | 0.855 | - - - | 0.602 | 1.68 | 1.66 | 1.62 | 1.53 | 1.61 | 1.62 | 17.87 | 17.75 | 19.69 | 0 | - - - | - - - | - - - | - - - | 22507 | 20697 | 19598 | 62802 | Over-range | 12561 | 10042 | 11347 | 34081 | 4184 | 3732 | 3862 | 12168 | 18643 | 18146 | 15992 | 52781 | 18643 | 18146 | 15992 | 52781 | - - - | - - - | - - - | - - -
5/2/2026 | 11:15:00 AM | 280.93 | 278.01 | 276.42 | 485.65 | 478.31 | 482.93 | 79.3111 | 73.8552 | 70.8651 | 0.2558 | 1.424 | 1.425 | 1.421 | 1.809 | 1.813 | 1.931 | Over-range | 60.01 | 18445 | 17806 | 15905 | 52156 | - - - | - - - | - - - | - - - | 18445 | 17806 | 15905 | 52156 | 11626 | 9277 | 10587 | 31490 | - - - | - - - | - - - | - - - | 11626 | 9277 | 10587 | 31490 | 22183 | 20428 | 19494 | 62105 | # # # | # # # | # # # | # # # | 0.832 | 0.872 | 0.816 | 0.84 | # # # | # # # | # # # | - - - | 0.845 | 0.885 | 0.832 | 0.854 | - - - | 0.604 | 1.65 | 1.64 | 1.61 | 1.51 | 1.59 | 1.6 | 17.35 | 17.15 | 18.94 | 0 | - - - | - - - | - - - | - - - | 22183 | 20428 | 19494 | 62105 | Over-range | 12317 | 9999 | 11261 | 33689 | 3977 | 3646 | 3749 | 11719 | 18453 | 17785 | 15966 | 52203 | 18453 | 17785 | 15966 | 52203 | - - - | - - - | - - - | - - -
5/2/2026 | 11:30:00 AM | 280.43 | 277.48 | 275.89 | 484.74 | 477.4 | 482.03 | 80.7554 | 75.1232 | 71.3514 | 0.2469 | 1.424 | 1.425 | 1.422 | 1.809 | 1.812 | 1.924 | Over-range | 60 | 18719 | 18148 | 15986 | 52852 | - - - | - - - | - - - | - - - | 18719 | 18148 | 15986 | 52852 | 11832 | 9223 | 10566 | 31621 | - - - | - - - | - - - | - - - | 11832 | 9223 | 10566 | 31621 | 22518 | 20705 | 19563 | 62785 | # # # | # # # | # # # | # # # | 0.831 | 0.876 | 0.817 | 0.842 | # # # | # # # | # # # | - - - | 0.845 | 0.89 | 0.833 | 0.856 | - - - | 0.598 | 1.64 | 1.65 | 1.59 | 1.5 | 1.59 | 1.59 | 17.01 | 17.05 | 18.83 | 0 | - - - | - - - | - - - | - - - | 22518 | 20705 | 19563 | 62785 | Over-range | 12507 | 9953 | 11265 | 33859 | 3941 | 3640 | 3807 | 11810 | 18791 | 18114 | 15989 | 52895 | 18791 | 18114 | 15989 | 52895 | - - - | - - - | - - - | - - -
5/2/2026 | 11:45:00 AM | 280.43 | 277.62 | 275.99 | 484.84 | 477.67 | 482.08 | 80.6025 | 74.9687 | 72.6105 | 0.262 | 1.425 | 1.426 | 1.423 | 1.824 | 1.841 | 1.964 | Over-range | 60.01 | 18736 | 17960 | 16238 | 52934 | - - - | - - - | - - - | - - - | 18736 | 17960 | 16238 | 52934 | 11530 | 9345 | 10690 | 31565 | - - - | - - - | - - - | - - - | 11530 | 9345 | 10690 | 31565 | 22449 | 20642 | 19900 | 62991 | # # # | # # # | # # # | # # # | 0.835 | 0.87 | 0.816 | 0.84 | # # # | # # # | # # # | - - - | 0.85 | 0.885 | 0.834 | 0.857 | - - - | 0.596 | 1.62 | 1.62 | 1.58 | 1.49 | 1.56 | 1.57 | 18.58 | 18.17 | 20.22 | 0 | - - - | - - - | - - - | - - - | 22449 | 20642 | 19900 | 62991 | Over-range | 12352 | 10150 | 11486 | 34092 | 4316 | 3862 | 4101 | 12585 | 18754 | 17977 | 16259 | 52990 | 18754 | 17977 | 16259 | 52990 | - - - | - - - | - - - | - - -
5/2/2026 | 12:00:00 PM | 280.73 | 277.81 | 276.23 | 485.3 | 477.97 | 482.59 | 83.3456 | 76.9696 | 74.6892 | 0.2593 | 1.424 | 1.425 | 1.422 | 1.815 | 1.84 | 1.962 | Over-range | 60.01 | 19562 | 18636 | 16805 | 55003 | - - - | - - - | - - - | - - - | 19562 | 18636 | 16805 | 55003 | 11795 | 9411 | 10981 | 32187 | - - - | - - - | - - - | - - - | 11795 | 9411 | 10981 | 32187 | 23288 | 21263 | 20520 | 65072 | # # # | # # # | # # # | # # # | 0.84 | 0.876 | 0.819 | 0.845 | # # # | # # # | # # # | - - - | 0.855 | 0.892 | 0.836 | 0.861 | - - - | 0.585 | 1.63 | 1.63 | 1.61 | 1.5 | 1.58 | 1.58 | 18.28 | 18.01 | 20.08 | 0 | - - - | - - - | - - - | - - - | 23288 | 21263 | 20520 | 65072 | Over-range | 12624 | 10227 | 11766 | 34743 | 4411 | 3921 | 4144 | 12839 | 19538 | 18673 | 16842 | 55053 | 19538 | 18673 | 16842 | 55053 | - - - | - - - | - - - | - - -
5/2/2026 | 12:15:00 PM | 282.27 | 279.28 | 277.7 | 487.91 | 480.46 | 485.25 | 78.585 | 73.075 | 70.0891 | 0.2614 | 1.426 | 1.426 | 1.424 | 1.853 | 1.859 | 1.96 | Over-range | 59.98 | 18200 | 17544 | 15640 | 51384 | - - - | - - - | - - - | - - - | 18200 | 17544 | 15640 | 51384 | 11581 | 9208 | 10539 | 31328 | - - - | - - - | - - - | - - - | 11581 | 9208 | 10539 | 31328 | 22013 | 20227 | 19309 | 61549 | # # # | # # # | # # # | # # # | 0.827 | 0.867 | 0.81 | 0.835 | # # # | # # # | # # # | - - - | 0.843 | 0.884 | 0.829 | 0.852 | - - - | 0.61 | 1.6 | 1.56 | 1.53 | 1.45 | 1.52 | 1.52 | 18.92 | 19.04 | 20.68 | 0 | - - - | - - - | - - - | - - - | 22013 | 20227 | 19309 | 61549 | Over-range | 12374 | 10051 | 11310 | 33845 | 4251 | 3936 | 4005 | 12525 | 18209 | 17528 | 15705 | 51442 | 18209 | 17528 | 15705 | 51442 | - - - | - - - | - - - | - - -
5/2/2026 | 12:30:00 PM | 282.19 | 279.21 | 277.57 | 487.77 | 480.32 | 485.05 | 80.8785 | 75.2674 | 71.5049 | 0.2636 | 1.425 | 1.425 | 1.423 | 1.843 | 1.847 | 1.942 | Over-range | 59.99 | 18796 | 18215 | 16052 | 53063 | - - - | - - - | - - - | - - - | 18796 | 18215 | 16052 | 53063 | 11892 | 9307 | 10685 | 31884 | - - - | - - - | - - - | - - - | 11892 | 9307 | 10685 | 31884 | 22684 | 20864 | 19718 | 63265 | # # # | # # # | # # # | # # # | 0.829 | 0.873 | 0.814 | 0.839 | # # # | # # # | # # # | - - - | 0.843 | 0.889 | 0.832 | 0.855 | - - - | 0.601 | 1.57 | 1.56 | 1.51 | 1.43 | 1.5 | 1.5 | 18.32 | 18.62 | 20.1 | 0 | - - - | - - - | - - - | - - - | 22684 | 20864 | 19718 | 63265 | Over-range | 12690 | 10160 | 11439 | 34418 | 4328 | 3982 | 3986 | 12685 | 18767 | 18250 | 16099 | 53115 | 18767 | 18250 | 16099 | 53115 | - - - | - - - | - - - | - - -
5/2/2026 | 12:45:00 PM | 282.08 | 279.03 | 277.48 | 487.5 | 480.04 | 484.93 | 80.4062 | 74.8733 | 71.4783 | 0.2618 | 1.425 | 1.426 | 1.424 | 1.842 | 1.847 | 1.938 | Over-range | 59.99 | 18647 | 18042 | 16004 | 52693 | - - - | - - - | - - - | - - - | 18647 | 18042 | 16004 | 52693 | 11902 | 9447 | 10737 | 32085 | - - - | - - - | - - - | - - - | 11902 | 9447 | 10737 | 32085 | 22564 | 20763 | 19720 | 63047 | # # # | # # # | # # # | # # # | 0.826 | 0.869 | 0.812 | 0.836 | # # # | # # # | # # # | - - - | 0.842 | 0.885 | 0.829 | 0.852 | - - - | 0.609 | 1.59 | 1.57 | 1.54 | 1.45 | 1.52 | 1.52 | 18.36 | 18.52 | 20.15 | 0 | - - - | - - - | - - - | - - - | 22564 | 20763 | 19720 | 63047 | Over-range | 12689 | 10255 | 11507 | 34569 | 4314 | 3907 | 4060 | 12631 | 18674 | 18095 | 15982 | 52750 | 18674 | 18095 | 15982 | 52750 | - - - | - - - | - - - | - - -
5/2/2026 | 1:00:00 PM | 282.25 | 279.25 | 277.66 | 487.83 | 480.41 | 485.22 | 80.6588 | 75.1063 | 71.614 | 0.2629 | 1.425 | 1.425 | 1.423 | 1.834 | 1.845 | 1.948 | Over-range | 59.99 | 18749 | 18137 | 16081 | 52967 | - - - | - - - | - - - | - - - | 18749 | 18137 | 16081 | 52967 | 11808 | 9343 | 10658 | 31809 | - - - | - - - | - - - | - - - | 11808 | 9343 | 10658 | 31809 | 22596 | 20792 | 19735 | 63123 | # # # | # # # | # # # | # # # | 0.83 | 0.872 | 0.815 | 0.839 | # # # | # # # | # # # | - - - | 0.845 | 0.888 | 0.832 | 0.855 | - - - | 0.601 | 1.55 | 1.52 | 1.46 | 1.39 | 1.46 | 1.45 | 18.38 | 18.46 | 20.19 | 0 | - - - | - - - | - - - | - - - | 22596 | 20792 | 19735 | 63123 | Over-range | 12605 | 10150 | 11427 | 34304 | 4300 | 3864 | 4025 | 12552 | 18753 | 18202 | 16063 | 53018 | 18753 | 18202 | 16063 | 53018 | - - - | - - - | - - - | - - -
5/2/2026 | 1:15:00 PM | 282.26 | 279.26 | 277.71 | 487.78 | 480.53 | 485.28 | 81.4922 | 75.6195 | 72.5912 | 0.2658 | 1.427 | 1.426 | 1.424 | 1.825 | 1.841 | 1.947 | Over-range | 59.99 | 18936 | 18228 | 16242 | 53406 | - - - | - - - | - - - | - - - | 18936 | 18228 | 16242 | 53406 | 12047 | 9593 | 10988 | 32628 | - - - | - - - | - - - | - - - | 12047 | 9593 | 10988 | 32628 | 22862 | 20968 | 20032 | 63862 | # # # | # # # | # # # | # # # | 0.828 | 0.869 | 0.811 | 0.836 | # # # | # # # | # # # | - - - | 0.843 | 0.885 | 0.827 | 0.852 | - - - | 0.611 | 1.52 | 1.51 | 1.41 | 1.38 | 1.42 | 1.42 | 17.99 | 18.04 | 19.77 | 0 | - - - | - - - | - - - | - - - | 22862 | 20968 | 20032 | 63862 | Over-range | 12804 | 10352 | 11716 | 34993 | 4244 | 3807 | 3986 | 12401 | 18943 | 18287 | 16230 | 53460 | 18943 | 18287 | 16230 | 53460 | - - - | - - - | - - - | - - -
5/2/2026 | 1:30:00 PM | 282.34 | 279.27 | 277.78 | 487.92 | 480.5 | 485.44 | 81.559 | 75.7285 | 72.7135 | 0.2641 | 1.427 | 1.427 | 1.425 | 1.843 | 1.867 | 1.971 | Over-range | 59.99 | 18992 | 18268 | 16304 | 53564 | - - - | - - - | - - - | - - - | 18992 | 18268 | 16304 | 53564 | 11900 | 9438 | 10820 | 32158 | - - - | - - - | - - - | - - - | 11900 | 9438 | 10820 | 32158 | 22869 | 20983 | 20054 | 63906 | # # # | # # # | # # # | # # # | 0.83 | 0.871 | 0.813 | 0.838 | # # # | # # # | # # # | - - - | 0.847 | 0.887 | 0.831 | 0.855 | - - - | 0.6 | 1.53 | 1.51 | 1.44 | 1.4 | 1.44 | 1.44 | 18.87 | 19.07 | 20.89 | 0 | - - - | - - - | - - - | - - - | 22869 | 20983 | 20054 | 63906 | Over-range | 12732 | 10308 | 11663 | 34821 | 4413 | 4044 | 4249 | 13051 | 19043 | 18282 | 16294 | 53619 | 19043 | 18282 | 16294 | 53619 | - - - | - - - | - - - | - - -
5/2/2026 | 1:45:00 PM | 282.42 | 279.37 | 277.8 | 488.1 | 480.6 | 485.51 | 82.8619 | 76.7748 | 73.443 | 0.265 | 1.427 | 1.426 | 1.424 | 1.858 | 1.875 | 1.977 | Over-range | 59.99 | 19211 | 18491 | 16374 | 54076 | - - - | - - - | - - - | - - - | 19211 | 18491 | 16374 | 54076 | 12185 | 9534 | 11006 | 32724 | - - - | - - - | - - - | - - - | 12185 | 9534 | 11006 | 32724 | 23240 | 21276 | 20251 | 64768 | # # # | # # # | # # # | # # # | 0.827 | 0.869 | 0.809 | 0.835 | # # # | # # # | # # # | - - - | 0.843 | 0.886 | 0.828 | 0.853 | - - - | 0.605 | 1.54 | 1.5 | 1.42 | 1.4 | 1.43 | 1.42 | 19.26 | 19.7 | 21.36 | 0 | - - - | - - - | - - - | - - - | 23240 | 21276 | 20251 | 64768 | Over-range | 13061 | 10498 | 11896 | 35586 | 4580 | 4289 | 4407 | 13663 | 19270 | 18460 | 16397 | 54127 | 19270 | 18460 | 16397 | 54127 | - - - | - - - | - - - | - - -
5/2/2026 | 2:00:00 PM | 282.25 | 279.17 | 277.67 | 487.72 | 480.35 | 485.27 | 80.7088 | 74.839 | 71.9222 | 0.262 | 1.427 | 1.426 | 1.424 | 1.876 | 1.902 | 2.003 | Over-range | 59.99 | 18796 | 18047 | 16104 | 52947 | - - - | - - - | - - - | - - - | 18796 | 18047 | 16104 | 52947 | 11734 | 9259 | 10676 | 31670 | - - - | - - - | - - - | - - - | 11734 | 9259 | 10676 | 31670 | 22644 | 20747 | 19846 | 63237 | # # # | # # # | # # # | # # # | 0.83 | 0.87 | 0.812 | 0.837 | # # # | # # # | # # # | - - - | 0.848 | 0.888 | 0.832 | 0.856 | - - - | 0.598 | 1.5 | 1.46 | 1.38 | 1.38 | 1.39 | 1.38 | 19.96 | 20.33 | 22.12 | 0 | - - - | - - - | - - - | - - - | 22644 | 20747 | 19846 | 63237 | Over-range | 12621 | 10220 | 11586 | 34544 | 4555 | 4244 | 4415 | 13551 | 18856 | 18030 | 16115 | 53001 | 18856 | 18030 | 16115 | 53001 | - - - | - - - | - - - | - - -
5/2/2026 | 2:15:00 PM | 282.39 | 279.27 | 277.85 | 487.92 | 480.57 | 485.58 | 81.2624 | 74.9847 | 71.8872 | 0.2628 | 1.427 | 1.426 | 1.423 | 1.867 | 1.888 | 1.998 | Over-range | 59.99 | 18904 | 18123 | 16058 | 53085 | - - - | - - - | - - - | - - - | 18904 | 18123 | 16058 | 53085 | 11889 | 9285 | 10792 | 31966 | - - - | - - - | - - - | - - - | 11889 | 9285 | 10792 | 31966 | 22815 | 20799 | 19851 | 63465 | # # # | # # # | # # # | # # # | 0.829 | 0.871 | 0.809 | 0.836 | # # # | # # # | # # # | - - - | 0.846 | 0.889 | 0.828 | 0.855 | - - - | 0.602 | 1.49 | 1.44 | 1.37 | 1.37 | 1.38 | 1.37 | 19.48 | 19.74 | 21.6 | 0 | - - - | - - - | - - - | - - - | 22815 | 20799 | 19851 | 63465 | Over-range | 12765 | 10193 | 11661 | 34754 | 4551 | 4118 | 4335 | 13386 | 18940 | 18175 | 16021 | 53136 | 18940 | 18175 | 16021 | 53136 | - - - | - - - | - - - | - - -
5/2/2026 | 2:30:00 PM | 282.38 | 279.22 | 277.85 | 487.85 | 480.51 | 485.6 | 80.4983 | 74.3874 | 71.634 | 0.2606 | 1.427 | 1.426 | 1.423 | 1.858 | 1.875 | 1.995 | Over-range | 59.98 | 18719 | 17920 | 16001 | 52639 | - - - | - - - | - - - | - - - | 18719 | 17920 | 16001 | 52639 | 11811 | 9317 | 10778 | 31906 | - - - | - - - | - - - | - - - | 11811 | 9317 | 10778 | 31906 | 22569 | 20597 | 19760 | 62926 | # # # | # # # | # # # | # # # | 0.829 | 0.87 | 0.81 | 0.837 | # # # | # # # | # # # | - - - | 0.846 | 0.886 | 0.828 | 0.853 | - - - | 0.606 | 1.48 | 1.45 | 1.34 | 1.35 | 1.37 | 1.34 | 18.99 | 18.97 | 20.93 | 0 | - - - | - - - | - - - | - - - | 22569 | 20597 | 19760 | 62926 | Over-range | 12603 | 10140 | 11583 | 34450 | 4309 | 3921 | 4164 | 12756 | 18783 | 17907 | 16002 | 52692 | 18783 | 17907 | 16002 | 52692 | - - - | - - - | - - - | - - -
5/2/2026 | 2:45:00 PM | 282.1 | 278.95 | 277.6 | 487.35 | 480.06 | 485.17 | 81.2165 | 74.7205 | 71.7445 | 0.2606 | 1.427 | 1.426 | 1.423 | 1.835 | 1.85 | 1.98 | Over-range | 59.98 | 18847 | 18032 | 15963 | 52843 | - - - | - - - | - - - | - - - | 18847 | 18032 | 15963 | 52843 | 11985 | 9296 | 10906 | 32188 | - - - | - - - | - - - | - - - | 11985 | 9296 | 10906 | 32188 | 22767 | 20686 | 19779 | 63232 | # # # | # # # | # # # | # # # | 0.828 | 0.872 | 0.807 | 0.836 | # # # | # # # | # # # | - - - | 0.842 | 0.887 | 0.825 | 0.851 | - - - | 0.609 | 1.45 | 1.42 | 1.36 | 1.34 | 1.36 | 1.33 | 18.18 | 18.11 | 20.1 | 0 | - - - | - - - | - - - | - - - | 22767 | 20686 | 19779 | 63232 | Over-range | 12755 | 10111 | 11660 | 34669 | 4248 | 3871 | 4016 | 12573 | 18849 | 18011 | 16023 | 52884 | 18849 | 18011 | 16023 | 52884 | - - - | - - - | - - - | - - -
5/2/2026 | 3:00:00 PM | 282.45 | 279.35 | 277.92 | 488 | 480.72 | 485.7 | 79.6892 | 73.2667 | 71.1096 | 0.2597 | 1.427 | 1.426 | 1.422 | 1.829 | 1.839 | 1.976 | Over-range | 59.98 | 18512 | 17609 | 15795 | 51916 | - - - | - - - | - - - | - - - | 18512 | 17609 | 15795 | 51916 | 11821 | 9367 | 10921 | 32109 | - - - | - - - | - - - | - - - | 11821 | 9367 | 10921 | 32109 | 22356 | 20305 | 19622 | 62283 | # # # | # # # | # # # | # # # | 0.828 | 0.867 | 0.805 | 0.834 | # # # | # # # | # # # | - - - | 0.842 | 0.881 | 0.822 | 0.848 | - - - | 0.619 | 1.46 | 1.43 | 1.32 | 1.34 | 1.36 | 1.33 | 17.83 | 17.59 | 19.57 | 0 | - - - | - - - | - - - | - - - | 22356 | 20305 | 19622 | 62283 | Over-range | 12527 | 10097 | 11630 | 34379 | 4043 | 3678 | 3904 | 12009 | 18557 | 17565 | 15835 | 51958 | 18557 | 17565 | 15835 | 51958 | - - - | - - - | - - - | - - -
5/2/2026 | 3:15:00 PM | 282.16 | 279.01 | 277.61 | 487.5 | 480.1 | 485.21 | 82.1049 | 75.3717 | 72.4252 | 0.2606 | 1.427 | 1.426 | 1.423 | 1.825 | 1.836 | 1.968 | Over-range | 60 | 19099 | 18241 | 16136 | 53476 | - - - | - - - | - - - | - - - | 19099 | 18241 | 16136 | 53476 | 12162 | 9421 | 11042 | 32625 | - - - | - - - | - - - | - - - | 12162 | 9421 | 11042 | 32625 | 23037 | 20890 | 19981 | 63908 | # # # | # # # | # # # | # # # | 0.829 | 0.873 | 0.808 | 0.837 | # # # | # # # | # # # | - - - | 0.843 | 0.887 | 0.824 | 0.852 | - - - | 0.61 | 1.45 | 1.43 | 1.33 | 1.34 | 1.35 | 1.33 | 17.63 | 17.53 | 19.58 | 0 | - - - | - - - | - - - | - - - | 23037 | 20890 | 19981 | 63908 | Over-range | 12874 | 10170 | 11775 | 34968 | 4125 | 3741 | 3998 | 12321 | 19168 | 18218 | 16135 | 53520 | 19168 | 18218 | 16135 | 53520 | - - - | - - - | - - - | - - -
5/2/2026 | 3:30:00 PM | 282.14 | 279.03 | 277.54 | 487.53 | 480.05 | 485.09 | 79.0761 | 72.8109 | 70.2093 | 0.2568 | 1.426 | 1.425 | 1.423 | 1.841 | 1.846 | 1.979 | Over-range | 59.99 | 18333 | 17526 | 15599 | 51458 | - - - | - - - | - - - | - - - | 18333 | 17526 | 15599 | 51458 | 11760 | 9246 | 10738 | 31744 | - - - | - - - | - - - | - - - | 11760 | 9246 | 10738 | 31744 | 22189 | 20189 | 19370 | 61747 | # # # | # # # | # # # | # # # | 0.826 | 0.868 | 0.805 | 0.833 | # # # | # # # | # # # | - - - | 0.841 | 0.883 | 0.823 | 0.849 | - - - | 0.617 | 1.47 | 1.43 | 1.35 | 1.34 | 1.36 | 1.34 | 18.22 | 18.01 | 19.98 | 0 | - - - | - - - | - - - | - - - | 22189 | 20189 | 19370 | 61747 | Over-range | 12493 | 10010 | 11472 | 34102 | 4117 | 3746 | 3948 | 12198 | 18385 | 17487 | 15632 | 51503 | 18385 | 17487 | 15632 | 51503 | - - - | - - - | - - - | - - -
5/2/2026 | 3:45:00 PM | 282.26 | 279.17 | 277.69 | 487.7 | 480.39 | 485.29 | 83.2299 | 76.965 | 73.446 | 0.2647 | 1.426 | 1.425 | 1.422 | 1.849 | 1.857 | 1.974 | Over-range | 59.98 | 19340 | 18627 | 16418 | 54384 | - - - | - - - | - - - | - - - | 19340 | 18627 | 16418 | 54384 | 12322 | 9554 | 11109 | 32985 | - - - | - - - | - - - | - - - | 12322 | 9554 | 11109 | 32985 | 23370 | 21348 | 20274 | 64992 | # # # | # # # | # # # | # # # | 0.828 | 0.873 | 0.81 | 0.837 | # # # | # # # | # # # | - - - | 0.842 | 0.888 | 0.828 | 0.853 | - - - | 0.607 | 1.48 | 1.44 | 1.31 | 1.35 | 1.35 | 1.33 | 18.26 | 18.45 | 20.24 | 0 | - - - | - - - | - - - | - - - | 23370 | 21348 | 20274 | 64992 | Over-range | 13107 | 10410 | 11881 | 35542 | 4381 | 4052 | 4129 | 13001 | 19349 | 18608 | 16478 | 54435 | 19349 | 18608 | 16478 | 54435 | - - - | - - - | - - - | - - -
5/2/2026 | 4:00:00 PM | 282.09 | 278.93 | 277.53 | 487.38 | 479.98 | 485.04 | 79.5429 | 73.3892 | 70.9793 | 0.2592 | 1.426 | 1.425 | 1.422 | 1.861 | 1.873 | 1.995 | Over-range | 59.98 | 18463 | 17630 | 15789 | 51882 | - - - | - - - | - - - | - - - | 18463 | 17630 | 15789 | 51882 | 11697 | 9298 | 10795 | 31789 | - - - | - - - | - - - | - - - | 11697 | 9298 | 10795 | 31789 | 22320 | 20344 | 19588 | 62252 | # # # | # # # | # # # | # # # | 0.827 | 0.867 | 0.806 | 0.833 | # # # | # # # | # # # | - - - | 0.843 | 0.883 | 0.825 | 0.851 | - - - | 0.613 | 1.48 | 1.43 | 1.32 | 1.35 | 1.35 | 1.34 | 19.17 | 19.08 | 21.02 | 0 | - - - | - - - | - - - | - - - | 22320 | 20344 | 19588 | 62252 | Over-range | 12536 | 10141 | 11582 | 34377 | 4416 | 3963 | 4109 | 12830 | 18430 | 17665 | 15837 | 51932 | 18430 | 17665 | 15837 | 51932 | - - - | - - - | - - - | - - -
5/2/2026 | 4:15:00 PM | 282.12 | 279.01 | 277.49 | 487.49 | 479.98 | 485.05 | 81.7747 | 75.4809 | 72.2375 | 0.2616 | 1.427 | 1.425 | 1.423 | 1.849 | 1.851 | 1.983 | Over-range | 59.99 | 19050 | 18292 | 16176 | 53518 | - - - | - - - | - - - | - - - | 19050 | 18292 | 16176 | 53518 | 11970 | 9319 | 10862 | 32151 | - - - | - - - | - - - | - - - | 11970 | 9319 | 10862 | 32151 | 22948 | 20927 | 19929 | 63804 | # # # | # # # | # # # | # # # | 0.83 | 0.874 | 0.812 | 0.839 | # # # | # # # | # # # | - - - | 0.845 | 0.89 | 0.83 | 0.855 | - - - | 0.601 | 1.47 | 1.42 | 1.35 | 1.35 | 1.36 | 1.34 | 18.62 | 18.5 | 20.44 | 0 | - - - | - - - | - - - | - - - | 22948 | 20927 | 19929 | 63804 | Over-range | 12788 | 10152 | 11629 | 34708 | 4403 | 3938 | 4061 | 12814 | 19017 | 18332 | 16217 | 53565 | 19017 | 18332 | 16217 | 53565 | - - - | - - - | - - - | - - -
5/2/2026 | 4:30:00 PM | 282.07 | 278.95 | 277.47 | 487.37 | 479.96 | 484.99 | 79.8798 | 73.7778 | 71.1871 | 0.2609 | 1.426 | 1.425 | 1.422 | 1.871 | 1.885 | 2.001 | Over-range | 59.97 | 18489 | 17682 | 15800 | 51972 | - - - | - - - | - - - | - - - | 18489 | 17682 | 15800 | 51972 | 11708 | 9299 | 10758 | 31765 | - - - | - - - | - - - | - - - | 11708 | 9299 | 10758 | 31765 | 22367 | 20403 | 19602 | 62372 | # # # | # # # | # # # | # # # | 0.827 | 0.867 | 0.806 | 0.833 | # # # | # # # | # # # | - - - | 0.843 | 0.884 | 0.825 | 0.851 | - - - | 0.611 | 1.47 | 1.43 | 1.32 | 1.35 | 1.35 | 1.33 | 19.6 | 19.58 | 21.51 | 0 | - - - | - - - | - - - | - - - | 22367 | 20403 | 19602 | 62372 | Over-range | 12579 | 10166 | 11588 | 34452 | 4487 | 4006 | 4207 | 13039 | 18480 | 17741 | 15797 | 52018 | 18480 | 17741 | 15797 | 52018 | - - - | - - - | - - - | - - -
5/2/2026 | 4:45:00 PM | 281.92 | 278.82 | 277.31 | 487.11 | 479.73 | 484.69 | 82.9573 | 76.916 | 73.7115 | 0.2662 | 1.426 | 1.425 | 1.423 | 1.874 | 1.885 | 1.993 | Over-range | 59.99 | 19300 | 18552 | 16502 | 54355 | - - - | - - - | - - - | - - - | 19300 | 18552 | 16502 | 54355 | 12000 | 9428 | 10870 | 32298 | - - - | - - - | - - - | - - - | 12000 | 9428 | 10870 | 32298 | 23228 | 21274 | 20290 | 64792 | # # # | # # # | # # # | # # # | 0.831 | 0.872 | 0.813 | 0.839 | # # # | # # # | # # # | - - - | 0.849 | 0.89 | 0.833 | 0.857 | - - - | 0.594 | 1.48 | 1.44 | 1.33 | 1.36 | 1.36 | 1.34 | 19.54 | 19.77 | 21.59 | 0 | - - - | - - - | - - - | - - - | 23228 | 21274 | 20290 | 64792 | Over-range | 12909 | 10387 | 11789 | 35212 | 4637 | 4249 | 4457 | 13707 | 19368 | 18570 | 16467 | 54405 | 19368 | 18570 | 16467 | 54405 | - - - | - - - | - - - | - - -
5/2/2026 | 5:00:00 PM | 281.98 | 278.84 | 277.31 | 487.24 | 479.67 | 484.77 | 81.3378 | 75.3263 | 72.5012 | 0.2621 | 1.425 | 1.424 | 1.422 | 1.882 | 1.888 | 2.002 | Over-range | 59.99 | 18946 | 18158 | 16233 | 53337 | - - - | - - - | - - - | - - - | 18946 | 18158 | 16233 | 53337 | 11797 | 9321 | 10749 | 31867 | - - - | - - - | - - - | - - - | 11797 | 9321 | 10749 | 31867 | 22807 | 20864 | 19986 | 63657 | # # # | # # # | # # # | # # # | 0.831 | 0.87 | 0.812 | 0.838 | # # # | # # # | # # # | - - - | 0.849 | 0.888 | 0.833 | 0.857 | - - - | 0.598 | 1.49 | 1.45 | 1.32 | 1.36 | 1.36 | 1.34 | 19.96 | 20.1 | 21.89 | 0 | - - - | - - - | - - - | - - - | 22807 | 20864 | 19986 | 63657 | Over-range | 12690 | 10264 | 11648 | 34720 | 4592 | 4220 | 4411 | 13555 | 19019 | 18138 | 16233 | 53390 | 19019 | 18138 | 16233 | 53390 | - - - | - - - | - - - | - - -
5/2/2026 | 5:15:00 PM | 282.28 | 279.2 | 277.76 | 487.75 | 480.45 | 485.39 | 82.5629 | 76.4744 | 73.6108 | 0.2646 | 1.427 | 1.425 | 1.423 | 1.87 | 1.879 | 1.986 | Over-range | 60 | 19269 | 18482 | 16522 | 54272 | - - - | - - - | - - - | - - - | 19269 | 18482 | 16522 | 54272 | 12013 | 9486 | 10956 | 32455 | - - - | - - - | - - - | - - - | 12013 | 9486 | 10956 | 32455 | 23182 | 21223 | 20329 | 64734 | # # # | # # # | # # # | # # # | 0.831 | 0.871 | 0.813 | 0.838 | # # # | # # # | # # # | - - - | 0.848 | 0.888 | 0.832 | 0.856 | - - - | 0.598 | 1.5 | 1.47 | 1.35 | 1.38 | 1.38 | 1.36 | 19.31 | 19.54 | 21.26 | 0 | - - - | - - - | - - - | - - - | 23182 | 21223 | 20329 | 64734 | Over-range | 12881 | 10420 | 11834 | 35256 | 4553 | 4230 | 4385 | 13518 | 19335 | 18455 | 16538 | 54328 | 19335 | 18455 | 16538 | 54328 | - - - | - - - | - - - | - - -
5/2/2026 | 5:30:00 PM | 282.1 | 279.11 | 277.57 | 487.52 | 480.27 | 485.01 | 82.4109 | 76.5602 | 73.4365 | 0.2663 | 1.427 | 1.425 | 1.423 | 1.869 | 1.871 | 1.982 | Over-range | 59.97 | 19169 | 18465 | 16463 | 54096 | - - - | - - - | - - - | - - - | 19169 | 18465 | 16463 | 54096 | 12055 | 9561 | 10989 | 32605 | - - - | - - - | - - - | - - - | 12055 | 9561 | 10989 | 32605 | 23115 | 21227 | 20263 | 64605 | # # # | # # # | # # # | # # # | 0.829 | 0.87 | 0.813 | 0.837 | # # # | # # # | # # # | - - - | 0.845 | 0.887 | 0.831 | 0.855 | - - - | 0.603 | 1.5 | 1.46 | 1.33 | 1.38 | 1.37 | 1.35 | 19.1 | 19.24 | 20.84 | 0 | - - - | - - - | - - - | - - - | 23115 | 21227 | 20263 | 64605 | Over-range | 12910 | 10458 | 11802 | 35289 | 4524 | 4148 | 4213 | 13235 | 19156 | 18484 | 16509 | 54149 | 19156 | 18484 | 16509 | 54149 | - - - | - - - | - - - | - - -
5/2/2026 | 5:45:00 PM | 282.41 | 279.3 | 277.85 | 487.99 | 480.58 | 485.58 | 81.0252 | 74.9391 | 72.1229 | 0.2627 | 1.427 | 1.425 | 1.422 | 1.86 | 1.864 | 1.988 | Over-range | 60 | 18827 | 18037 | 16098 | 52962 | - - - | - - - | - - - | - - - | 18827 | 18037 | 16098 | 52962 | 11855 | 9361 | 10849 | 32065 | - - - | - - - | - - - | - - - | 11855 | 9361 | 10849 | 32065 | 22714 | 20749 | 19886 | 63349 | # # # | # # # | # # # | # # # | 0.829 | 0.869 | 0.81 | 0.836 | # # # | # # # | # # # | - - - | 0.845 | 0.886 | 0.828 | 0.853 | - - - | 0.605 | 1.5 | 1.46 | 1.32 | 1.37 | 1.37 | 1.35 | 18.96 | 18.91 | 20.78 | 0 | - - - | - - - | - - - | - - - | 22714 | 20749 | 19886 | 63349 | Over-range | 12693 | 10231 | 11657 | 34704 | 4415 | 4016 | 4147 | 12944 | 18825 | 18038 | 16147 | 53010 | 18825 | 18038 | 16147 | 53010 | - - - | - - - | - - - | - - -
5/2/2026 | 6:00:00 PM | 282.05 | 278.93 | 277.45 | 487.37 | 479.92 | 484.91 | 80.1574 | 73.8393 | 70.8201 | 0.2602 | 1.426 | 1.425 | 1.422 | 1.848 | 1.853 | 1.983 | Over-range | 59.98 | 18588 | 17807 | 15754 | 52149 | - - - | - - - | - - - | - - - | 18588 | 17807 | 15754 | 52149 | 11839 | 9208 | 10723 | 31770 | - - - | - - - | - - - | - - - | 11839 | 9208 | 10723 | 31770 | 22465 | 20442 | 19515 | 62422 | # # # | # # # | # # # | # # # | 0.827 | 0.871 | 0.807 | 0.835 | # # # | # # # | # # # | - - - | 0.843 | 0.886 | 0.825 | 0.852 | - - - | 0.609 | 1.5 | 1.45 | 1.34 | 1.37 | 1.38 | 1.35 | 18.56 | 18.58 | 20.51 | 0 | - - - | - - - | - - - | - - - | 22465 | 20442 | 19515 | 62422 | Over-range | 12610 | 10025 | 11505 | 34277 | 4230 | 3863 | 4073 | 12577 | 18655 | 17778 | 15763 | 52195 | 18655 | 17778 | 15763 | 52195 | - - - | - - - | - - - | - - -
5/2/2026 | 6:15:00 PM | 282.34 | 279.3 | 277.75 | 487.92 | 480.56 | 485.37 | 79.5026 | 73.6287 | 70.8392 | 0.26 | 1.427 | 1.425 | 1.423 | 1.837 | 1.842 | 1.975 | Over-range | 59.99 | 18484 | 17746 | 15840 | 52071 | - - - | - - - | - - - | - - - | 18484 | 17746 | 15840 | 52071 | 11724 | 9287 | 10704 | 31715 | - - - | - - - | - - - | - - - | 11724 | 9287 | 10704 | 31715 | 22296 | 20403 | 19542 | 62241 | # # # | # # # | # # # | # # # | 0.829 | 0.87 | 0.811 | 0.837 | # # # | # # # | # # # | - - - | 0.844 | 0.885 | 0.828 | 0.853 | - - - | 0.609 | 1.5 | 1.46 | 1.36 | 1.38 | 1.38 | 1.36 | 18.45 | 18.17 | 20.13 | 0 | - - - | - - - | - - - | - - - | 22296 | 20403 | 19542 | 62241 | Over-range | 12463 | 10054 | 11434 | 34071 | 4148 | 3780 | 3949 | 12238 | 18517 | 17713 | 15892 | 52122 | 18517 | 17713 | 15892 | 52122 | - - - | - - - | - - - | - - -
5/2/2026 | 6:30:00 PM | 282.52 | 279.34 | 277.86 | 488.16 | 480.59 | 485.68 | 81.5078 | 74.8442 | 71.8122 | 0.262 | 1.427 | 1.425 | 1.422 | 1.825 | 1.83 | 1.972 | Over-range | 59.99 | 18957 | 18122 | 15995 | 53073 | - - - | - - - | - - - | - - - | 18957 | 18122 | 15995 | 53073 | 12083 | 9374 | 10988 | 32445 | - - - | - - - | - - - | - - - | 12083 | 9374 | 10988 | 32445 | 22898 | 20766 | 19830 | 63494 | # # # | # # # | # # # | # # # | 0.828 | 0.873 | 0.807 | 0.836 | # # # | # # # | # # # | - - - | 0.842 | 0.887 | 0.823 | 0.851 | - - - | 0.611 | 1.51 | 1.45 | 1.37 | 1.38 | 1.38 | 1.37 | 17.88 | 17.64 | 19.72 | 0 | - - - | - - - | - - - | - - - | 22898 | 20766 | 19830 | 63494 | Over-range | 12837 | 10127 | 11710 | 34824 | 4235 | 3736 | 3951 | 12373 | 18953 | 18156 | 16006 | 53116 | 18953 | 18156 | 16006 | 53116 | - - - | - - - | - - - | - - -
5/2/2026 | 6:45:00 PM | 282.78 | 279.64 | 278.08 | 488.69 | 481.02 | 486.06 | 79.4788 | 73.1125 | 70.7031 | 0.2603 | 1.426 | 1.424 | 1.422 | 1.823 | 1.819 | 1.97 | Over-range | 59.99 | 18455 | 17596 | 15704 | 51754 | - - - | - - - | - - - | - - - | 18455 | 17596 | 15704 | 51754 | 11855 | 9389 | 10928 | 32171 | - - - | - - - | - - - | - - - | 11855 | 9389 | 10928 | 32171 | 22356 | 20312 | 19547 | 62215 | # # # | # # # | # # # | # # # | 0.826 | 0.866 | 0.803 | 0.832 | # # # | # # # | # # # | - - - | 0.839 | 0.881 | 0.82 | 0.847 | - - - | 0.622 | 1.49 | 1.47 | 1.35 | 1.38 | 1.38 | 1.36 | 17.82 | 17.33 | 19.44 | 0 | - - - | - - - | - - - | - - - | 22356 | 20312 | 19547 | 62215 | Over-range | 12603 | 10125 | 11623 | 34478 | 4152 | 3672 | 3836 | 12055 | 18427 | 17606 | 15761 | 51794 | 18427 | 17606 | 15761 | 51794 | - - - | - - - | - - - | - - -
5/2/2026 | 7:00:00 PM | 283.1 | 279.96 | 278.45 | 489.19 | 481.68 | 486.65 | 80.2621 | 73.726 | 70.8461 | 0.2619 | 1.426 | 1.424 | 1.422 | 1.805 | 1.799 | 1.964 | Over-range | 60.01 | 18626 | 17816 | 15746 | 52188 | - - - | - - - | - - - | - - - | 18626 | 17816 | 15746 | 52188 | 12050 | 9431 | 10988 | 32469 | - - - | - - - | - - - | - - - | 12050 | 9431 | 10988 | 32469 | 22562 | 20470 | 19579 | 62611 | # # # | # # # | # # # | # # # | 0.826 | 0.87 | 0.804 | 0.834 | # # # | # # # | # # # | - - - | 0.838 | 0.883 | 0.818 | 0.847 | - - - | 0.622 | 1.51 | 1.47 | 1.35 | 1.38 | 1.38 | 1.37 | 16.87 | 16.28 | 18.56 | 0 | - - - | - - - | - - - | - - - | 22562 | 20470 | 19579 | 62611 | Over-range | 12724 | 10065 | 11625 | 34559 | 3969 | 3404 | 3685 | 11521 | 18619 | 17869 | 15741 | 52230 | 18619 | 17869 | 15741 | 52230 | - - - | - - - | - - - | - - -
5/2/2026 | 7:15:00 PM | 283.39 | 280.55 | 278.88 | 489.98 | 482.67 | 487.15 | 78.385 | 72.4645 | 69.5557 | 0.2592 | 1.427 | 1.425 | 1.422 | 1.797 | 1.776 | 1.948 | Over-range | 59.99 | 18119 | 17457 | 15457 | 51034 | - - - | - - - | - - - | - - - | 18119 | 17457 | 15457 | 51034 | 12026 | 9555 | 10953 | 32534 | - - - | - - - | - - - | - - - | 12026 | 9555 | 10953 | 32534 | 22085 | 20188 | 19278 | 61551 | # # # | # # # | # # # | # # # | 0.82 | 0.865 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.832 | 0.876 | 0.815 | 0.841 | - - - | 0.637 | 1.53 | 1.45 | 1.34 | 1.39 | 1.37 | 1.37 | 16.3 | 15.51 | 17.63 | 0 | - - - | - - - | - - - | - - - | 22085 | 20188 | 19278 | 61551 | Over-range | 12620 | 10128 | 11509 | 34385 | 3719 | 3263 | 3439 | 10849 | 18116 | 17451 | 15502 | 51070 | 18116 | 17451 | 15502 | 51070 | - - - | - - - | - - - | - - -
5/2/2026 | 7:30:00 PM | 283.38 | 280.57 | 278.89 | 490.02 | 482.68 | 487.13 | 78.6505 | 72.7971 | 69.6315 | 0.2585 | 1.427 | 1.425 | 1.422 | 1.796 | 1.768 | 1.95 | Over-range | 59.97 | 18178 | 17551 | 15494 | 51223 | - - - | - - - | - - - | - - - | 18178 | 17551 | 15494 | 51223 | 12006 | 9482 | 10846 | 32334 | - - - | - - - | - - - | - - - | 12006 | 9482 | 10846 | 32334 | 22113 | 20234 | 19257 | 61604 | # # # | # # # | # # # | # # # | 0.822 | 0.867 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.834 | 0.878 | 0.818 | 0.843 | - - - | 0.631 | 1.52 | 1.44 | 1.35 | 1.39 | 1.36 | 1.36 | 16.13 | 15.25 | 17.4 | 0 | - - - | - - - | - - - | - - - | 22113 | 20234 | 19257 | 61604 | Over-range | 12584 | 10053 | 11422 | 34190 | 3633 | 3209 | 3455 | 10743 | 18228 | 17516 | 15515 | 51259 | 18228 | 17516 | 15515 | 51259 | - - - | - - - | - - - | - - -
5/2/2026 | 7:45:00 PM | 283.46 | 280.69 | 278.92 | 490.19 | 482.82 | 487.22 | 78.6635 | 72.9182 | 69.7203 | 0.2598 | 1.428 | 1.425 | 1.423 | 1.811 | 1.787 | 1.959 | Over-range | 59.98 | 18135 | 17536 | 15477 | 51148 | - - - | - - - | - - - | - - - | 18135 | 17536 | 15477 | 51148 | 12040 | 9568 | 10880 | 32488 | - - - | - - - | - - - | - - - | 12040 | 9568 | 10880 | 32488 | 22135 | 20288 | 19293 | 61716 | # # # | # # # | # # # | # # # | 0.819 | 0.864 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.832 | 0.876 | 0.816 | 0.841 | - - - | 0.635 | 1.53 | 1.47 | 1.34 | 1.39 | 1.36 | 1.36 | 16.69 | 16.02 | 18.06 | 0 | - - - | - - - | - - - | - - - | 22135 | 20288 | 19293 | 61716 | Over-range | 12678 | 10181 | 11502 | 34487 | 3838 | 3348 | 3606 | 11208 | 18174 | 17550 | 15458 | 51182 | 18174 | 17550 | 15458 | 51182 | - - - | - - - | - - - | - - -
5/2/2026 | 8:00:00 PM | 283.62 | 280.94 | 279.08 | 490.57 | 483.22 | 487.43 | 79.3412 | 73.8771 | 70.6981 | 0.2513 | 1.427 | 1.425 | 1.421 | 1.819 | 1.794 | 1.967 | Over-range | 59.97 | 18424 | 17871 | 15852 | 52146 | - - - | - - - | - - - | - - - | 18424 | 17871 | 15852 | 52146 | 12099 | 9710 | 10933 | 32743 | - - - | - - - | - - - | - - - | 12099 | 9710 | 10933 | 32743 | 22397 | 20641 | 19627 | 62665 | # # # | # # # | # # # | # # # | 0.823 | 0.866 | 0.808 | 0.832 | # # # | # # # | # # # | - - - | 0.836 | 0.878 | 0.822 | 0.845 | - - - | 0.628 | 1.52 | 1.45 | 1.31 | 1.38 | 1.35 | 1.34 | 16.96 | 16.27 | 18.26 | 0 | - - - | - - - | - - - | - - - | 22397 | 20641 | 19627 | 62665 | Over-range | 12730 | 10319 | 11565 | 34730 | 3873 | 3409 | 3693 | 11348 | 18487 | 17872 | 15824 | 52184 | 18487 | 17872 | 15824 | 52184 | - - - | - - - | - - - | - - -
5/2/2026 | 8:15:00 PM | 284.18 | 281.49 | 279.72 | 491.5 | 484.24 | 488.51 | 79.2871 | 73.456 | 70.302 | 0.2516 | 1.427 | 1.425 | 1.422 | 1.81 | 1.792 | 1.969 | Over-range | 59.97 | 18353 | 17750 | 15670 | 51773 | - - - | - - - | - - - | - - - | 18353 | 17750 | 15670 | 51773 | 12195 | 9680 | 11015 | 32890 | - - - | - - - | - - - | - - - | 12195 | 9680 | 11015 | 32890 | 22397 | 20531 | 19537 | 62466 | # # # | # # # | # # # | # # # | 0.82 | 0.865 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.832 | 0.876 | 0.816 | 0.842 | - - - | 0.635 | 1.57 | 1.43 | 1.34 | 1.4 | 1.37 | 1.38 | 16.91 | 16.32 | 18.36 | 0 | - - - | - - - | - - - | - - - | 22397 | 20531 | 19537 | 62466 | Over-range | 12830 | 10305 | 11658 | 34921 | 3868 | 3423 | 3711 | 11419 | 18418 | 17732 | 15654 | 51805 | 18418 | 17732 | 15654 | 51805 | - - - | - - - | - - - | - - -
5/2/2026 | 8:30:00 PM | 284.15 | 281.56 | 279.74 | 491.53 | 484.38 | 488.44 | 78.764 | 73.252 | 70.6226 | 0.2608 | 1.427 | 1.424 | 1.421 | 1.828 | 1.805 | 1.971 | Over-range | 59.98 | 18285 | 17631 | 15788 | 51704 | - - - | - - - | - - - | - - - | 18285 | 17631 | 15788 | 51704 | 11984 | 9714 | 10982 | 32680 | - - - | - - - | - - - | - - - | 11984 | 9714 | 10982 | 32680 | 22228 | 20458 | 19617 | 62303 | # # # | # # # | # # # | # # # | 0.823 | 0.862 | 0.805 | 0.83 | # # # | # # # | # # # | - - - | 0.836 | 0.874 | 0.82 | 0.843 | - - - | 0.632 | 1.54 | 1.44 | 1.34 | 1.39 | 1.36 | 1.37 | 17.31 | 16.8 | 18.56 | 0 | - - - | - - - | - - - | - - - | 22228 | 20458 | 19617 | 62303 | Over-range | 12633 | 10360 | 11631 | 34729 | 3877 | 3492 | 3724 | 11434 | 18351 | 17596 | 15787 | 51734 | 18351 | 17596 | 15787 | 51734 | - - - | - - - | - - - | - - -
5/2/2026 | 8:45:00 PM | 284.06 | 281.38 | 279.6 | 491.29 | 484.1 | 488.25 | 82.4293 | 76.1832 | 73.0294 | 0.2486 | 1.427 | 1.425 | 1.423 | 1.817 | 1.803 | 1.956 | Over-range | 59.98 | 19219 | 18501 | 16357 | 54078 | - - - | - - - | - - - | - - - | 19219 | 18501 | 16357 | 54078 | 12445 | 9807 | 11315 | 33567 | - - - | - - - | - - - | - - - | 12445 | 9807 | 11315 | 33567 | 23285 | 21290 | 20291 | 64867 | # # # | # # # | # # # | # # # | 0.825 | 0.869 | 0.806 | 0.834 | # # # | # # # | # # # | - - - | 0.839 | 0.882 | 0.821 | 0.847 | - - - | 0.621 | 1.59 | 1.43 | 1.38 | 1.41 | 1.38 | 1.4 | 16.96 | 16.78 | 18.41 | 0 | - - - | - - - | - - - | - - - | 23285 | 21290 | 20291 | 64867 | Over-range | 13132 | 10513 | 11990 | 35774 | 4075 | 3676 | 3858 | 12054 | 19268 | 18487 | 16358 | 54113 | 19268 | 18487 | 16358 | 54113 | - - - | - - - | - - - | - - -
5/2/2026 | 9:00:00 PM | 284.23 | 281.61 | 279.81 | 491.67 | 484.45 | 488.57 | 79.4092 | 73.5173 | 70.9975 | 0.2608 | 1.427 | 1.425 | 1.422 | 1.84 | 1.821 | 1.979 | Over-range | 59.98 | 18515 | 17784 | 15898 | 52197 | - - - | - - - | - - - | - - - | 18515 | 17784 | 15898 | 52197 | 11983 | 9659 | 11066 | 32708 | - - - | - - - | - - - | - - - | 11983 | 9659 | 11066 | 32708 | 22476 | 20600 | 19772 | 62848 | # # # | # # # | # # # | # # # | 0.824 | 0.863 | 0.804 | 0.831 | # # # | # # # | # # # | - - - | 0.838 | 0.878 | 0.82 | 0.845 | - - - | 0.627 | 1.57 | 1.46 | 1.34 | 1.4 | 1.37 | 1.39 | 17.99 | 17.62 | 19.3 | 0 | - - - | - - - | - - - | - - - | 22476 | 20600 | 19772 | 62848 | Over-range | 12734 | 10385 | 11745 | 34978 | 4211 | 3719 | 3838 | 12114 | 18486 | 17821 | 15925 | 52233 | 18486 | 17821 | 15925 | 52233 | - - - | - - - | - - - | - - -
5/2/2026 | 9:15:00 PM | 284.44 | 281.9 | 280.11 | 492.09 | 485 | 488.99 | 81.1447 | 75.0927 | 72.145 | 0.248 | 1.427 | 1.425 | 1.422 | 1.844 | 1.829 | 1.986 | Over-range | 59.99 | 18889 | 18180 | 16137 | 53206 | - - - | - - - | - - - | - - - | 18889 | 18180 | 16137 | 53206 | 12184 | 9699 | 11180 | 33063 | - - - | - - - | - - - | - - - | 12184 | 9699 | 11180 | 33063 | 22908 | 20981 | 20047 | 63935 | # # # | # # # | # # # | # # # | 0.825 | 0.867 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.839 | 0.881 | 0.821 | 0.847 | - - - | 0.621 | 1.58 | 1.44 | 1.36 | 1.41 | 1.38 | 1.4 | 18.09 | 17.92 | 19.53 | 0 | - - - | - - - | - - - | - - - | 22908 | 20981 | 20047 | 63935 | Over-range | 12954 | 10459 | 11880 | 35420 | 4283 | 3802 | 3907 | 12384 | 18853 | 18226 | 16156 | 53236 | 18853 | 18226 | 16156 | 53236 | - - - | - - - | - - - | - - -
5/2/2026 | 9:30:00 PM | 284.63 | 282.04 | 280.24 | 492.34 | 485.32 | 489.24 | 79.4774 | 73.7956 | 71.0414 | 0.2581 | 1.427 | 1.425 | 1.422 | 1.844 | 1.837 | 1.984 | Over-range | 59.99 | 18510 | 17837 | 15911 | 52258 | - - - | - - - | - - - | - - - | 18510 | 17837 | 15911 | 52258 | 12021 | 9643 | 11021 | 32684 | - - - | - - - | - - - | - - - | 12021 | 9643 | 11021 | 32684 | 22476 | 20654 | 19771 | 62900 | # # # | # # # | # # # | # # # | 0.824 | 0.864 | 0.805 | 0.831 | # # # | # # # | # # # | - - - | 0.838 | 0.878 | 0.821 | 0.846 | - - - | 0.625 | 1.58 | 1.46 | 1.39 | 1.42 | 1.39 | 1.42 | 18.17 | 18.09 | 19.66 | 0 | - - - | - - - | - - - | - - - | 22476 | 20654 | 19771 | 62900 | Over-range | 12743 | 10399 | 11725 | 34981 | 4131 | 3805 | 3910 | 12198 | 18541 | 17802 | 15952 | 52294 | 18541 | 17802 | 15952 | 52294 | - - - | - - - | - - - | - - -
5/2/2026 | 9:45:00 PM | 285.21 | 282.67 | 280.76 | 493.48 | 486.23 | 490.16 | 80.2858 | 74.439 | 71.4199 | 0.2497 | 1.427 | 1.425 | 1.422 | 1.831 | 1.81 | 1.974 | Over-range | 59.99 | 18683 | 18023 | 15984 | 52691 | - - - | - - - | - - - | - - - | 18683 | 18023 | 15984 | 52691 | 12245 | 9759 | 11157 | 33160 | - - - | - - - | - - - | - - - | 12245 | 9759 | 11157 | 33160 | 22737 | 20864 | 19904 | 63505 | # # # | # # # | # # # | # # # | 0.822 | 0.864 | 0.803 | 0.83 | # # # | # # # | # # # | - - - | 0.836 | 0.877 | 0.819 | 0.844 | - - - | 0.629 | 1.59 | 1.47 | 1.38 | 1.42 | 1.4 | 1.42 | 17.61 | 17.37 | 18.98 | 0 | - - - | - - - | - - - | - - - | 22737 | 20864 | 19904 | 63505 | Over-range | 12945 | 10487 | 11844 | 35398 | 4079 | 3730 | 3862 | 12064 | 18735 | 17978 | 16013 | 52726 | 18735 | 17978 | 16013 | 52726 | - - - | - - - | - - - | - - -
5/2/2026 | 10:00:00 PM | 285.29 | 282.82 | 281.01 | 493.59 | 486.63 | 490.48 | 80.7089 | 74.6673 | 71.7006 | 0.2511 | 1.427 | 1.425 | 1.422 | 1.812 | 1.793 | 1.958 | Over-range | 60 | 18789 | 18112 | 16044 | 52945 | - - - | - - - | - - - | - - - | 18789 | 18112 | 16044 | 52945 | 12420 | 9882 | 11323 | 33625 | - - - | - - - | - - - | - - - | 12420 | 9882 | 11323 | 33625 | 22884 | 20958 | 20016 | 63858 | # # # | # # # | # # # | # # # | 0.821 | 0.864 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.834 | 0.876 | 0.815 | 0.842 | - - - | 0.635 | 1.6 | 1.47 | 1.41 | 1.43 | 1.41 | 1.43 | 16.78 | 16.44 | 18.12 | 0 | - - - | - - - | - - - | - - - | 22884 | 20958 | 20016 | 63858 | Over-range | 13056 | 10530 | 11955 | 35670 | 3901 | 3526 | 3723 | 11578 | 18852 | 18073 | 16050 | 52975 | 18852 | 18073 | 16050 | 52975 | - - - | - - - | - - - | - - -
5/2/2026 | 10:15:00 PM | 285.51 | 283.07 | 281.26 | 493.95 | 487.15 | 490.85 | 78.8109 | 73.0069 | 70.7372 | 0.2575 | 1.428 | 1.425 | 1.422 | 1.824 | 1.809 | 1.971 | Over-range | 59.98 | 18439 | 17697 | 15882 | 52018 | - - - | - - - | - - - | - - - | 18439 | 17697 | 15882 | 52018 | 12027 | 9742 | 11172 | 32941 | - - - | - - - | - - - | - - - | 12027 | 9742 | 11172 | 32941 | 22395 | 20547 | 19794 | 62736 | # # # | # # # | # # # | # # # | 0.823 | 0.861 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.836 | 0.875 | 0.817 | 0.843 | - - - | 0.633 | 1.6 | 1.5 | 1.42 | 1.44 | 1.42 | 1.45 | 17.32 | 17.01 | 18.61 | 0 | - - - | - - - | - - - | - - - | 22395 | 20547 | 19794 | 62736 | Over-range | 12704 | 10426 | 11804 | 35044 | 3985 | 3609 | 3700 | 11649 | 18430 | 17682 | 15940 | 52052 | 18430 | 17682 | 15940 | 52052 | - - - | - - - | - - - | - - -
5/2/2026 | 10:30:00 PM | 285.3 | 282.81 | 281.08 | 493.58 | 486.72 | 490.54 | 81.7013 | 75.2847 | 72.7618 | 0.25 | 1.428 | 1.425 | 1.423 | 1.809 | 1.794 | 1.961 | Over-range | 59.98 | 19105 | 18296 | 16296 | 53697 | - - - | - - - | - - - | - - - | 19105 | 18296 | 16296 | 53697 | 12486 | 9950 | 11541 | 33977 | - - - | - - - | - - - | - - - | 12486 | 9950 | 11541 | 33977 | 23192 | 21161 | 20339 | 64692 | # # # | # # # | # # # | # # # | 0.824 | 0.865 | 0.801 | 0.83 | # # # | # # # | # # # | - - - | 0.836 | 0.877 | 0.816 | 0.843 | - - - | 0.633 | 1.6 | 1.48 | 1.41 | 1.43 | 1.42 | 1.45 | 16.87 | 16.62 | 18.29 | 0 | - - - | - - - | - - - | - - - | 23192 | 21161 | 20339 | 64692 | Over-range | 13142 | 10619 | 12160 | 36052 | 4011 | 3625 | 3744 | 11809 | 19111 | 18274 | 16344 | 53728 | 19111 | 18274 | 16344 | 53728 | - - - | - - - | - - - | - - -
5/2/2026 | 10:45:00 PM | 285.63 | 283.17 | 281.33 | 494.2 | 487.26 | 491 | 79.2262 | 73.2615 | 71.0252 | 0.2533 | 1.428 | 1.426 | 1.422 | 1.803 | 1.78 | 1.962 | Over-range | 59.99 | 18453 | 17697 | 15851 | 52001 | - - - | - - - | - - - | - - - | 18453 | 17697 | 15851 | 52001 | 12206 | 9890 | 11339 | 33435 | - - - | - - - | - - - | - - - | 12206 | 9890 | 11339 | 33435 | 22508 | 20610 | 19864 | 62982 | # # # | # # # | # # # | # # # | 0.82 | 0.859 | 0.798 | 0.826 | # # # | # # # | # # # | - - - | 0.832 | 0.871 | 0.812 | 0.839 | - - - | 0.643 | 1.65 | 1.51 | 1.44 | 1.46 | 1.44 | 1.48 | 16.76 | 16.18 | 17.96 | 0 | - - - | - - - | - - - | - - - | 22508 | 20610 | 19864 | 62982 | Over-range | 12871 | 10539 | 11953 | 35477 | 3935 | 3495 | 3630 | 11440 | 18440 | 17684 | 15903 | 52026 | 18440 | 17684 | 15903 | 52026 | - - - | - - - | - - - | - - -
5/2/2026 | 11:00:00 PM | 286.01 | 283.65 | 281.79 | 494.89 | 488.16 | 491.69 | 79.9965 | 73.9295 | 71.0911 | 0.2573 | 1.427 | 1.425 | 1.422 | 1.783 | 1.752 | 1.945 | Over-range | 59.99 | 18578 | 17907 | 15849 | 52335 | - - - | - - - | - - - | - - - | 18578 | 17907 | 15849 | 52335 | 12476 | 9955 | 11435 | 33866 | - - - | - - - | - - - | - - - | 12476 | 9955 | 11435 | 33866 | 22695 | 20769 | 19862 | 63326 | # # # | # # # | # # # | # # # | 0.819 | 0.862 | 0.798 | 0.826 | # # # | # # # | # # # | - - - | 0.829 | 0.873 | 0.811 | 0.838 | - - - | 0.647 | 1.65 | 1.48 | 1.44 | 1.46 | 1.43 | 1.47 | 15.68 | 15.14 | 16.84 | 0 | - - - | - - - | - - - | - - - | 22695 | 20769 | 19862 | 63326 | Over-range | 13027 | 10509 | 11959 | 35625 | 3632 | 3254 | 3383 | 10734 | 18588 | 17873 | 15897 | 52359 | 18588 | 17873 | 15897 | 52359 | - - - | - - - | - - - | - - -
5/2/2026 | 11:15:00 PM | 285.97 | 283.47 | 281.7 | 494.76 | 487.81 | 491.65 | 78.1188 | 72.012 | 69.6429 | 0.2415 | 1.427 | 1.425 | 1.421 | 1.783 | 1.744 | 1.952 | Over-range | 59.98 | 18147 | 17412 | 15494 | 51053 | - - - | - - - | - - - | - - - | 18147 | 17412 | 15494 | 51053 | 12264 | 9847 | 11299 | 33409 | - - - | - - - | - - - | - - - | 12264 | 9847 | 11299 | 33409 | 22209 | 20267 | 19493 | 61969 | # # # | # # # | # # # | # # # | 0.817 | 0.859 | 0.795 | 0.824 | # # # | # # # | # # # | - - - | 0.828 | 0.869 | 0.807 | 0.835 | - - - | 0.654 | 1.63 | 1.49 | 1.42 | 1.45 | 1.43 | 1.47 | 15.7 | 14.84 | 16.77 | 0 | - - - | - - - | - - - | - - - | 22209 | 20267 | 19493 | 61969 | Over-range | 12798 | 10363 | 11819 | 35104 | 3544 | 3120 | 3358 | 10459 | 18188 | 17366 | 15523 | 51077 | 18188 | 17366 | 15523 | 51077 | - - - | - - - | - - - | - - -
5/2/2026 | 11:30:00 PM | 286.29 | 283.78 | 282.02 | 495.29 | 488.38 | 492.18 | 79.9527 | 73.8488 | 70.9126 | 0.2577 | 1.428 | 1.426 | 1.422 | 1.777 | 1.738 | 1.941 | Over-range | 59.99 | 18632 | 17963 | 15877 | 52473 | - - - | - - - | - - - | - - - | 18632 | 17963 | 15877 | 52473 | 12494 | 9952 | 11441 | 33887 | - - - | - - - | - - - | - - - | 12494 | 9952 | 11441 | 33887 | 22758 | 20810 | 19877 | 63444 | # # # | # # # | # # # | # # # | 0.819 | 0.863 | 0.799 | 0.827 | # # # | # # # | # # # | - - - | 0.829 | 0.873 | 0.811 | 0.838 | - - - | 0.646 | 1.63 | 1.52 | 1.46 | 1.47 | 1.46 | 1.49 | 15.43 | 14.57 | 16.42 | 0 | - - - | - - - | - - - | - - - | 22758 | 20810 | 19877 | 63444 | Over-range | 13060 | 10491 | 11946 | 35631 | 3663 | 3181 | 3294 | 10621 | 18599 | 17960 | 15932 | 52492 | 18599 | 17960 | 15932 | 52492 | - - - | - - - | - - - | - - -
5/2/2026 | 11:45:00 PM | 286.79 | 284.3 | 282.58 | 496.12 | 489.38 | 493.08 | 79.0638 | 73.1389 | 70.6014 | 0.2504 | 1.428 | 1.426 | 1.422 | 1.792 | 1.769 | 1.952 | Over-range | 59.98 | 18393 | 17702 | 15753 | 51848 | - - - | - - - | - - - | - - - | 18393 | 17702 | 15753 | 51848 | 12383 | 9998 | 11439 | 33820 | - - - | - - - | - - - | - - - | 12383 | 9998 | 11439 | 33820 | 22540 | 20641 | 19819 | 63000 | # # # | # # # | # # # | # # # | 0.816 | 0.858 | 0.795 | 0.823 | # # # | # # # | # # # | - - - | 0.828 | 0.869 | 0.808 | 0.835 | - - - | 0.652 | 1.68 | 1.51 | 1.46 | 1.49 | 1.47 | 1.51 | 16.27 | 15.69 | 17.46 | 0 | - - - | - - - | - - - | - - - | 22540 | 20641 | 19819 | 63000 | Over-range | 13013 | 10592 | 12008 | 35734 | 3871 | 3359 | 3516 | 11154 | 18359 | 17740 | 15776 | 51874 | 18359 | 17740 | 15776 | 51874 | - - - | - - - | - - - | - - -
5/3/2026 | 12:00:00 AM | 287.01 | 284.63 | 282.8 | 496.66 | 489.82 | 493.44 | 79.5338 | 73.7179 | 71.1787 | 0.2508 | 1.428 | 1.426 | 1.422 | 1.8 | 1.776 | 1.953 | Over-range | 59.99 | 18563 | 17880 | 15957 | 52400 | - - - | - - - | - - - | - - - | 18563 | 17880 | 15957 | 52400 | 12366 | 10034 | 11439 | 33839 | - - - | - - - | - - - | - - - | 12366 | 10034 | 11439 | 33839 | 22675 | 20817 | 19985 | 63477 | # # # | # # # | # # # | # # # | 0.819 | 0.859 | 0.798 | 0.826 | # # # | # # # | # # # | - - - | 0.831 | 0.871 | 0.812 | 0.838 | - - - | 0.646 | 1.67 | 1.52 | 1.49 | 1.49 | 1.48 | 1.52 | 16.59 | 16.1 | 17.74 | 0 | - - - | - - - | - - - | - - - | 22675 | 20817 | 19985 | 63477 | Over-range | 13015 | 10648 | 12023 | 35801 | 3936 | 3440 | 3572 | 11332 | 18530 | 17919 | 15978 | 52428 | 18530 | 17919 | 15978 | 52428 | - - - | - - - | - - - | - - -
5/3/2026 | 12:15:00 AM | 287.29 | 284.83 | 283.11 | 497.05 | 490.28 | 493.96 | 81.4232 | 75.1835 | 72.7992 | 0.2584 | 1.428 | 1.426 | 1.422 | 1.788 | 1.763 | 1.939 | Over-range | 59.98 | 19031 | 18253 | 16302 | 53587 | - - - | - - - | - - - | - - - | 19031 | 18253 | 16302 | 53587 | 12742 | 10330 | 11806 | 34878 | - - - | - - - | - - - | - - - | 12742 | 10330 | 11806 | 34878 | 23250 | 21260 | 20478 | 64987 | # # # | # # # | # # # | # # # | 0.819 | 0.859 | 0.796 | 0.825 | # # # | # # # | # # # | - - - | 0.83 | 0.87 | 0.808 | 0.836 | - - - | 0.651 | 1.7 | 1.52 | 1.48 | 1.5 | 1.48 | 1.52 | 16 | 15.57 | 17.22 | 0 | - - - | - - - | - - - | - - - | 23250 | 21260 | 20478 | 64987 | Over-range | 13348 | 10887 | 12381 | 36738 | 3859 | 3325 | 3620 | 11223 | 19057 | 18300 | 16261 | 53618 | 19057 | 18300 | 16261 | 53618 | - - - | - - - | - - - | - - -
5/3/2026 | 12:30:00 AM | 286.62 | 284.22 | 282.41 | 495.93 | 489.19 | 492.75 | 79.5958 | 73.7013 | 71.558 | 0.2532 | 1.427 | 1.424 | 1.421 | 1.796 | 1.763 | 1.947 | Over-range | 59.98 | 18612 | 17859 | 16043 | 52514 | - - - | - - - | - - - | - - - | 18612 | 17859 | 16043 | 52514 | 12364 | 10117 | 11504 | 33985 | - - - | - - - | - - - | - - - | 12364 | 10117 | 11504 | 33985 | 22694 | 20815 | 20092 | 63601 | # # # | # # # | # # # | # # # | 0.82 | 0.858 | 0.799 | 0.826 | # # # | # # # | # # # | - - - | 0.832 | 0.869 | 0.811 | 0.838 | - - - | 0.647 | 1.66 | 1.54 | 1.46 | 1.48 | 1.48 | 1.5 | 16.34 | 15.71 | 17.42 | 0 | - - - | - - - | - - - | - - - | 22694 | 20815 | 20092 | 63601 | Over-range | 12977 | 10680 | 12084 | 35851 | 3830 | 3309 | 3592 | 11099 | 18641 | 17889 | 16009 | 52538 | 18641 | 17889 | 16009 | 52538 | - - - | - - - | - - - | - - -
5/3/2026 | 12:45:00 AM | 285.38 | 283.09 | 281.4 | 493.82 | 487.38 | 490.81 | 80.3263 | 74.5648 | 71.8583 | 0.2508 | 1.427 | 1.424 | 1.421 | 1.805 | 1.782 | 1.958 | Over-range | 59.99 | 18717 | 18062 | 16114 | 52893 | - - - | - - - | - - - | - - - | 18717 | 18062 | 16114 | 52893 | 12305 | 9921 | 11311 | 33537 | - - - | - - - | - - - | - - - | 12305 | 9921 | 11311 | 33537 | 22780 | 20948 | 20082 | 63810 | # # # | # # # | # # # | # # # | 0.822 | 0.862 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.835 | 0.874 | 0.817 | 0.842 | - - - | 0.634 | 1.67 | 1.54 | 1.48 | 1.49 | 1.48 | 1.52 | 16.87 | 16.49 | 18.18 | 0 | - - - | - - - | - - - | - - - | 22780 | 20948 | 20082 | 63810 | Over-range | 12970 | 10589 | 11969 | 35645 | 3950 | 3558 | 3776 | 11671 | 18770 | 18037 | 16113 | 52920 | 18770 | 18037 | 16113 | 52920 | - - - | - - - | - - - | - - -
5/3/2026 | 1:00:00 AM | 285.83 | 283.56 | 281.85 | 494.61 | 488.21 | 491.57 | 79.2719 | 73.8916 | 71.6383 | 0.254 | 1.428 | 1.425 | 1.422 | 1.82 | 1.801 | 1.964 | Over-range | 59.99 | 18515 | 17850 | 16117 | 52481 | - - - | - - - | - - - | - - - | 18515 | 17850 | 16117 | 52481 | 12139 | 9983 | 11308 | 33430 | - - - | - - - | - - - | - - - | 12139 | 9983 | 11308 | 33430 | 22516 | 20797 | 20061 | 63374 | # # # | # # # | # # # | # # # | 0.822 | 0.858 | 0.803 | 0.828 | # # # | # # # | # # # | - - - | 0.835 | 0.871 | 0.818 | 0.842 | - - - | 0.637 | 1.68 | 1.52 | 1.47 | 1.49 | 1.46 | 1.52 | 17.34 | 16.98 | 18.5 | 0 | - - - | - - - | - - - | - - - | 22516 | 20797 | 20061 | 63374 | Over-range | 12807 | 10659 | 11935 | 35498 | 3978 | 3641 | 3721 | 11654 | 18516 | 17820 | 16179 | 52515 | 18516 | 17820 | 16179 | 52515 | - - - | - - - | - - - | - - -
5/3/2026 | 1:15:00 AM | 285.75 | 283.42 | 281.71 | 494.41 | 487.96 | 491.38 | 81.1116 | 75.5287 | 72.7502 | 0.2494 | 1.428 | 1.426 | 1.422 | 1.807 | 1.796 | 1.956 | Over-range | 59.97 | 19005 | 18376 | 16431 | 53812 | - - - | - - - | - - - | - - - | 19005 | 18376 | 16431 | 53812 | 12380 | 10021 | 11420 | 33821 | - - - | - - - | - - - | - - - | 12380 | 10021 | 11420 | 33821 | 23060 | 21276 | 20382 | 64717 | # # # | # # # | # # # | # # # | 0.824 | 0.864 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.837 | 0.877 | 0.821 | 0.845 | - - - | 0.628 | 1.68 | 1.57 | 1.52 | 1.52 | 1.51 | 1.55 | 16.99 | 16.78 | 18.33 | 0 | - - - | - - - | - - - | - - - | 23060 | 21276 | 20382 | 64717 | Over-range | 13054 | 10712 | 12049 | 35927 | 4044 | 3691 | 3743 | 11846 | 18980 | 18372 | 16496 | 53848 | 18980 | 18372 | 16496 | 53848 | - - - | - - - | - - - | - - -
5/3/2026 | 1:30:00 AM | 285.78 | 283.3 | 281.61 | 494.41 | 487.64 | 491.38 | 79.2644 | 73.5514 | 71.2316 | 0.2524 | 1.428 | 1.426 | 1.423 | 1.82 | 1.802 | 1.973 | Over-range | 59.99 | 18511 | 17797 | 15982 | 52290 | - - - | - - - | - - - | - - - | 18511 | 17797 | 15982 | 52290 | 12099 | 9856 | 11233 | 33188 | - - - | - - - | - - - | - - - | 12099 | 9856 | 11233 | 33188 | 22522 | 20695 | 19935 | 63152 | # # # | # # # | # # # | # # # | 0.822 | 0.86 | 0.802 | 0.828 | # # # | # # # | # # # | - - - | 0.836 | 0.874 | 0.817 | 0.842 | - - - | 0.635 | 1.72 | 1.56 | 1.53 | 1.53 | 1.52 | 1.55 | 17.72 | 17.25 | 19.01 | 0 | - - - | - - - | - - - | - - - | 22522 | 20695 | 19935 | 63152 | Over-range | 12822 | 10548 | 11904 | 35380 | 4127 | 3642 | 3826 | 11929 | 18500 | 17825 | 15995 | 52321 | 18500 | 17825 | 15995 | 52321 | - - - | - - - | - - - | - - -
5/3/2026 | 1:45:00 AM | 286.15 | 283.62 | 281.89 | 495.04 | 488.1 | 491.95 | 80.6074 | 74.5673 | 71.9723 | 0.2483 | 1.427 | 1.425 | 1.421 | 1.814 | 1.793 | 1.979 | Over-range | 59.99 | 18802 | 18062 | 16106 | 52970 | - - - | - - - | - - - | - - - | 18802 | 18062 | 16106 | 52970 | 12339 | 9903 | 11343 | 33585 | - - - | - - - | - - - | - - - | 12339 | 9903 | 11343 | 33585 | 22887 | 20950 | 20121 | 63959 | # # # | # # # | # # # | # # # | 0.822 | 0.862 | 0.801 | 0.828 | # # # | # # # | # # # | - - - | 0.835 | 0.875 | 0.815 | 0.842 | - - - | 0.634 | 1.67 | 1.56 | 1.51 | 1.5 | 1.5 | 1.53 | 17.46 | 16.94 | 18.87 | 0 | - - - | - - - | - - - | - - - | 22887 | 20950 | 20121 | 63959 | Over-range | 13038 | 10593 | 12043 | 35797 | 4073 | 3628 | 3920 | 12014 | 18868 | 18041 | 16087 | 52996 | 18868 | 18041 | 16087 | 52996 | - - - | - - - | - - - | - - -
5/3/2026 | 2:00:00 AM | 286.21 | 283.75 | 282.04 | 495.13 | 488.43 | 492.14 | 80.0209 | 73.881 | 71.7641 | 0.2542 | 1.428 | 1.425 | 1.422 | 1.801 | 1.788 | 1.963 | Over-range | 60 | 18723 | 17914 | 16074 | 52711 | - - - | - - - | - - - | - - - | 18723 | 17914 | 16074 | 52711 | 12332 | 9971 | 11455 | 33757 | - - - | - - - | - - - | - - - | 12332 | 9971 | 11455 | 33757 | 22776 | 20822 | 20118 | 63715 | # # # | # # # | # # # | # # # | 0.822 | 0.86 | 0.799 | 0.827 | # # # | # # # | # # # | - - - | 0.835 | 0.872 | 0.813 | 0.84 | - - - | 0.64 | 1.68 | 1.53 | 1.5 | 1.5 | 1.49 | 1.53 | 16.84 | 16.51 | 18.22 | 0 | - - - | - - - | - - - | - - - | 22776 | 20822 | 20118 | 63715 | Over-range | 12962 | 10603 | 12087 | 35768 | 3886 | 3505 | 3757 | 11531 | 18779 | 17881 | 16079 | 52739 | 18779 | 17881 | 16079 | 52739 | - - - | - - - | - - - | - - -
5/3/2026 | 2:15:00 AM | 286.4 | 283.95 | 282.22 | 495.52 | 488.74 | 492.43 | 80.6326 | 74.5898 | 72.3202 | 0.2505 | 1.428 | 1.425 | 1.422 | 1.802 | 1.778 | 1.96 | Over-range | 59.99 | 18874 | 18097 | 16234 | 53205 | - - - | - - - | - - - | - - - | 18874 | 18097 | 16234 | 53205 | 12405 | 10100 | 11537 | 34043 | - - - | - - - | - - - | - - - | 12405 | 10100 | 11537 | 34043 | 22956 | 21028 | 20284 | 64268 | # # # | # # # | # # # | # # # | 0.822 | 0.861 | 0.8 | 0.828 | # # # | # # # | # # # | - - - | 0.835 | 0.873 | 0.813 | 0.84 | - - - | 0.64 | 1.67 | 1.54 | 1.51 | 1.51 | 1.5 | 1.53 | 16.74 | 16.16 | 17.98 | 0 | - - - | - - - | - - - | - - - | 22956 | 21028 | 20284 | 64268 | Over-range | 13061 | 10696 | 12150 | 36023 | 3984 | 3417 | 3711 | 11490 | 18887 | 18151 | 16197 | 53234 | 18887 | 18151 | 16197 | 53234 | - - - | - - - | - - - | - - -
5/3/2026 | 2:30:00 AM | 286.69 | 284.22 | 282.55 | 495.97 | 489.26 | 492.99 | 80.855 | 74.516 | 72.0688 | 0.2575 | 1.428 | 1.425 | 1.422 | 1.795 | 1.779 | 1.959 | Over-range | 59.98 | 18869 | 18084 | 16100 | 53052 | - - - | - - - | - - - | - - - | 18869 | 18084 | 16100 | 53052 | 12543 | 10084 | 11626 | 34253 | - - - | - - - | - - - | - - - | 12543 | 10084 | 11626 | 34253 | 23036 | 21018 | 20228 | 64282 | # # # | # # # | # # # | # # # | 0.819 | 0.86 | 0.796 | 0.825 | # # # | # # # | # # # | - - - | 0.831 | 0.873 | 0.809 | 0.838 | - - - | 0.646 | 1.71 | 1.56 | 1.53 | 1.52 | 1.52 | 1.55 | 16.61 | 16.13 | 17.99 | 0 | - - - | - - - | - - - | - - - | 23036 | 21018 | 20228 | 64282 | Over-range | 13208 | 10698 | 12233 | 36268 | 4012 | 3446 | 3682 | 11569 | 18843 | 18146 | 16091 | 53080 | 18843 | 18146 | 16091 | 53080 | - - - | - - - | - - - | - - -
5/3/2026 | 2:45:00 AM | 286.92 | 284.52 | 282.8 | 496.43 | 489.8 | 493.36 | 78.0229 | 72.2688 | 70.2714 | 0.2486 | 1.427 | 1.424 | 1.421 | 1.801 | 1.772 | 1.964 | Over-range | 59.99 | 18206 | 17463 | 15717 | 51385 | - - - | - - - | - - - | - - - | 18206 | 17463 | 15717 | 51385 | 12151 | 9978 | 11321 | 33450 | - - - | - - - | - - - | - - - | 12151 | 9978 | 11321 | 33450 | 22256 | 20415 | 19745 | 62416 | # # # | # # # | # # # | # # # | 0.818 | 0.855 | 0.796 | 0.823 | # # # | # # # | # # # | - - - | 0.831 | 0.867 | 0.809 | 0.836 | - - - | 0.651 | 1.69 | 1.52 | 1.5 | 1.5 | 1.49 | 1.53 | 16.73 | 16.01 | 17.86 | 0 | - - - | - - - | - - - | - - - | 22256 | 20415 | 19745 | 62416 | Over-range | 12788 | 10555 | 11938 | 35386 | 3867 | 3324 | 3679 | 11218 | 18250 | 17491 | 15669 | 51411 | 18250 | 17491 | 15669 | 51411 | - - - | - - - | - - - | - - -
5/3/2026 | 3:00:00 AM | 286.95 | 284.5 | 282.87 | 496.42 | 489.81 | 493.48 | 81.0148 | 74.8173 | 72.151 | 0.252 | 1.427 | 1.424 | 1.422 | 1.772 | 1.746 | 1.937 | Over-range | 59.98 | 18954 | 18238 | 16199 | 53391 | - - - | - - - | - - - | - - - | 18954 | 18238 | 16199 | 53391 | 12692 | 10181 | 11660 | 34533 | - - - | - - - | - - - | - - - | 12692 | 10181 | 11660 | 34533 | 23127 | 21152 | 20291 | 64570 | # # # | # # # | # # # | # # # | 0.82 | 0.862 | 0.798 | 0.827 | # # # | # # # | # # # | - - - | 0.83 | 0.872 | 0.81 | 0.838 | - - - | 0.647 | 1.65 | 1.54 | 1.49 | 1.49 | 1.48 | 1.52 | 15.41 | 14.76 | 16.69 | 0 | - - - | - - - | - - - | - - - | 23127 | 21152 | 20291 | 64570 | Over-range | 13247 | 10703 | 12209 | 36290 | 3677 | 3187 | 3509 | 10835 | 18994 | 18246 | 16171 | 53410 | 18994 | 18246 | 16171 | 53410 | - - - | - - - | - - - | - - -
5/3/2026 | 3:15:00 AM | 286.91 | 284.56 | 282.87 | 496.45 | 489.88 | 493.42 | 77.3895 | 71.6474 | 69.585 | 0.2453 | 1.427 | 1.424 | 1.421 | 1.793 | 1.767 | 1.956 | Over-range | 59.97 | 17982 | 17258 | 15499 | 50739 | - - - | - - - | - - - | - - - | 17982 | 17258 | 15499 | 50739 | 12136 | 9913 | 11272 | 33321 | - - - | - - - | - - - | - - - | 12136 | 9913 | 11272 | 33321 | 22023 | 20189 | 19516 | 61728 | # # # | # # # | # # # | # # # | 0.817 | 0.855 | 0.794 | 0.822 | # # # | # # # | # # # | - - - | 0.828 | 0.865 | 0.807 | 0.834 | - - - | 0.657 | 1.69 | 1.52 | 1.49 | 1.5 | 1.49 | 1.53 | 16.28 | 15.66 | 17.48 | 0 | - - - | - - - | - - - | - - - | 22023 | 20189 | 19516 | 61728 | Over-range | 12707 | 10465 | 11846 | 35125 | 3631 | 3221 | 3519 | 10740 | 18042 | 17227 | 15494 | 50763 | 18042 | 17227 | 15494 | 50763 | - - - | - - - | - - - | - - -
5/3/2026 | 3:30:00 AM | 287.01 | 284.71 | 283.01 | 496.61 | 490.23 | 493.58 | 78.9173 | 73.1363 | 70.6653 | 0.249 | 1.427 | 1.424 | 1.421 | 1.784 | 1.75 | 1.937 | Over-range | 59.98 | 18430 | 17758 | 15856 | 52043 | - - - | - - - | - - - | - - - | 18430 | 17758 | 15856 | 52043 | 12381 | 10034 | 11426 | 33841 | - - - | - - - | - - - | - - - | 12381 | 10034 | 11426 | 33841 | 22511 | 20669 | 19868 | 63049 | # # # | # # # | # # # | # # # | 0.819 | 0.859 | 0.798 | 0.825 | # # # | # # # | # # # | - - - | 0.83 | 0.869 | 0.81 | 0.836 | - - - | 0.65 | 1.69 | 1.51 | 1.52 | 1.5 | 1.49 | 1.53 | 15.62 | 15.08 | 16.74 | 0 | - - - | - - - | - - - | - - - | 22511 | 20669 | 19868 | 63049 | Over-range | 12921 | 10565 | 11962 | 35565 | 3587 | 3198 | 3437 | 10634 | 18475 | 17740 | 15852 | 52067 | 18475 | 17740 | 15852 | 52067 | - - - | - - - | - - - | - - -
5/3/2026 | 3:45:00 AM | 287.12 | 284.77 | 283.12 | 496.79 | 490.31 | 493.82 | 80.2336 | 74.6394 | 72.1141 | 0.2577 | 1.428 | 1.425 | 1.422 | 1.798 | 1.778 | 1.942 | Over-range | 59.97 | 18744 | 18097 | 16218 | 53059 | - - - | - - - | - - - | - - - | 18744 | 18097 | 16218 | 53059 | 12553 | 10242 | 11622 | 34416 | - - - | - - - | - - - | - - - | 12553 | 10242 | 11622 | 34416 | 22921 | 21123 | 20305 | 64348 | # # # | # # # | # # # | # # # | 0.818 | 0.857 | 0.799 | 0.825 | # # # | # # # | # # # | - - - | 0.829 | 0.869 | 0.812 | 0.837 | - - - | 0.649 | 1.71 | 1.56 | 1.52 | 1.53 | 1.52 | 1.55 | 16.28 | 15.88 | 17.48 | 0 | - - - | - - - | - - - | - - - | 22921 | 21123 | 20305 | 64348 | Over-range | 13178 | 10873 | 12204 | 36363 | 3885 | 3527 | 3604 | 11386 | 18726 | 18080 | 16275 | 53081 | 18726 | 18080 | 16275 | 53081 | - - - | - - - | - - - | - - -
5/3/2026 | 4:00:00 AM | 287.23 | 284.91 | 283.22 | 497 | 490.53 | 493.99 | 79.9447 | 74.1582 | 71.9691 | 0.2516 | 1.426 | 1.423 | 1.421 | 1.812 | 1.787 | 1.958 | Over-range | 59.98 | 18727 | 17994 | 16189 | 52909 | - - - | - - - | - - - | - - - | 18727 | 17994 | 16189 | 52909 | 12391 | 10122 | 11564 | 34078 | - - - | - - - | - - - | - - - | 12391 | 10122 | 11564 | 34078 | 22830 | 20984 | 20259 | 64073 | # # # | # # # | # # # | # # # | 0.82 | 0.858 | 0.799 | 0.826 | # # # | # # # | # # # | - - - | 0.832 | 0.87 | 0.813 | 0.839 | - - - | 0.644 | 1.69 | 1.55 | 1.48 | 1.5 | 1.49 | 1.53 | 16.85 | 16.55 | 18.1 | 0 | - - - | - - - | - - - | - - - | 22830 | 20984 | 20259 | 64073 | Over-range | 13051 | 10782 | 12170 | 36110 | 3979 | 3601 | 3673 | 11610 | 18700 | 17985 | 16247 | 52932 | 18700 | 17985 | 16247 | 52932 | - - - | - - - | - - - | - - -
5/3/2026 | 4:15:00 AM | 287.16 | 284.91 | 283.25 | 496.89 | 490.64 | 493.93 | 80.298 | 74.475 | 72.2725 | 0.259 | 1.427 | 1.424 | 1.421 | 1.808 | 1.79 | 1.948 | Over-range | 59.99 | 18756 | 18033 | 16202 | 52991 | - - - | - - - | - - - | - - - | 18756 | 18033 | 16202 | 52991 | 12520 | 10263 | 11697 | 34480 | - - - | - - - | - - - | - - - | 12520 | 10263 | 11697 | 34480 | 22926 | 21074 | 20343 | 64343 | # # # | # # # | # # # | # # # | 0.818 | 0.856 | 0.796 | 0.824 | # # # | # # # | # # # | - - - | 0.83 | 0.868 | 0.81 | 0.836 | - - - | 0.651 | 1.7 | 1.53 | 1.52 | 1.5 | 1.49 | 1.54 | 16.64 | 16.44 | 17.91 | 0 | - - - | - - - | - - - | - - - | 22926 | 21074 | 20343 | 64343 | Over-range | 13177 | 10893 | 12291 | 36469 | 3996 | 3538 | 3659 | 11554 | 18716 | 18085 | 16216 | 53018 | 18716 | 18085 | 16216 | 53018 | - - - | - - - | - - - | - - -
5/3/2026 | 4:30:00 AM | 287.09 | 284.77 | 283.05 | 496.79 | 490.24 | 493.71 | 80.3799 | 74.8097 | 72.3861 | 0.2524 | 1.427 | 1.424 | 1.422 | 1.808 | 1.787 | 1.956 | Over-range | 59.99 | 18825 | 18167 | 16321 | 53312 | - - - | - - - | - - - | - - - | 18825 | 18167 | 16321 | 53312 | 12483 | 10212 | 11579 | 34274 | - - - | - - - | - - - | - - - | 12483 | 10212 | 11579 | 34274 | 22951 | 21168 | 20369 | 64487 | # # # | # # # | # # # | # # # | 0.82 | 0.858 | 0.801 | 0.827 | # # # | # # # | # # # | - - - | 0.832 | 0.871 | 0.816 | 0.84 | - - - | 0.643 | 1.68 | 1.52 | 1.5 | 1.5 | 1.48 | 1.53 | 16.86 | 16.45 | 18.09 | 0 | - - - | - - - | - - - | - - - | 22951 | 21168 | 20369 | 64487 | Over-range | 13122 | 10854 | 12178 | 36258 | 3950 | 3585 | 3675 | 11556 | 18807 | 18149 | 16381 | 53337 | 18807 | 18149 | 16381 | 53337 | - - - | - - - | - - - | - - -
5/3/2026 | 4:45:00 AM | 287.26 | 284.87 | 283.15 | 497.06 | 490.36 | 493.97 | 80.7425 | 75.0039 | 72.0937 | 0.2566 | 1.427 | 1.424 | 1.422 | 1.818 | 1.797 | 1.967 | Over-range | 59.99 | 18853 | 18230 | 16207 | 53291 | - - - | - - - | - - - | - - - | 18853 | 18230 | 16207 | 53291 | 12555 | 10103 | 11499 | 34157 | - - - | - - - | - - - | - - - | 12555 | 10103 | 11499 | 34157 | 23051 | 21210 | 20279 | 64540 | # # # | # # # | # # # | # # # | 0.818 | 0.86 | 0.799 | 0.826 | # # # | # # # | # # # | - - - | 0.831 | 0.873 | 0.814 | 0.839 | - - - | 0.641 | 1.7 | 1.54 | 1.5 | 1.51 | 1.49 | 1.54 | 17.26 | 17.03 | 18.7 | 0 | - - - | - - - | - - - | - - - | 23051 | 21210 | 20279 | 64540 | Over-range | 13248 | 10817 | 12172 | 36355 | 4086 | 3731 | 3857 | 12064 | 18870 | 18207 | 16240 | 53318 | 18870 | 18207 | 16240 | 53318 | - - - | - - - | - - - | - - -
5/3/2026 | 5:00:00 AM | 287.11 | 284.81 | 283.01 | 496.85 | 490.29 | 493.64 | 78.505 | 73.3423 | 70.9403 | 0.2513 | 1.427 | 1.424 | 1.422 | 1.833 | 1.813 | 1.969 | Over-range | 59.98 | 18358 | 17758 | 15986 | 52102 | - - - | - - - | - - - | - - - | 18358 | 17758 | 15986 | 52102 | 12160 | 10021 | 11279 | 33459 | - - - | - - - | - - - | - - - | 12160 | 10021 | 11279 | 33459 | 22421 | 20759 | 19961 | 63140 | # # # | # # # | # # # | # # # | 0.819 | 0.856 | 0.801 | 0.825 | # # # | # # # | # # # | - - - | 0.832 | 0.87 | 0.817 | 0.84 | - - - | 0.642 | 1.7 | 1.52 | 1.49 | 1.51 | 1.49 | 1.53 | 17.79 | 17.6 | 19.06 | 0 | - - - | - - - | - - - | - - - | 22421 | 20759 | 19961 | 63140 | Over-range | 12865 | 10737 | 11942 | 35637 | 4095 | 3752 | 3819 | 11965 | 18346 | 17752 | 16031 | 52129 | 18346 | 17752 | 16031 | 52129 | - - - | - - - | - - - | - - -
5/3/2026 | 5:15:00 AM | 287.05 | 284.7 | 283.01 | 496.68 | 490.14 | 493.65 | 81.9846 | 76.4329 | 73.4832 | 0.2557 | 1.427 | 1.423 | 1.421 | 1.814 | 1.807 | 1.956 | Over-range | 60 | 19260 | 18668 | 16661 | 54590 | - - - | - - - | - - - | - - - | 19260 | 18668 | 16661 | 54590 | 12671 | 10242 | 11604 | 34517 | - - - | - - - | - - - | - - - | 12671 | 10242 | 11604 | 34517 | 23434 | 21651 | 20700 | 65784 | # # # | # # # | # # # | # # # | 0.822 | 0.862 | 0.805 | 0.83 | # # # | # # # | # # # | - - - | 0.835 | 0.875 | 0.82 | 0.844 | - - - | 0.632 | 1.71 | 1.53 | 1.47 | 1.5 | 1.48 | 1.52 | 17.12 | 17.02 | 18.64 | 0 | - - - | - - - | - - - | - - - | 23434 | 21651 | 20700 | 65784 | Over-range | 13342 | 10957 | 12275 | 36687 | 4083 | 3802 | 3908 | 12162 | 19289 | 18620 | 16708 | 54617 | 19289 | 18620 | 16708 | 54617 | - - - | - - - | - - - | - - -
5/3/2026 | 5:30:00 AM | 287 | 284.74 | 282.99 | 496.7 | 490.19 | 493.53 | 79.5343 | 74.2394 | 71.8444 | 0.2537 | 1.426 | 1.423 | 1.421 | 1.827 | 1.817 | 1.963 | Over-range | 60 | 18624 | 17996 | 16207 | 52826 | - - - | - - - | - - - | - - - | 18624 | 17996 | 16207 | 52826 | 12293 | 10136 | 11386 | 33816 | - - - | - - - | - - - | - - - | 12293 | 10136 | 11386 | 33816 | 22708 | 21008 | 20217 | 63933 | # # # | # # # | # # # | # # # | 0.82 | 0.857 | 0.802 | 0.826 | # # # | # # # | # # # | - - - | 0.834 | 0.87 | 0.817 | 0.841 | - - - | 0.64 | 1.67 | 1.54 | 1.48 | 1.49 | 1.47 | 1.52 | 17.67 | 17.54 | 19.11 | 0 | - - - | - - - | - - - | - - - | 22708 | 21008 | 20217 | 63933 | Over-range | 12987 | 10828 | 12076 | 35987 | 4097 | 3722 | 3939 | 12060 | 18671 | 18000 | 16182 | 52853 | 18671 | 18000 | 16182 | 52853 | - - - | - - - | - - - | - - -
5/3/2026 | 5:45:00 AM | 286.86 | 284.52 | 282.8 | 496.34 | 489.86 | 493.27 | 80.3809 | 74.812 | 72.5329 | 0.2554 | 1.427 | 1.423 | 1.421 | 1.824 | 1.817 | 1.961 | Over-range | 60 | 18850 | 18143 | 16347 | 53340 | - - - | - - - | - - - | - - - | 18850 | 18143 | 16347 | 53340 | 12298 | 10091 | 11433 | 33822 | - - - | - - - | - - - | - - - | 12298 | 10091 | 11433 | 33822 | 22925 | 21138 | 20381 | 64444 | # # # | # # # | # # # | # # # | 0.822 | 0.858 | 0.802 | 0.828 | # # # | # # # | # # # | - - - | 0.836 | 0.872 | 0.817 | 0.842 | - - - | 0.634 | 1.66 | 1.53 | 1.47 | 1.48 | 1.46 | 1.51 | 17.59 | 17.59 | 19.11 | 0 | - - - | - - - | - - - | - - - | 22925 | 21138 | 20381 | 64444 | Over-range | 13033 | 10827 | 12158 | 36119 | 4190 | 3801 | 4014 | 12323 | 18887 | 18164 | 16317 | 53367 | 18887 | 18164 | 16317 | 53367 | - - - | - - - | - - - | - - -
5/3/2026 | 6:00:00 AM | 286.78 | 284.48 | 282.74 | 496.29 | 489.73 | 493.15 | 80.9763 | 75.2226 | 72.874 | 0.2545 | 1.427 | 1.423 | 1.422 | 1.809 | 1.792 | 1.945 | Over-range | 60.01 | 18982 | 18266 | 16416 | 53664 | - - - | - - - | - - - | - - - | 18982 | 18266 | 16416 | 53664 | 12520 | 10210 | 11603 | 34333 | - - - | - - - | - - - | - - - | 12520 | 10210 | 11603 | 34333 | 23099 | 21264 | 20487 | 64850 | # # # | # # # | # # # | # # # | 0.822 | 0.859 | 0.801 | 0.828 | # # # | # # # | # # # | - - - | 0.834 | 0.871 | 0.816 | 0.841 | - - - | 0.64 | 1.69 | 1.53 | 1.49 | 1.5 | 1.48 | 1.53 | 16.79 | 16.72 | 18.15 | 0 | - - - | - - - | - - - | - - - | 23099 | 21264 | 20487 | 64850 | Over-range | 13156 | 10876 | 12246 | 36384 | 3925 | 3641 | 3806 | 11729 | 19043 | 18221 | 16433 | 53697 | 19043 | 18221 | 16433 | 53697 | - - - | - - - | - - - | - - -
5/3/2026 | 6:15:00 AM | 286.47 | 284.07 | 282.36 | 495.67 | 489 | 492.59 | 80.0008 | 74.3116 | 72.035 | 0.2532 | 1.426 | 1.423 | 1.421 | 1.813 | 1.8 | 1.952 | Over-range | 60 | 18723 | 18004 | 16194 | 52920 | - - - | - - - | - - - | - - - | 18723 | 18004 | 16194 | 52920 | 12308 | 10048 | 11450 | 33806 | - - - | - - - | - - - | - - - | 12308 | 10048 | 11450 | 33806 | 22779 | 20959 | 20208 | 63945 | # # # | # # # | # # # | # # # | 0.822 | 0.859 | 0.801 | 0.828 | # # # | # # # | # # # | - - - | 0.834 | 0.872 | 0.816 | 0.841 | - - - | 0.639 | 1.67 | 1.5 | 1.47 | 1.47 | 1.46 | 1.5 | 16.97 | 16.82 | 18.35 | 0 | - - - | - - - | - - - | - - - | 22779 | 20959 | 20208 | 63945 | Over-range | 12965 | 10717 | 12075 | 35862 | 3958 | 3616 | 3718 | 11639 | 18715 | 17990 | 16240 | 52945 | 18715 | 17990 | 16240 | 52945 | - - - | - - - | - - - | - - -
5/3/2026 | 6:30:00 AM | 286.29 | 283.91 | 282.13 | 495.36 | 488.71 | 492.2 | 80.2999 | 74.6017 | 71.7404 | 0.2551 | 1.427 | 1.424 | 1.421 | 1.813 | 1.797 | 1.943 | Over-range | 60 | 18758 | 18115 | 16122 | 52995 | - - - | - - - | - - - | - - - | 18758 | 18115 | 16122 | 52995 | 12363 | 9985 | 11358 | 33706 | - - - | - - - | - - - | - - - | 12363 | 9985 | 11358 | 33706 | 22842 | 21016 | 20100 | 63958 | # # # | # # # | # # # | # # # | 0.821 | 0.862 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.834 | 0.875 | 0.816 | 0.842 | - - - | 0.636 | 1.65 | 1.49 | 1.45 | 1.46 | 1.44 | 1.49 | 16.8 | 16.87 | 18.25 | 0 | - - - | - - - | - - - | - - - | 22842 | 21016 | 20100 | 63958 | Over-range | 13026 | 10643 | 11993 | 35779 | 3984 | 3567 | 3737 | 11671 | 18772 | 18161 | 16089 | 53022 | 18772 | 18161 | 16089 | 53022 | - - - | - - - | - - - | - - -
5/3/2026 | 6:45:00 AM | 289.51 | 286.84 | 285.07 | 500.89 | 493.47 | 497.65 | 79.6794 | 74.0064 | 71.2868 | 0.2599 | 1.429 | 1.424 | 1.418 | 1.756 | 1.781 | 1.919 | Over-range | 60.01 | 18572 | 17933 | 15958 | 52463 | - - - | - - - | - - - | - - - | 18572 | 17933 | 15958 | 52463 | 12794 | 10414 | 11693 | 34901 | - - - | - - - | - - - | - - - | 12794 | 10414 | 11693 | 34901 | 22894 | 21035 | 20164 | 64093 | # # # | # # # | # # # | # # # | 0.811 | 0.853 | 0.791 | 0.819 | # # # | # # # | # # # | - - - | 0.823 | 0.863 | 0.804 | 0.83 | - - - | 0.665 | 1.78 | 1.59 | 1.54 | 1.58 | 1.53 | 1.61 | 15.79 | 15.43 | 17.7 | 0 | - - - | - - - | - - - | - - - | 22894 | 21035 | 20164 | 64093 | Over-range | 13372 | 10970 | 12305 | 36761 | 3717 | 3287 | 3695 | 11106 | 18629 | 17939 | 15915 | 52484 | 18629 | 17939 | 15915 | 52484 | - - - | - - - | - - - | - - -
5/3/2026 | 7:00:00 AM | 290.05 | 287.36 | 285.59 | 501.82 | 494.33 | 498.59 | 78.9035 | 73.2353 | 70.1481 | 0.2594 | 1.428 | 1.423 | 1.417 | 1.725 | 1.762 | 1.907 | Over-range | 60.02 | 18364 | 17819 | 15700 | 51882 | - - - | - - - | - - - | - - - | 18364 | 17819 | 15700 | 51882 | 12888 | 10417 | 11688 | 34993 | - - - | - - - | - - - | - - - | 12888 | 10417 | 11688 | 34993 | 22747 | 20895 | 19906 | 63548 | # # # | # # # | # # # | # # # | 0.807 | 0.853 | 0.789 | 0.816 | # # # | # # # | # # # | - - - | 0.817 | 0.862 | 0.8 | 0.827 | - - - | 0.675 | 1.79 | 1.63 | 1.55 | 1.61 | 1.54 | 1.64 | 14.9 | 14.37 | 17.04 | 0 | - - - | - - - | - - - | - - - | 22747 | 20895 | 19906 | 63548 | Over-range | 13417 | 10898 | 12225 | 36664 | 3577 | 3048 | 3439 | 10521 | 18351 | 17874 | 15672 | 51897 | 18351 | 17874 | 15672 | 51897 | - - - | - - - | - - - | - - -
5/3/2026 | 7:15:00 AM | 289.41 | 286.69 | 284.88 | 500.7 | 493.12 | 497.43 | 78.2425 | 72.7427 | 69.7792 | 0.2585 | 1.428 | 1.423 | 1.417 | 1.725 | 1.762 | 1.908 | Over-range | 60.01 | 18179 | 17636 | 15596 | 51411 | - - - | - - - | - - - | - - - | 18179 | 17636 | 15596 | 51411 | 12740 | 10315 | 11582 | 34638 | - - - | - - - | - - - | - - - | 12740 | 10315 | 11582 | 34638 | 22497 | 20693 | 19742 | 62932 | # # # | # # # | # # # | # # # | 0.808 | 0.852 | 0.79 | 0.817 | # # # | # # # | # # # | - - - | 0.817 | 0.862 | 0.802 | 0.827 | - - - | 0.674 | 1.79 | 1.63 | 1.54 | 1.61 | 1.55 | 1.63 | 14.98 | 14.4 | 17.03 | 0 | - - - | - - - | - - - | - - - | 22497 | 20693 | 19742 | 62932 | Over-range | 13246 | 10813 | 12093 | 36269 | 3485 | 3109 | 3347 | 10372 | 18150 | 17628 | 15646 | 51424 | 18150 | 17628 | 15646 | 51424 | - - - | - - - | - - - | - - -
5/3/2026 | 7:30:00 AM | 289.26 | 286.51 | 284.76 | 500.42 | 492.82 | 497.23 | 79.0804 | 73.4324 | 70.5806 | 0.2574 | 1.429 | 1.424 | 1.418 | 1.711 | 1.743 | 1.884 | Over-range | 60.03 | 18473 | 17877 | 15857 | 52207 | - - - | - - - | - - - | - - - | 18473 | 17877 | 15857 | 52207 | 12808 | 10378 | 11663 | 34849 | - - - | - - - | - - - | - - - | 12808 | 10378 | 11663 | 34849 | 22757 | 20914 | 19990 | 63660 | # # # | # # # | # # # | # # # | 0.812 | 0.855 | 0.793 | 0.82 | # # # | # # # | # # # | - - - | 0.821 | 0.864 | 0.805 | 0.83 | - - - | 0.668 | 1.82 | 1.65 | 1.6 | 1.64 | 1.58 | 1.68 | 14.44 | 13.84 | 16.36 | 0 | - - - | - - - | - - - | - - - | 22757 | 20914 | 19990 | 63660 | Over-range | 13284 | 10843 | 12164 | 36407 | 3403 | 3020 | 3342 | 10208 | 18481 | 17868 | 15879 | 52227 | 18481 | 17868 | 15879 | 52227 | - - - | - - - | - - - | - - -
5/3/2026 | 7:45:00 AM | 289.1 | 286.36 | 284.64 | 500.11 | 492.61 | 497 | 79.6649 | 74.0378 | 70.9776 | 0.2608 | 1.429 | 1.424 | 1.418 | 1.725 | 1.758 | 1.883 | Over-range | 60.02 | 18535 | 17964 | 15890 | 52389 | - - - | - - - | - - - | - - - | 18535 | 17964 | 15890 | 52389 | 12860 | 10392 | 11640 | 34892 | - - - | - - - | - - - | - - - | 12860 | 10392 | 11640 | 34892 | 22873 | 21032 | 20058 | 63963 | # # # | # # # | # # # | # # # | 0.81 | 0.854 | 0.792 | 0.819 | # # # | # # # | # # # | - - - | 0.821 | 0.864 | 0.804 | 0.83 | - - - | 0.666 | 1.84 | 1.69 | 1.59 | 1.66 | 1.6 | 1.69 | 14.85 | 14.62 | 16.96 | 0 | - - - | - - - | - - - | - - - | 22873 | 21032 | 20058 | 63963 | Over-range | 13387 | 10913 | 12222 | 36641 | 3531 | 3155 | 3567 | 10697 | 18596 | 17961 | 15847 | 52404 | 18596 | 17961 | 15847 | 52404 | - - - | - - - | - - - | - - -
5/3/2026 | 8:00:00 AM | 289.07 | 286.34 | 284.75 | 499.97 | 492.76 | 497.12 | 78.1586 | 72.769 | 70.2434 | 0.2607 | 1.428 | 1.423 | 1.418 | 1.737 | 1.774 | 1.893 | Over-range | 60.03 | 18182 | 17573 | 15723 | 51478 | - - - | - - - | - - - | - - - | 18182 | 17573 | 15723 | 51478 | 12591 | 10310 | 11525 | 34427 | - - - | - - - | - - - | - - - | 12591 | 10310 | 11525 | 34427 | 22421 | 20654 | 19850 | 62924 | # # # | # # # | # # # | # # # | 0.811 | 0.851 | 0.792 | 0.818 | # # # | # # # | # # # | - - - | 0.822 | 0.861 | 0.805 | 0.829 | - - - | 0.669 | 1.85 | 1.67 | 1.63 | 1.66 | 1.61 | 1.7 | 15.35 | 15.07 | 17.41 | 0 | - - - | - - - | - - - | - - - | 22421 | 20654 | 19850 | 62924 | Over-range | 13111 | 10836 | 12104 | 36154 | 3503 | 3194 | 3568 | 10642 | 18240 | 17544 | 15715 | 51499 | 18240 | 17544 | 15715 | 51499 | - - - | - - - | - - - | - - -
5/3/2026 | 8:15:00 AM | 288.7 | 285.97 | 284.43 | 499.35 | 492.11 | 496.54 | 80.315 | 74.6126 | 71.3036 | 0.2624 | 1.428 | 1.424 | 1.418 | 1.718 | 1.752 | 1.872 | Over-range | 60.01 | 18733 | 18202 | 16038 | 52972 | - - - | - - - | - - - | - - - | 18733 | 18202 | 16038 | 52972 | 13012 | 10437 | 11776 | 35225 | - - - | - - - | - - - | - - - | 13012 | 10437 | 11776 | 35225 | 23092 | 21231 | 20190 | 64513 | # # # | # # # | # # # | # # # | 0.811 | 0.857 | 0.794 | 0.821 | # # # | # # # | # # # | - - - | 0.82 | 0.867 | 0.806 | 0.831 | - - - | 0.665 | 1.82 | 1.69 | 1.64 | 1.66 | 1.62 | 1.7 | 14.33 | 14 | 16.27 | 0 | - - - | - - - | - - - | - - - | 23092 | 21231 | 20190 | 64513 | Over-range | 13497 | 10922 | 12256 | 36802 | 3480 | 3115 | 3291 | 10364 | 18697 | 18217 | 16085 | 52999 | 18697 | 18217 | 16085 | 52999 | - - - | - - - | - - - | - - -
5/3/2026 | 8:30:00 AM | 288.46 | 285.57 | 284.12 | 498.77 | 491.46 | 496.13 | 77.739 | 72.0615 | 69.5539 | 0.2585 | 1.429 | 1.424 | 1.418 | 1.73 | 1.781 | 1.897 | Over-range | 60.01 | 18016 | 17359 | 15473 | 50849 | - - - | - - - | - - - | - - - | 18016 | 17359 | 15473 | 50849 | 12486 | 10143 | 11476 | 34105 | - - - | - - - | - - - | - - - | 12486 | 10143 | 11476 | 34105 | 22234 | 20378 | 19592 | 62205 | # # # | # # # | # # # | # # # | 0.81 | 0.852 | 0.79 | 0.817 | # # # | # # # | # # # | - - - | 0.82 | 0.862 | 0.802 | 0.828 | - - - | 0.671 | 1.83 | 1.66 | 1.63 | 1.65 | 1.61 | 1.69 | 15.24 | 14.87 | 17.33 | 0 | - - - | - - - | - - - | - - - | 22234 | 20378 | 19592 | 62205 | Over-range | 13022 | 10658 | 12005 | 35797 | 3548 | 3129 | 3383 | 10466 | 17974 | 17390 | 15503 | 50867 | 17974 | 17390 | 15503 | 50867 | - - - | - - - | - - - | - - -
5/3/2026 | 8:45:00 AM | 288.37 | 285.36 | 283.91 | 498.51 | 491.03 | 495.93 | 79.6594 | 73.7029 | 70.8369 | 0.26 | 1.429 | 1.425 | 1.419 | 1.738 | 1.784 | 1.913 | Over-range | 60.02 | 18530 | 17868 | 15817 | 52215 | - - - | - - - | - - - | - - - | 18530 | 17868 | 15817 | 52215 | 12717 | 10162 | 11578 | 34458 | - - - | - - - | - - - | - - - | 12717 | 10162 | 11578 | 34458 | 22814 | 20861 | 19963 | 63638 | # # # | # # # | # # # | # # # | 0.812 | 0.857 | 0.792 | 0.821 | # # # | # # # | # # # | - - - | 0.823 | 0.868 | 0.806 | 0.832 | - - - | 0.66 | 1.79 | 1.64 | 1.58 | 1.61 | 1.57 | 1.65 | 15.68 | 15.37 | 17.9 | 0 | - - - | - - - | - - - | - - - | 22814 | 20861 | 19963 | 63638 | Over-range | 13295 | 10746 | 12164 | 36331 | 3725 | 3356 | 3595 | 11125 | 18508 | 17871 | 15864 | 52244 | 18508 | 17871 | 15864 | 52244 | - - - | - - - | - - - | - - -
5/3/2026 | 9:00:00 AM | 287.05 | 283.93 | 282.59 | 496.09 | 488.63 | 493.7 | 80.196 | 73.9026 | 71.2099 | 0.2575 | 1.428 | 1.424 | 1.42 | 1.759 | 1.785 | 1.926 | Over-range | 60.01 | 18679 | 17929 | 15895 | 52503 | - - - | - - - | - - - | - - - | 18679 | 17929 | 15895 | 52503 | 12629 | 10047 | 11554 | 34230 | - - - | - - - | - - - | - - - | 12629 | 10047 | 11554 | 34230 | 22903 | 20855 | 20012 | 63770 | # # # | # # # | # # # | # # # | 0.816 | 0.86 | 0.794 | 0.823 | # # # | # # # | # # # | - - - | 0.827 | 0.871 | 0.808 | 0.835 | - - - | 0.652 | 1.72 | 1.6 | 1.56 | 1.56 | 1.55 | 1.6 | 16.08 | 15.54 | 18.05 | 0 | - - - | - - - | - - - | - - - | 22903 | 20855 | 20012 | 63770 | Over-range | 13245 | 10641 | 12148 | 36167 | 3864 | 3380 | 3630 | 11325 | 18636 | 17951 | 15935 | 52523 | 18636 | 17951 | 15935 | 52523 | - - - | - - - | - - - | - - -
5/3/2026 | 9:15:00 AM | 284.09 | 281.43 | 279.88 | 491.17 | 484.5 | 488.59 | 79.6279 | 74.2864 | 71.6246 | 0.2428 | 1.428 | 1.426 | 1.425 | 1.804 | 1.8 | 1.944 | Over-range | 60.01 | 18547 | 17937 | 16107 | 52591 | - - - | - - - | - - - | - - - | 18547 | 17937 | 16107 | 52591 | 12069 | 9835 | 11124 | 33028 | - - - | - - - | - - - | - - - | 12069 | 9835 | 11124 | 33028 | 22498 | 20775 | 19929 | 63202 | # # # | # # # | # # # | # # # | 0.824 | 0.863 | 0.808 | 0.832 | # # # | # # # | # # # | - - - | 0.837 | 0.876 | 0.822 | 0.845 | - - - | 0.628 | 1.75 | 1.66 | 1.64 | 1.6 | 1.63 | 1.64 | 16.84 | 16.39 | 18.08 | 0 | - - - | - - - | - - - | - - - | 22498 | 20775 | 19929 | 63202 | Over-range | 12727 | 10470 | 11725 | 35024 | 3943 | 3493 | 3609 | 11378 | 18508 | 17979 | 16149 | 52635 | 18508 | 17979 | 16149 | 52635 | - - - | - - - | - - - | - - -
5/3/2026 | 9:30:00 AM | 284 | 281.15 | 279.74 | 490.88 | 484.04 | 488.48 | 80.5089 | 74.529 | 71.7669 | 0.2462 | 1.428 | 1.427 | 1.424 | 1.811 | 1.819 | 1.962 | Over-range | 60 | 18747 | 18021 | 16070 | 52838 | - - - | - - - | - - - | - - - | 18747 | 18021 | 16070 | 52838 | 12110 | 9658 | 11121 | 32889 | - - - | - - - | - - - | - - - | 12110 | 9658 | 11121 | 32889 | 22712 | 20789 | 19935 | 63437 | # # # | # # # | # # # | # # # | 0.825 | 0.867 | 0.806 | 0.833 | # # # | # # # | # # # | - - - | 0.839 | 0.88 | 0.821 | 0.847 | - - - | 0.622 | 1.71 | 1.6 | 1.59 | 1.56 | 1.59 | 1.59 | 17.28 | 17.03 | 18.85 | 0 | - - - | - - - | - - - | - - - | 22712 | 20789 | 19935 | 63437 | Over-range | 12814 | 10351 | 11785 | 35073 | 4074 | 3614 | 3793 | 11872 | 18728 | 18060 | 16084 | 52873 | 18728 | 18060 | 16084 | 52873 | - - - | - - - | - - - | - - -
5/3/2026 | 9:45:00 AM | 284.09 | 281.31 | 279.85 | 491.11 | 484.27 | 488.63 | 79.3528 | 73.7695 | 71.5866 | 0.2462 | 1.428 | 1.426 | 1.423 | 1.804 | 1.819 | 1.953 | Over-range | 60.01 | 18494 | 17752 | 16046 | 52293 | - - - | - - - | - - - | - - - | 18494 | 17752 | 16046 | 52293 | 11950 | 9745 | 11059 | 32754 | - - - | - - - | - - - | - - - | 11950 | 9745 | 11059 | 32754 | 22403 | 20598 | 19903 | 62904 | # # # | # # # | # # # | # # # | 0.826 | 0.862 | 0.806 | 0.831 | # # # | # # # | # # # | - - - | 0.839 | 0.875 | 0.822 | 0.845 | - - - | 0.626 | 1.66 | 1.57 | 1.53 | 1.51 | 1.52 | 1.54 | 17.31 | 17.01 | 18.91 | 0 | - - - | - - - | - - - | - - - | 22403 | 20598 | 19903 | 62904 | Over-range | 12627 | 10425 | 11759 | 34911 | 3972 | 3605 | 3900 | 11797 | 18566 | 17732 | 16036 | 52334 | 18566 | 17732 | 16036 | 52334 | - - - | - - - | - - - | - - -
5/3/2026 | 10:00:00 AM | 284.15 | 281.23 | 279.85 | 491.08 | 484.15 | 488.74 | 80.7663 | 74.4994 | 71.987 | 0.2507 | 1.428 | 1.425 | 1.422 | 1.772 | 1.796 | 1.938 | Over-range | 60.03 | 18821 | 18027 | 16088 | 52936 | - - - | - - - | - - - | - - - | 18821 | 18027 | 16088 | 52936 | 12291 | 9773 | 11308 | 33372 | - - - | - - - | - - - | - - - | 12291 | 9773 | 11308 | 33372 | 22820 | 20812 | 20025 | 63657 | # # # | # # # | # # # | # # # | 0.825 | 0.866 | 0.803 | 0.832 | # # # | # # # | # # # | - - - | 0.836 | 0.878 | 0.817 | 0.844 | - - - | 0.63 | 1.62 | 1.51 | 1.49 | 1.46 | 1.46 | 1.49 | 16.21 | 15.84 | 18.01 | 0 | - - - | - - - | - - - | - - - | 22820 | 20812 | 20025 | 63657 | Over-range | 12896 | 10387 | 11914 | 35327 | 3803 | 3420 | 3653 | 11309 | 18831 | 18011 | 16133 | 52976 | 18831 | 18011 | 16133 | 52976 | - - - | - - - | - - - | - - -
5/3/2026 | 10:15:00 AM | 283.52 | 280.49 | 279.26 | 489.84 | 482.96 | 487.77 | 79.6548 | 73.3634 | 71.2401 | 0.2488 | 1.427 | 1.424 | 1.421 | 1.784 | 1.805 | 1.951 | Over-range | 60 | 18557 | 17701 | 15897 | 52155 | - - - | - - - | - - - | - - - | 18557 | 17701 | 15897 | 52155 | 12028 | 9598 | 11109 | 32735 | - - - | - - - | - - - | - - - | 12028 | 9598 | 11109 | 32735 | 22464 | 20446 | 19782 | 62692 | # # # | # # # | # # # | # # # | 0.826 | 0.866 | 0.804 | 0.832 | # # # | # # # | # # # | - - - | 0.839 | 0.877 | 0.818 | 0.845 | - - - | 0.628 | 1.59 | 1.5 | 1.44 | 1.44 | 1.44 | 1.46 | 16.74 | 16.22 | 18.54 | 0 | - - - | - - - | - - - | - - - | 22464 | 20446 | 19782 | 62692 | Over-range | 12652 | 10221 | 11763 | 34759 | 3812 | 3409 | 3769 | 11392 | 18621 | 17658 | 15903 | 52182 | 18621 | 17658 | 15903 | 52182 | - - - | - - - | - - - | - - -
5/3/2026 | 10:30:00 AM | 283.22 | 280.07 | 278.93 | 489.23 | 482.24 | 487.28 | 81.1373 | 74.6779 | 72.3512 | 0.2566 | 1.426 | 1.424 | 1.421 | 1.787 | 1.809 | 1.959 | Over-range | 60.01 | 18966 | 18087 | 16213 | 53266 | - - - | - - - | - - - | - - - | 18966 | 18087 | 16213 | 53266 | 12112 | 9590 | 11158 | 32859 | - - - | - - - | - - - | - - - | 12112 | 9590 | 11158 | 32859 | 22864 | 20790 | 20076 | 63730 | # # # | # # # | # # # | # # # | 0.83 | 0.87 | 0.808 | 0.836 | # # # | # # # | # # # | - - - | 0.842 | 0.882 | 0.823 | 0.849 | - - - | 0.617 | 1.59 | 1.49 | 1.43 | 1.43 | 1.43 | 1.44 | 16.86 | 16.28 | 18.73 | 0 | - - - | - - - | - - - | - - - | 22864 | 20790 | 20076 | 63730 | Over-range | 12763 | 10237 | 11829 | 34961 | 3920 | 3486 | 3833 | 11659 | 19009 | 18055 | 16236 | 53300 | 19009 | 18055 | 16236 | 53300 | - - - | - - - | - - - | - - -
5/3/2026 | 10:45:00 AM | 283.32 | 280.23 | 279.08 | 489.41 | 482.58 | 487.48 | 80.3341 | 73.9581 | 71.6955 | 0.2489 | 1.427 | 1.425 | 1.421 | 1.788 | 1.817 | 1.956 | Over-range | 60.01 | 18706 | 17842 | 15987 | 52535 | - - - | - - - | - - - | - - - | 18706 | 17842 | 15987 | 52535 | 12040 | 9546 | 11130 | 32716 | - - - | - - - | - - - | - - - | 12040 | 9546 | 11130 | 32716 | 22630 | 20582 | 19886 | 63098 | # # # | # # # | # # # | # # # | 0.827 | 0.867 | 0.804 | 0.833 | # # # | # # # | # # # | - - - | 0.839 | 0.88 | 0.82 | 0.846 | - - - | 0.623 | 1.59 | 1.49 | 1.44 | 1.44 | 1.43 | 1.45 | 16.98 | 16.67 | 18.92 | 0 | - - - | - - - | - - - | - - - | 22630 | 20582 | 19886 | 63098 | Over-range | 12721 | 10237 | 11810 | 34897 | 3980 | 3583 | 3835 | 11812 | 18709 | 17822 | 16036 | 52566 | 18709 | 17822 | 16036 | 52566 | - - - | - - - | - - - | - - -
5/3/2026 | 11:00:00 AM | 283.12 | 280 | 278.89 | 489.05 | 482.18 | 487.16 | 78.6189 | 72.438 | 70.4293 | 0.2563 | 1.428 | 1.425 | 1.422 | 1.787 | 1.816 | 1.958 | Over-range | 60.01 | 18328 | 17456 | 15730 | 51513 | - - - | - - - | - - - | - - - | 18328 | 17456 | 15730 | 51513 | 11716 | 9345 | 10862 | 31924 | - - - | - - - | - - - | - - - | 11716 | 9345 | 10862 | 31924 | 22112 | 20125 | 19507 | 61744 | # # # | # # # | # # # | # # # | 0.829 | 0.867 | 0.806 | 0.834 | # # # | # # # | # # # | - - - | 0.842 | 0.88 | 0.822 | 0.848 | - - - | 0.62 | 1.6 | 1.48 | 1.47 | 1.44 | 1.45 | 1.47 | 17.09 | 16.62 | 18.95 | 0 | - - - | - - - | - - - | - - - | 22112 | 20125 | 19507 | 61744 | Over-range | 12361 | 10000 | 11525 | 34005 | 3826 | 3451 | 3744 | 11402 | 18361 | 17411 | 15780 | 51552 | 18361 | 17411 | 15780 | 51552 | - - - | - - - | - - - | - - -
5/3/2026 | 11:15:00 AM | 282.79 | 279.67 | 278.58 | 488.48 | 481.62 | 486.63 | 81.0069 | 74.3136 | 71.8849 | 0.2518 | 1.428 | 1.426 | 1.422 | 1.775 | 1.792 | 1.944 | Over-range | 60 | 18890 | 17998 | 16047 | 52935 | - - - | - - - | - - - | - - - | 18890 | 17998 | 16047 | 52935 | 12138 | 9502 | 11146 | 32785 | - - - | - - - | - - - | - - - | 12138 | 9502 | 11146 | 32785 | 22787 | 20651 | 19907 | 63345 | # # # | # # # | # # # | # # # | 0.829 | 0.872 | 0.806 | 0.836 | # # # | # # # | # # # | - - - | 0.841 | 0.883 | 0.821 | 0.848 | - - - | 0.619 | 1.57 | 1.5 | 1.45 | 1.43 | 1.44 | 1.46 | 16.18 | 15.74 | 18.08 | 0 | - - - | - - - | - - - | - - - | 22787 | 20651 | 19907 | 63345 | Over-range | 12737 | 10115 | 11771 | 34766 | 3759 | 3374 | 3689 | 11293 | 18941 | 17953 | 16074 | 52968 | 18941 | 17953 | 16074 | 52968 | - - - | - - - | - - - | - - -
5/3/2026 | 11:30:00 AM | 282.92 | 279.9 | 278.73 | 488.73 | 482.05 | 486.84 | 77.7969 | 71.649 | 69.9857 | 0.2522 | 1.429 | 1.426 | 1.423 | 1.792 | 1.806 | 1.947 | Over-range | 60.02 | 18145 | 17242 | 15618 | 51006 | - - - | - - - | - - - | - - - | 18145 | 17242 | 15618 | 51006 | 11625 | 9370 | 10889 | 31884 | - - - | - - - | - - - | - - - | 11625 | 9370 | 10889 | 31884 | 21900 | 19934 | 19402 | 61237 | # # # | # # # | # # # | # # # | 0.829 | 0.865 | 0.805 | 0.833 | # # # | # # # | # # # | - - - | 0.841 | 0.877 | 0.82 | 0.846 | - - - | 0.625 | 1.61 | 1.5 | 1.45 | 1.45 | 1.45 | 1.47 | 16.62 | 16.18 | 18.26 | 0 | - - - | - - - | - - - | - - - | 21900 | 19934 | 19402 | 61237 | Over-range | 12255 | 9992 | 11502 | 33860 | 3772 | 3369 | 3599 | 11102 | 18139 | 17230 | 15669 | 51038 | 18139 | 17230 | 15669 | 51038 | - - - | - - - | - - - | - - -
5/3/2026 | 11:45:00 AM | 282.79 | 279.66 | 278.56 | 488.42 | 481.62 | 486.63 | 80.8188 | 74.2459 | 71.9746 | 0.258 | 1.428 | 1.426 | 1.423 | 1.787 | 1.81 | 1.943 | Over-range | 60.02 | 18803 | 17896 | 16022 | 52722 | - - - | - - - | - - - | - - - | 18803 | 17896 | 16022 | 52722 | 12055 | 9520 | 11122 | 32696 | - - - | - - - | - - - | - - - | 12055 | 9520 | 11122 | 32696 | 22701 | 20596 | 19903 | 63200 | # # # | # # # | # # # | # # # | 0.828 | 0.869 | 0.805 | 0.834 | # # # | # # # | # # # | - - - | 0.841 | 0.881 | 0.819 | 0.847 | - - - | 0.62 | 1.57 | 1.53 | 1.46 | 1.44 | 1.44 | 1.47 | 16.5 | 16.21 | 18.45 | 0 | - - - | - - - | - - - | - - - | 22701 | 20596 | 19903 | 63200 | Over-range | 12704 | 10169 | 11792 | 34800 | 3875 | 3444 | 3796 | 11554 | 18850 | 17898 | 16008 | 52756 | 18850 | 17898 | 16008 | 52756 | - - - | - - - | - - - | - - -
5/3/2026 | 12:00:00 PM | 282.47 | 279.35 | 278.24 | 487.9 | 481.05 | 486.07 | 80.4636 | 74.1168 | 71.8671 | 0.2547 | 1.429 | 1.426 | 1.423 | 1.798 | 1.816 | 1.955 | Over-range | 60.01 | 18722 | 17857 | 16035 | 52614 | - - - | - - - | - - - | - - - | 18722 | 17857 | 16035 | 52614 | 11993 | 9557 | 11063 | 32614 | - - - | - - - | - - - | - - - | 11993 | 9557 | 11063 | 32614 | 22597 | 20561 | 19876 | 63034 | # # # | # # # | # # # | # # # | 0.829 | 0.869 | 0.807 | 0.835 | # # # | # # # | # # # | - - - | 0.842 | 0.881 | 0.821 | 0.848 | - - - | 0.62 | 1.6 | 1.53 | 1.46 | 1.45 | 1.46 | 1.49 | 16.95 | 16.48 | 18.82 | 0 | - - - | - - - | - - - | - - - | 22597 | 20561 | 19876 | 63034 | Over-range | 12647 | 10182 | 11734 | 34689 | 3913 | 3423 | 3827 | 11560 | 18782 | 17871 | 16002 | 52654 | 18782 | 17871 | 16002 | 52654 | - - - | - - - | - - - | - - -
5/3/2026 | 12:15:00 PM | 282.49 | 279.4 | 278.29 | 487.94 | 481.17 | 486.11 | 80.2843 | 73.9714 | 71.7101 | 0.2592 | 1.429 | 1.427 | 1.424 | 1.803 | 1.821 | 1.954 | Over-range | 60 | 18714 | 17854 | 16030 | 52599 | - - - | - - - | - - - | - - - | 18714 | 17854 | 16030 | 52599 | 11925 | 9469 | 10987 | 32381 | - - - | - - - | - - - | - - - | 11925 | 9469 | 10987 | 32381 | 22562 | 20544 | 19845 | 62950 | # # # | # # # | # # # | # # # | 0.83 | 0.869 | 0.808 | 0.836 | # # # | # # # | # # # | - - - | 0.843 | 0.882 | 0.823 | 0.849 | - - - | 0.616 | 1.61 | 1.54 | 1.46 | 1.46 | 1.47 | 1.5 | 16.98 | 16.76 | 18.92 | 0 | - - - | - - - | - - - | - - - | 22562 | 20544 | 19845 | 62950 | Over-range | 12595 | 10148 | 11688 | 34556 | 3930 | 3537 | 3877 | 11739 | 18778 | 17835 | 16020 | 52634 | 18778 | 17835 | 16020 | 52634 | - - - | - - - | - - - | - - -
5/3/2026 | 12:30:00 PM | 282.37 | 279.34 | 278.19 | 487.8 | 481.06 | 485.89 | 79.6601 | 73.3475 | 71.1511 | 0.2516 | 1.429 | 1.426 | 1.423 | 1.804 | 1.819 | 1.953 | Over-range | 60.01 | 18515 | 17653 | 15845 | 52014 | - - - | - - - | - - - | - - - | 18515 | 17653 | 15845 | 52014 | 11851 | 9414 | 10988 | 32253 | - - - | - - - | - - - | - - - | 11851 | 9414 | 10988 | 32253 | 22357 | 20343 | 19666 | 62366 | # # # | # # # | # # # | # # # | 0.828 | 0.868 | 0.806 | 0.834 | # # # | # # # | # # # | - - - | 0.841 | 0.881 | 0.821 | 0.848 | - - - | 0.62 | 1.6 | 1.53 | 1.45 | 1.45 | 1.44 | 1.48 | 16.99 | 16.73 | 18.78 | 0 | - - - | - - - | - - - | - - - | 22357 | 20343 | 19666 | 62366 | Over-range | 12522 | 10095 | 11636 | 34378 | 3927 | 3536 | 3718 | 11580 | 18501 | 17645 | 15907 | 52052 | 18501 | 17645 | 15907 | 52052 | - - - | - - - | - - - | - - -
5/3/2026 | 12:45:00 PM | 282.25 | 279.19 | 278.07 | 487.57 | 480.81 | 485.7 | 79.821 | 73.7867 | 71.6467 | 0.2588 | 1.429 | 1.426 | 1.424 | 1.807 | 1.825 | 1.952 | Over-range | 60.01 | 18620 | 17780 | 16045 | 52445 | - - - | - - - | - - - | - - - | 18620 | 17780 | 16045 | 52445 | 11773 | 9417 | 10915 | 32105 | - - - | - - - | - - - | - - - | 11773 | 9417 | 10915 | 32105 | 22416 | 20477 | 19810 | 62703 | # # # | # # # | # # # | # # # | 0.831 | 0.868 | 0.81 | 0.836 | # # # | # # # | # # # | - - - | 0.844 | 0.882 | 0.826 | 0.851 | - - - | 0.612 | 1.65 | 1.53 | 1.46 | 1.46 | 1.46 | 1.5 | 17.28 | 17.09 | 19.13 | 0 | - - - | - - - | - - - | - - - | 22416 | 20477 | 19810 | 62703 | Over-range | 12466 | 10137 | 11606 | 34323 | 3998 | 3658 | 3847 | 11863 | 18632 | 17748 | 16113 | 52493 | 18632 | 17748 | 16113 | 52493 | - - - | - - - | - - - | - - -
5/3/2026 | 1:00:00 PM | 282.08 | 279.04 | 277.89 | 487.27 | 480.55 | 485.4 | 80.9121 | 74.7668 | 72.2703 | 0.2651 | 1.429 | 1.426 | 1.424 | 1.805 | 1.823 | 1.947 | Over-range | 60.01 | 18852 | 18044 | 16180 | 53075 | - - - | - - - | - - - | - - - | 18852 | 18044 | 16180 | 53075 | 11959 | 9474 | 10991 | 32424 | - - - | - - - | - - - | - - - | 11959 | 9474 | 10991 | 32424 | 22700 | 20730 | 19965 | 63395 | # # # | # # # | # # # | # # # | 0.831 | 0.87 | 0.81 | 0.837 | # # # | # # # | # # # | - - - | 0.844 | 0.883 | 0.827 | 0.851 | - - - | 0.611 | 1.63 | 1.51 | 1.5 | 1.47 | 1.47 | 1.51 | 17.1 | 17 | 18.97 | 0 | - - - | - - - | - - - | - - - | 22700 | 20730 | 19965 | 63395 | Over-range | 12636 | 10192 | 11686 | 34638 | 3978 | 3664 | 3872 | 11905 | 18890 | 17998 | 16227 | 53115 | 18890 | 17998 | 16227 | 53115 | - - - | - - - | - - - | - - -
5/3/2026 | 1:15:00 PM | 282.1 | 279.14 | 277.98 | 487.33 | 480.77 | 485.47 | 78.5416 | 72.7939 | 70.9776 | 0.2616 | 1.43 | 1.427 | 1.425 | 1.825 | 1.845 | 1.957 | Over-range | 60.01 | 18303 | 17454 | 15882 | 51638 | - - - | - - - | - - - | - - - | 18303 | 17454 | 15882 | 51638 | 11452 | 9290 | 10729 | 31470 | - - - | - - - | - - - | - - - | 11452 | 9290 | 10729 | 31470 | 21990 | 20142 | 19577 | 61708 | # # # | # # # | # # # | # # # | 0.832 | 0.867 | 0.811 | 0.837 | # # # | # # # | # # # | - - - | 0.846 | 0.881 | 0.828 | 0.852 | - - - | 0.609 | 1.64 | 1.56 | 1.48 | 1.48 | 1.47 | 1.52 | 17.9 | 17.87 | 19.72 | 0 | - - - | - - - | - - - | - - - | 21990 | 20142 | 19577 | 61708 | Over-range | 12180 | 10038 | 11434 | 33752 | 4039 | 3706 | 3853 | 11904 | 18295 | 17441 | 15949 | 51685 | 18295 | 17441 | 15949 | 51685 | - - - | - - - | - - - | - - -
5/3/2026 | 1:30:00 PM | 282.04 | 279.09 | 277.93 | 487.27 | 480.64 | 485.37 | 81.8514 | 75.6564 | 73.2585 | 0.2663 | 1.429 | 1.426 | 1.424 | 1.809 | 1.824 | 1.939 | Over-range | 60.01 | 19126 | 18284 | 16453 | 53863 | - - - | - - - | - - - | - - - | 19126 | 18284 | 16453 | 53863 | 12011 | 9583 | 11085 | 32679 | - - - | - - - | - - - | - - - | 12011 | 9583 | 11085 | 32679 | 22959 | 20982 | 20244 | 64184 | # # # | # # # | # # # | # # # | 0.833 | 0.871 | 0.813 | 0.839 | # # # | # # # | # # # | - - - | 0.847 | 0.885 | 0.828 | 0.853 | - - - | 0.607 | 1.63 | 1.51 | 1.48 | 1.47 | 1.46 | 1.5 | 17.15 | 17.12 | 18.94 | 0 | - - - | - - - | - - - | - - - | 22959 | 20982 | 20244 | 64184 | Over-range | 12696 | 10282 | 11785 | 34884 | 4027 | 3649 | 3922 | 11975 | 19180 | 18289 | 16443 | 53912 | 19180 | 18289 | 16443 | 53912 | - - - | - - - | - - - | - - -
5/3/2026 | 1:45:00 PM | 281.62 | 278.68 | 277.52 | 486.53 | 479.95 | 484.66 | 81.0855 | 74.8771 | 72.9759 | 0.2658 | 1.429 | 1.426 | 1.424 | 1.815 | 1.826 | 1.937 | Over-range | 60.01 | 18838 | 17931 | 16247 | 53016 | - - - | - - - | - - - | - - - | 18838 | 17931 | 16247 | 53016 | 11900 | 9616 | 11104 | 32619 | - - - | - - - | - - - | - - - | 11900 | 9616 | 11104 | 32619 | 22685 | 20704 | 20108 | 63497 | # # # | # # # | # # # | # # # | 0.83 | 0.866 | 0.808 | 0.835 | # # # | # # # | # # # | - - - | 0.844 | 0.879 | 0.823 | 0.849 | - - - | 0.615 | 1.62 | 1.51 | 1.49 | 1.47 | 1.46 | 1.5 | 17.22 | 17.17 | 18.94 | 0 | - - - | - - - | - - - | - - - | 22685 | 20704 | 20108 | 63497 | Over-range | 12621 | 10324 | 11828 | 34885 | 4071 | 3632 | 3954 | 12005 | 18886 | 17965 | 16205 | 53057 | 18886 | 17965 | 16205 | 53057 | - - - | - - - | - - - | - - -
5/3/2026 | 2:00:00 PM | 281.66 | 278.72 | 277.63 | 486.52 | 480.16 | 484.78 | 79.8678 | 73.7197 | 71.6801 | 0.2616 | 1.431 | 1.428 | 1.426 | 1.812 | 1.831 | 1.944 | Over-range | 60 | 18597 | 17721 | 16009 | 52327 | - - - | - - - | - - - | - - - | 18597 | 17721 | 16009 | 52327 | 11686 | 9341 | 10851 | 31878 | - - - | - - - | - - - | - - - | 11686 | 9341 | 10851 | 31878 | 22332 | 20376 | 19750 | 62458 | # # # | # # # | # # # | # # # | 0.833 | 0.87 | 0.811 | 0.838 | # # # | # # # | # # # | - - - | 0.847 | 0.883 | 0.826 | 0.852 | - - - | 0.609 | 1.65 | 1.55 | 1.49 | 1.49 | 1.48 | 1.52 | 17.14 | 17.24 | 19.08 | 0 | - - - | - - - | - - - | - - - | 22332 | 20376 | 19750 | 62458 | Over-range | 12357 | 10041 | 11555 | 34069 | 3905 | 3585 | 3872 | 11728 | 18668 | 17699 | 16005 | 52372 | 18668 | 17699 | 16005 | 52372 | - - - | - - - | - - - | - - -
5/3/2026 | 2:15:00 PM | 281.9 | 279.03 | 277.84 | 487.1 | 480.55 | 485.14 | 80.145 | 73.9644 | 71.8865 | 0.2634 | 1.43 | 1.427 | 1.424 | 1.819 | 1.831 | 1.956 | Over-range | 60.01 | 18660 | 17793 | 16053 | 52506 | - - - | - - - | - - - | - - - | 18660 | 17793 | 16053 | 52506 | 11793 | 9471 | 10955 | 32220 | - - - | - - - | - - - | - - - | 11793 | 9471 | 10955 | 32220 | 22453 | 20488 | 19841 | 62782 | # # # | # # # | # # # | # # # | 0.831 | 0.868 | 0.809 | 0.836 | # # # | # # # | # # # | - - - | 0.845 | 0.882 | 0.824 | 0.851 | - - - | 0.614 | 1.65 | 1.52 | 1.46 | 1.48 | 1.46 | 1.5 | 17.36 | 17.27 | 19.21 | 0 | - - - | - - - | - - - | - - - | 22453 | 20488 | 19841 | 62782 | Over-range | 12481 | 10147 | 11650 | 34394 | 3997 | 3557 | 3882 | 11792 | 18710 | 17819 | 16020 | 52549 | 18710 | 17819 | 16020 | 52549 | - - - | - - - | - - - | - - -
5/3/2026 | 2:30:00 PM | 281.98 | 279.12 | 277.99 | 487.21 | 480.78 | 485.36 | 79.6174 | 73.5385 | 71.6624 | 0.2629 | 1.43 | 1.427 | 1.425 | 1.807 | 1.828 | 1.95 | Over-range | 60 | 18548 | 17669 | 16013 | 52230 | - - - | - - - | - - - | - - - | 18548 | 17669 | 16013 | 52230 | 11678 | 9449 | 10938 | 32065 | - - - | - - - | - - - | - - - | 11678 | 9449 | 10938 | 32065 | 22307 | 20373 | 19791 | 62470 | # # # | # # # | # # # | # # # | 0.832 | 0.867 | 0.809 | 0.836 | # # # | # # # | # # # | - - - | 0.845 | 0.881 | 0.824 | 0.85 | - - - | 0.614 | 1.63 | 1.56 | 1.47 | 1.49 | 1.47 | 1.51 | 17.19 | 16.99 | 19.05 | 0 | - - - | - - - | - - - | - - - | 22307 | 20373 | 19791 | 62470 | Over-range | 12384 | 10125 | 11619 | 34238 | 4011 | 3529 | 3811 | 11694 | 18534 | 17732 | 16008 | 52274 | 18534 | 17732 | 16008 | 52274 | - - - | - - - | - - - | - - -
5/3/2026 | 2:45:00 PM | 281.7 | 278.85 | 277.7 | 486.69 | 480.38 | 484.81 | 80.0544 | 74.0059 | 71.7181 | 0.2647 | 1.43 | 1.427 | 1.424 | 1.802 | 1.817 | 1.946 | Over-range | 60.01 | 18602 | 17792 | 16004 | 52398 | - - - | - - - | - - - | - - - | 18602 | 17792 | 16004 | 52398 | 11759 | 9417 | 10911 | 32087 | - - - | - - - | - - - | - - - | 11759 | 9417 | 10911 | 32087 | 22395 | 20467 | 19767 | 62629 | # # # | # # # | # # # | # # # | 0.831 | 0.869 | 0.81 | 0.837 | # # # | # # # | # # # | - - - | 0.844 | 0.882 | 0.824 | 0.85 | - - - | 0.612 | 1.64 | 1.53 | 1.48 | 1.48 | 1.47 | 1.51 | 16.85 | 16.63 | 18.65 | 0 | - - - | - - - | - - - | - - - | 22395 | 20467 | 19767 | 62629 | Over-range | 12454 | 10094 | 11584 | 34253 | 3980 | 3510 | 3775 | 11643 | 18595 | 17845 | 16003 | 52442 | 18595 | 17845 | 16003 | 52442 | - - - | - - - | - - - | - - -
5/3/2026 | 3:00:00 PM | 281.76 | 278.96 | 277.78 | 486.88 | 480.51 | 484.92 | 78.0912 | 72.2118 | 70.4389 | 0.2587 | 1.43 | 1.427 | 1.425 | 1.786 | 1.795 | 1.929 | Over-range | 60.01 | 18160 | 17320 | 15717 | 51197 | - - - | - - - | - - - | - - - | 18160 | 17320 | 15717 | 51197 | 11573 | 9411 | 10855 | 31839 | - - - | - - - | - - - | - - - | 11573 | 9411 | 10855 | 31839 | 21869 | 19998 | 19439 | 61305 | # # # | # # # | # # # | # # # | 0.83 | 0.866 | 0.809 | 0.835 | # # # | # # # | # # # | - - - | 0.842 | 0.878 | 0.822 | 0.847 | - - - | 0.622 | 1.61 | 1.53 | 1.49 | 1.48 | 1.46 | 1.51 | 16.13 | 15.6 | 17.63 | 0 | - - - | - - - | - - - | - - - | 21869 | 19998 | 19439 | 61305 | Over-range | 12177 | 9985 | 11428 | 33695 | 3687 | 3239 | 3473 | 10748 | 18144 | 17349 | 15750 | 51243 | 18144 | 17349 | 15750 | 51243 | - - - | - - - | - - - | - - -
5/3/2026 | 3:15:00 PM | 281.38 | 278.48 | 277.38 | 486.13 | 479.69 | 484.32 | 80.8455 | 74.2936 | 72.2154 | 0.2613 | 1.429 | 1.426 | 1.424 | 1.756 | 1.767 | 1.904 | Over-range | 60.01 | 18839 | 17924 | 16115 | 52878 | - - - | - - - | - - - | - - - | 18839 | 17924 | 16115 | 52878 | 11993 | 9520 | 11169 | 32682 | - - - | - - - | - - - | - - - | 11993 | 9520 | 11169 | 32682 | 22631 | 20561 | 19915 | 63107 | # # # | # # # | # # # | # # # | 0.833 | 0.872 | 0.809 | 0.838 | # # # | # # # | # # # | - - - | 0.842 | 0.882 | 0.822 | 0.849 | - - - | 0.618 | 1.61 | 1.54 | 1.46 | 1.47 | 1.45 | 1.5 | 14.89 | 14.47 | 16.56 | 0 | - - - | - - - | - - - | - - - | 22631 | 20561 | 19915 | 63107 | Over-range | 12532 | 10061 | 11690 | 34415 | 3526 | 3148 | 3340 | 10475 | 18821 | 17913 | 16181 | 52915 | 18821 | 17913 | 16181 | 52915 | - - - | - - - | - - - | - - -
5/3/2026 | 3:30:00 PM | 281.31 | 278.51 | 277.34 | 486.05 | 479.79 | 484.15 | 78.6824 | 72.5957 | 71.0521 | 0.2601 | 1.43 | 1.427 | 1.425 | 1.773 | 1.779 | 1.906 | Over-range | 60 | 18226 | 17327 | 15758 | 51311 | - - - | - - - | - - - | - - - | 18226 | 17327 | 15758 | 51311 | 11735 | 9534 | 11033 | 32302 | - - - | - - - | - - - | - - - | 11735 | 9534 | 11033 | 32302 | 21983 | 20059 | 19566 | 61607 | # # # | # # # | # # # | # # # | 0.829 | 0.864 | 0.805 | 0.833 | # # # | # # # | # # # | - - - | 0.84 | 0.874 | 0.818 | 0.844 | - - - | 0.629 | 1.63 | 1.55 | 1.46 | 1.48 | 1.45 | 1.5 | 15.32 | 15 | 16.85 | 0 | - - - | - - - | - - - | - - - | 21983 | 20059 | 19566 | 61607 | Over-range | 12281 | 10093 | 11585 | 34065 | 3476 | 3179 | 3396 | 10423 | 18257 | 17285 | 15803 | 51345 | 18257 | 17285 | 15803 | 51345 | - - - | - - - | - - - | - - -
5/3/2026 | 3:45:00 PM | 281.2 | 278.38 | 277.26 | 485.84 | 479.58 | 484.03 | 80.2812 | 74.1919 | 72.0394 | 0.2616 | 1.431 | 1.428 | 1.426 | 1.786 | 1.798 | 1.916 | Over-range | 60.01 | 18616 | 17778 | 16037 | 52431 | - - - | - - - | - - - | - - - | 18616 | 17778 | 16037 | 52431 | 11791 | 9453 | 10993 | 32236 | - - - | - - - | - - - | - - - | 11791 | 9453 | 10993 | 32236 | 22390 | 20457 | 19800 | 62647 | # # # | # # # | # # # | # # # | 0.831 | 0.869 | 0.81 | 0.837 | # # # | # # # | # # # | - - - | 0.843 | 0.881 | 0.824 | 0.85 | - - - | 0.615 | 1.62 | 1.52 | 1.48 | 1.48 | 1.46 | 1.51 | 16.05 | 15.95 | 17.72 | 0 | - - - | - - - | - - - | - - - | 22390 | 20457 | 19800 | 62647 | Over-range | 12424 | 10097 | 11595 | 34234 | 3779 | 3420 | 3552 | 11146 | 18582 | 17794 | 16098 | 52473 | 18582 | 17794 | 16098 | 52473 | - - - | - - - | - - - | - - -
5/3/2026 | 4:00:00 PM | 281.15 | 278.35 | 277.15 | 485.81 | 479.42 | 483.87 | 78.003 | 72.1895 | 70.1431 | 0.2576 | 1.43 | 1.427 | 1.425 | 1.797 | 1.803 | 1.931 | Over-range | 60 | 18065 | 17274 | 15605 | 50944 | - - - | - - - | - - - | - - - | 18065 | 17274 | 15605 | 50944 | 11546 | 9335 | 10767 | 31648 | - - - | - - - | - - - | - - - | 11546 | 9335 | 10767 | 31648 | 21782 | 19932 | 19300 | 61014 | # # # | # # # | # # # | # # # | 0.829 | 0.867 | 0.809 | 0.835 | # # # | # # # | # # # | - - - | 0.841 | 0.879 | 0.823 | 0.848 | - - - | 0.621 | 1.63 | 1.54 | 1.48 | 1.48 | 1.46 | 1.51 | 16.46 | 16.09 | 18.02 | 0 | - - - | - - - | - - - | - - - | 21782 | 19932 | 19300 | 61014 | Over-range | 12164 | 9933 | 11347 | 33552 | 3740 | 3308 | 3494 | 10894 | 18036 | 17305 | 15645 | 50986 | 18036 | 17305 | 15645 | 50986 | - - - | - - - | - - - | - - -
5/3/2026 | 4:15:00 PM | 281 | 278.21 | 277 | 485.54 | 479.2 | 483.59 | 79.1032 | 73.3236 | 71.0296 | 0.2594 | 1.43 | 1.427 | 1.425 | 1.783 | 1.786 | 1.913 | Over-range | 60 | 18376 | 17615 | 15884 | 51875 | - - - | - - - | - - - | - - - | 18376 | 17615 | 15884 | 51875 | 11653 | 9409 | 10787 | 31849 | - - - | - - - | - - - | - - - | 11653 | 9409 | 10787 | 31849 | 22085 | 20245 | 19544 | 61873 | # # # | # # # | # # # | # # # | 0.832 | 0.87 | 0.813 | 0.838 | # # # | # # # | # # # | - - - | 0.844 | 0.881 | 0.825 | 0.85 | - - - | 0.614 | 1.62 | 1.52 | 1.46 | 1.47 | 1.45 | 1.5 | 15.76 | 15.4 | 17.31 | 0 | - - - | - - - | - - - | - - - | 22085 | 20245 | 19544 | 61873 | Over-range | 12242 | 9965 | 11375 | 33694 | 3635 | 3169 | 3501 | 10676 | 18413 | 17662 | 15850 | 51925 | 18413 | 17662 | 15850 | 51925 | - - - | - - - | - - - | - - -
5/3/2026 | 4:30:00 PM | 280.93 | 278.07 | 276.93 | 485.35 | 479 | 483.51 | 78.8632 | 72.8252 | 70.8911 | 0.259 | 1.43 | 1.427 | 1.425 | 1.777 | 1.783 | 1.913 | Over-range | 59.99 | 18293 | 17449 | 15775 | 51517 | - - - | - - - | - - - | - - - | 18293 | 17449 | 15775 | 51517 | 11690 | 9430 | 10872 | 31991 | - - - | - - - | - - - | - - - | 11690 | 9430 | 10872 | 31991 | 22028 | 20112 | 19510 | 61650 | # # # | # # # | # # # | # # # | 0.83 | 0.868 | 0.809 | 0.836 | # # # | # # # | # # # | - - - | 0.842 | 0.878 | 0.821 | 0.847 | - - - | 0.621 | 1.61 | 1.52 | 1.47 | 1.47 | 1.45 | 1.5 | 15.65 | 15.28 | 17.28 | 0 | - - - | - - - | - - - | - - - | 22028 | 20112 | 19510 | 61650 | Over-range | 12263 | 9988 | 11467 | 33831 | 3578 | 3174 | 3532 | 10663 | 18356 | 17450 | 15751 | 51557 | 18356 | 17450 | 15751 | 51557 | - - - | - - - | - - - | - - -
5/3/2026 | 4:45:00 PM | 280.66 | 277.88 | 276.61 | 485.04 | 478.51 | 482.97 | 79.2552 | 73.5255 | 71.3759 | 0.2587 | 1.43 | 1.427 | 1.425 | 1.798 | 1.8 | 1.92 | Over-range | 59.99 | 18417 | 17637 | 15959 | 52013 | - - - | - - - | - - - | - - - | 18417 | 17637 | 15959 | 52013 | 11596 | 9368 | 10740 | 31704 | - - - | - - - | - - - | - - - | 11596 | 9368 | 10740 | 31704 | 22121 | 20300 | 19623 | 62044 | # # # | # # # | # # # | # # # | 0.833 | 0.869 | 0.813 | 0.838 | # # # | # # # | # # # | - - - | 0.846 | 0.881 | 0.828 | 0.852 | - - - | 0.61 | 1.64 | 1.55 | 1.46 | 1.49 | 1.47 | 1.52 | 16.53 | 16.33 | 18.11 | 0 | - - - | - - - | - - - | - - - | 22121 | 20300 | 19623 | 62044 | Over-range | 12238 | 10027 | 11403 | 33773 | 3775 | 3451 | 3709 | 11278 | 18488 | 17608 | 15966 | 52061 | 18488 | 17608 | 15966 | 52061 | - - - | - - - | - - - | - - -
5/3/2026 | 5:00:00 PM | 280.55 | 277.66 | 276.47 | 484.72 | 478.17 | 482.81 | 80.7916 | 74.5823 | 72.4963 | 0.2606 | 1.429 | 1.427 | 1.425 | 1.792 | 1.798 | 1.917 | Over-range | 60 | 18779 | 17903 | 16171 | 52853 | - - - | - - - | - - - | - - - | 18779 | 17903 | 16171 | 52853 | 11823 | 9458 | 10979 | 32260 | - - - | - - - | - - - | - - - | 11823 | 9458 | 10979 | 32260 | 22528 | 20563 | 19913 | 63005 | # # # | # # # | # # # | # # # | 0.834 | 0.871 | 0.812 | 0.839 | # # # | # # # | # # # | - - - | 0.846 | 0.882 | 0.827 | 0.852 | - - - | 0.61 | 1.61 | 1.53 | 1.47 | 1.47 | 1.46 | 1.5 | 16.26 | 16.14 | 17.91 | 0 | - - - | - - - | - - - | - - - | 22528 | 20563 | 19913 | 63005 | Over-range | 12438 | 10103 | 11610 | 34268 | 3753 | 3457 | 3679 | 11270 | 18837 | 17861 | 16206 | 52904 | 18837 | 17861 | 16206 | 52904 | - - - | - - - | - - - | - - -
5/3/2026 | 5:15:00 PM | 280.53 | 277.81 | 276.58 | 484.78 | 478.53 | 482.81 | 78.957 | 73.3597 | 71.7053 | 0.2594 | 1.429 | 1.426 | 1.425 | 1.801 | 1.804 | 1.915 | Over-range | 60 | 18408 | 17582 | 16077 | 52067 | - - - | - - - | - - - | - - - | 18408 | 17582 | 16077 | 52067 | 11520 | 9462 | 10803 | 31785 | - - - | - - - | - - - | - - - | 11520 | 9462 | 10803 | 31785 | 22059 | 20283 | 19745 | 62086 | # # # | # # # | # # # | # # # | 0.835 | 0.867 | 0.814 | 0.839 | # # # | # # # | # # # | - - - | 0.848 | 0.879 | 0.829 | 0.852 | - - - | 0.611 | 1.6 | 1.54 | 1.44 | 1.46 | 1.44 | 1.48 | 16.49 | 16.35 | 18.02 | 0 | - - - | - - - | - - - | - - - | 22059 | 20283 | 19745 | 62086 | Over-range | 12147 | 10100 | 11452 | 33790 | 3747 | 3437 | 3706 | 11185 | 18480 | 17558 | 16073 | 52112 | 18480 | 17558 | 16073 | 52112 | - - - | - - - | - - - | - - -
5/3/2026 | 5:30:00 PM | 280.23 | 277.51 | 276.35 | 484.27 | 478.03 | 482.37 | 81.1039 | 75.1786 | 72.7148 | 0.2617 | 1.429 | 1.427 | 1.425 | 1.793 | 1.797 | 1.904 | Over-range | 60 | 18845 | 18074 | 16276 | 53195 | - - - | - - - | - - - | - - - | 18845 | 18074 | 16276 | 53195 | 11844 | 9482 | 10920 | 32246 | - - - | - - - | - - - | - - - | 11844 | 9482 | 10920 | 32246 | 22603 | 20730 | 19977 | 63310 | # # # | # # # | # # # | # # # | 0.834 | 0.872 | 0.815 | 0.84 | # # # | # # # | # # # | - - - | 0.846 | 0.884 | 0.829 | 0.853 | - - - | 0.606 | 1.63 | 1.52 | 1.47 | 1.47 | 1.45 | 1.5 | 16.22 | 16.23 | 17.86 | 0 | - - - | - - - | - - - | - - - | 22603 | 20730 | 19977 | 63310 | Over-range | 12473 | 10138 | 11572 | 34298 | 3794 | 3484 | 3726 | 11378 | 18919 | 18056 | 16267 | 53241 | 18919 | 18056 | 16267 | 53241 | - - - | - - - | - - - | - - -
5/3/2026 | 5:45:00 PM | 280.34 | 277.73 | 276.54 | 484.55 | 478.44 | 482.59 | 78.1782 | 72.7314 | 70.9246 | 0.2577 | 1.429 | 1.427 | 1.425 | 1.809 | 1.814 | 1.925 | Over-range | 60 | 18115 | 17339 | 15820 | 51274 | - - - | - - - | - - - | - - - | 18115 | 17339 | 15820 | 51274 | 11384 | 9329 | 10644 | 31357 | - - - | - - - | - - - | - - - | 11384 | 9329 | 10644 | 31357 | 21759 | 20030 | 19463 | 61253 | # # # | # # # | # # # | # # # | 0.833 | 0.866 | 0.813 | 0.837 | # # # | # # # | # # # | - - - | 0.846 | 0.878 | 0.828 | 0.851 | - - - | 0.612 | 1.6 | 1.53 | 1.45 | 1.47 | 1.44 | 1.49 | 16.95 | 16.84 | 18.52 | 0 | - - - | - - - | - - - | - - - | 21759 | 20030 | 19463 | 61253 | Over-range | 12040 | 10007 | 11323 | 33461 | 3799 | 3510 | 3752 | 11354 | 18186 | 17309 | 15829 | 51324 | 18186 | 17309 | 15829 | 51324 | - - - | - - - | - - - | - - -
5/3/2026 | 6:00:00 PM | 280.06 | 277.47 | 276.22 | 484.06 | 477.97 | 482.06 | 80.1932 | 74.472 | 72.1464 | 0.2607 | 1.429 | 1.426 | 1.425 | 1.801 | 1.802 | 1.912 | Over-range | 60 | 18667 | 17912 | 16183 | 52762 | - - - | - - - | - - - | - - - | 18667 | 17912 | 16183 | 52762 | 11646 | 9401 | 10812 | 31858 | - - - | - - - | - - - | - - - | 11646 | 9401 | 10812 | 31858 | 22351 | 20546 | 19824 | 62721 | # # # | # # # | # # # | # # # | 0.835 | 0.872 | 0.816 | 0.841 | # # # | # # # | # # # | - - - | 0.847 | 0.884 | 0.83 | 0.854 | - - - | 0.604 | 1.6 | 1.53 | 1.47 | 1.47 | 1.45 | 1.49 | 16.3 | 16.28 | 17.85 | 0 | - - - | - - - | - - - | - - - | 22351 | 20546 | 19824 | 62721 | Over-range | 12286 | 10051 | 11440 | 33884 | 3811 | 3459 | 3637 | 11256 | 18680 | 17938 | 16190 | 52807 | 18680 | 17938 | 16190 | 52807 | - - - | - - - | - - - | - - -
5/3/2026 | 6:15:00 PM | 280.26 | 277.34 | 276.14 | 484.22 | 477.56 | 482.28 | 78.5355 | 72.3344 | 70.4974 | 0.2564 | 1.428 | 1.426 | 1.424 | 1.809 | 1.816 | 1.939 | Over-range | 60 | 18213 | 17317 | 15658 | 51189 | - - - | - - - | - - - | - - - | 18213 | 17317 | 15658 | 51189 | 11458 | 9199 | 10719 | 31376 | - - - | - - - | - - - | - - - | 11458 | 9199 | 10719 | 31376 | 21893 | 19937 | 19354 | 61184 | # # # | # # # | # # # | # # # | 0.832 | 0.869 | 0.809 | 0.837 | # # # | # # # | # # # | - - - | 0.845 | 0.882 | 0.824 | 0.85 | - - - | 0.613 | 1.58 | 1.51 | 1.47 | 1.46 | 1.45 | 1.47 | 17.09 | 16.75 | 18.7 | 0 | - - - | - - - | - - - | - - - | 21893 | 19937 | 19354 | 61184 | Over-range | 12141 | 9866 | 11365 | 33486 | 3912 | 3467 | 3676 | 11410 | 18194 | 17343 | 15694 | 51231 | 18194 | 17343 | 15694 | 51231 | - - - | - - - | - - - | - - -
5/3/2026 | 6:30:00 PM | 280.48 | 277.58 | 276.29 | 484.65 | 477.92 | 482.56 | 80.2939 | 74.146 | 71.7006 | 0.2587 | 1.428 | 1.426 | 1.424 | 1.806 | 1.804 | 1.936 | Over-range | 60 | 18638 | 17815 | 15991 | 52444 | - - - | - - - | - - - | - - - | 18638 | 17815 | 15991 | 52444 | 11686 | 9275 | 10801 | 31762 | - - - | - - - | - - - | - - - | 11686 | 9275 | 10801 | 31762 | 22355 | 20407 | 19660 | 62422 | # # # | # # # | # # # | # # # | 0.834 | 0.873 | 0.813 | 0.84 | # # # | # # # | # # # | - - - | 0.846 | 0.886 | 0.828 | 0.853 | - - - | 0.606 | 1.6 | 1.5 | 1.43 | 1.45 | 1.44 | 1.45 | 16.73 | 16.47 | 18.3 | 0 | - - - | - - - | - - - | - - - | 22355 | 20407 | 19660 | 62422 | Over-range | 12338 | 9939 | 11424 | 33824 | 3851 | 3476 | 3619 | 11342 | 18629 | 17807 | 16055 | 52491 | 18629 | 17807 | 16055 | 52491 | - - - | - - - | - - - | - - -
5/3/2026 | 6:45:00 PM | 280.37 | 277.47 | 276.2 | 484.42 | 477.77 | 482.41 | 79.7395 | 73.5452 | 71.564 | 0.2598 | 1.428 | 1.426 | 1.424 | 1.797 | 1.802 | 1.928 | Over-range | 59.99 | 18457 | 17575 | 15871 | 51902 | - - - | - - - | - - - | - - - | 18457 | 17575 | 15871 | 51902 | 11685 | 9390 | 10908 | 31983 | - - - | - - - | - - - | - - - | 11685 | 9390 | 10908 | 31983 | 22210 | 20247 | 19625 | 62082 | # # # | # # # | # # # | # # # | 0.831 | 0.868 | 0.809 | 0.836 | # # # | # # # | # # # | - - - | 0.843 | 0.88 | 0.823 | 0.849 | - - - | 0.616 | 1.58 | 1.51 | 1.42 | 1.44 | 1.43 | 1.44 | 16.35 | 16.07 | 17.91 | 0 | - - - | - - - | - - - | - - - | 22210 | 20247 | 19625 | 62082 | Over-range | 12334 | 10025 | 11523 | 33997 | 3811 | 3374 | 3583 | 11146 | 18442 | 17604 | 15897 | 51943 | 18442 | 17604 | 15897 | 51943 | - - - | - - - | - - - | - - -
5/3/2026 | 7:00:00 PM | 280.79 | 277.95 | 276.6 | 485.28 | 478.5 | 483.07 | 80.3372 | 74.1646 | 71.8768 | 0.2597 | 1.428 | 1.426 | 1.424 | 1.797 | 1.79 | 1.933 | Over-range | 60 | 18685 | 17847 | 16053 | 52585 | - - - | - - - | - - - | - - - | 18685 | 17847 | 16053 | 52585 | 11764 | 9417 | 10928 | 32108 | - - - | - - - | - - - | - - - | 11764 | 9417 | 10928 | 32108 | 22442 | 20489 | 19775 | 62705 | # # # | # # # | # # # | # # # | 0.833 | 0.871 | 0.812 | 0.839 | # # # | # # # | # # # | - - - | 0.844 | 0.883 | 0.826 | 0.851 | - - - | 0.611 | 1.57 | 1.49 | 1.43 | 1.43 | 1.42 | 1.44 | 16.38 | 15.92 | 17.85 | 0 | - - - | - - - | - - - | - - - | 22442 | 20489 | 19775 | 62705 | Over-range | 12422 | 10048 | 11537 | 34127 | 3874 | 3392 | 3587 | 11241 | 18651 | 17887 | 16086 | 52625 | 18651 | 17887 | 16086 | 52625 | - - - | - - - | - - - | - - -
5/3/2026 | 7:15:00 PM | 280.71 | 278.01 | 276.54 | 485.3 | 478.53 | 482.88 | 80.4758 | 74.7015 | 71.8854 | 0.2595 | 1.428 | 1.426 | 1.424 | 1.792 | 1.781 | 1.919 | Over-range | 60 | 18645 | 17962 | 16058 | 52664 | - - - | - - - | - - - | - - - | 18645 | 17962 | 16058 | 52664 | 11914 | 9559 | 10911 | 32384 | - - - | - - - | - - - | - - - | 11914 | 9559 | 10911 | 32384 | 22466 | 20629 | 19760 | 62854 | # # # | # # # | # # # | # # # | 0.83 | 0.871 | 0.813 | 0.838 | # # # | # # # | # # # | - - - | 0.842 | 0.882 | 0.825 | 0.85 | - - - | 0.615 | 1.57 | 1.48 | 1.4 | 1.43 | 1.41 | 1.42 | 16.04 | 15.54 | 17.49 | 0 | - - - | - - - | - - - | - - - | 22466 | 20629 | 19760 | 62854 | Over-range | 12527 | 10133 | 11504 | 34282 | 3779 | 3269 | 3556 | 10991 | 18662 | 18014 | 16030 | 52706 | 18662 | 18014 | 16030 | 52706 | - - - | - - - | - - - | - - -
5/3/2026 | 7:30:00 PM | 280.83 | 278.05 | 276.6 | 485.44 | 478.63 | 483.01 | 79.9736 | 74.3454 | 71.6282 | 0.2606 | 1.428 | 1.426 | 1.425 | 1.794 | 1.782 | 1.927 | Over-range | 59.99 | 18566 | 17886 | 16043 | 52495 | - - - | - - - | - - - | - - - | 18566 | 17886 | 16043 | 52495 | 11803 | 9515 | 10820 | 32137 | - - - | - - - | - - - | - - - | 11803 | 9515 | 10820 | 32137 | 22335 | 20539 | 19700 | 62574 | # # # | # # # | # # # | # # # | 0.831 | 0.871 | 0.814 | 0.839 | # # # | # # # | # # # | - - - | 0.843 | 0.882 | 0.827 | 0.851 | - - - | 0.612 | 1.56 | 1.49 | 1.43 | 1.44 | 1.43 | 1.44 | 16.19 | 15.56 | 17.58 | 0 | - - - | - - - | - - - | - - - | 22335 | 20539 | 19700 | 62574 | Over-range | 12411 | 10085 | 11422 | 34030 | 3742 | 3252 | 3572 | 10934 | 18605 | 17923 | 16013 | 52540 | 18605 | 17923 | 16013 | 52540 | - - - | - - - | - - - | - - -
5/3/2026 | 7:45:00 PM | 281.23 | 278.56 | 277.06 | 486.2 | 479.53 | 483.71 | 79.5935 | 74.0299 | 71.1208 | 0.2586 | 1.428 | 1.426 | 1.424 | 1.823 | 1.81 | 1.951 | Over-range | 60 | 18417 | 17781 | 15878 | 52075 | - - - | - - - | - - - | - - - | 18417 | 17781 | 15878 | 52075 | 11786 | 9415 | 10777 | 31978 | - - - | - - - | - - - | - - - | 11786 | 9415 | 10777 | 31978 | 22250 | 20475 | 19578 | 62303 | # # # | # # # | # # # | # # # | 0.828 | 0.868 | 0.811 | 0.836 | # # # | # # # | # # # | - - - | 0.84 | 0.881 | 0.826 | 0.849 | - - - | 0.614 | 1.58 | 1.47 | 1.41 | 1.43 | 1.41 | 1.42 | 17.07 | 16.8 | 18.5 | 0 | - - - | - - - | - - - | - - - | 22250 | 20475 | 19578 | 62303 | Over-range | 12470 | 10127 | 11437 | 34147 | 3943 | 3612 | 3707 | 11631 | 18417 | 17757 | 15936 | 52110 | 18417 | 17757 | 15936 | 52110 | - - - | - - - | - - - | - - -
5/3/2026 | 8:00:00 PM | 281.31 | 278.67 | 277.23 | 486.34 | 479.8 | 483.94 | 78.9642 | 73.6544 | 71.3312 | 0.2565 | 1.428 | 1.426 | 1.424 | 1.823 | 1.819 | 1.953 | Over-range | 60.01 | 18352 | 17675 | 16001 | 52028 | - - - | - - - | - - - | - - - | 18352 | 17675 | 16001 | 52028 | 11613 | 9473 | 10767 | 31854 | - - - | - - - | - - - | - - - | 11613 | 9473 | 10767 | 31854 | 22082 | 20385 | 19655 | 62123 | # # # | # # # | # # # | # # # | 0.831 | 0.867 | 0.814 | 0.838 | # # # | # # # | # # # | - - - | 0.844 | 0.88 | 0.83 | 0.851 | - - - | 0.612 | 1.59 | 1.51 | 1.41 | 1.44 | 1.42 | 1.43 | 17.26 | 16.88 | 18.7 | 0 | - - - | - - - | - - - | - - - | 22082 | 20385 | 19655 | 62123 | Over-range | 12274 | 10145 | 11404 | 33919 | 3889 | 3551 | 3678 | 11421 | 18346 | 17652 | 16069 | 52067 | 18346 | 17652 | 16069 | 52067 | - - - | - - - | - - - | - - -
5/3/2026 | 8:15:00 PM | 281.56 | 278.93 | 277.31 | 486.89 | 480.04 | 484.18 | 80.5391 | 74.9285 | 71.7481 | 0.2588 | 1.428 | 1.426 | 1.424 | 1.822 | 1.806 | 1.96 | Over-range | 59.99 | 18679 | 18077 | 16070 | 52826 | - - - | - - - | - - - | - - - | 18679 | 18077 | 16070 | 52826 | 11986 | 9537 | 10858 | 32381 | - - - | - - - | - - - | - - - | 11986 | 9537 | 10858 | 32381 | 22553 | 20762 | 19777 | 63092 | # # # | # # # | # # # | # # # | 0.828 | 0.871 | 0.813 | 0.837 | # # # | # # # | # # # | - - - | 0.842 | 0.883 | 0.827 | 0.851 | - - - | 0.613 | 1.57 | 1.5 | 1.4 | 1.44 | 1.42 | 1.43 | 17 | 16.64 | 18.52 | 0 | - - - | - - - | - - - | - - - | 22553 | 20762 | 19777 | 63092 | Over-range | 12632 | 10201 | 11518 | 34473 | 3894 | 3536 | 3760 | 11575 | 18745 | 18044 | 16074 | 52862 | 18745 | 18044 | 16074 | 52862 | - - - | - - - | - - - | - - -
5/3/2026 | 8:30:00 PM | 281.66 | 278.9 | 277.34 | 486.93 | 480.03 | 484.32 | 80.071 | 74.4713 | 72.0554 | 0.2595 | 1.428 | 1.426 | 1.423 | 1.835 | 1.822 | 1.968 | Over-range | 59.99 | 18581 | 17866 | 16105 | 52551 | - - - | - - - | - - - | - - - | 18581 | 17866 | 16105 | 52551 | 11882 | 9634 | 10951 | 32468 | - - - | - - - | - - - | - - - | 11882 | 9634 | 10951 | 32468 | 22431 | 20639 | 19873 | 62943 | # # # | # # # | # # # | # # # | 0.828 | 0.866 | 0.81 | 0.835 | # # # | # # # | # # # | - - - | 0.842 | 0.878 | 0.826 | 0.849 | - - - | 0.618 | 1.56 | 1.48 | 1.4 | 1.43 | 1.41 | 1.41 | 17.43 | 17.03 | 18.83 | 0 | - - - | - - - | - - - | - - - | 22431 | 20639 | 19873 | 62943 | Over-range | 12557 | 10320 | 11632 | 34612 | 3956 | 3600 | 3824 | 11706 | 18640 | 17825 | 16125 | 52589 | 18640 | 17825 | 16125 | 52589 | - - - | - - - | - - - | - - -
5/3/2026 | 8:45:00 PM | 281.35 | 278.52 | 276.93 | 486.41 | 479.26 | 483.72 | 82.3148 | 75.8794 | 73.1817 | 0.2603 | 1.428 | 1.426 | 1.423 | 1.822 | 1.801 | 1.959 | Over-range | 59.99 | 19147 | 18298 | 16331 | 53775 | - - - | - - - | - - - | - - - | 19147 | 18298 | 16331 | 53775 | 12021 | 9471 | 11058 | 32550 | - - - | - - - | - - - | - - - | 12021 | 9471 | 11058 | 32550 | 22995 | 20955 | 20116 | 64066 | # # # | # # # | # # # | # # # | 0.833 | 0.873 | 0.812 | 0.839 | # # # | # # # | # # # | - - - | 0.845 | 0.886 | 0.827 | 0.853 | - - - | 0.605 | 1.58 | 1.5 | 1.41 | 1.43 | 1.42 | 1.43 | 16.98 | 16.62 | 18.42 | 0 | - - - | - - - | - - - | - - - | 22995 | 20955 | 20116 | 64066 | Over-range | 12718 | 10188 | 11727 | 34767 | 4017 | 3634 | 3777 | 11858 | 19164 | 18257 | 16386 | 53807 | 19164 | 18257 | 16386 | 53807 | - - - | - - - | - - - | - - -
5/3/2026 | 9:00:00 PM | 281.63 | 278.92 | 277.22 | 487.04 | 479.89 | 484.12 | 80.9354 | 74.9611 | 72.3712 | 0.2595 | 1.428 | 1.426 | 1.423 | 1.834 | 1.808 | 1.965 | Over-range | 60.01 | 18857 | 18099 | 16212 | 53168 | - - - | - - - | - - - | - - - | 18857 | 18099 | 16212 | 53168 | 11950 | 9586 | 11033 | 32569 | - - - | - - - | - - - | - - - | 11950 | 9586 | 11033 | 32569 | 22710 | 20816 | 19979 | 63506 | # # # | # # # | # # # | # # # | 0.83 | 0.87 | 0.811 | 0.837 | # # # | # # # | # # # | - - - | 0.843 | 0.883 | 0.826 | 0.851 | - - - | 0.613 | 1.58 | 1.48 | 1.38 | 1.43 | 1.4 | 1.42 | 17.29 | 16.83 | 18.54 | 0 | - - - | - - - | - - - | - - - | 22710 | 20816 | 19979 | 63506 | Over-range | 12649 | 10273 | 11668 | 34706 | 4058 | 3604 | 3704 | 11732 | 18826 | 18109 | 16267 | 53202 | 18826 | 18109 | 16267 | 53202 | - - - | - - - | - - - | - - -
5/3/2026 | 9:15:00 PM | 281.65 | 279.01 | 277.36 | 487.05 | 480.18 | 484.26 | 82.1775 | 76.3118 | 73.4716 | 0.2634 | 1.428 | 1.426 | 1.424 | 1.844 | 1.826 | 1.968 | Over-range | 60.01 | 19172 | 18448 | 16516 | 54136 | - - - | - - - | - - - | - - - | 19172 | 18448 | 16516 | 54136 | 12008 | 9604 | 11004 | 32616 | - - - | - - - | - - - | - - - | 12008 | 9604 | 11004 | 32616 | 23024 | 21161 | 20266 | 64451 | # # # | # # # | # # # | # # # | 0.833 | 0.872 | 0.815 | 0.84 | # # # | # # # | # # # | - - - | 0.847 | 0.886 | 0.831 | 0.855 | - - - | 0.603 | 1.6 | 1.5 | 1.42 | 1.45 | 1.43 | 1.45 | 17.72 | 17.58 | 19.2 | 0 | - - - | - - - | - - - | - - - | 23024 | 21161 | 20266 | 64451 | Over-range | 12742 | 10353 | 11734 | 34947 | 4162 | 3773 | 3980 | 12276 | 19231 | 18440 | 16503 | 54174 | 19231 | 18440 | 16503 | 54174 | - - - | - - - | - - - | - - -
5/3/2026 | 9:30:00 PM | 282.11 | 279.47 | 277.79 | 487.9 | 480.89 | 485.02 | 81.1942 | 75.2121 | 72.4614 | 0.2627 | 1.428 | 1.427 | 1.424 | 1.844 | 1.83 | 1.981 | Over-range | 60.02 | 18921 | 18183 | 16243 | 53347 | - - - | - - - | - - - | - - - | 18921 | 18183 | 16243 | 53347 | 11960 | 9561 | 10962 | 32483 | - - - | - - - | - - - | - - - | 11960 | 9561 | 10962 | 32483 | 22801 | 20907 | 20030 | 63738 | # # # | # # # | # # # | # # # | 0.83 | 0.87 | 0.811 | 0.837 | # # # | # # # | # # # | - - - | 0.845 | 0.884 | 0.827 | 0.852 | - - - | 0.609 | 1.62 | 1.51 | 1.42 | 1.46 | 1.44 | 1.46 | 18.07 | 17.83 | 19.63 | 0 | - - - | - - - | - - - | - - - | 22801 | 20907 | 20030 | 63738 | Over-range | 12717 | 10309 | 11710 | 34856 | 4225 | 3762 | 4029 | 12375 | 18977 | 18205 | 16204 | 53386 | 18977 | 18205 | 16204 | 53386 | - - - | - - - | - - - | - - -
5/3/2026 | 9:45:00 PM | 282.61 | 279.86 | 278.2 | 488.71 | 481.51 | 485.85 | 80.9334 | 74.8825 | 72.2979 | 0.2609 | 1.428 | 1.427 | 1.423 | 1.838 | 1.825 | 1.988 | Over-range | 60.02 | 18873 | 18091 | 16193 | 53156 | - - - | - - - | - - - | - - - | 18873 | 18091 | 16193 | 53156 | 11905 | 9520 | 10990 | 32415 | - - - | - - - | - - - | - - - | 11905 | 9520 | 10990 | 32415 | 22743 | 20814 | 19991 | 63548 | # # # | # # # | # # # | # # # | 0.83 | 0.869 | 0.81 | 0.837 | # # # | # # # | # # # | - - - | 0.844 | 0.884 | 0.827 | 0.852 | - - - | 0.61 | 1.63 | 1.51 | 1.39 | 1.45 | 1.43 | 1.45 | 18.01 | 17.54 | 19.51 | 0 | - - - | - - - | - - - | - - - | 22743 | 20814 | 19991 | 63548 | Over-range | 12674 | 10268 | 11704 | 34767 | 4234 | 3733 | 3913 | 12247 | 18846 | 18119 | 16229 | 53193 | 18846 | 18119 | 16229 | 53193 | - - - | - - - | - - - | - - -
5/3/2026 | 10:00:00 PM | 282.86 | 280.1 | 278.38 | 489.11 | 481.91 | 486.22 | 81.5217 | 75.0141 | 72.1374 | 0.2624 | 1.428 | 1.427 | 1.423 | 1.825 | 1.802 | 1.98 | Over-range | 60.02 | 19006 | 18207 | 16126 | 53338 | - - - | - - - | - - - | - - - | 19006 | 18207 | 16126 | 53338 | 12168 | 9539 | 11128 | 32835 | - - - | - - - | - - - | - - - | 12168 | 9539 | 11128 | 32835 | 22949 | 20890 | 19977 | 63816 | # # # | # # # | # # # | # # # | 0.828 | 0.872 | 0.807 | 0.836 | # # # | # # # | # # # | - - - | 0.841 | 0.884 | 0.823 | 0.849 | - - - | 0.616 | 1.61 | 1.49 | 1.44 | 1.46 | 1.44 | 1.46 | 17.31 | 16.81 | 18.72 | 0 | - - - | - - - | - - - | - - - | 22949 | 20890 | 19977 | 63816 | Over-range | 12856 | 10231 | 11783 | 35012 | 4058 | 3614 | 3787 | 11908 | 19018 | 18184 | 16172 | 53374 | 19018 | 18184 | 16172 | 53374 | - - - | - - - | - - - | - - -
5/3/2026 | 10:15:00 PM | 283.29 | 280.36 | 278.71 | 489.76 | 482.27 | 486.95 | 79.5056 | 72.8645 | 70.7222 | 0.2586 | 1.428 | 1.427 | 1.423 | 1.824 | 1.8 | 1.993 | Over-range | 60 | 18565 | 17645 | 15772 | 51983 | - - - | - - - | - - - | - - - | 18565 | 17645 | 15772 | 51983 | 11862 | 9399 | 10995 | 32255 | - - - | - - - | - - - | - - - | 11862 | 9399 | 10995 | 32255 | 22418 | 20314 | 19613 | 62346 | # # # | # # # | # # # | # # # | 0.828 | 0.869 | 0.804 | 0.834 | # # # | # # # | # # # | - - - | 0.842 | 0.881 | 0.82 | 0.848 | - - - | 0.621 | 1.66 | 1.55 | 1.47 | 1.5 | 1.48 | 1.51 | 17.54 | 16.63 | 18.93 | 0 | - - - | - - - | - - - | - - - | 22418 | 20314 | 19613 | 62346 | Over-range | 12560 | 10054 | 11648 | 34395 | 4033 | 3478 | 3755 | 11680 | 18566 | 17642 | 15811 | 52018 | 18566 | 17642 | 15811 | 52018 | - - - | - - - | - - - | - - -
5/3/2026 | 10:30:00 PM | 283.58 | 280.69 | 279 | 490.32 | 482.81 | 487.43 | 81.6038 | 74.6253 | 72.0206 | 0.2414 | 1.428 | 1.427 | 1.423 | 1.82 | 1.792 | 1.983 | Over-range | 60.02 | 19016 | 18092 | 16021 | 53129 | - - - | - - - | - - - | - - - | 19016 | 18092 | 16021 | 53129 | 12191 | 9533 | 11240 | 32964 | - - - | - - - | - - - | - - - | 12191 | 9533 | 11240 | 32964 | 22978 | 20769 | 19947 | 63694 | # # # | # # # | # # # | # # # | 0.828 | 0.871 | 0.803 | 0.834 | # # # | # # # | # # # | - - - | 0.84 | 0.884 | 0.818 | 0.848 | - - - | 0.621 | 1.67 | 1.54 | 1.49 | 1.5 | 1.49 | 1.52 | 17.27 | 16.55 | 18.65 | 0 | - - - | - - - | - - - | - - - | 22978 | 20769 | 19947 | 63694 | Over-range | 12894 | 10186 | 11872 | 35104 | 4097 | 3487 | 3723 | 11789 | 18981 | 18138 | 16042 | 53161 | 18981 | 18138 | 16042 | 53161 | - - - | - - - | - - - | - - -
5/3/2026 | 10:45:00 PM | 283.9 | 281 | 279.24 | 490.87 | 483.34 | 487.88 | 81.4575 | 74.7579 | 72.2108 | 0.2639 | 1.427 | 1.426 | 1.422 | 1.797 | 1.765 | 1.964 | Over-range | 60.02 | 18926 | 18064 | 16031 | 53021 | - - - | - - - | - - - | - - - | 18926 | 18064 | 16031 | 53021 | 12405 | 9823 | 11436 | 33664 | - - - | - - - | - - - | - - - | 12405 | 9823 | 11436 | 33664 | 22993 | 20859 | 20039 | 63891 | # # # | # # # | # # # | # # # | 0.823 | 0.866 | 0.8 | 0.83 | # # # | # # # | # # # | - - - | 0.834 | 0.877 | 0.813 | 0.842 | - - - | 0.635 | 1.65 | 1.51 | 1.46 | 1.48 | 1.47 | 1.49 | 16.25 | 15.27 | 17.46 | 0 | - - - | - - - | - - - | - - - | 22993 | 20859 | 20039 | 63891 | Over-range | 13044 | 10409 | 12007 | 35601 | 3915 | 3322 | 3542 | 11255 | 18887 | 18087 | 16077 | 53050 | 18887 | 18087 | 16077 | 53050 | - - - | - - - | - - - | - - -
5/3/2026 | 11:00:00 PM | 284.2 | 281.15 | 279.44 | 491.33 | 483.53 | 488.37 | 80.0539 | 73.3004 | 70.3171 | 0.2485 | 1.428 | 1.427 | 1.422 | 1.786 | 1.746 | 1.968 | Over-range | 60.02 | 18633 | 17827 | 15657 | 52117 | - - - | - - - | - - - | - - - | 18633 | 17827 | 15657 | 52117 | 12224 | 9511 | 11134 | 32870 | - - - | - - - | - - - | - - - | 12224 | 9511 | 11134 | 32870 | 22626 | 20469 | 19534 | 62628 | # # # | # # # | # # # | # # # | 0.824 | 0.871 | 0.802 | 0.832 | # # # | # # # | # # # | - - - | 0.834 | 0.881 | 0.814 | 0.844 | - - - | 0.631 | 1.65 | 1.51 | 1.46 | 1.48 | 1.47 | 1.5 | 15.99 | 14.74 | 17.22 | 0 | - - - | - - - | - - - | - - - | 22626 | 20469 | 19534 | 62628 | Over-range | 12829 | 10046 | 11669 | 34702 | 3782 | 3122 | 3382 | 10824 | 18589 | 17858 | 15701 | 52148 | 18589 | 17858 | 15701 | 52148 | - - - | - - - | - - - | - - -
5/3/2026 | 11:15:00 PM | 284 | 280.94 | 279.27 | 490.95 | 483.21 | 488.05 | 80.1243 | 73.0309 | 70.3525 | 0.256 | 1.428 | 1.427 | 1.422 | 1.769 | 1.731 | 1.959 | Over-range | 59.99 | 18600 | 17713 | 15564 | 51878 | - - - | - - - | - - - | - - - | 18600 | 17713 | 15564 | 51878 | 12334 | 9603 | 11255 | 33192 | - - - | - - - | - - - | - - - | 12334 | 9603 | 11255 | 33192 | 22643 | 20392 | 19539 | 62574 | # # # | # # # | # # # | # # # | 0.822 | 0.869 | 0.797 | 0.829 | # # # | # # # | # # # | - - - | 0.833 | 0.878 | 0.808 | 0.84 | - - - | 0.64 | 1.67 | 1.55 | 1.53 | 1.51 | 1.52 | 1.54 | 15.57 | 14.24 | 16.86 | 0 | - - - | - - - | - - - | - - - | 22643 | 20392 | 19539 | 62574 | Over-range | 12907 | 10091 | 11803 | 34965 | 3686 | 2976 | 3445 | 10672 | 18628 | 17748 | 15529 | 51905 | 18628 | 17748 | 15529 | 51905 | - - - | - - - | - - - | - - -
5/3/2026 | 11:30:00 PM | 284.19 | 281.16 | 279.54 | 491.2 | 483.74 | 488.45 | 78.1367 | 71.461 | 69.2454 | 0.2476 | 1.428 | 1.426 | 1.422 | 1.775 | 1.741 | 1.967 | Over-range | 60.02 | 18151 | 17253 | 15340 | 50744 | - - - | - - - | - - - | - - - | 18151 | 17253 | 15340 | 50744 | 11914 | 9399 | 10969 | 32281 | - - - | - - - | - - - | - - - | 11914 | 9399 | 10969 | 32281 | 22016 | 19887 | 19185 | 61088 | # # # | # # # | # # # | # # # | 0.824 | 0.868 | 0.8 | 0.831 | # # # | # # # | # # # | - - - | 0.836 | 0.877 | 0.812 | 0.842 | - - - | 0.636 | 1.69 | 1.55 | 1.5 | 1.51 | 1.51 | 1.54 | 15.89 | 14.57 | 17.19 | 0 | - - - | - - - | - - - | - - - | 22016 | 19887 | 19185 | 61088 | Over-range | 12453 | 9877 | 11510 | 33983 | 3519 | 2931 | 3393 | 10335 | 18212 | 17233 | 15330 | 50775 | 18212 | 17233 | 15330 | 50775 | - - - | - - - | - - - | - - -
5/3/2026 | 11:45:00 PM | 284.73 | 281.75 | 280.12 | 492.23 | 484.72 | 489.39 | 81.4096 | 74.553 | 71.5538 | 0.2565 | 1.428 | 1.427 | 1.423 | 1.773 | 1.739 | 1.952 | Over-range | 60.02 | 18947 | 18133 | 15927 | 53007 | - - - | - - - | - - - | - - - | 18947 | 18133 | 15927 | 53007 | 12517 | 9731 | 11402 | 33651 | - - - | - - - | - - - | - - - | 12517 | 9731 | 11402 | 33651 | 23052 | 20863 | 19921 | 63836 | # # # | # # # | # # # | # # # | 0.822 | 0.869 | 0.8 | 0.83 | # # # | # # # | # # # | - - - | 0.832 | 0.879 | 0.812 | 0.841 | - - - | 0.635 | 1.68 | 1.53 | 1.52 | 1.51 | 1.5 | 1.54 | 15.6 | 14.51 | 16.88 | 0 | - - - | - - - | - - - | - - - | 23052 | 20863 | 19921 | 63836 | Over-range | 13115 | 10293 | 11950 | 35520 | 3776 | 3218 | 3438 | 10988 | 18919 | 18130 | 15983 | 53032 | 18919 | 18130 | 15983 | 53032 | - - - | - - - | - - - | - - -
5/4/2026 | 12:00:00 AM | 284.99 | 281.97 | 280.48 | 492.59 | 485.22 | 489.99 | 78.3813 | 71.5756 | 69.6643 | 0.2403 | 1.427 | 1.425 | 1.421 | 1.79 | 1.767 | 1.984 | Over-range | 60.02 | 18254 | 17307 | 15446 | 51007 | - - - | - - - | - - - | - - - | 18254 | 17307 | 15446 | 51007 | 12013 | 9526 | 11131 | 32670 | - - - | - - - | - - - | - - - | 12013 | 9526 | 11131 | 32670 | 22206 | 20035 | 19414 | 61655 | # # # | # # # | # # # | # # # | 0.822 | 0.864 | 0.796 | 0.827 | # # # | # # # | # # # | - - - | 0.835 | 0.875 | 0.809 | 0.84 | - - - | 0.641 | 1.69 | 1.56 | 1.51 | 1.51 | 1.51 | 1.54 | 16.68 | 15.48 | 18.17 | 0 | - - - | - - - | - - - | - - - | 22206 | 20035 | 19414 | 61655 | Over-range | 12637 | 10080 | 11749 | 34605 | 3791 | 3165 | 3643 | 11056 | 18305 | 17300 | 15425 | 51030 | 18305 | 17300 | 15425 | 51030 | - - - | - - - | - - - | - - -
5/4/2026 | 12:15:00 AM | 285.1 | 281.94 | 280.37 | 492.71 | 485.06 | 489.98 | 81.6372 | 74.4439 | 72.1322 | 0.2489 | 1.427 | 1.425 | 1.422 | 1.775 | 1.747 | 1.964 | Over-range | 59.99 | 19068 | 18091 | 16037 | 53195 | - - - | - - - | - - - | - - - | 19068 | 18091 | 16037 | 53195 | 12544 | 9809 | 11566 | 33919 | - - - | - - - | - - - | - - - | 12544 | 9809 | 11566 | 33919 | 23158 | 20858 | 20114 | 64129 | # # # | # # # | # # # | # # # | 0.823 | 0.867 | 0.797 | 0.83 | # # # | # # # | # # # | - - - | 0.834 | 0.877 | 0.811 | 0.841 | - - - | 0.638 | 1.69 | 1.58 | 1.51 | 1.52 | 1.52 | 1.55 | 15.96 | 14.85 | 17.4 | 0 | - - - | - - - | - - - | - - - | 23158 | 20858 | 20114 | 64129 | Over-range | 13136 | 10367 | 12129 | 35789 | 3784 | 3244 | 3546 | 11109 | 19074 | 18052 | 16096 | 53222 | 19074 | 18052 | 16096 | 53222 | - - - | - - - | - - - | - - -
5/4/2026 | 12:30:00 AM | 285.11 | 281.97 | 280.41 | 492.78 | 485.07 | 490.03 | 80.4994 | 73.2722 | 71.0532 | 0.2498 | 1.427 | 1.425 | 1.421 | 1.776 | 1.751 | 1.973 | Over-range | 60.01 | 18748 | 17762 | 15733 | 52243 | - - - | - - - | - - - | - - - | 18748 | 17762 | 15733 | 52243 | 12359 | 9666 | 11430 | 33455 | - - - | - - - | - - - | - - - | 12359 | 9666 | 11430 | 33455 | 22804 | 20499 | 19787 | 63090 | # # # | # # # | # # # | # # # | 0.822 | 0.867 | 0.795 | 0.828 | # # # | # # # | # # # | - - - | 0.833 | 0.877 | 0.808 | 0.84 | - - - | 0.64 | 1.68 | 1.54 | 1.53 | 1.52 | 1.52 | 1.54 | 16.21 | 14.95 | 17.58 | 0 | - - - | - - - | - - - | - - - | 22804 | 20499 | 19787 | 63090 | Over-range | 12974 | 10221 | 11989 | 35341 | 3820 | 3192 | 3490 | 11036 | 18712 | 17761 | 15792 | 52265 | 18712 | 17761 | 15792 | 52265 | - - - | - - - | - - - | - - -
5/4/2026 | 12:45:00 AM | 285.33 | 282.31 | 280.7 | 493.27 | 485.67 | 490.41 | 80.4722 | 74.0192 | 71.4442 | 0.2496 | 1.427 | 1.426 | 1.421 | 1.791 | 1.774 | 1.981 | Over-range | 60 | 18773 | 17951 | 15956 | 52680 | - - - | - - - | - - - | - - - | 18773 | 17951 | 15956 | 52680 | 12287 | 9743 | 11256 | 33286 | - - - | - - - | - - - | - - - | 12287 | 9743 | 11256 | 33286 | 22810 | 20730 | 19916 | 63456 | # # # | # # # | # # # | # # # | 0.823 | 0.866 | 0.801 | 0.83 | # # # | # # # | # # # | - - - | 0.836 | 0.877 | 0.816 | 0.843 | - - - | 0.632 | 1.71 | 1.58 | 1.53 | 1.53 | 1.54 | 1.57 | 16.95 | 15.86 | 18.44 | 0 | - - - | - - - | - - - | - - - | 22810 | 20730 | 19916 | 63456 | Over-range | 12943 | 10344 | 11903 | 35327 | 3949 | 3358 | 3759 | 11516 | 18816 | 17938 | 15957 | 52711 | 18816 | 17938 | 15957 | 52711 | - - - | - - - | - - - | - - -
5/4/2026 | 1:00:00 AM | 285.46 | 282.32 | 280.72 | 493.39 | 485.67 | 490.56 | 82.9365 | 76.0339 | 72.9383 | 0.2483 | 1.427 | 1.425 | 1.421 | 1.805 | 1.785 | 1.988 | Over-range | 60.01 | 19391 | 18561 | 16319 | 54272 | - - - | - - - | - - - | - - - | 19391 | 18561 | 16319 | 54272 | 12674 | 9850 | 11478 | 34002 | - - - | - - - | - - - | - - - | 12674 | 9850 | 11478 | 34002 | 23548 | 21327 | 20358 | 65233 | # # # | # # # | # # # | # # # | 0.824 | 0.87 | 0.802 | 0.832 | # # # | # # # | # # # | - - - | 0.837 | 0.882 | 0.816 | 0.845 | - - - | 0.626 | 1.71 | 1.57 | 1.51 | 1.52 | 1.53 | 1.55 | 17.07 | 16.27 | 18.77 | 0 | - - - | - - - | - - - | - - - | 23548 | 21327 | 20358 | 65233 | Over-range | 13353 | 10491 | 12159 | 36165 | 4097 | 3509 | 3916 | 12033 | 19451 | 18557 | 16293 | 54301 | 19451 | 18557 | 16293 | 54301 | - - - | - - - | - - - | - - -
5/4/2026 | 1:15:00 AM | 285.34 | 282.11 | 280.63 | 493.09 | 485.35 | 490.47 | 80.2162 | 73.3771 | 71.0818 | 0.2518 | 1.427 | 1.425 | 1.421 | 1.821 | 1.811 | 2.012 | Over-range | 60 | 18720 | 17784 | 15819 | 52323 | - - - | - - - | - - - | - - - | 18720 | 17784 | 15819 | 52323 | 12135 | 9576 | 11189 | 32900 | - - - | - - - | - - - | - - - | 12135 | 9576 | 11189 | 32900 | 22737 | 20536 | 19810 | 63084 | # # # | # # # | # # # | # # # | 0.823 | 0.866 | 0.799 | 0.829 | # # # | # # # | # # # | - - - | 0.838 | 0.879 | 0.814 | 0.844 | - - - | 0.629 | 1.72 | 1.6 | 1.55 | 1.55 | 1.56 | 1.58 | 18.17 | 17.22 | 19.89 | 0 | - - - | - - - | - - - | - - - | 22737 | 20536 | 19810 | 63084 | Over-range | 12897 | 10253 | 11912 | 35205 | 4249 | 3545 | 3975 | 12201 | 18723 | 17836 | 15790 | 52349 | 18723 | 17836 | 15790 | 52349 | - - - | - - - | - - - | - - -
5/4/2026 | 1:30:00 AM | 285.11 | 281.87 | 280.4 | 492.67 | 484.95 | 490.08 | 80.9714 | 74.079 | 71.5945 | 0.2509 | 1.427 | 1.425 | 1.421 | 1.806 | 1.802 | 1.997 | Over-range | 60 | 18941 | 18020 | 15986 | 52947 | - - - | - - - | - - - | - - - | 18941 | 18020 | 15986 | 52947 | 12232 | 9588 | 11209 | 33029 | - - - | - - - | - - - | - - - | 12232 | 9588 | 11209 | 33029 | 22950 | 20735 | 19949 | 63634 | # # # | # # # | # # # | # # # | 0.825 | 0.869 | 0.801 | 0.832 | # # # | # # # | # # # | - - - | 0.839 | 0.882 | 0.817 | 0.846 | - - - | 0.624 | 1.71 | 1.58 | 1.54 | 1.54 | 1.55 | 1.56 | 17.7 | 16.81 | 19.51 | 0 | - - - | - - - | - - - | - - - | 22950 | 20735 | 19949 | 63634 | Over-range | 12952 | 10245 | 11924 | 35271 | 4148 | 3504 | 3966 | 12077 | 18986 | 18048 | 15949 | 52983 | 18986 | 18048 | 15949 | 52983 | - - - | - - - | - - - | - - -
5/4/2026 | 1:45:00 AM | 285.37 | 282.14 | 280.73 | 493.05 | 485.55 | 490.57 | 81.7369 | 74.6331 | 72.1778 | 0.2474 | 1.427 | 1.425 | 1.421 | 1.795 | 1.794 | 1.984 | Over-range | 60.01 | 19099 | 18142 | 16069 | 53310 | - - - | - - - | - - - | - - - | 19099 | 18142 | 16069 | 53310 | 12423 | 9692 | 11394 | 33509 | - - - | - - - | - - - | - - - | 12423 | 9692 | 11394 | 33509 | 23185 | 20901 | 20130 | 64215 | # # # | # # # | # # # | # # # | 0.824 | 0.868 | 0.798 | 0.83 | # # # | # # # | # # # | - - - | 0.838 | 0.88 | 0.813 | 0.844 | - - - | 0.629 | 1.73 | 1.61 | 1.55 | 1.55 | 1.57 | 1.59 | 17.19 | 16.52 | 19.09 | 0 | - - - | - - - | - - - | - - - | 23185 | 20901 | 20130 | 64215 | Over-range | 13128 | 10356 | 12107 | 35748 | 4114 | 3524 | 3977 | 12112 | 19159 | 18144 | 16034 | 53337 | 19159 | 18144 | 16034 | 53337 | - - - | - - - | - - - | - - -
5/4/2026 | 2:00:00 AM | 285.67 | 282.48 | 281.01 | 493.68 | 486.03 | 491.08 | 79.6655 | 72.6409 | 70.6722 | 0.2482 | 1.427 | 1.425 | 1.421 | 1.806 | 1.794 | 2.006 | Over-range | 60.01 | 18610 | 17604 | 15703 | 51917 | - - - | - - - | - - - | - - - | 18610 | 17604 | 15703 | 51917 | 12106 | 9516 | 11233 | 32855 | - - - | - - - | - - - | - - - | 12106 | 9516 | 11233 | 32855 | 22592 | 20339 | 19709 | 62640 | # # # | # # # | # # # | # # # | 0.824 | 0.866 | 0.797 | 0.829 | # # # | # # # | # # # | - - - | 0.837 | 0.878 | 0.813 | 0.843 | - - - | 0.633 | 1.73 | 1.62 | 1.53 | 1.55 | 1.56 | 1.58 | 17.69 | 16.73 | 19.39 | 0 | - - - | - - - | - - - | - - - | 22592 | 20339 | 19709 | 62640 | Over-range | 12801 | 10175 | 11899 | 35019 | 4047 | 3496 | 3820 | 11817 | 18618 | 17567 | 15761 | 51946 | 18618 | 17567 | 15761 | 51946 | - - - | - - - | - - - | - - -
5/4/2026 | 2:15:00 AM | 285.53 | 282.29 | 280.96 | 493.32 | 485.83 | 490.99 | 81.8174 | 74.2311 | 72.4706 | 0.2478 | 1.426 | 1.424 | 1.421 | 1.785 | 1.782 | 1.98 | Over-range | 60.01 | 19202 | 18070 | 16132 | 53404 | - - - | - - - | - - - | - - - | 19202 | 18070 | 16132 | 53404 | 12412 | 9735 | 11601 | 33748 | - - - | - - - | - - - | - - - | 12412 | 9735 | 11601 | 33748 | 23246 | 20830 | 20254 | 64330 | # # # | # # # | # # # | # # # | 0.826 | 0.868 | 0.797 | 0.83 | # # # | # # # | # # # | - - - | 0.838 | 0.879 | 0.811 | 0.843 | - - - | 0.632 | 1.7 | 1.59 | 1.55 | 1.54 | 1.56 | 1.57 | 16.79 | 15.86 | 18.51 | 0 | - - - | - - - | - - - | - - - | 23246 | 20830 | 20254 | 64330 | Over-range | 13095 | 10347 | 12238 | 35840 | 4071 | 3395 | 3790 | 11767 | 19173 | 18107 | 16146 | 53425 | 19173 | 18107 | 16146 | 53425 | - - - | - - - | - - - | - - -
5/4/2026 | 2:30:00 AM | 285.56 | 282.38 | 281 | 493.39 | 486.03 | 490.99 | 81.044 | 73.7192 | 71.8373 | 0.251 | 1.427 | 1.424 | 1.421 | 1.797 | 1.791 | 1.986 | Over-range | 60.01 | 18955 | 17892 | 15953 | 52800 | - - - | - - - | - - - | - - - | 18955 | 17892 | 15953 | 52800 | 12328 | 9703 | 11503 | 33534 | - - - | - - - | - - - | - - - | 12328 | 9703 | 11503 | 33534 | 22999 | 20661 | 20051 | 63711 | # # # | # # # | # # # | # # # | 0.824 | 0.866 | 0.796 | 0.829 | # # # | # # # | # # # | - - - | 0.837 | 0.878 | 0.81 | 0.842 | - - - | 0.635 | 1.72 | 1.6 | 1.56 | 1.55 | 1.57 | 1.58 | 17.13 | 16.33 | 18.83 | 0 | - - - | - - - | - - - | - - - | 22999 | 20661 | 20051 | 63711 | Over-range | 13018 | 10321 | 12136 | 35627 | 4082 | 3414 | 3772 | 11753 | 18923 | 17946 | 15961 | 52830 | 18923 | 17946 | 15961 | 52830 | - - - | - - - | - - - | - - -
5/4/2026 | 2:45:00 AM | 285.8 | 282.6 | 281.25 | 493.83 | 486.37 | 491.43 | 79.967 | 73.1388 | 70.951 | 0.2488 | 1.427 | 1.425 | 1.421 | 1.789 | 1.779 | 1.977 | Over-range | 60 | 18704 | 17763 | 15830 | 52296 | - - - | - - - | - - - | - - - | 18704 | 17763 | 15830 | 52296 | 12203 | 9649 | 11308 | 33160 | - - - | - - - | - - - | - - - | 12203 | 9649 | 11308 | 33160 | 22724 | 20526 | 19836 | 63085 | # # # | # # # | # # # | # # # | 0.823 | 0.865 | 0.798 | 0.829 | # # # | # # # | # # # | - - - | 0.835 | 0.877 | 0.812 | 0.842 | - - - | 0.634 | 1.71 | 1.61 | 1.56 | 1.55 | 1.57 | 1.58 | 16.85 | 15.8 | 18.43 | 0 | - - - | - - - | - - - | - - - | 22724 | 20526 | 19836 | 63085 | Over-range | 12890 | 10260 | 11937 | 35231 | 4030 | 3360 | 3709 | 11560 | 18669 | 17810 | 15846 | 52325 | 18669 | 17810 | 15846 | 52325 | - - - | - - - | - - - | - - -
5/4/2026 | 3:00:00 AM | 285.9 | 282.83 | 281.41 | 494.11 | 486.77 | 491.61 | 80.6846 | 73.656 | 71.0128 | 0.2444 | 1.427 | 1.425 | 1.421 | 1.774 | 1.754 | 1.962 | Over-range | 60.02 | 18822 | 17930 | 15807 | 52559 | - - - | - - - | - - - | - - - | 18822 | 17930 | 15807 | 52559 | 12450 | 9711 | 11412 | 33573 | - - - | - - - | - - - | - - - | 12450 | 9711 | 11412 | 33573 | 22904 | 20655 | 19835 | 63394 | # # # | # # # | # # # | # # # | 0.822 | 0.868 | 0.797 | 0.829 | # # # | # # # | # # # | - - - | 0.833 | 0.879 | 0.81 | 0.841 | - - - | 0.639 | 1.71 | 1.57 | 1.56 | 1.54 | 1.56 | 1.57 | 16.01 | 15.1 | 17.58 | 0 | - - - | - - - | - - - | - - - | 22904 | 20655 | 19835 | 63394 | Over-range | 13046 | 10243 | 11972 | 35421 | 3789 | 3147 | 3513 | 10994 | 18817 | 17969 | 15803 | 52589 | 18817 | 17969 | 15803 | 52589 | - - - | - - - | - - - | - - -
5/4/2026 | 3:15:00 AM | 285.84 | 282.84 | 281.46 | 493.98 | 486.91 | 491.59 | 79.5356 | 72.8044 | 70.7674 | 0.2478 | 1.426 | 1.423 | 1.42 | 1.773 | 1.76 | 1.958 | Over-range | 60 | 18597 | 17681 | 15785 | 52062 | - - - | - - - | - - - | - - - | 18597 | 17681 | 15785 | 52062 | 12294 | 9770 | 11413 | 33476 | - - - | - - - | - - - | - - - | 12294 | 9770 | 11413 | 33476 | 22636 | 20482 | 19825 | 62943 | # # # | # # # | # # # | # # # | 0.822 | 0.863 | 0.796 | 0.827 | # # # | # # # | # # # | - - - | 0.833 | 0.874 | 0.809 | 0.839 | - - - | 0.643 | 1.7 | 1.59 | 1.54 | 1.53 | 1.55 | 1.57 | 15.99 | 15.06 | 17.53 | 0 | - - - | - - - | - - - | - - - | 22636 | 20482 | 19825 | 62943 | Over-range | 12897 | 10325 | 11983 | 35344 | 3772 | 3214 | 3534 | 10987 | 18584 | 17686 | 15811 | 52081 | 18584 | 17686 | 15811 | 52081 | - - - | - - - | - - - | - - -
5/4/2026 | 3:30:00 AM | 285.93 | 283.01 | 281.59 | 494.25 | 487.13 | 491.77 | 79.1259 | 72.4633 | 70.2702 | 0.2461 | 1.426 | 1.424 | 1.421 | 1.772 | 1.757 | 1.955 | Over-range | 60 | 18483 | 17600 | 15672 | 51755 | - - - | - - - | - - - | - - - | 18483 | 17600 | 15672 | 51755 | 12185 | 9675 | 11290 | 33150 | - - - | - - - | - - - | - - - | 12185 | 9675 | 11290 | 33150 | 22481 | 20354 | 19652 | 62487 | # # # | # # # | # # # | # # # | 0.822 | 0.865 | 0.798 | 0.828 | # # # | # # # | # # # | - - - | 0.833 | 0.875 | 0.81 | 0.84 | - - - | 0.641 | 1.72 | 1.58 | 1.54 | 1.53 | 1.55 | 1.57 | 15.91 | 15 | 17.39 | 0 | - - - | - - - | - - - | - - - | 22481 | 20354 | 19652 | 62487 | Over-range | 12791 | 10211 | 11847 | 34988 | 3762 | 3135 | 3461 | 10831 | 18453 | 17649 | 15676 | 51778 | 18453 | 17649 | 15676 | 51778 | - - - | - - - | - - - | - - -
5/4/2026 | 3:45:00 AM | 286.04 | 283.01 | 281.71 | 494.33 | 487.21 | 492 | 81.3777 | 74.5229 | 72.0152 | 0.2499 | 1.426 | 1.423 | 1.42 | 1.767 | 1.757 | 1.948 | Over-range | 60 | 19020 | 18133 | 16083 | 53236 | - - - | - - - | - - - | - - - | 19020 | 18133 | 16083 | 53236 | 12546 | 9853 | 11548 | 33947 | - - - | - - - | - - - | - - - | 12546 | 9853 | 11548 | 33947 | 23131 | 20928 | 20148 | 64207 | # # # | # # # | # # # | # # # | 0.822 | 0.866 | 0.798 | 0.829 | # # # | # # # | # # # | - - - | 0.833 | 0.877 | 0.811 | 0.84 | - - - | 0.638 | 1.71 | 1.55 | 1.55 | 1.52 | 1.54 | 1.56 | 15.82 | 15.09 | 17.42 | 0 | - - - | - - - | - - - | - - - | 23131 | 20928 | 20148 | 64207 | Over-range | 13148 | 10428 | 12121 | 35848 | 3813 | 3295 | 3564 | 11188 | 19004 | 18129 | 16126 | 53258 | 19004 | 18129 | 16126 | 53258 | - - - | - - - | - - - | - - -
5/4/2026 | 4:00:00 AM | 285.78 | 282.86 | 281.5 | 493.94 | 487.02 | 491.52 | 78.4127 | 72.0928 | 70.3455 | 0.2531 | 1.425 | 1.423 | 1.421 | 1.794 | 1.788 | 1.962 | Over-range | 60 | 18379 | 17462 | 15747 | 51589 | - - - | - - - | - - - | - - - | 18379 | 17462 | 15747 | 51589 | 11905 | 9626 | 11172 | 32704 | - - - | - - - | - - - | - - - | 11905 | 9626 | 11172 | 32704 | 22277 | 20248 | 19677 | 62202 | # # # | # # # | # # # | # # # | 0.825 | 0.862 | 0.8 | 0.829 | # # # | # # # | # # # | - - - | 0.838 | 0.875 | 0.814 | 0.842 | - - - | 0.634 | 1.69 | 1.58 | 1.58 | 1.52 | 1.55 | 1.57 | 16.91 | 16.26 | 18.4 | 0 | - - - | - - - | - - - | - - - | 22277 | 20248 | 19677 | 62202 | Over-range | 12580 | 10236 | 11787 | 34721 | 3949 | 3361 | 3642 | 11330 | 18345 | 17523 | 15752 | 51619 | 18345 | 17523 | 15752 | 51619 | - - - | - - - | - - - | - - -
5/4/2026 | 4:15:00 AM | 286.06 | 283.15 | 281.73 | 494.5 | 487.38 | 491.97 | 81.133 | 74.7278 | 72.0254 | 0.2512 | 1.425 | 1.424 | 1.421 | 1.79 | 1.78 | 1.954 | Over-range | 60 | 19000 | 18206 | 16176 | 53383 | - - - | - - - | - - - | - - - | 19000 | 18206 | 16176 | 53383 | 12421 | 9864 | 11418 | 33702 | - - - | - - - | - - - | - - - | 12421 | 9864 | 11418 | 33702 | 23075 | 21014 | 20169 | 64257 | # # # | # # # | # # # | # # # | 0.823 | 0.866 | 0.802 | 0.831 | # # # | # # # | # # # | - - - | 0.836 | 0.879 | 0.816 | 0.844 | - - - | 0.631 | 1.72 | 1.6 | 1.61 | 1.54 | 1.6 | 1.61 | 16.71 | 16.19 | 18.31 | 0 | - - - | - - - | - - - | - - - | 23075 | 21014 | 20169 | 64257 | Over-range | 13087 | 10480 | 12035 | 35739 | 4025 | 3444 | 3709 | 11621 | 18972 | 18268 | 16179 | 53419 | 18972 | 18268 | 16179 | 53419 | - - - | - - - | - - - | - - -
5/4/2026 | 4:30:00 AM | 285.89 | 283.03 | 281.58 | 494.26 | 487.19 | 491.66 | 80.1146 | 73.7617 | 71.3967 | 0.2494 | 1.425 | 1.424 | 1.421 | 1.792 | 1.784 | 1.95 | Over-range | 60.01 | 18737 | 17906 | 15987 | 52630 | - - - | - - - | - - - | - - - | 18737 | 17906 | 15987 | 52630 | 12287 | 9809 | 11375 | 33472 | - - - | - - - | - - - | - - - | 12287 | 9809 | 11375 | 33472 | 22774 | 20734 | 19984 | 63492 | # # # | # # # | # # # | # # # | 0.823 | 0.864 | 0.8 | 0.829 | # # # | # # # | # # # | - - - | 0.835 | 0.876 | 0.814 | 0.842 | - - - | 0.636 | 1.71 | 1.6 | 1.58 | 1.53 | 1.58 | 1.6 | 16.7 | 16.28 | 18.24 | 0 | - - - | - - - | - - - | - - - | 22774 | 20734 | 19984 | 63492 | Over-range | 12939 | 10441 | 11979 | 35488 | 3944 | 3473 | 3649 | 11487 | 18711 | 17922 | 16029 | 52661 | 18711 | 17922 | 16029 | 52661 | - - - | - - - | - - - | - - -
5/4/2026 | 4:45:00 AM | 285.55 | 282.75 | 281.39 | 493.65 | 486.85 | 491.19 | 80.9921 | 75.0988 | 72.7413 | 0.2528 | 1.425 | 1.423 | 1.421 | 1.797 | 1.803 | 1.944 | Over-range | 60 | 19002 | 18222 | 16400 | 53624 | - - - | - - - | - - - | - - - | 19002 | 18222 | 16400 | 53624 | 12232 | 9903 | 11361 | 33496 | - - - | - - - | - - - | - - - | 12232 | 9903 | 11361 | 33496 | 22996 | 21089 | 20344 | 64429 | # # # | # # # | # # # | # # # | 0.826 | 0.864 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.839 | 0.877 | 0.821 | 0.846 | - - - | 0.625 | 1.7 | 1.59 | 1.59 | 1.52 | 1.58 | 1.59 | 17 | 16.76 | 18.62 | 0 | - - - | - - - | - - - | - - - | 22996 | 21089 | 20344 | 64429 | Over-range | 12938 | 10592 | 12025 | 35667 | 4096 | 3649 | 3827 | 11935 | 18970 | 18258 | 16430 | 53658 | 18970 | 18258 | 16430 | 53658 | - - - | - - - | - - - | - - -
5/4/2026 | 5:00:00 AM | 285.37 | 282.57 | 281.13 | 493.42 | 486.39 | 490.81 | 81.4824 | 75.3108 | 72.3951 | 0.2517 | 1.425 | 1.424 | 1.422 | 1.803 | 1.803 | 1.947 | Over-range | 60 | 19076 | 18331 | 16289 | 53696 | - - - | - - - | - - - | - - - | 19076 | 18331 | 16289 | 53696 | 12331 | 9771 | 11300 | 33402 | - - - | - - - | - - - | - - - | 12331 | 9771 | 11300 | 33402 | 23106 | 21123 | 20217 | 64446 | # # # | # # # | # # # | # # # | 0.826 | 0.868 | 0.806 | 0.833 | # # # | # # # | # # # | - - - | 0.839 | 0.882 | 0.821 | 0.847 | - - - | 0.622 | 1.74 | 1.62 | 1.61 | 1.54 | 1.61 | 1.63 | 17.21 | 17.21 | 19.01 | 0 | - - - | - - - | - - - | - - - | 23106 | 21123 | 20217 | 64446 | Over-range | 13032 | 10483 | 11965 | 35611 | 4117 | 3708 | 3839 | 12083 | 19056 | 18352 | 16330 | 53738 | 19056 | 18352 | 16330 | 53738 | - - - | - - - | - - - | - - -
5/4/2026 | 5:15:00 AM | 285.2 | 282.52 | 281.04 | 493.21 | 486.33 | 490.53 | 80.2914 | 74.6643 | 71.8492 | 0.2514 | 1.425 | 1.424 | 1.422 | 1.807 | 1.811 | 1.934 | Over-range | 60 | 18778 | 18120 | 16192 | 53090 | - - - | - - - | - - - | - - - | 18778 | 18120 | 16192 | 53090 | 12230 | 9830 | 11177 | 33237 | - - - | - - - | - - - | - - - | 12230 | 9830 | 11177 | 33237 | 22788 | 20973 | 20087 | 63849 | # # # | # # # | # # # | # # # | 0.824 | 0.864 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.838 | 0.877 | 0.822 | 0.846 | - - - | 0.626 | 1.75 | 1.67 | 1.67 | 1.58 | 1.64 | 1.68 | 17.07 | 17.16 | 18.89 | 0 | - - - | - - - | - - - | - - - | 22788 | 20973 | 20087 | 63849 | Over-range | 12904 | 10547 | 11876 | 35440 | 3998 | 3718 | 3909 | 11986 | 18842 | 18088 | 16198 | 53128 | 18842 | 18088 | 16198 | 53128 | - - - | - - - | - - - | - - -
5/4/2026 | 5:30:00 AM | 284.94 | 282.41 | 280.86 | 492.87 | 486.18 | 490.08 | 80.7087 | 75.3547 | 72.4667 | 0.2541 | 1.426 | 1.425 | 1.424 | 1.824 | 1.813 | 1.921 | Over-range | 60 | 18891 | 18276 | 16380 | 53547 | - - - | - - - | - - - | - - - | 18891 | 18276 | 16380 | 53547 | 12147 | 9873 | 11165 | 33185 | - - - | - - - | - - - | - - - | 12147 | 9873 | 11165 | 33185 | 22860 | 21133 | 20223 | 64215 | # # # | # # # | # # # | # # # | 0.826 | 0.865 | 0.81 | 0.834 | # # # | # # # | # # # | - - - | 0.84 | 0.879 | 0.825 | 0.848 | - - - | 0.62 | 1.81 | 1.71 | 1.73 | 1.62 | 1.7 | 1.74 | 17.26 | 17.48 | 18.83 | 0 | - - - | - - - | - - - | - - - | 22860 | 21133 | 20223 | 64215 | Over-range | 12865 | 10597 | 11849 | 35416 | 4131 | 3749 | 3866 | 12075 | 18892 | 18340 | 16368 | 53600 | 18892 | 18340 | 16368 | 53600 | - - - | - - - | - - - | - - -
5/4/2026 | 5:45:00 AM | 284.56 | 282.04 | 280.47 | 492.27 | 485.44 | 489.43 | 81.4366 | 75.8736 | 72.6172 | 0.2533 | 1.426 | 1.425 | 1.423 | 1.827 | 1.81 | 1.918 | Over-range | 60.01 | 19060 | 18455 | 16419 | 53933 | - - - | - - - | - - - | - - - | 19060 | 18455 | 16419 | 53933 | 12222 | 9776 | 11163 | 33160 | - - - | - - - | - - - | - - - | 12222 | 9776 | 11163 | 33160 | 23058 | 21271 | 20257 | 64587 | # # # | # # # | # # # | # # # | 0.827 | 0.868 | 0.811 | 0.835 | # # # | # # # | # # # | - - - | 0.84 | 0.882 | 0.826 | 0.849 | - - - | 0.615 | 1.88 | 1.75 | 1.79 | 1.68 | 1.75 | 1.81 | 17.17 | 17.47 | 18.72 | 0 | - - - | - - - | - - - | - - - | 23058 | 21271 | 20257 | 64587 | Over-range | 12963 | 10554 | 11848 | 35483 | 4205 | 3870 | 3857 | 12307 | 19026 | 18489 | 16469 | 53984 | 19026 | 18489 | 16469 | 53984 | - - - | - - - | - - - | - - -
5/4/2026 | 6:00:00 AM | 283.89 | 281.4 | 279.83 | 491.13 | 484.37 | 488.28 | 78.9251 | 73.5194 | 70.8658 | 0.2506 | 1.426 | 1.425 | 1.423 | 1.824 | 1.812 | 1.928 | Over-range | 60.01 | 18437 | 17784 | 15966 | 52187 | - - - | - - - | - - - | - - - | 18437 | 17784 | 15966 | 52187 | 11792 | 9582 | 10875 | 32250 | - - - | - - - | - - - | - - - | 11792 | 9582 | 10875 | 32250 | 22277 | 20546 | 19709 | 62532 | # # # | # # # | # # # | # # # | 0.828 | 0.866 | 0.81 | 0.835 | # # # | # # # | # # # | - - - | 0.842 | 0.88 | 0.825 | 0.849 | - - - | 0.618 | 1.85 | 1.76 | 1.79 | 1.67 | 1.74 | 1.8 | 17.32 | 17.39 | 18.88 | 0 | - - - | - - - | - - - | - - - | 22277 | 20546 | 19709 | 62532 | Over-range | 12496 | 10278 | 11545 | 34423 | 4035 | 3622 | 3786 | 11764 | 18452 | 17839 | 15947 | 52237 | 18452 | 17839 | 15947 | 52237 | - - - | - - - | - - - | - - -
5/4/2026 | 6:15:00 AM | 282.79 | 280.34 | 278.67 | 489.21 | 482.47 | 486.33 | 80.1442 | 74.8409 | 71.8595 | 0.2513 | 1.426 | 1.426 | 1.424 | 1.825 | 1.808 | 1.916 | Over-range | 59.98 | 18727 | 18132 | 16236 | 53095 | - - - | - - - | - - - | - - - | 18727 | 18132 | 16236 | 53095 | 11857 | 9583 | 10884 | 32323 | - - - | - - - | - - - | - - - | 11857 | 9583 | 10884 | 32323 | 22555 | 20862 | 19923 | 63340 | # # # | # # # | # # # | # # # | 0.83 | 0.869 | 0.815 | 0.838 | # # # | # # # | # # # | - - - | 0.843 | 0.883 | 0.829 | 0.852 | - - - | 0.609 | 1.94 | 1.83 | 1.88 | 1.73 | 1.82 | 1.88 | 16.89 | 16.95 | 18.3 | 0 | - - - | - - - | - - - | - - - | 22555 | 20862 | 19923 | 63340 | Over-range | 12564 | 10302 | 11534 | 34506 | 4047 | 3678 | 3707 | 11770 | 18700 | 18176 | 16276 | 53153 | 18700 | 18176 | 16276 | 53153 | - - - | - - - | - - - | - - -
5/4/2026 | 6:30:00 AM | 282.07 | 279.52 | 277.88 | 487.93 | 480.97 | 485.08 | 80.733 | 75.0955 | 72.0005 | 0.2511 | 1.425 | 1.425 | 1.424 | 1.836 | 1.822 | 1.93 | Over-range | 60 | 18885 | 18231 | 16263 | 53378 | - - - | - - - | - - - | - - - | 18885 | 18231 | 16263 | 53378 | 11779 | 9383 | 10773 | 31935 | - - - | - - - | - - - | - - - | 11779 | 9383 | 10773 | 31935 | 22660 | 20869 | 19901 | 63430 | # # # | # # # | # # # | # # # | 0.833 | 0.874 | 0.817 | 0.842 | # # # | # # # | # # # | - - - | 0.847 | 0.888 | 0.833 | 0.856 | - - - | 0.598 | 1.92 | 1.88 | 1.85 | 1.73 | 1.81 | 1.88 | 17.38 | 17.48 | 19.02 | 0 | - - - | - - - | - - - | - - - | 22660 | 20869 | 19901 | 63430 | Over-range | 12517 | 10145 | 11460 | 34240 | 4140 | 3772 | 3818 | 12090 | 18875 | 18261 | 16303 | 53440 | 18875 | 18261 | 16303 | 53440 | - - - | - - - | - - - | - - -
5/4/2026 | 6:45:00 AM | 281.91 | 279.45 | 277.83 | 487.65 | 480.95 | 484.9 | 79.1418 | 74.1349 | 71.2685 | 0.251 | 1.425 | 1.426 | 1.423 | 1.839 | 1.825 | 1.94 | Over-range | 60 | 18415 | 17853 | 16061 | 52330 | - - - | - - - | - - - | - - - | 18415 | 17853 | 16061 | 52330 | 11559 | 9431 | 10621 | 31610 | - - - | - - - | - - - | - - - | 11559 | 9431 | 10621 | 31610 | 22171 | 20565 | 19668 | 62403 | # # # | # # # | # # # | # # # | 0.831 | 0.868 | 0.817 | 0.839 | # # # | # # # | # # # | - - - | 0.845 | 0.883 | 0.832 | 0.853 | - - - | 0.604 | 1.9 | 1.85 | 1.83 | 1.7 | 1.78 | 1.85 | 17.6 | 17.5 | 19.06 | 0 | - - - | - - - | - - - | - - - | 22171 | 20565 | 19668 | 62403 | Over-range | 12328 | 10180 | 11332 | 33936 | 4166 | 3718 | 3836 | 12012 | 18403 | 17924 | 16052 | 52379 | 18403 | 17924 | 16052 | 52379 | - - - | - - - | - - - | - - -
5/4/2026 | 7:00:00 AM | 282.46 | 280.02 | 278.47 | 488.53 | 482.01 | 486 | 79.4621 | 74.4301 | 71.4636 | 0.2509 | 1.426 | 1.426 | 1.422 | 1.808 | 1.798 | 1.931 | Over-range | 60.03 | 18498 | 17971 | 16133 | 52602 | - - - | - - - | - - - | - - - | 18498 | 17971 | 16133 | 52602 | 11812 | 9606 | 10807 | 32225 | - - - | - - - | - - - | - - - | 11812 | 9606 | 10807 | 32225 | 22312 | 20692 | 19776 | 62779 | # # # | # # # | # # # | # # # | 0.829 | 0.869 | 0.816 | 0.838 | # # # | # # # | # # # | - - - | 0.842 | 0.881 | 0.83 | 0.851 | - - - | 0.613 | 1.88 | 1.86 | 1.82 | 1.69 | 1.77 | 1.84 | 16.55 | 16.15 | 18.05 | 0 | - - - | - - - | - - - | - - - | 22312 | 20692 | 19776 | 62779 | Over-range | 12468 | 10243 | 11426 | 34240 | 3899 | 3461 | 3616 | 11304 | 18495 | 18009 | 16148 | 52652 | 18495 | 18009 | 16148 | 52652 | - - - | - - - | - - - | - - -
5/4/2026 | 7:15:00 AM | 281.94 | 279.55 | 277.94 | 487.72 | 481.1 | 485.1 | 79.7828 | 74.8007 | 71.5085 | 0.2484 | 1.425 | 1.426 | 1.422 | 1.802 | 1.792 | 1.923 | Over-range | 60 | 18519 | 18055 | 16126 | 52700 | - - - | - - - | - - - | - - - | 18519 | 18055 | 16126 | 52700 | 11859 | 9565 | 10754 | 32178 | - - - | - - - | - - - | - - - | 11859 | 9565 | 10754 | 32178 | 22347 | 20753 | 19738 | 62838 | # # # | # # # | # # # | # # # | 0.829 | 0.87 | 0.817 | 0.839 | # # # | # # # | # # # | - - - | 0.841 | 0.882 | 0.831 | 0.852 | - - - | 0.611 | 1.86 | 1.81 | 1.81 | 1.66 | 1.75 | 1.81 | 16.38 | 16.03 | 17.88 | 0 | - - - | - - - | - - - | - - - | 22347 | 20753 | 19738 | 62838 | Over-range | 12501 | 10221 | 11371 | 34199 | 3845 | 3499 | 3582 | 11273 | 18527 | 18045 | 16175 | 52746 | 18527 | 18045 | 16175 | 52746 | - - - | - - - | - - - | - - -
5/4/2026 | 7:30:00 AM | 281.82 | 279.4 | 277.87 | 487.43 | 480.95 | 484.94 | 77.3783 | 72.6867 | 69.9304 | 0.2473 | 1.425 | 1.427 | 1.422 | 1.831 | 1.831 | 1.945 | Over-range | 60.02 | 17985 | 17484 | 15774 | 51243 | - - - | - - - | - - - | - - - | 17985 | 17484 | 15774 | 51243 | 11382 | 9342 | 10418 | 31142 | - - - | - - - | - - - | - - - | 11382 | 9342 | 10418 | 31142 | 21677 | 20166 | 19307 | 61150 | # # # | # # # | # # # | # # # | 0.83 | 0.867 | 0.817 | 0.838 | # # # | # # # | # # # | - - - | 0.844 | 0.881 | 0.832 | 0.853 | - - - | 0.608 | 1.87 | 1.84 | 1.83 | 1.69 | 1.77 | 1.83 | 17.46 | 17.24 | 19.15 | 0 | - - - | - - - | - - - | - - - | 21677 | 20166 | 19307 | 61150 | Over-range | 12093 | 10036 | 11121 | 33340 | 3984 | 3566 | 3795 | 11615 | 18030 | 17532 | 15737 | 51299 | 18030 | 17532 | 15737 | 51299 | - - - | - - - | - - - | - - -
5/4/2026 | 7:45:00 AM | 281.85 | 279.47 | 277.97 | 487.51 | 481.12 | 485.04 | 81.5717 | 76.3772 | 74.0148 | 0.2565 | 1.426 | 1.427 | 1.422 | 1.828 | 1.837 | 1.964 | Over-range | 60.02 | 19108 | 18447 | 16782 | 54337 | - - - | - - - | - - - | - - - | 19108 | 18447 | 16782 | 54337 | 11715 | 9644 | 10863 | 32221 | - - - | - - - | - - - | - - - | 11715 | 9644 | 10863 | 32221 | 22860 | 21201 | 20451 | 64512 | # # # | # # # | # # # | # # # | 0.836 | 0.87 | 0.821 | 0.842 | # # # | # # # | # # # | - - - | 0.852 | 0.885 | 0.837 | 0.858 | - - - | 0.593 | 1.88 | 1.83 | 1.79 | 1.68 | 1.75 | 1.81 | 18.14 | 17.69 | 19.85 | 0 | - - - | - - - | - - - | - - - | 22860 | 21201 | 20451 | 64512 | Over-range | 12532 | 10425 | 11670 | 34720 | 4352 | 3860 | 4171 | 12651 | 19165 | 18492 | 16744 | 54400 | 19165 | 18492 | 16744 | 54400 | - - - | - - - | - - - | - - -
5/4/2026 | 8:00:00 AM | 281.99 | 279.48 | 278.05 | 487.62 | 481.14 | 485.31 | 81.0525 | 75.8928 | 73.4087 | 0.2548 | 1.425 | 1.427 | 1.422 | 1.828 | 1.839 | 1.958 | Over-range | 60.04 | 19005 | 18376 | 16677 | 54058 | - - - | - - - | - - - | - - - | 19005 | 18376 | 16677 | 54058 | 11741 | 9622 | 10819 | 32181 | - - - | - - - | - - - | - - - | 11741 | 9622 | 10819 | 32181 | 22769 | 21117 | 20328 | 64214 | # # # | # # # | # # # | # # # | 0.835 | 0.87 | 0.82 | 0.842 | # # # | # # # | # # # | - - - | 0.851 | 0.885 | 0.837 | 0.858 | - - - | 0.595 | 1.85 | 1.84 | 1.76 | 1.66 | 1.73 | 1.8 | 18.18 | 17.82 | 20.02 | 0 | - - - | - - - | - - - | - - - | 22769 | 21117 | 20328 | 64214 | Over-range | 12533 | 10396 | 11616 | 34638 | 4309 | 3864 | 4160 | 12600 | 19076 | 18399 | 16647 | 54122 | 19076 | 18399 | 16647 | 54122 | - - - | - - - | - - - | - - -
5/4/2026 | 8:15:00 AM | 281.52 | 278.89 | 277.5 | 486.71 | 480.13 | 484.45 | 80.1732 | 75.0788 | 72.5837 | 0.2546 | 1.425 | 1.427 | 1.422 | 1.852 | 1.854 | 1.967 | Over-range | 60.03 | 18754 | 18113 | 16443 | 53310 | - - - | - - - | - - - | - - - | 18754 | 18113 | 16443 | 53310 | 11471 | 9393 | 10587 | 31452 | - - - | - - - | - - - | - - - | 11471 | 9393 | 10587 | 31452 | 22439 | 20800 | 20018 | 63257 | # # # | # # # | # # # | # # # | 0.836 | 0.871 | 0.821 | 0.843 | # # # | # # # | # # # | - - - | 0.852 | 0.887 | 0.839 | 0.86 | - - - | 0.59 | 1.85 | 1.82 | 1.79 | 1.66 | 1.75 | 1.81 | 18.65 | 18.41 | 20.37 | 0 | - - - | - - - | - - - | - - - | 22439 | 20800 | 20018 | 63257 | Over-range | 12312 | 10211 | 11405 | 34018 | 4374 | 3907 | 4148 | 12686 | 18794 | 18173 | 16408 | 53375 | 18794 | 18173 | 16408 | 53375 | - - - | - - - | - - - | - - -
5/4/2026 | 8:30:00 AM | 281.15 | 278.39 | 277.21 | 485.89 | 479.4 | 483.99 | 81.9625 | 76.562 | 73.5915 | 0.2591 | 1.426 | 1.428 | 1.422 | 1.864 | 1.879 | 1.97 | Over-range | 60.03 | 19173 | 18526 | 16679 | 54377 | - - - | - - - | - - - | - - - | 19173 | 18526 | 16679 | 54377 | 11716 | 9366 | 10713 | 31795 | - - - | - - - | - - - | - - - | 11716 | 9366 | 10713 | 31795 | 22934 | 21198 | 20297 | 64429 | # # # | # # # | # # # | # # # | 0.836 | 0.874 | 0.822 | 0.844 | # # # | # # # | # # # | - - - | 0.852 | 0.891 | 0.841 | 0.861 | - - - | 0.585 | 1.88 | 1.84 | 1.83 | 1.68 | 1.78 | 1.83 | 18.82 | 19.14 | 20.81 | 0 | - - - | - - - | - - - | - - - | 22934 | 21198 | 20297 | 64429 | Over-range | 12578 | 10291 | 11557 | 34531 | 4495 | 4191 | 4257 | 13248 | 19192 | 18531 | 16725 | 54448 | 19192 | 18531 | 16725 | 54448 | - - - | - - - | - - - | - - -
5/4/2026 | 8:45:00 AM | 280.48 | 277.43 | 276.39 | 484.48 | 477.73 | 482.83 | 81.4903 | 75.9213 | 73.3574 | 0.2521 | 1.426 | 1.428 | 1.422 | 1.922 | 1.921 | 2.012 | Over-range | 60.02 | 18967 | 18207 | 16494 | 53667 | - - - | - - - | - - - | - - - | 18967 | 18207 | 16494 | 53667 | 11424 | 9150 | 10549 | 31124 | - - - | - - - | - - - | - - - | 11424 | 9150 | 10549 | 31124 | 22708 | 20910 | 20137 | 63755 | # # # | # # # | # # # | # # # | 0.835 | 0.871 | 0.819 | 0.842 | # # # | # # # | # # # | - - - | 0.855 | 0.892 | 0.842 | 0.863 | - - - | 0.58 | 1.85 | 1.84 | 1.85 | 1.67 | 1.8 | 1.82 | 20.95 | 21.32 | 22.86 | 0 | - - - | - - - | - - - | - - - | 22708 | 20910 | 20137 | 63755 | Over-range | 12473 | 10261 | 11537 | 34369 | 4905 | 4548 | 4574 | 14296 | 18954 | 18240 | 16558 | 53752 | 18954 | 18240 | 16558 | 53752 | - - - | - - - | - - - | - - -
5/4/2026 | 9:00:00 AM | 280.28 | 277.15 | 276.21 | 483.99 | 477.35 | 482.54 | 83.3096 | 77.5646 | 74.5989 | 0.2625 | 1.426 | 1.428 | 1.422 | 1.917 | 1.915 | 2.002 | Over-range | 60.01 | 19449 | 18693 | 16849 | 54992 | - - - | - - - | - - - | - - - | 19449 | 18693 | 16849 | 54992 | 11581 | 9177 | 10602 | 31360 | - - - | - - - | - - - | - - - | 11581 | 9177 | 10602 | 31360 | 23200 | 21342 | 20472 | 65014 | # # # | # # # | # # # | # # # | 0.838 | 0.876 | 0.823 | 0.846 | # # # | # # # | # # # | - - - | 0.858 | 0.897 | 0.845 | 0.867 | - - - | 0.57 | 1.84 | 1.87 | 1.81 | 1.67 | 1.79 | 1.82 | 20.69 | 21.15 | 22.79 | 0 | - - - | - - - | - - - | - - - | 23200 | 21342 | 20472 | 65014 | Over-range | 12639 | 10282 | 11615 | 34646 | 4974 | 4559 | 4663 | 14489 | 19467 | 18768 | 16840 | 55074 | 19467 | 18768 | 16840 | 55074 | - - - | - - - | - - - | - - -
5/4/2026 | 9:15:00 AM | 279.98 | 276.79 | 275.81 | 483.5 | 476.65 | 481.92 | 83.182 | 77.4736 | 74.2702 | 0.261 | 1.426 | 1.428 | 1.423 | 1.913 | 1.899 | 1.987 | Over-range | 60 | 19386 | 18659 | 16753 | 54797 | - - - | - - - | - - - | - - - | 19386 | 18659 | 16753 | 54797 | 11638 | 9147 | 10550 | 31335 | - - - | - - - | - - - | - - - | 11638 | 9147 | 10550 | 31335 | 23146 | 21291 | 20354 | 64790 | # # # | # # # | # # # | # # # | 0.838 | 0.876 | 0.823 | 0.846 | # # # | # # # | # # # | - - - | 0.857 | 0.897 | 0.845 | 0.866 | - - - | 0.572 | 1.81 | 1.81 | 1.78 | 1.63 | 1.75 | 1.77 | 20.51 | 21.07 | 22.55 | 0 | - - - | - - - | - - - | - - - | 23146 | 21291 | 20354 | 64790 | Over-range | 12639 | 10241 | 11549 | 34541 | 4847 | 4534 | 4624 | 14315 | 19478 | 18651 | 16751 | 54879 | 19478 | 18651 | 16751 | 54879 | - - - | - - - | - - - | - - -
5/4/2026 | 9:30:00 AM | 279.69 | 276.44 | 275.51 | 482.98 | 476.02 | 481.44 | 81.059 | 75.3672 | 72.655 | 0.256 | 1.427 | 1.429 | 1.424 | 1.922 | 1.907 | 1.997 | Over-range | 60.01 | 18940 | 18142 | 16396 | 53478 | - - - | - - - | - - - | - - - | 18940 | 18142 | 16396 | 53478 | 11177 | 8840 | 10283 | 30300 | - - - | - - - | - - - | - - - | 11177 | 8840 | 10283 | 30300 | 22557 | 20713 | 19911 | 63181 | # # # | # # # | # # # | # # # | 0.84 | 0.876 | 0.824 | 0.846 | # # # | # # # | # # # | - - - | 0.86 | 0.898 | 0.847 | 0.868 | - - - | 0.567 | 1.81 | 1.81 | 1.74 | 1.62 | 1.73 | 1.75 | 21.18 | 21.68 | 23.14 | 0 | - - - | - - - | - - - | - - - | 22557 | 20713 | 19911 | 63181 | Over-range | 12245 | 9983 | 11286 | 33617 | 4931 | 4571 | 4583 | 14363 | 18933 | 18180 | 16457 | 53569 | 18933 | 18180 | 16457 | 53569 | - - - | - - - | - - - | - - -
5/4/2026 | 9:45:00 AM | 280.06 | 276.9 | 275.89 | 483.65 | 476.88 | 481.99 | 83.5761 | 77.7216 | 74.4294 | 0.2687 | 1.426 | 1.428 | 1.424 | 1.907 | 1.895 | 1.974 | Over-range | 60.01 | 19489 | 18744 | 16777 | 55010 | - - - | - - - | - - - | - - - | 19489 | 18744 | 16777 | 55010 | 11679 | 9148 | 10606 | 31433 | - - - | - - - | - - - | - - - | 11679 | 9148 | 10606 | 31433 | 23279 | 21386 | 20414 | 65079 | # # # | # # # | # # # | # # # | 0.837 | 0.876 | 0.822 | 0.845 | # # # | # # # | # # # | - - - | 0.857 | 0.897 | 0.843 | 0.866 | - - - | 0.571 | 1.8 | 1.84 | 1.8 | 1.64 | 1.76 | 1.77 | 20.38 | 21.05 | 22.49 | 0 | - - - | - - - | - - - | - - - | 23279 | 21386 | 20414 | 65079 | Over-range | 12716 | 10273 | 11616 | 34722 | 4933 | 4590 | 4650 | 14498 | 19537 | 18801 | 16760 | 55097 | 19537 | 18801 | 16760 | 55097 | - - - | - - - | - - - | - - -
5/4/2026 | 10:00:00 AM | 281.26 | 278.05 | 277.06 | 485.68 | 478.86 | 484.09 | 80.3354 | 74.3844 | 72.0423 | 0.2661 | 1.427 | 1.429 | 1.425 | 1.897 | 1.888 | 1.963 | Over-range | 60.01 | 18736 | 17869 | 16163 | 52769 | - - - | - - - | - - - | - - - | 18736 | 17869 | 16163 | 52769 | 11376 | 9066 | 10526 | 30969 | - - - | - - - | - - - | - - - | 11376 | 9066 | 10526 | 30969 | 22436 | 20518 | 19813 | 62768 | # # # | # # # | # # # | # # # | 0.835 | 0.871 | 0.816 | 0.841 | # # # | # # # | # # # | - - - | 0.854 | 0.891 | 0.836 | 0.861 | - - - | 0.587 | 1.77 | 1.8 | 1.77 | 1.62 | 1.73 | 1.74 | 20.11 | 20.68 | 22.09 | 0 | - - - | - - - | - - - | - - - | 22436 | 20518 | 19813 | 62768 | Over-range | 12334 | 10069 | 11448 | 33956 | 4668 | 4293 | 4409 | 13661 | 18775 | 17931 | 16142 | 52847 | 18775 | 17931 | 16142 | 52847 | - - - | - - - | - - - | - - -
5/4/2026 | 10:15:00 AM | 280.79 | 277.47 | 276.53 | 484.81 | 477.81 | 483.26 | 82.8313 | 76.6491 | 73.8639 | 0.2673 | 1.426 | 1.429 | 1.425 | 1.91 | 1.889 | 1.966 | Over-range | 60.02 | 19425 | 18540 | 16686 | 54651 | - - - | - - - | - - - | - - - | 19425 | 18540 | 16686 | 54651 | 11580 | 9049 | 10631 | 31260 | - - - | - - - | - - - | - - - | 11580 | 9049 | 10631 | 31260 | 23146 | 21149 | 20321 | 64617 | # # # | # # # | # # # | # # # | 0.839 | 0.877 | 0.821 | 0.846 | # # # | # # # | # # # | - - - | 0.858 | 0.898 | 0.843 | 0.866 | - - - | 0.572 | 1.79 | 1.81 | 1.8 | 1.62 | 1.75 | 1.76 | 20.36 | 21.1 | 22.29 | 0 | - - - | - - - | - - - | - - - | 23146 | 21149 | 20321 | 64617 | Over-range | 12581 | 10165 | 11589 | 34453 | 4850 | 4572 | 4548 | 14300 | 19459 | 18529 | 16756 | 54744 | 19459 | 18529 | 16756 | 54744 | - - - | - - - | - - - | - - -
5/4/2026 | 10:30:00 AM | 280.71 | 277.39 | 276.39 | 484.67 | 477.64 | 483.04 | 82.8455 | 76.5706 | 73.6251 | 0.2666 | 1.426 | 1.429 | 1.425 | 1.911 | 1.887 | 1.958 | Over-range | 60.01 | 19356 | 18494 | 16559 | 54409 | - - - | - - - | - - - | - - - | 19356 | 18494 | 16559 | 54409 | 11699 | 9116 | 10719 | 31534 | - - - | - - - | - - - | - - - | 11699 | 9116 | 10719 | 31534 | 23158 | 21137 | 20256 | 64551 | # # # | # # # | # # # | # # # | 0.836 | 0.875 | 0.818 | 0.843 | # # # | # # # | # # # | - - - | 0.855 | 0.896 | 0.839 | 0.863 | - - - | 0.58 | 1.82 | 1.84 | 1.82 | 1.65 | 1.78 | 1.79 | 20.21 | 21.01 | 22.16 | 0 | - - - | - - - | - - - | - - - | 23158 | 21137 | 20256 | 64551 | Over-range | 12706 | 10224 | 11657 | 34708 | 4884 | 4564 | 4508 | 14300 | 19351 | 18532 | 16618 | 54501 | 19351 | 18532 | 16618 | 54501 | - - - | - - - | - - - | - - -
5/4/2026 | 10:45:00 AM | 280.74 | 277.31 | 276.38 | 484.64 | 477.5 | 483.11 | 81.7519 | 75.8095 | 72.9197 | 0.2649 | 1.426 | 1.429 | 1.425 | 1.923 | 1.896 | 1.973 | Over-range | 60.01 | 19046 | 18203 | 16374 | 53623 | - - - | - - - | - - - | - - - | 19046 | 18203 | 16374 | 53623 | 11346 | 8911 | 10400 | 30657 | - - - | - - - | - - - | - - - | 11346 | 8911 | 10400 | 30657 | 22757 | 20817 | 19976 | 63550 | # # # | # # # | # # # | # # # | 0.837 | 0.874 | 0.82 | 0.844 | # # # | # # # | # # # | - - - | 0.858 | 0.897 | 0.842 | 0.866 | - - - | 0.572 | 1.79 | 1.83 | 1.83 | 1.64 | 1.77 | 1.78 | 21.24 | 21.87 | 23.17 | 0 | - - - | - - - | - - - | - - - | 22757 | 20817 | 19976 | 63550 | Over-range | 12438 | 10073 | 11423 | 34044 | 4996 | 4605 | 4632 | 14534 | 19059 | 18282 | 16378 | 53718 | 19059 | 18282 | 16378 | 53718 | - - - | - - - | - - - | - - -
5/4/2026 | 11:00:00 AM | 280.81 | 277.54 | 276.52 | 484.9 | 477.88 | 483.23 | 83.8976 | 77.8817 | 74.1688 | 0.2652 | 1.427 | 1.429 | 1.426 | 1.895 | 1.864 | 1.942 | Over-range | 60.02 | 19629 | 18915 | 16791 | 55335 | - - - | - - - | - - - | - - - | 19629 | 18915 | 16791 | 55335 | 11883 | 9174 | 10710 | 31768 | - - - | - - - | - - - | - - - | 11883 | 9174 | 10710 | 31768 | 23467 | 21516 | 20422 | 65405 | # # # | # # # | # # # | # # # | 0.837 | 0.879 | 0.822 | 0.846 | # # # | # # # | # # # | - - - | 0.854 | 0.899 | 0.843 | 0.866 | - - - | 0.574 | 1.85 | 1.85 | 1.83 | 1.67 | 1.8 | 1.82 | 19.67 | 20.29 | 21.57 | 0 | - - - | - - - | - - - | - - - | 23467 | 21516 | 20422 | 65405 | Over-range | 12854 | 10245 | 11615 | 34845 | 4827 | 4491 | 4422 | 14112 | 19626 | 18950 | 16852 | 55428 | 19626 | 18950 | 16852 | 55428 | - - - | - - - | - - - | - - -
5/4/2026 | 11:15:00 AM | 280.72 | 277.42 | 276.53 | 484.63 | 477.85 | 483.19 | 80.243 | 74.3911 | 71.8607 | 0.261 | 1.428 | 1.43 | 1.427 | 1.92 | 1.901 | 1.969 | Over-range | 60.01 | 18691 | 17849 | 16125 | 52664 | - - - | - - - | - - - | - - - | 18691 | 17849 | 16125 | 52664 | 11214 | 8867 | 10359 | 30439 | - - - | - - - | - - - | - - - | 11214 | 8867 | 10359 | 30439 | 22356 | 20462 | 19716 | 62534 | # # # | # # # | # # # | # # # | 0.836 | 0.872 | 0.818 | 0.842 | # # # | # # # | # # # | - - - | 0.856 | 0.895 | 0.841 | 0.864 | - - - | 0.578 | 1.84 | 1.84 | 1.84 | 1.67 | 1.78 | 1.81 | 20.99 | 21.75 | 22.95 | 0 | - - - | - - - | - - - | - - - | 22356 | 20462 | 19716 | 62534 | Over-range | 12258 | 9992 | 11333 | 33687 | 4856 | 4522 | 4508 | 14175 | 18690 | 17896 | 16175 | 52760 | 18690 | 17896 | 16175 | 52760 | - - - | - - - | - - - | - - -
5/4/2026 | 11:30:00 AM | 280.4 | 277.15 | 276.17 | 484.15 | 477.31 | 482.58 | 82.3689 | 75.7624 | 73.9535 | 0.2638 | 1.428 | 1.43 | 1.426 | 1.88 | 1.877 | 1.95 | Over-range | 60.01 | 19389 | 18298 | 16675 | 54361 | - - - | - - - | - - - | - - - | 19389 | 18298 | 16675 | 54361 | 11296 | 8950 | 10641 | 30888 | - - - | - - - | - - - | - - - | 11296 | 8950 | 10641 | 30888 | 22958 | 20857 | 20293 | 64108 | # # # | # # # | # # # | # # # | 0.845 | 0.877 | 0.822 | 0.848 | # # # | # # # | # # # | - - - | 0.863 | 0.897 | 0.842 | 0.867 | - - - | 0.568 | 1.82 | 1.86 | 1.82 | 1.66 | 1.78 | 1.8 | 19.71 | 20.44 | 21.66 | 0 | - - - | - - - | - - - | - - - | 22958 | 20857 | 20293 | 64108 | Over-range | 12281 | 9993 | 11553 | 33945 | 4723 | 4360 | 4407 | 13820 | 19387 | 18357 | 16708 | 54452 | 19387 | 18357 | 16708 | 54452 | - - - | - - - | - - - | - - -
5/4/2026 | 11:45:00 AM | 280.25 | 276.98 | 276.02 | 483.87 | 477.01 | 482.33 | 83.4451 | 77.5461 | 74.6735 | 0.2649 | 1.428 | 1.43 | 1.426 | 1.924 | 1.908 | 1.973 | Over-range | 60 | 19511 | 18682 | 16851 | 55045 | - - - | - - - | - - - | - - - | 19511 | 18682 | 16851 | 55045 | 11535 | 9100 | 10606 | 31241 | - - - | - - - | - - - | - - - | 11535 | 9100 | 10606 | 31241 | 23269 | 21356 | 20500 | 65124 | # # # | # # # | # # # | # # # | 0.839 | 0.875 | 0.822 | 0.845 | # # # | # # # | # # # | - - - | 0.859 | 0.898 | 0.845 | 0.868 | - - - | 0.568 | 1.84 | 1.87 | 1.82 | 1.67 | 1.79 | 1.81 | 21.23 | 22.01 | 23.22 | 0 | - - - | - - - | - - - | - - - | 23269 | 21356 | 20500 | 65124 | Over-range | 12662 | 10325 | 11660 | 34754 | 5146 | 4805 | 4770 | 15012 | 19507 | 18749 | 16889 | 55145 | 19507 | 18749 | 16889 | 55145 | - - - | - - - | - - - | - - -
5/4/2026 | 12:00:00 PM | 280.13 | 276.98 | 275.97 | 483.74 | 477.03 | 482.15 | 84.2325 | 78.3855 | 75.7355 | 0.2667 | 1.428 | 1.43 | 1.427 | 1.94 | 1.925 | 1.981 | Over-range | 60 | 19722 | 18853 | 17113 | 55687 | - - - | - - - | - - - | - - - | 19722 | 18853 | 17113 | 55687 | 11460 | 9095 | 10615 | 31170 | - - - | - - - | - - - | - - - | 11460 | 9095 | 10615 | 31170 | 23442 | 21551 | 20760 | 65753 | # # # | # # # | # # # | # # # | 0.841 | 0.875 | 0.824 | 0.847 | # # # | # # # | # # # | - - - | 0.864 | 0.9 | 0.849 | 0.871 | - - - | 0.56 | 1.84 | 1.85 | 1.83 | 1.67 | 1.78 | 1.81 | 22.03 | 23.05 | 23.96 | 0 | - - - | - - - | - - - | - - - | 23442 | 21551 | 20760 | 65753 | Over-range | 12664 | 10428 | 11743 | 34934 | 5310 | 5027 | 4943 | 15550 | 19729 | 18890 | 17177 | 55797 | 19729 | 18890 | 17177 | 55797 | - - - | - - - | - - - | - - -
5/4/2026 | 12:15:00 PM | 279.62 | 276.61 | 275.59 | 482.93 | 476.46 | 481.34 | 83.5341 | 77.6461 | 74.6781 | 0.5305 | 1.428 | 1.428 | 1.426 | 1.968 | 1.959 | 2.045 | Over-range | 59.99 | 19490 | 18662 | 16831 | 54982 | - - - | - - - | - - - | - - - | 19490 | 18662 | 16831 | 54982 | 11433 | 9002 | 10457 | 30892 | - - - | - - - | - - - | - - - | 11433 | 9002 | 10457 | 30892 | 23221 | 21335 | 20450 | 65006 | # # # | # # # | # # # | # # # | 0.839 | 0.875 | 0.823 | 0.846 | # # # | # # # | # # # | - - - | 0.862 | 0.899 | 0.849 | 0.87 | - - - | 0.562 | 1.68 | 1.67 | 1.65 | 1.5 | 1.59 | 1.62 | 22.18 | 23.02 | 24.34 | 0 | - - - | - - - | - - - | - - - | 23221 | 21335 | 20450 | 65006 | Over-range | 12616 | 10326 | 11605 | 34649 | 5252 | 4985 | 4954 | 15466 | 19537 | 18647 | 16888 | 55072 | 19537 | 18647 | 16888 | 55072 | - - - | - - - | - - - | - - -
5/4/2026 | 12:30:00 PM | 279.58 | 276.57 | 275.57 | 482.87 | 476.39 | 481.31 | 83.701 | 77.9652 | 74.9957 | 0.6406 | 1.429 | 1.43 | 1.428 | 1.976 | 1.98 | 2.09 | Over-range | 59.99 | 19528 | 18727 | 16939 | 55194 | - - - | - - - | - - - | - - - | 19528 | 18727 | 16939 | 55194 | 11509 | 9169 | 10492 | 31169 | - - - | - - - | - - - | - - - | 11509 | 9169 | 10492 | 31169 | 23280 | 21437 | 20560 | 65277 | # # # | # # # | # # # | # # # | 0.839 | 0.874 | 0.824 | 0.846 | # # # | # # # | # # # | - - - | 0.862 | 0.897 | 0.849 | 0.869 | - - - | 0.565 | 1.6 | 1.56 | 1.52 | 1.4 | 1.46 | 1.52 | 22.1 | 22.55 | 24.27 | 0 | - - - | - - - | - - - | - - - | 23280 | 21437 | 20560 | 65277 | Over-range | 12666 | 10419 | 11642 | 34823 | 5223 | 4891 | 4986 | 15353 | 19619 | 18708 | 16957 | 55284 | 19619 | 18708 | 16957 | 55284 | - - - | - - - | - - - | - - -
5/4/2026 | 12:45:00 PM | 278.9 | 275.85 | 274.86 | 481.66 | 475.14 | 480.11 | 84.3029 | 78.5693 | 75.0054 | 0.6287 | 1.428 | 1.429 | 1.426 | 1.995 | 1.987 | 2.104 | Over-range | 59.98 | 19650 | 18910 | 16939 | 55499 | - - - | - - - | - - - | - - - | 19650 | 18910 | 16939 | 55499 | 11419 | 8930 | 10270 | 30619 | - - - | - - - | - - - | - - - | 11419 | 8930 | 10270 | 30619 | 23393 | 21545 | 20498 | 65436 | # # # | # # # | # # # | # # # | 0.84 | 0.878 | 0.826 | 0.848 | # # # | # # # | # # # | - - - | 0.864 | 0.903 | 0.853 | 0.873 | - - - | 0.552 | 1.56 | 1.53 | 1.52 | 1.39 | 1.45 | 1.5 | 22.63 | 23.17 | 25.08 | 0 | - - - | - - - | - - - | - - - | 23393 | 21545 | 20498 | 65436 | Over-range | 12675 | 10299 | 11525 | 34608 | 5411 | 5044 | 5145 | 15878 | 19730 | 18940 | 16916 | 55586 | 19730 | 18940 | 16916 | 55586 | - - - | - - - | - - - | - - -
5/4/2026 | 1:00:00 PM | 279.15 | 276.21 | 275.24 | 482.13 | 475.9 | 480.6 | 80.9887 | 75.7745 | 73.0928 | 0.6252 | 1.428 | 1.428 | 1.426 | 2.017 | 2.013 | 2.121 | Over-range | 59.98 | 18891 | 18144 | 16518 | 53553 | - - - | - - - | - - - | - - - | 18891 | 18144 | 16518 | 53553 | 10966 | 8843 | 10059 | 29867 | - - - | - - - | - - - | - - - | 10966 | 8843 | 10059 | 29867 | 22511 | 20827 | 20024 | 63361 | # # # | # # # | # # # | # # # | 0.839 | 0.871 | 0.825 | 0.845 | # # # | # # # | # # # | - - - | 0.865 | 0.898 | 0.853 | 0.872 | - - - | 0.558 | 1.59 | 1.56 | 1.54 | 1.41 | 1.46 | 1.51 | 23.6 | 24.13 | 25.8 | 0 | - - - | - - - | - - - | - - - | 22511 | 20827 | 20024 | 63361 | Over-range | 12236 | 10216 | 11310 | 33841 | 5378 | 5067 | 5124 | 15769 | 18953 | 18146 | 16546 | 53644 | 18953 | 18146 | 16546 | 53644 | - - - | - - - | - - - | - - -
5/4/2026 | 1:15:00 PM | 279.16 | 276.19 | 275.16 | 482.17 | 475.74 | 480.54 | 84.7031 | 79.1628 | 75.7951 | 0.6286 | 1.428 | 1.429 | 1.426 | 2.023 | 2.006 | 2.113 | Over-range | 59.98 | 19773 | 19026 | 17161 | 55960 | - - - | - - - | - - - | - - - | 19773 | 19026 | 17161 | 55960 | 11354 | 8962 | 10293 | 30610 | - - - | - - - | - - - | - - - | 11354 | 8962 | 10293 | 30610 | 23502 | 21716 | 20725 | 65943 | # # # | # # # | # # # | # # # | 0.841 | 0.876 | 0.828 | 0.849 | # # # | # # # | # # # | - - - | 0.867 | 0.903 | 0.857 | 0.876 | - - - | 0.547 | 1.59 | 1.55 | 1.5 | 1.39 | 1.44 | 1.5 | 23.63 | 24.35 | 25.9 | 0 | - - - | - - - | - - - | - - - | 23502 | 21716 | 20725 | 65943 | Over-range | 12697 | 10454 | 11610 | 34855 | 5607 | 5317 | 5300 | 16470 | 19828 | 19010 | 17212 | 56051 | 19828 | 19010 | 17212 | 56051 | - - - | - - - | - - - | - - -
5/4/2026 | 1:30:00 PM | 278.89 | 275.89 | 274.9 | 481.65 | 475.24 | 480.12 | 83.6269 | 78.2232 | 75.2287 | 0.6268 | 1.428 | 1.428 | 1.426 | 2.078 | 2.044 | 2.148 | Over-range | 59.98 | 19537 | 18754 | 17026 | 55317 | - - - | - - - | - - - | - - - | 19537 | 18754 | 17026 | 55317 | 11023 | 8774 | 10089 | 29886 | - - - | - - - | - - - | - - - | 11023 | 8774 | 10089 | 29886 | 23228 | 21482 | 20587 | 65297 | # # # | # # # | # # # | # # # | 0.841 | 0.873 | 0.827 | 0.847 | # # # | # # # | # # # | - - - | 0.87 | 0.905 | 0.86 | 0.879 | - - - | 0.54 | 1.57 | 1.54 | 1.52 | 1.38 | 1.44 | 1.49 | 25.57 | 26.44 | 27.88 | 0 | - - - | - - - | - - - | - - - | 23228 | 21482 | 20587 | 65297 | Over-range | 12558 | 10468 | 11563 | 34671 | 5965 | 5659 | 5601 | 17430 | 19550 | 18774 | 17093 | 55416 | 19550 | 18774 | 17093 | 55416 | - - - | - - - | - - - | - - -
5/4/2026 | 1:45:00 PM | 278.92 | 275.92 | 274.92 | 481.68 | 475.31 | 480.17 | 86.8566 | 81.0413 | 78.1108 | 0.6381 | 1.429 | 1.429 | 1.427 | 2.051 | 2.017 | 2.112 | Over-range | 59.98 | 20288 | 19407 | 17650 | 57346 | - - - | - - - | - - - | - - - | 20288 | 19407 | 17650 | 57346 | 11483 | 9143 | 10575 | 31201 | - - - | - - - | - - - | - - - | 11483 | 9143 | 10575 | 31201 | 24085 | 22216 | 21345 | 67646 | # # # | # # # | # # # | # # # | 0.842 | 0.874 | 0.827 | 0.848 | # # # | # # # | # # # | - - - | 0.869 | 0.903 | 0.857 | 0.876 | - - - | 0.544 | 1.6 | 1.55 | 1.54 | 1.4 | 1.47 | 1.52 | 24.26 | 25.22 | 26.39 | 0 | - - - | - - - | - - - | - - - | 24085 | 22216 | 21345 | 67646 | Over-range | 12962 | 10785 | 11985 | 35820 | 5932 | 5647 | 5562 | 17373 | 20305 | 19419 | 17718 | 57442 | 20305 | 19419 | 17718 | 57442 | - - - | - - - | - - - | - - -
5/4/2026 | 2:00:00 PM | 278.91 | 275.95 | 274.9 | 481.74 | 475.3 | 480.12 | 85.2262 | 79.2609 | 76.1687 | 0.6396 | 1.429 | 1.43 | 1.427 | 2.035 | 2.006 | 2.106 | Over-range | 59.99 | 19888 | 19026 | 17174 | 56089 | - - - | - - - | - - - | - - - | 19888 | 19026 | 17174 | 56089 | 11439 | 8993 | 10445 | 30876 | - - - | - - - | - - - | - - - | 11439 | 8993 | 10445 | 30876 | 23654 | 21749 | 20826 | 66230 | # # # | # # # | # # # | # # # | 0.841 | 0.875 | 0.825 | 0.847 | # # # | # # # | # # # | - - - | 0.867 | 0.903 | 0.854 | 0.874 | - - - | 0.551 | 1.56 | 1.57 | 1.55 | 1.4 | 1.47 | 1.52 | 23.75 | 24.66 | 26.04 | 0 | - - - | - - - | - - - | - - - | 23654 | 21749 | 20826 | 66230 | Over-range | 12799 | 10526 | 11770 | 35194 | 5683 | 5417 | 5373 | 16728 | 19953 | 19002 | 17227 | 56182 | 19953 | 19002 | 17227 | 56182 | - - - | - - - | - - - | - - -
5/4/2026 | 2:15:00 PM | 278.54 | 275.44 | 274.48 | 480.98 | 474.43 | 479.52 | 85.4239 | 79.6729 | 76.4966 | 0.6443 | 1.429 | 1.43 | 1.428 | 2.049 | 2.015 | 2.119 | Over-range | 59.98 | 19929 | 19094 | 17280 | 56303 | - - - | - - - | - - - | - - - | 19929 | 19094 | 17280 | 56303 | 11304 | 8961 | 10328 | 30593 | - - - | - - - | - - - | - - - | 11304 | 8961 | 10328 | 30593 | 23654 | 21797 | 20871 | 66321 | # # # | # # # | # # # | # # # | 0.843 | 0.876 | 0.828 | 0.849 | # # # | # # # | # # # | - - - | 0.869 | 0.905 | 0.857 | 0.877 | - - - | 0.543 | 1.61 | 1.59 | 1.58 | 1.42 | 1.5 | 1.54 | 24.26 | 24.98 | 26.54 | 0 | - - - | - - - | - - - | - - - | 23654 | 21797 | 20871 | 66321 | Over-range | 12734 | 10499 | 11693 | 35021 | 5800 | 5413 | 5424 | 16869 | 19942 | 19176 | 17286 | 56404 | 19942 | 19176 | 17286 | 56404 | - - - | - - - | - - - | - - -
5/4/2026 | 2:30:00 PM | 278.83 | 275.8 | 274.82 | 481.51 | 475.09 | 480.03 | 85.1227 | 78.8816 | 75.6892 | 0.6404 | 1.43 | 1.43 | 1.428 | 2.018 | 1.993 | 2.099 | Over-range | 59.98 | 19827 | 18940 | 17017 | 55784 | - - - | - - - | - - - | - - - | 19827 | 18940 | 17017 | 55784 | 11486 | 8946 | 10467 | 30899 | - - - | - - - | - - - | - - - | 11486 | 8946 | 10467 | 30899 | 23604 | 21618 | 20679 | 65901 | # # # | # # # | # # # | # # # | 0.84 | 0.876 | 0.823 | 0.847 | # # # | # # # | # # # | - - - | 0.865 | 0.903 | 0.851 | 0.873 | - - - | 0.554 | 1.63 | 1.62 | 1.57 | 1.44 | 1.51 | 1.56 | 23.22 | 24.09 | 25.58 | 0 | - - - | - - - | - - - | - - - | 23604 | 21618 | 20679 | 65901 | Over-range | 12800 | 10407 | 11737 | 35053 | 5566 | 5246 | 5234 | 16332 | 19875 | 18946 | 17056 | 55878 | 19875 | 18946 | 17056 | 55878 | - - - | - - - | - - - | - - -
5/4/2026 | 2:45:00 PM | 279.09 | 276.06 | 275.07 | 481.98 | 475.54 | 480.44 | 82.2719 | 76.5687 | 73.7622 | 0.6431 | 1.43 | 1.431 | 1.428 | 2.01 | 1.987 | 2.092 | Over-range | 59.98 | 19162 | 18326 | 16604 | 54092 | - - - | - - - | - - - | - - - | 19162 | 18326 | 16604 | 54092 | 11143 | 8882 | 10250 | 30274 | - - - | - - - | - - - | - - - | 11143 | 8882 | 10250 | 30274 | 22838 | 21006 | 20173 | 64017 | # # # | # # # | # # # | # # # | 0.839 | 0.872 | 0.823 | 0.845 | # # # | # # # | # # # | - - - | 0.863 | 0.899 | 0.85 | 0.871 | - - - | 0.56 | 1.65 | 1.65 | 1.58 | 1.46 | 1.52 | 1.58 | 22.94 | 23.51 | 24.99 | 0 | - - - | - - - | - - - | - - - | 22838 | 21006 | 20173 | 64017 | Over-range | 12411 | 10244 | 11441 | 34187 | 5392 | 5037 | 5012 | 15679 | 19162 | 18372 | 16660 | 54193 | 19162 | 18372 | 16660 | 54193 | - - - | - - - | - - - | - - -
5/4/2026 | 3:00:00 PM | 279.06 | 276.06 | 275.03 | 481.96 | 475.47 | 480.41 | 83.9266 | 77.6998 | 74.2639 | 0.6451 | 1.43 | 1.431 | 1.428 | 1.945 | 1.931 | 2.049 | Over-range | 59.98 | 19558 | 18748 | 16728 | 55034 | - - - | - - - | - - - | - - - | 19558 | 18748 | 16728 | 55034 | 11634 | 9064 | 10530 | 31227 | - - - | - - - | - - - | - - - | 11634 | 9064 | 10530 | 31227 | 23309 | 21330 | 20317 | 64955 | # # # | # # # | # # # | # # # | 0.839 | 0.879 | 0.823 | 0.847 | # # # | # # # | # # # | - - - | 0.859 | 0.9 | 0.845 | 0.868 | - - - | 0.567 | 1.63 | 1.61 | 1.58 | 1.45 | 1.51 | 1.57 | 20.52 | 20.82 | 22.6 | 0 | - - - | - - - | - - - | - - - | 23309 | 21330 | 20317 | 64955 | Over-range | 12673 | 10162 | 11520 | 34477 | 4956 | 4526 | 4605 | 14415 | 19581 | 18813 | 16721 | 55115 | 19581 | 18813 | 16721 | 55115 | - - - | - - - | - - - | - - -
5/4/2026 | 3:15:00 PM | 278.99 | 276.03 | 274.96 | 481.89 | 475.4 | 480.25 | 79.6478 | 73.7581 | 71.1283 | 0.6361 | 1.43 | 1.43 | 1.427 | 1.939 | 1.929 | 2.057 | Over-range | 59.99 | 18451 | 17615 | 15894 | 51960 | - - - | - - - | - - - | - - - | 18451 | 17615 | 15894 | 51960 | 11079 | 8837 | 10172 | 30089 | - - - | - - - | - - - | - - - | 11079 | 8837 | 10172 | 30089 | 22050 | 20180 | 19399 | 61629 | # # # | # # # | # # # | # # # | 0.837 | 0.873 | 0.819 | 0.843 | # # # | # # # | # # # | - - - | 0.857 | 0.893 | 0.841 | 0.864 | - - - | 0.579 | 1.64 | 1.6 | 1.58 | 1.45 | 1.51 | 1.57 | 20.7 | 20.75 | 22.59 | 0 | - - - | - - - | - - - | - - - | 22050 | 20180 | 19399 | 61629 | Over-range | 12066 | 9833 | 11111 | 33111 | 4689 | 4227 | 4385 | 13572 | 18493 | 17675 | 15873 | 52041 | 18493 | 17675 | 15873 | 52041 | - - - | - - - | - - - | - - -
5/4/2026 | 3:30:00 PM | 278.61 | 275.63 | 274.55 | 481.18 | 474.71 | 479.58 | 82.7575 | 76.3273 | 73.4258 | 0.6435 | 1.429 | 1.43 | 1.428 | 1.869 | 1.871 | 2 | Over-range | 59.97 | 19235 | 18349 | 16447 | 54032 | - - - | - - - | - - - | - - - | 19235 | 18349 | 16447 | 54032 | 11645 | 9164 | 10673 | 31482 | - - - | - - - | - - - | - - - | 11645 | 9164 | 10673 | 31482 | 22925 | 20901 | 20037 | 63863 | # # # | # # # | # # # | # # # | 0.839 | 0.878 | 0.821 | 0.846 | # # # | # # # | # # # | - - - | 0.854 | 0.894 | 0.838 | 0.862 | - - - | 0.583 | 1.63 | 1.6 | 1.57 | 1.43 | 1.5 | 1.56 | 17.97 | 17.92 | 19.81 | 0 | - - - | - - - | - - - | - - - | 22925 | 20901 | 20037 | 63863 | Over-range | 12465 | 9994 | 11434 | 34016 | 4362 | 3904 | 4015 | 12641 | 19224 | 18405 | 16470 | 54099 | 19224 | 18405 | 16470 | 54099 | - - - | - - - | - - - | - - -
5/4/2026 | 3:45:00 PM | 278.77 | 275.76 | 274.67 | 481.49 | 474.87 | 479.83 | 81.7556 | 75.4633 | 72.8225 | 0.6425 | 1.429 | 1.43 | 1.428 | 1.895 | 1.889 | 2.019 | Over-range | 59.99 | 18938 | 18039 | 16238 | 53215 | - - - | - - - | - - - | - - - | 18938 | 18039 | 16238 | 53215 | 11527 | 9167 | 10591 | 31285 | - - - | - - - | - - - | - - - | 11527 | 9167 | 10591 | 31285 | 22660 | 20667 | 19876 | 63203 | # # # | # # # | # # # | # # # | 0.836 | 0.873 | 0.817 | 0.842 | # # # | # # # | # # # | - - - | 0.853 | 0.89 | 0.835 | 0.859 | - - - | 0.588 | 1.63 | 1.57 | 1.56 | 1.43 | 1.49 | 1.54 | 19.04 | 19.01 | 20.88 | 0 | - - - | - - - | - - - | - - - | 22660 | 20667 | 19876 | 63203 | Over-range | 12428 | 10064 | 11447 | 34051 | 4534 | 4037 | 4232 | 13119 | 18976 | 18104 | 16206 | 53286 | 18976 | 18104 | 16206 | 53286 | - - - | - - - | - - - | - - -
5/4/2026 | 4:00:00 PM | 278.73 | 275.62 | 274.59 | 481.35 | 474.64 | 479.77 | 84.9971 | 78.8646 | 75.3709 | 0.6484 | 1.43 | 1.431 | 1.428 | 1.945 | 1.924 | 2.041 | Over-range | 59.98 | 19808 | 19002 | 17000 | 55810 | - - - | - - - | - - - | - - - | 19808 | 19002 | 17000 | 55810 | 11714 | 9151 | 10565 | 31430 | - - - | - - - | - - - | - - - | 11714 | 9151 | 10565 | 31430 | 23565 | 21606 | 20581 | 65752 | # # # | # # # | # # # | # # # | 0.841 | 0.879 | 0.826 | 0.849 | # # # | # # # | # # # | - - - | 0.861 | 0.9 | 0.848 | 0.87 | - - - | 0.563 | 1.65 | 1.59 | 1.61 | 1.45 | 1.52 | 1.58 | 20.6 | 20.92 | 22.61 | 0 | - - - | - - - | - - - | - - - | 23565 | 21606 | 20581 | 65752 | Over-range | 12759 | 10273 | 11590 | 34739 | 4979 | 4598 | 4693 | 14585 | 19886 | 19017 | 16996 | 55898 | 19886 | 19017 | 16996 | 55898 | - - - | - - - | - - - | - - -
5/4/2026 | 4:15:00 PM | 278.43 | 275.39 | 274.37 | 480.83 | 474.31 | 479.32 | 81.7583 | 75.7201 | 72.8352 | 0.6453 | 1.43 | 1.431 | 1.428 | 1.95 | 1.93 | 2.047 | Over-range | 59.97 | 18965 | 18118 | 16305 | 53388 | - - - | - - - | - - - | - - - | 18965 | 18118 | 16305 | 53388 | 11314 | 8915 | 10306 | 30535 | - - - | - - - | - - - | - - - | 11314 | 8915 | 10306 | 30535 | 22623 | 20703 | 19851 | 63178 | # # # | # # # | # # # | # # # | 0.838 | 0.875 | 0.821 | 0.845 | # # # | # # # | # # # | - - - | 0.859 | 0.896 | 0.844 | 0.866 | - - - | 0.572 | 1.65 | 1.6 | 1.59 | 1.44 | 1.51 | 1.57 | 20.86 | 21.24 | 22.97 | 0 | - - - | - - - | - - - | - - - | 22623 | 20703 | 19851 | 63178 | Over-range | 12327 | 10006 | 11313 | 33752 | 4815 | 4472 | 4594 | 14169 | 19058 | 18101 | 16315 | 53474 | 19058 | 18101 | 16315 | 53474 | - - - | - - - | - - - | - - -
5/4/2026 | 4:30:00 PM | 278.37 | 275.39 | 274.32 | 480.76 | 474.28 | 479.21 | 82.8721 | 76.7709 | 73.7914 | 0.6468 | 1.43 | 1.431 | 1.428 | 1.919 | 1.901 | 2.019 | Over-range | 59.98 | 19280 | 18448 | 16586 | 54314 | - - - | - - - | - - - | - - - | 19280 | 18448 | 16586 | 54314 | 11535 | 9087 | 10511 | 31133 | - - - | - - - | - - - | - - - | 11535 | 9087 | 10511 | 31133 | 22963 | 21034 | 20140 | 64137 | # # # | # # # | # # # | # # # | 0.84 | 0.877 | 0.824 | 0.847 | # # # | # # # | # # # | - - - | 0.858 | 0.896 | 0.844 | 0.866 | - - - | 0.573 | 1.67 | 1.61 | 1.59 | 1.45 | 1.52 | 1.57 | 19.64 | 19.89 | 21.52 | 0 | - - - | - - - | - - - | - - - | 22963 | 21034 | 20140 | 64137 | Over-range | 12467 | 10094 | 11417 | 34087 | 4653 | 4327 | 4380 | 13671 | 19337 | 18422 | 16638 | 54398 | 19337 | 18422 | 16638 | 54398 | - - - | - - - | - - - | - - -
5/4/2026 | 4:45:00 PM | 280.47 | 277.39 | 276.37 | 484.35 | 477.71 | 482.84 | 82.8241 | 76.4605 | 73.4099 | 0.6447 | 1.43 | 1.431 | 1.428 | 1.915 | 1.906 | 2.031 | Over-range | 59.98 | 19252 | 18389 | 16452 | 54094 | - - - | - - - | - - - | - - - | 19252 | 18389 | 16452 | 54094 | 11753 | 9192 | 10669 | 31614 | - - - | - - - | - - - | - - - | 11753 | 9192 | 10669 | 31614 | 23081 | 21051 | 20146 | 64278 | # # # | # # # | # # # | # # # | 0.834 | 0.874 | 0.817 | 0.842 | # # # | # # # | # # # | - - - | 0.853 | 0.892 | 0.838 | 0.861 | - - - | 0.584 | 1.67 | 1.61 | 1.6 | 1.45 | 1.52 | 1.58 | 19.94 | 20.13 | 21.85 | 0 | - - - | - - - | - - - | - - - | 23081 | 21051 | 20146 | 64278 | Over-range | 12715 | 10221 | 11609 | 34665 | 4750 | 4379 | 4483 | 13948 | 19336 | 18364 | 16475 | 54176 | 19336 | 18364 | 16475 | 54176 | - - - | - - - | - - - | - - -
5/4/2026 | 5:00:00 PM | 281.43 | 278.62 | 277.49 | 486.23 | 479.87 | 484.52 | 81.5368 | 75.8938 | 73.0866 | 0.6429 | 1.43 | 1.432 | 1.428 | 1.917 | 1.911 | 2.031 | Over-range | 59.98 | 19058 | 18308 | 16530 | 53896 | - - - | - - - | - - - | - - - | 19058 | 18308 | 16530 | 53896 | 11641 | 9341 | 10643 | 31625 | - - - | - - - | - - - | - - - | 11641 | 9341 | 10643 | 31625 | 22835 | 21031 | 20172 | 64037 | # # # | # # # | # # # | # # # | 0.835 | 0.871 | 0.819 | 0.842 | # # # | # # # | # # # | - - - | 0.853 | 0.889 | 0.84 | 0.861 | - - - | 0.587 | 1.71 | 1.64 | 1.59 | 1.48 | 1.54 | 1.6 | 19.9 | 20.11 | 21.8 | 0 | - - - | - - - | - - - | - - - | 22835 | 21031 | 20172 | 64037 | Over-range | 12573 | 10340 | 11554 | 34563 | 4684 | 4369 | 4429 | 13752 | 19113 | 18290 | 16582 | 53985 | 19113 | 18290 | 16582 | 53985 | - - - | - - - | - - - | - - -
5/4/2026 | 5:15:00 PM | 282.05 | 279.31 | 278.17 | 487.34 | 481.21 | 485.54 | 82.4603 | 76.7223 | 73.818 | 0.6399 | 1.43 | 1.431 | 1.43 | 1.898 | 1.909 | 2.028 | Over-range | 60 | 19264 | 18512 | 16669 | 54445 | - - - | - - - | - - - | - - - | 19264 | 18512 | 16669 | 54445 | 11899 | 9538 | 10871 | 32308 | - - - | - - - | - - - | - - - | 11899 | 9538 | 10871 | 32308 | 23129 | 21295 | 20412 | 64837 | # # # | # # # | # # # | # # # | 0.833 | 0.869 | 0.817 | 0.84 | # # # | # # # | # # # | - - - | 0.851 | 0.887 | 0.837 | 0.858 | - - - | 0.593 | 1.64 | 1.59 | 1.57 | 1.45 | 1.49 | 1.54 | 19.34 | 19.76 | 21.3 | 0 | - - - | - - - | - - - | - - - | 23129 | 21295 | 20412 | 64837 | Over-range | 12793 | 10514 | 11773 | 35180 | 4609 | 4346 | 4438 | 13685 | 19342 | 18492 | 16692 | 54526 | 19342 | 18492 | 16692 | 54526 | - - - | - - - | - - - | - - -
5/4/2026 | 5:30:00 PM | 281.75 | 278.8 | 277.75 | 486.71 | 480.28 | 484.97 | 80.5629 | 74.7335 | 72.4053 | 0.6351 | 1.43 | 1.431 | 1.43 | 1.89 | 1.909 | 2.032 | Over-range | 59.98 | 18838 | 17984 | 16309 | 53131 | - - - | - - - | - - - | - - - | 18838 | 17984 | 16309 | 53131 | 11605 | 9368 | 10712 | 31684 | - - - | - - - | - - - | - - - | 11605 | 9368 | 10712 | 31684 | 22598 | 20728 | 20012 | 63339 | # # # | # # # | # # # | # # # | 0.834 | 0.868 | 0.815 | 0.839 | # # # | # # # | # # # | - - - | 0.851 | 0.885 | 0.835 | 0.857 | - - - | 0.596 | 1.62 | 1.55 | 1.51 | 1.41 | 1.46 | 1.51 | 19.34 | 19.63 | 21.33 | 0 | - - - | - - - | - - - | - - - | 22598 | 20728 | 20012 | 63339 | Over-range | 12476 | 10299 | 11589 | 34458 | 4509 | 4212 | 4354 | 13345 | 18910 | 17958 | 16346 | 53214 | 18910 | 17958 | 16346 | 53214 | - - - | - - - | - - - | - - -
5/4/2026 | 5:45:00 PM | 281.79 | 278.91 | 277.76 | 486.82 | 480.41 | 485 | 84.1274 | 78.0897 | 74.6487 | 0.6372 | 1.43 | 1.432 | 1.43 | 1.865 | 1.876 | 2 | Over-range | 59.97 | 19641 | 18905 | 16848 | 55394 | - - - | - - - | - - - | - - - | 19641 | 18905 | 16848 | 55394 | 12224 | 9636 | 11038 | 32898 | - - - | - - - | - - - | - - - | 12224 | 9636 | 11038 | 32898 | 23590 | 21654 | 20620 | 65865 | # # # | # # # | # # # | # # # | 0.833 | 0.873 | 0.817 | 0.841 | # # # | # # # | # # # | - - - | 0.849 | 0.889 | 0.835 | 0.858 | - - - | 0.594 | 1.6 | 1.57 | 1.52 | 1.42 | 1.47 | 1.51 | 18.26 | 18.51 | 20.17 | 0 | - - - | - - - | - - - | - - - | 23590 | 21654 | 20620 | 65865 | Over-range | 13053 | 10540 | 11874 | 35587 | 4487 | 4185 | 4291 | 13323 | 19717 | 18891 | 16867 | 55476 | 19717 | 18891 | 16867 | 55476 | - - - | - - - | - - - | - - -
5/4/2026 | 6:00:00 PM | 282.1 | 279.24 | 278.12 | 487.35 | 481.02 | 485.59 | 79.0396 | 73.0726 | 70.6178 | 0.6345 | 1.43 | 1.431 | 1.429 | 1.837 | 1.876 | 2.014 | Over-range | 59.99 | 18346 | 17520 | 15769 | 51635 | - - - | - - - | - - - | - - - | 18346 | 17520 | 15769 | 51635 | 11606 | 9313 | 10659 | 31578 | - - - | - - - | - - - | - - - | 11606 | 9313 | 10659 | 31578 | 22133 | 20231 | 19487 | 61851 | # # # | # # # | # # # | # # # | 0.829 | 0.866 | 0.809 | 0.835 | # # # | # # # | # # # | - - - | 0.845 | 0.882 | 0.827 | 0.851 | - - - | 0.612 | 1.57 | 1.5 | 1.48 | 1.38 | 1.42 | 1.46 | 18.26 | 18.31 | 20.16 | 0 | - - - | - - - | - - - | - - - | 22133 | 20231 | 19487 | 61851 | Over-range | 12372 | 10102 | 11437 | 34016 | 4170 | 3807 | 4040 | 12332 | 18426 | 17522 | 15758 | 51706 | 18426 | 17522 | 15758 | 51706 | - - - | - - - | - - - | - - -
5/4/2026 | 6:15:00 PM | 283.01 | 280.2 | 278.95 | 489.02 | 482.57 | 487.06 | 81.8946 | 75.6839 | 72.7323 | 0.6363 | 1.43 | 1.43 | 1.429 | 1.812 | 1.864 | 2.016 | Over-range | 60 | 19072 | 18276 | 16310 | 53658 | - - - | - - - | - - - | - - - | 19072 | 18276 | 16310 | 53658 | 12158 | 9667 | 11066 | 32892 | - - - | - - - | - - - | - - - | 12158 | 9667 | 11066 | 32892 | 23022 | 21043 | 20146 | 64212 | # # # | # # # | # # # | # # # | 0.828 | 0.869 | 0.81 | 0.836 | # # # | # # # | # # # | - - - | 0.843 | 0.883 | 0.826 | 0.851 | - - - | 0.613 | 1.47 | 1.41 | 1.34 | 1.29 | 1.29 | 1.34 | 17.57 | 17.58 | 19.5 | 0 | - - - | - - - | - - - | - - - | 23022 | 21043 | 20146 | 64212 | Over-range | 12889 | 10418 | 11815 | 35242 | 4177 | 3792 | 4044 | 12382 | 19152 | 18295 | 16281 | 53728 | 19152 | 18295 | 16281 | 53728 | - - - | - - - | - - - | - - -
5/4/2026 | 6:30:00 PM | 283.21 | 280.5 | 279.22 | 489.47 | 483.07 | 487.44 | 80.0824 | 74.1083 | 71.4277 | 0.6312 | 1.43 | 1.428 | 1.429 | 1.836 | 1.883 | 2.037 | Over-range | 59.97 | 18617 | 17839 | 15988 | 52444 | - - - | - - - | - - - | - - - | 18617 | 17839 | 15988 | 52444 | 11930 | 9560 | 10902 | 32392 | - - - | - - - | - - - | - - - | 11930 | 9560 | 10902 | 32392 | 22531 | 20631 | 19807 | 62969 | # # # | # # # | # # # | # # # | 0.826 | 0.865 | 0.807 | 0.833 | # # # | # # # | # # # | - - - | 0.842 | 0.88 | 0.825 | 0.849 | - - - | 0.618 | 1.46 | 1.37 | 1.3 | 1.27 | 1.26 | 1.31 | 18.31 | 18.35 | 20.27 | 0 | - - - | - - - | - - - | - - - | 22531 | 20631 | 19807 | 62969 | Over-range | 12685 | 10352 | 11682 | 34827 | 4215 | 3886 | 4111 | 12539 | 18703 | 17818 | 15989 | 52510 | 18703 | 17818 | 15989 | 52510 | - - - | - - - | - - - | - - -
5/4/2026 | 6:45:00 PM | 282.96 | 280.14 | 278.93 | 488.94 | 482.53 | 486.95 | 80.8984 | 75.0117 | 72.1136 | 0.6337 | 1.43 | 1.429 | 1.429 | 1.829 | 1.881 | 2.029 | Over-range | 59.97 | 18806 | 18057 | 16161 | 53024 | - - - | - - - | - - - | - - - | 18806 | 18057 | 16161 | 53024 | 11989 | 9588 | 10920 | 32497 | - - - | - - - | - - - | - - - | 11989 | 9588 | 10920 | 32497 | 22733 | 20845 | 19968 | 63546 | # # # | # # # | # # # | # # # | 0.827 | 0.866 | 0.809 | 0.834 | # # # | # # # | # # # | - - - | 0.843 | 0.881 | 0.827 | 0.85 | - - - | 0.613 | 1.46 | 1.38 | 1.31 | 1.28 | 1.27 | 1.32 | 18.03 | 18.05 | 20.06 | 0 | - - - | - - - | - - - | - - - | 22733 | 20845 | 19968 | 63546 | Over-range | 12757 | 10394 | 11712 | 34974 | 4245 | 3908 | 4130 | 12621 | 18884 | 18046 | 16165 | 53095 | 18884 | 18046 | 16165 | 53095 | - - - | - - - | - - - | - - -
5/4/2026 | 7:00:00 PM | 283.14 | 280.44 | 279.08 | 489.38 | 482.98 | 487.16 | 81.1009 | 75.1711 | 72.1795 | 0.6282 | 1.43 | 1.428 | 1.429 | 1.823 | 1.869 | 2.019 | Over-range | 59.98 | 18839 | 18122 | 16160 | 53121 | - - - | - - - | - - - | - - - | 18839 | 18122 | 16160 | 53121 | 12197 | 9742 | 11101 | 33040 | - - - | - - - | - - - | - - - | 12197 | 9742 | 11101 | 33040 | 22842 | 20955 | 20028 | 63825 | # # # | # # # | # # # | # # # | 0.825 | 0.865 | 0.807 | 0.832 | # # # | # # # | # # # | - - - | 0.839 | 0.879 | 0.823 | 0.847 | - - - | 0.622 | 1.4 | 1.3 | 1.2 | 1.22 | 1.18 | 1.23 | 17.45 | 17.54 | 19.33 | 0 | - - - | - - - | - - - | - - - | 22842 | 20955 | 20028 | 63825 | Over-range | 12910 | 10507 | 11821 | 35352 | 4124 | 3841 | 3960 | 12283 | 18885 | 18092 | 16204 | 53181 | 18885 | 18092 | 16204 | 53181 | - - - | - - - | - - - | - - -
5/4/2026 | 7:15:00 PM | 283.63 | 281.06 | 279.72 | 490.35 | 484.06 | 488.15 | 81.1229 | 75.4317 | 72.8098 | 0.6271 | 1.43 | 1.428 | 1.429 | 1.824 | 1.874 | 2.027 | Over-range | 59.99 | 18947 | 18206 | 16409 | 53561 | - - - | - - - | - - - | - - - | 18947 | 18206 | 16409 | 53561 | 12104 | 9840 | 11160 | 33104 | - - - | - - - | - - - | - - - | 12104 | 9840 | 11160 | 33104 | 22896 | 21079 | 20262 | 64238 | # # # | # # # | # # # | # # # | 0.828 | 0.864 | 0.81 | 0.834 | # # # | # # # | # # # | - - - | 0.842 | 0.879 | 0.827 | 0.849 | - - - | 0.618 | 1.42 | 1.32 | 1.2 | 1.24 | 1.18 | 1.24 | 17.81 | 17.78 | 19.61 | 0 | - - - | - - - | - - - | - - - | 22896 | 21079 | 20262 | 64238 | Over-range | 12850 | 10613 | 11878 | 35440 | 4236 | 3904 | 3991 | 12436 | 18941 | 18210 | 16478 | 53629 | 18941 | 18210 | 16478 | 53629 | - - - | - - - | - - - | - - -
5/4/2026 | 7:30:00 PM | 283.83 | 281.35 | 279.94 | 490.79 | 484.51 | 488.47 | 80.8661 | 75.0642 | 71.9054 | 0.6244 | 1.431 | 1.428 | 1.429 | 1.807 | 1.86 | 2.024 | Over-range | 59.97 | 18794 | 18135 | 16134 | 53063 | - - - | - - - | - - - | - - - | 18794 | 18135 | 16134 | 53063 | 12205 | 9797 | 11124 | 33125 | - - - | - - - | - - - | - - - | 12205 | 9797 | 11124 | 33125 | 22827 | 20983 | 20008 | 63818 | # # # | # # # | # # # | # # # | 0.823 | 0.864 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.837 | 0.879 | 0.822 | 0.846 | - - - | 0.624 | 1.42 | 1.32 | 1.21 | 1.25 | 1.18 | 1.25 | 17.46 | 17.39 | 19.24 | 0 | - - - | - - - | - - - | - - - | 22827 | 20983 | 20008 | 63818 | Over-range | 12948 | 10542 | 11822 | 35426 | 4216 | 3790 | 3898 | 12255 | 18770 | 18194 | 16156 | 53120 | 18770 | 18194 | 16156 | 53120 | - - - | - - - | - - - | - - -
5/4/2026 | 7:45:00 PM | 284.1 | 281.67 | 280.14 | 491.29 | 485.02 | 488.83 | 80.7531 | 75.5796 | 72.5124 | 0.6206 | 1.43 | 1.427 | 1.428 | 1.839 | 1.89 | 2.045 | Over-range | 59.98 | 18720 | 18137 | 16277 | 53134 | - - - | - - - | - - - | - - - | 18720 | 18137 | 16277 | 53134 | 12130 | 9941 | 11058 | 33129 | - - - | - - - | - - - | - - - | 12130 | 9941 | 11058 | 33129 | 22778 | 21108 | 20163 | 64049 | # # # | # # # | # # # | # # # | 0.822 | 0.859 | 0.807 | 0.83 | # # # | # # # | # # # | - - - | 0.838 | 0.876 | 0.825 | 0.847 | - - - | 0.624 | 1.42 | 1.32 | 1.19 | 1.25 | 1.18 | 1.24 | 18.74 | 18.71 | 20.52 | 0 | - - - | - - - | - - - | - - - | 22778 | 21108 | 20163 | 64049 | Over-range | 12960 | 10773 | 11879 | 35705 | 4443 | 4036 | 4228 | 12984 | 18765 | 18190 | 16245 | 53199 | 18765 | 18190 | 16245 | 53199 | - - - | - - - | - - - | - - -
5/4/2026 | 8:00:00 PM | 284.58 | 282.21 | 280.71 | 492.18 | 486.01 | 489.72 | 81.887 | 76.5929 | 73.1318 | 0.6177 | 1.431 | 1.428 | 1.428 | 1.852 | 1.897 | 2.055 | Over-range | 59.98 | 19110 | 18568 | 16552 | 54230 | - - - | - - - | - - - | - - - | 19110 | 18568 | 16552 | 54230 | 12291 | 9914 | 11090 | 33296 | - - - | - - - | - - - | - - - | 12291 | 9914 | 11090 | 33296 | 23174 | 21477 | 20407 | 65058 | # # # | # # # | # # # | # # # | 0.825 | 0.865 | 0.811 | 0.834 | # # # | # # # | # # # | - - - | 0.841 | 0.881 | 0.83 | 0.851 | - - - | 0.614 | 1.45 | 1.32 | 1.21 | 1.26 | 1.19 | 1.26 | 18.92 | 19.07 | 20.87 | 0 | - - - | - - - | - - - | - - - | 23174 | 21477 | 20407 | 65058 | Over-range | 13104 | 10782 | 11926 | 35916 | 4468 | 4170 | 4316 | 13260 | 19186 | 18566 | 16553 | 54305 | 19186 | 18566 | 16553 | 54305 | - - - | - - - | - - - | - - -
5/4/2026 | 8:15:00 PM | 284.92 | 282.57 | 281.04 | 492.81 | 486.6 | 490.28 | 79.6667 | 74.5593 | 71.77 | 0.6165 | 1.43 | 1.427 | 1.428 | 1.848 | 1.898 | 2.057 | Over-range | 59.97 | 18508 | 17916 | 16135 | 52559 | - - - | - - - | - - - | - - - | 18508 | 17916 | 16135 | 52559 | 12038 | 9946 | 11063 | 33047 | - - - | - - - | - - - | - - - | 12038 | 9946 | 11063 | 33047 | 22556 | 20918 | 20037 | 63511 | # # # | # # # | # # # | # # # | 0.821 | 0.857 | 0.805 | 0.828 | # # # | # # # | # # # | - - - | 0.837 | 0.874 | 0.823 | 0.845 | - - - | 0.629 | 1.43 | 1.3 | 1.19 | 1.24 | 1.16 | 1.23 | 19.09 | 19.08 | 20.83 | 0 | - - - | - - - | - - - | - - - | 22556 | 20918 | 20037 | 63511 | Over-range | 12884 | 10782 | 11868 | 35621 | 4485 | 4060 | 4196 | 12992 | 18500 | 17992 | 16128 | 52620 | 18500 | 17992 | 16128 | 52620 | - - - | - - - | - - - | - - -
5/4/2026 | 8:30:00 PM | 284.77 | 282.35 | 280.73 | 492.5 | 486.11 | 489.89 | 81.8242 | 76.5957 | 73.2048 | 0.6134 | 1.43 | 1.427 | 1.428 | 1.846 | 1.89 | 2.046 | Over-range | 59.98 | 19115 | 18579 | 16587 | 54281 | - - - | - - - | - - - | - - - | 19115 | 18579 | 16587 | 54281 | 12333 | 10031 | 11163 | 33526 | - - - | - - - | - - - | - - - | 12333 | 10031 | 11163 | 33526 | 23206 | 21527 | 20461 | 65194 | # # # | # # # | # # # | # # # | 0.824 | 0.863 | 0.811 | 0.833 | # # # | # # # | # # # | - - - | 0.84 | 0.879 | 0.828 | 0.849 | - - - | 0.618 | 1.43 | 1.29 | 1.19 | 1.23 | 1.16 | 1.22 | 18.62 | 18.64 | 20.38 | 0 | - - - | - - - | - - - | - - - | 23206 | 21527 | 20461 | 65194 | Over-range | 13153 | 10863 | 11971 | 36086 | 4493 | 4095 | 4248 | 13128 | 19148 | 18632 | 16564 | 54344 | 19148 | 18632 | 16564 | 54344 | - - - | - - - | - - - | - - -
5/4/2026 | 8:45:00 PM | 284.8 | 282.35 | 280.68 | 492.53 | 486.06 | 489.88 | 82.9593 | 77.2185 | 74.1934 | 0.6137 | 1.431 | 1.427 | 1.428 | 1.875 | 1.921 | 2.063 | Over-range | 59.98 | 19356 | 18660 | 16697 | 54713 | - - - | - - - | - - - | - - - | 19356 | 18660 | 16697 | 54713 | 12396 | 10033 | 11312 | 33741 | - - - | - - - | - - - | - - - | 12396 | 10033 | 11312 | 33741 | 23490 | 21654 | 20693 | 65837 | # # # | # # # | # # # | # # # | 0.824 | 0.862 | 0.807 | 0.831 | # # # | # # # | # # # | - - - | 0.842 | 0.88 | 0.826 | 0.849 | - - - | 0.617 | 1.42 | 1.3 | 1.18 | 1.24 | 1.17 | 1.22 | 19.46 | 19.72 | 21.38 | 0 | - - - | - - - | - - - | - - - | 23490 | 21654 | 20693 | 65837 | Over-range | 13293 | 10966 | 12207 | 36570 | 4717 | 4347 | 4510 | 13873 | 19421 | 18696 | 16661 | 54778 | 19421 | 18696 | 16661 | 54778 | - - - | - - - | - - - | - - -
5/4/2026 | 9:00:00 PM | 284.9 | 282.47 | 280.75 | 492.8 | 486.19 | 489.99 | 82.8217 | 77.2967 | 74.3071 | 0.6111 | 1.431 | 1.427 | 1.428 | 1.898 | 1.937 | 2.077 | Over-range | 59.98 | 19410 | 18723 | 16821 | 54954 | - - - | - - - | - - - | - - - | 19410 | 18723 | 16821 | 54954 | 12194 | 9920 | 11190 | 33304 | - - - | - - - | - - - | - - - | 12194 | 9920 | 11190 | 33304 | 23460 | 21688 | 20735 | 65882 | # # # | # # # | # # # | # # # | 0.827 | 0.863 | 0.811 | 0.834 | # # # | # # # | # # # | - - - | 0.846 | 0.883 | 0.832 | 0.854 | - - - | 0.606 | 1.42 | 1.3 | 1.18 | 1.24 | 1.17 | 1.23 | 20.22 | 20.47 | 21.97 | 0 | - - - | - - - | - - - | - - - | 23460 | 21688 | 20735 | 65882 | Over-range | 13169 | 10934 | 12112 | 36311 | 4883 | 4511 | 4548 | 14212 | 19397 | 18769 | 16849 | 55016 | 19397 | 18769 | 16849 | 55016 | - - - | - - - | - - - | - - -
5/4/2026 | 9:15:00 PM | 285.41 | 282.87 | 281.3 | 493.55 | 486.98 | 490.95 | 84.5945 | 78.6214 | 75.4778 | 0.6135 | 1.431 | 1.427 | 1.427 | 1.892 | 1.942 | 2.083 | Over-range | 59.99 | 19877 | 19135 | 17102 | 56114 | - - - | - - - | - - - | - - - | 19877 | 19135 | 17102 | 56114 | 12524 | 10072 | 11436 | 34032 | - - - | - - - | - - - | - - - | 12524 | 10072 | 11436 | 34032 | 24046 | 22132 | 21136 | 67314 | # # # | # # # | # # # | # # # | 0.827 | 0.865 | 0.809 | 0.834 | # # # | # # # | # # # | - - - | 0.846 | 0.884 | 0.83 | 0.853 | - - - | 0.607 | 1.44 | 1.31 | 1.21 | 1.26 | 1.2 | 1.25 | 20.33 | 20.72 | 22.34 | 0 | - - - | - - - | - - - | - - - | 24046 | 22132 | 21136 | 67314 | Over-range | 13525 | 11111 | 12410 | 37155 | 5035 | 4624 | 4755 | 14716 | 19906 | 19205 | 17069 | 56181 | 19906 | 19205 | 17069 | 56181 | - - - | - - - | - - - | - - -
5/4/2026 | 9:30:00 PM | 285.84 | 283.35 | 281.72 | 494.32 | 487.8 | 491.7 | 81.2594 | 75.8408 | 72.9738 | 0.6101 | 1.431 | 1.428 | 1.428 | 1.923 | 1.972 | 2.105 | Over-range | 59.99 | 19019 | 18333 | 16486 | 53838 | - - - | - - - | - - - | - - - | 19019 | 18333 | 16486 | 53838 | 12001 | 9774 | 11030 | 32805 | - - - | - - - | - - - | - - - | 12001 | 9774 | 11030 | 32805 | 23071 | 21323 | 20414 | 64807 | # # # | # # # | # # # | # # # | 0.824 | 0.86 | 0.808 | 0.831 | # # # | # # # | # # # | - - - | 0.845 | 0.882 | 0.83 | 0.852 | - - - | 0.609 | 1.46 | 1.32 | 1.24 | 1.27 | 1.2 | 1.27 | 21.49 | 21.94 | 23.46 | 0 | - - - | - - - | - - - | - - - | 23071 | 21323 | 20414 | 64807 | Over-range | 13053 | 10877 | 12027 | 36048 | 5051 | 4696 | 4721 | 14718 | 19006 | 18392 | 16515 | 53912 | 19006 | 18392 | 16515 | 53912 | - - - | - - - | - - - | - - -
5/4/2026 | 9:45:00 PM | 285.06 | 282.58 | 281.02 | 492.97 | 486.52 | 490.43 | 82.9463 | 77.0366 | 73.9443 | 0.6114 | 1.431 | 1.426 | 1.427 | 1.892 | 1.924 | 2.075 | Over-range | 59.99 | 19420 | 18698 | 16693 | 54811 | - - - | - - - | - - - | - - - | 19420 | 18698 | 16693 | 54811 | 12329 | 9852 | 11253 | 33434 | - - - | - - - | - - - | - - - | 12329 | 9852 | 11253 | 33434 | 23532 | 21643 | 20670 | 65845 | # # # | # # # | # # # | # # # | 0.825 | 0.864 | 0.808 | 0.832 | # # # | # # # | # # # | - - - | 0.843 | 0.882 | 0.828 | 0.851 | - - - | 0.61 | 1.44 | 1.3 | 1.23 | 1.25 | 1.19 | 1.25 | 19.82 | 20.1 | 21.73 | 0 | - - - | - - - | - - - | - - - | 23532 | 21643 | 20670 | 65845 | Over-range | 13273 | 10876 | 12173 | 36433 | 4809 | 4511 | 4542 | 14188 | 19437 | 18677 | 16757 | 54871 | 19437 | 18677 | 16757 | 54871 | - - - | - - - | - - - | - - -
5/4/2026 | 10:00:00 PM | 284.16 | 281.76 | 280.15 | 491.5 | 485.08 | 488.85 | 81.3786 | 75.5934 | 72.7451 | 0.6097 | 1.43 | 1.426 | 1.426 | 1.88 | 1.916 | 2.075 | Over-range | 59.99 | 19010 | 18287 | 16383 | 53679 | - - - | - - - | - - - | - - - | 19010 | 18287 | 16383 | 53679 | 12064 | 9748 | 11094 | 32905 | - - - | - - - | - - - | - - - | 12064 | 9748 | 11094 | 32905 | 23007 | 21170 | 20266 | 64443 | # # # | # # # | # # # | # # # | 0.826 | 0.864 | 0.808 | 0.833 | # # # | # # # | # # # | - - - | 0.843 | 0.882 | 0.828 | 0.851 | - - - | 0.613 | 1.43 | 1.29 | 1.19 | 1.24 | 1.17 | 1.23 | 19.6 | 19.66 | 21.32 | 0 | - - - | - - - | - - - | - - - | 23007 | 21170 | 20266 | 64443 | Over-range | 12952 | 10655 | 11919 | 35630 | 4636 | 4230 | 4285 | 13450 | 18984 | 18328 | 16423 | 53736 | 18984 | 18328 | 16423 | 53736 | - - - | - - - | - - - | - - -
5/4/2026 | 10:15:00 PM | 283.66 | 281.24 | 279.68 | 490.61 | 484.24 | 487.99 | 82.2225 | 76.354 | 74.1054 | 0.3425 | 1.429 | 1.427 | 1.425 | 1.845 | 1.855 | 1.967 | Over-range | 59.99 | 19270 | 18467 | 16703 | 54440 | - - - | - - - | - - - | - - - | 19270 | 18467 | 16703 | 54440 | 12128 | 9870 | 11336 | 33335 | - - - | - - - | - - - | - - - | 12128 | 9870 | 11336 | 33335 | 23210 | 21355 | 20626 | 65190 | # # # | # # # | # # # | # # # | 0.83 | 0.865 | 0.81 | 0.835 | # # # | # # # | # # # | - - - | 0.845 | 0.881 | 0.827 | 0.851 | - - - | 0.612 | 1.6 | 1.46 | 1.4 | 1.43 | 1.4 | 1.44 | 18.29 | 18.6 | 19.9 | 0 | - - - | - - - | - - - | - - - | 23210 | 21355 | 20626 | 65190 | Over-range | 12932 | 10711 | 12092 | 35838 | 4410 | 4084 | 4128 | 12935 | 19242 | 18495 | 16761 | 54499 | 19242 | 18495 | 16761 | 54499 | - - - | - - - | - - - | - - -
5/4/2026 | 10:30:00 PM | 283.14 | 280.54 | 278.98 | 489.64 | 482.86 | 487.01 | 82.262 | 75.9478 | 73.4356 | 0.2594 | 1.429 | 1.428 | 1.425 | 1.849 | 1.858 | 1.975 | Over-range | 59.98 | 19219 | 18381 | 16455 | 54055 | - - - | - - - | - - - | - - - | 19219 | 18381 | 16455 | 54055 | 12088 | 9593 | 11187 | 32868 | - - - | - - - | - - - | - - - | 12088 | 9593 | 11187 | 32868 | 23166 | 21173 | 20368 | 64707 | # # # | # # # | # # # | # # # | 0.83 | 0.868 | 0.808 | 0.835 | # # # | # # # | # # # | - - - | 0.845 | 0.885 | 0.826 | 0.852 | - - - | 0.608 | 1.64 | 1.52 | 1.44 | 1.47 | 1.44 | 1.48 | 18.79 | 19.11 | 20.64 | 0 | - - - | - - - | - - - | - - - | 23166 | 21173 | 20368 | 64707 | Over-range | 12927 | 10497 | 11994 | 35541 | 4481 | 4168 | 4225 | 13242 | 19216 | 18373 | 16523 | 54112 | 19216 | 18373 | 16523 | 54112 | - - - | - - - | - - - | - - -
5/4/2026 | 10:45:00 PM | 283.69 | 281.12 | 279.5 | 490.63 | 483.83 | 487.91 | 81.4931 | 75.4747 | 73.3625 | 0.2606 | 1.429 | 1.428 | 1.425 | 1.841 | 1.849 | 1.969 | Over-range | 59.98 | 18968 | 18120 | 16372 | 53459 | - - - | - - - | - - - | - - - | 18968 | 18120 | 16372 | 53459 | 12034 | 9780 | 11254 | 33068 | - - - | - - - | - - - | - - - | 12034 | 9780 | 11254 | 33068 | 22923 | 21007 | 20328 | 64258 | # # # | # # # | # # # | # # # | 0.827 | 0.863 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.843 | 0.879 | 0.823 | 0.848 | - - - | 0.619 | 1.64 | 1.52 | 1.44 | 1.48 | 1.45 | 1.49 | 18.53 | 18.6 | 20.18 | 0 | - - - | - - - | - - - | - - - | 22923 | 21007 | 20328 | 64258 | Over-range | 12856 | 10601 | 12028 | 35593 | 4390 | 3962 | 4123 | 12800 | 18957 | 18169 | 16387 | 53513 | 18957 | 18169 | 16387 | 53513 | - - - | - - - | - - - | - - -
5/4/2026 | 11:00:00 PM | 284.15 | 281.58 | 279.97 | 491.39 | 484.69 | 488.7 | 82.0969 | 75.9195 | 73.4033 | 0.2624 | 1.43 | 1.428 | 1.425 | 1.807 | 1.812 | 1.942 | Over-range | 60 | 19222 | 18435 | 16499 | 54156 | - - - | - - - | - - - | - - - | 19222 | 18435 | 16499 | 54156 | 12355 | 9888 | 11376 | 33619 | - - - | - - - | - - - | - - - | 12355 | 9888 | 11376 | 33619 | 23223 | 21265 | 20447 | 64935 | # # # | # # # | # # # | # # # | 0.828 | 0.867 | 0.807 | 0.834 | # # # | # # # | # # # | - - - | 0.841 | 0.88 | 0.822 | 0.848 | - - - | 0.621 | 1.67 | 1.54 | 1.47 | 1.5 | 1.47 | 1.51 | 16.9 | 16.96 | 18.66 | 0 | - - - | - - - | - - - | - - - | 23223 | 21265 | 20447 | 64935 | Over-range | 13025 | 10590 | 12070 | 35807 | 4035 | 3708 | 3949 | 12082 | 19296 | 18423 | 16485 | 54205 | 19296 | 18423 | 16485 | 54205 | - - - | - - - | - - - | - - -
5/4/2026 | 11:15:00 PM | 284.3 | 281.53 | 279.95 | 491.53 | 484.49 | 488.93 | 80.5173 | 73.9963 | 71.7167 | 0.2587 | 1.43 | 1.429 | 1.426 | 1.816 | 1.822 | 1.962 | Over-range | 59.97 | 18746 | 17872 | 15959 | 52577 | - - - | - - - | - - - | - - - | 18746 | 17872 | 15959 | 52577 | 12197 | 9675 | 11263 | 33135 | - - - | - - - | - - - | - - - | 12197 | 9675 | 11263 | 33135 | 22761 | 20690 | 19959 | 63410 | # # # | # # # | # # # | # # # | 0.824 | 0.864 | 0.8 | 0.829 | # # # | # # # | # # # | - - - | 0.838 | 0.878 | 0.816 | 0.844 | - - - | 0.63 | 1.69 | 1.55 | 1.51 | 1.52 | 1.5 | 1.53 | 17.68 | 17.66 | 19.49 | 0 | - - - | - - - | - - - | - - - | 22761 | 20690 | 19959 | 63410 | Over-range | 12902 | 10413 | 11975 | 35419 | 4105 | 3755 | 3970 | 12235 | 18797 | 17840 | 15993 | 52629 | 18797 | 17840 | 15993 | 52629 | - - - | - - - | - - - | - - -
5/4/2026 | 11:30:00 PM | 284.78 | 281.86 | 280.41 | 492.22 | 485.09 | 489.81 | 81.3125 | 74.6339 | 72.3422 | 0.26 | 1.43 | 1.428 | 1.425 | 1.813 | 1.82 | 1.966 | Over-range | 60 | 19036 | 18124 | 16191 | 53350 | - - - | - - - | - - - | - - - | 19036 | 18124 | 16191 | 53350 | 12242 | 9658 | 11312 | 33212 | - - - | - - - | - - - | - - - | 12242 | 9658 | 11312 | 33212 | 23034 | 20906 | 20173 | 64113 | # # # | # # # | # # # | # # # | 0.826 | 0.867 | 0.803 | 0.832 | # # # | # # # | # # # | - - - | 0.84 | 0.881 | 0.819 | 0.847 | - - - | 0.623 | 1.69 | 1.56 | 1.5 | 1.51 | 1.5 | 1.53 | 17.66 | 17.49 | 19.51 | 0 | - - - | - - - | - - - | - - - | 23034 | 20906 | 20173 | 64113 | Over-range | 12963 | 10409 | 12025 | 35532 | 4161 | 3787 | 3983 | 12351 | 19057 | 18087 | 16254 | 53399 | 19057 | 18087 | 16254 | 53399 | - - - | - - - | - - - | - - -
5/4/2026 | 11:45:00 PM | 284.99 | 282.09 | 280.55 | 492.63 | 485.46 | 490.04 | 82.1509 | 75.6106 | 72.8631 | 0.2638 | 1.43 | 1.428 | 1.425 | 1.836 | 1.846 | 1.978 | Over-range | 59.99 | 19174 | 18336 | 16273 | 53783 | - - - | - - - | - - - | - - - | 19174 | 18336 | 16273 | 53783 | 12353 | 9730 | 11352 | 33435 | - - - | - - - | - - - | - - - | 12353 | 9730 | 11352 | 33435 | 23287 | 21189 | 20321 | 64797 | # # # | # # # | # # # | # # # | 0.823 | 0.865 | 0.801 | 0.83 | # # # | # # # | # # # | - - - | 0.839 | 0.882 | 0.819 | 0.846 | - - - | 0.622 | 1.69 | 1.6 | 1.54 | 1.54 | 1.53 | 1.56 | 18.6 | 18.73 | 20.59 | 0 | - - - | - - - | - - - | - - - | 23287 | 21189 | 20321 | 64797 | Over-range | 13198 | 10596 | 12155 | 36086 | 4533 | 4085 | 4232 | 13258 | 19151 | 18387 | 16299 | 53837 | 19151 | 18387 | 16299 | 53837 | - - - | - - - | - - - | - - -
5/5/2026 | 12:00:00 AM | 285.18 | 282.36 | 280.78 | 493.04 | 485.9 | 490.37 | 80.9934 | 74.9618 | 72.6035 | 0.2627 | 1.43 | 1.428 | 1.425 | 1.854 | 1.87 | 2.001 | Over-range | 59.99 | 18980 | 18167 | 16320 | 53467 | - - - | - - - | - - - | - - - | 18980 | 18167 | 16320 | 53467 | 12077 | 9725 | 11158 | 32960 | - - - | - - - | - - - | - - - | 12077 | 9725 | 11158 | 32960 | 22977 | 21036 | 20276 | 64288 | # # # | # # # | # # # | # # # | 0.826 | 0.864 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.843 | 0.881 | 0.824 | 0.849 | - - - | 0.617 | 1.7 | 1.56 | 1.51 | 1.52 | 1.51 | 1.54 | 19.41 | 19.46 | 21.39 | 0 | - - - | - - - | - - - | - - - | 22977 | 21036 | 20276 | 64288 | Over-range | 12943 | 10591 | 12020 | 35667 | 4565 | 4113 | 4390 | 13389 | 19020 | 18209 | 16291 | 53520 | 19020 | 18209 | 16291 | 53520 | - - - | - - - | - - - | - - -
5/5/2026 | 12:15:00 AM | 285.21 | 282.31 | 280.73 | 493.08 | 485.77 | 490.36 | 82.8223 | 76.1888 | 73.4717 | 0.2644 | 1.428 | 1.426 | 1.423 | 1.851 | 1.855 | 2.006 | Over-range | 59.98 | 19388 | 18530 | 16463 | 54380 | - - - | - - - | - - - | - - - | 19388 | 18530 | 16463 | 54380 | 12407 | 9760 | 11400 | 33568 | - - - | - - - | - - - | - - - | 12407 | 9760 | 11400 | 33568 | 23497 | 21376 | 20512 | 65385 | # # # | # # # | # # # | # # # | 0.825 | 0.867 | 0.803 | 0.832 | # # # | # # # | # # # | - - - | 0.841 | 0.883 | 0.821 | 0.849 | - - - | 0.617 | 1.69 | 1.55 | 1.49 | 1.52 | 1.5 | 1.52 | 19.08 | 19.05 | 21.04 | 0 | - - - | - - - | - - - | - - - | 23497 | 21376 | 20512 | 65385 | Over-range | 13267 | 10644 | 12225 | 36274 | 4603 | 4155 | 4321 | 13484 | 19373 | 18543 | 16516 | 54431 | 19373 | 18543 | 16516 | 54431 | - - - | - - - | - - - | - - -
5/5/2026 | 12:30:00 AM | 285.35 | 282.47 | 280.79 | 493.37 | 486.02 | 490.45 | 82.6626 | 76.2974 | 73.8463 | 0.2659 | 1.428 | 1.426 | 1.423 | 1.853 | 1.849 | 1.995 | Over-range | 59.97 | 19380 | 18526 | 16576 | 54482 | - - - | - - - | - - - | - - - | 19380 | 18526 | 16576 | 54482 | 12452 | 9957 | 11521 | 33930 | - - - | - - - | - - - | - - - | 12452 | 9957 | 11521 | 33930 | 23497 | 21449 | 20649 | 65594 | # # # | # # # | # # # | # # # | 0.825 | 0.864 | 0.803 | 0.831 | # # # | # # # | # # # | - - - | 0.84 | 0.88 | 0.821 | 0.847 | - - - | 0.623 | 1.67 | 1.57 | 1.47 | 1.51 | 1.49 | 1.51 | 18.87 | 18.81 | 20.61 | 0 | - - - | - - - | - - - | - - - | 23497 | 21449 | 20649 | 65594 | Over-range | 13280 | 10800 | 12303 | 36505 | 4544 | 4116 | 4245 | 13269 | 19363 | 18532 | 16634 | 54529 | 19363 | 18532 | 16634 | 54529 | - - - | - - - | - - - | - - -
5/5/2026 | 12:45:00 AM | 285.64 | 282.62 | 281.01 | 493.74 | 486.27 | 490.96 | 83.2938 | 76.7654 | 74.2895 | 0.2673 | 1.428 | 1.426 | 1.423 | 1.859 | 1.861 | 2.005 | Over-range | 59.99 | 19499 | 18597 | 16630 | 54727 | - - - | - - - | - - - | - - - | 19499 | 18597 | 16630 | 54727 | 12414 | 9885 | 11493 | 33793 | - - - | - - - | - - - | - - - | 12414 | 9885 | 11493 | 33793 | 23626 | 21514 | 20722 | 65862 | # # # | # # # | # # # | # # # | 0.825 | 0.864 | 0.803 | 0.831 | # # # | # # # | # # # | - - - | 0.841 | 0.882 | 0.821 | 0.848 | - - - | 0.618 | 1.67 | 1.57 | 1.47 | 1.51 | 1.49 | 1.51 | 19.38 | 19.33 | 21.27 | 0 | - - - | - - - | - - - | - - - | 23626 | 21514 | 20722 | 65862 | Over-range | 13326 | 10794 | 12348 | 36597 | 4729 | 4221 | 4405 | 13731 | 19468 | 18651 | 16655 | 54774 | 19468 | 18651 | 16655 | 54774 | - - - | - - - | - - - | - - -
5/5/2026 | 1:00:00 AM | 286.01 | 283.11 | 281.49 | 494.48 | 487.15 | 491.65 | 83.9951 | 77.7135 | 74.7342 | 0.2534 | 1.428 | 1.425 | 1.422 | 1.861 | 1.86 | 2.001 | Over-range | 59.99 | 19710 | 18936 | 16841 | 55487 | - - - | - - - | - - - | - - - | 19710 | 18936 | 16841 | 55487 | 12612 | 9998 | 11551 | 34161 | - - - | - - - | - - - | - - - | 12612 | 9998 | 11551 | 34161 | 23895 | 21861 | 20919 | 66675 | # # # | # # # | # # # | # # # | 0.825 | 0.866 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.841 | 0.883 | 0.824 | 0.85 | - - - | 0.616 | 1.69 | 1.57 | 1.48 | 1.52 | 1.5 | 1.52 | 19.37 | 19.36 | 21.2 | 0 | - - - | - - - | - - - | - - - | 23895 | 21861 | 20919 | 66675 | Over-range | 13502 | 10910 | 12395 | 36938 | 4723 | 4277 | 4406 | 13785 | 19690 | 18955 | 16887 | 55533 | 19690 | 18955 | 16887 | 55533 | - - - | - - - | - - - | - - -
5/5/2026 | 1:15:00 AM | 285.29 | 282.31 | 280.86 | 493.07 | 485.93 | 490.56 | 80.7156 | 74.422 | 72.3984 | 0.2636 | 1.427 | 1.424 | 1.422 | 1.87 | 1.886 | 2.024 | Over-range | 59.98 | 18934 | 18032 | 16240 | 53206 | - - - | - - - | - - - | - - - | 18934 | 18032 | 16240 | 53206 | 12017 | 9625 | 11139 | 32781 | - - - | - - - | - - - | - - - | 12017 | 9625 | 11139 | 32781 | 22923 | 20897 | 20234 | 64054 | # # # | # # # | # # # | # # # | 0.826 | 0.863 | 0.803 | 0.831 | # # # | # # # | # # # | - - - | 0.844 | 0.88 | 0.823 | 0.849 | - - - | 0.616 | 1.65 | 1.54 | 1.47 | 1.5 | 1.48 | 1.49 | 20.06 | 20.01 | 22.16 | 0 | - - - | - - - | - - - | - - - | 22923 | 20897 | 20234 | 64054 | Over-range | 12914 | 10548 | 12061 | 35639 | 4641 | 4234 | 4544 | 13744 | 19012 | 18004 | 16233 | 53249 | 19012 | 18004 | 16233 | 53249 | - - - | - - - | - - - | - - -
5/5/2026 | 1:30:00 AM | 285.4 | 282.43 | 280.89 | 493.33 | 486.05 | 490.65 | 82.8189 | 76.4938 | 73.8023 | 0.2527 | 1.427 | 1.424 | 1.422 | 1.865 | 1.872 | 2.013 | Over-range | 59.98 | 19445 | 18622 | 16617 | 54684 | - - - | - - - | - - - | - - - | 19445 | 18622 | 16617 | 54684 | 12340 | 9772 | 11339 | 33451 | - - - | - - - | - - - | - - - | 12340 | 9772 | 11339 | 33451 | 23520 | 21480 | 20623 | 65624 | # # # | # # # | # # # | # # # | 0.827 | 0.867 | 0.806 | 0.833 | # # # | # # # | # # # | - - - | 0.844 | 0.884 | 0.826 | 0.851 | - - - | 0.612 | 1.68 | 1.53 | 1.48 | 1.51 | 1.5 | 1.5 | 19.62 | 19.62 | 21.57 | 0 | - - - | - - - | - - - | - - - | 23520 | 21480 | 20623 | 65624 | Over-range | 13227 | 10695 | 12205 | 36254 | 4676 | 4269 | 4438 | 13751 | 19449 | 18614 | 16662 | 54725 | 19449 | 18614 | 16662 | 54725 | - - - | - - - | - - - | - - -
5/5/2026 | 1:45:00 AM | 285.87 | 282.99 | 281.51 | 494.2 | 487.1 | 491.58 | 81.3081 | 74.8711 | 72.6197 | 0.2616 | 1.427 | 1.424 | 1.422 | 1.864 | 1.87 | 2.021 | Over-range | 59.99 | 19038 | 18154 | 16256 | 53448 | - - - | - - - | - - - | - - - | 19038 | 18154 | 16256 | 53448 | 12209 | 9726 | 11325 | 33259 | - - - | - - - | - - - | - - - | 12209 | 9726 | 11325 | 33259 | 23118 | 21048 | 20323 | 64489 | # # # | # # # | # # # | # # # | 0.824 | 0.863 | 0.8 | 0.829 | # # # | # # # | # # # | - - - | 0.84 | 0.88 | 0.82 | 0.847 | - - - | 0.622 | 1.69 | 1.58 | 1.49 | 1.52 | 1.51 | 1.52 | 19.69 | 19.57 | 21.67 | 0 | - - - | - - - | - - - | - - - | 23118 | 21048 | 20323 | 64489 | Over-range | 13101 | 10632 | 12182 | 36040 | 4650 | 4200 | 4397 | 13610 | 19029 | 18159 | 16300 | 53487 | 19029 | 18159 | 16300 | 53487 | - - - | - - - | - - - | - - -
5/5/2026 | 2:00:00 AM | 286.35 | 283.64 | 282.1 | 495.13 | 488.27 | 492.43 | 81.9671 | 75.6074 | 73.6345 | 0.2532 | 1.427 | 1.424 | 1.422 | 1.854 | 1.861 | 2.007 | Over-range | 60 | 19240 | 18343 | 16530 | 54113 | - - - | - - - | - - - | - - - | 19240 | 18343 | 16530 | 54113 | 12396 | 9987 | 11573 | 33956 | - - - | - - - | - - - | - - - | 12396 | 9987 | 11573 | 33956 | 23344 | 21310 | 20653 | 65308 | # # # | # # # | # # # | # # # | 0.824 | 0.861 | 0.8 | 0.829 | # # # | # # # | # # # | - - - | 0.84 | 0.876 | 0.819 | 0.845 | - - - | 0.627 | 1.71 | 1.55 | 1.48 | 1.52 | 1.5 | 1.51 | 18.98 | 18.9 | 20.78 | 0 | - - - | - - - | - - - | - - - | 23344 | 21310 | 20653 | 65308 | Over-range | 13214 | 10835 | 12374 | 36539 | 4487 | 4116 | 4292 | 13243 | 19251 | 18312 | 16589 | 54152 | 19251 | 18312 | 16589 | 54152 | - - - | - - - | - - - | - - -
5/5/2026 | 2:15:00 AM | 286.24 | 283.64 | 282.14 | 494.99 | 488.4 | 492.35 | 82.5268 | 76.0459 | 73.8419 | 0.2525 | 1.427 | 1.424 | 1.422 | 1.856 | 1.861 | 2.001 | Over-range | 59.98 | 19360 | 18476 | 16566 | 54402 | - - - | - - - | - - - | - - - | 19360 | 18476 | 16566 | 54402 | 12481 | 9959 | 11590 | 34030 | - - - | - - - | - - - | - - - | 12481 | 9959 | 11590 | 34030 | 23485 | 21420 | 20703 | 65608 | # # # | # # # | # # # | # # # | 0.824 | 0.863 | 0.8 | 0.829 | # # # | # # # | # # # | - - - | 0.84 | 0.878 | 0.818 | 0.846 | - - - | 0.625 | 1.68 | 1.55 | 1.48 | 1.52 | 1.5 | 1.52 | 18.75 | 18.99 | 20.66 | 0 | - - - | - - - | - - - | - - - | 23485 | 21420 | 20703 | 65608 | Over-range | 13286 | 10824 | 12404 | 36641 | 4445 | 4145 | 4320 | 13291 | 19412 | 18427 | 16601 | 54440 | 19412 | 18427 | 16601 | 54440 | - - - | - - - | - - - | - - -
5/5/2026 | 2:30:00 AM | 286.17 | 283.54 | 282.13 | 494.81 | 488.3 | 492.31 | 81.6602 | 75.3405 | 73.8638 | 0.2637 | 1.426 | 1.423 | 1.421 | 1.871 | 1.883 | 2.015 | Over-range | 59.99 | 19170 | 18197 | 16558 | 53925 | - - - | - - - | - - - | - - - | 19170 | 18197 | 16558 | 53925 | 12252 | 9994 | 11556 | 33801 | - - - | - - - | - - - | - - - | 12252 | 9994 | 11556 | 33801 | 23232 | 21213 | 20712 | 65157 | # # # | # # # | # # # | # # # | 0.825 | 0.858 | 0.799 | 0.828 | # # # | # # # | # # # | - - - | 0.842 | 0.875 | 0.819 | 0.845 | - - - | 0.627 | 1.68 | 1.58 | 1.51 | 1.53 | 1.51 | 1.53 | 19.67 | 19.85 | 21.6 | 0 | - - - | - - - | - - - | - - - | 23232 | 21213 | 20712 | 65157 | Over-range | 13117 | 10890 | 12432 | 36545 | 4588 | 4239 | 4501 | 13633 | 19235 | 18169 | 16559 | 53963 | 19235 | 18169 | 16559 | 53963 | - - - | - - - | - - - | - - -
5/5/2026 | 2:45:00 AM | 286.31 | 283.75 | 282.25 | 495.13 | 488.61 | 492.49 | 82.0979 | 75.9676 | 73.9388 | 0.2572 | 1.428 | 1.424 | 1.422 | 1.855 | 1.867 | 1.999 | Over-range | 59.98 | 19238 | 18385 | 16591 | 54214 | - - - | - - - | - - - | - - - | 19238 | 18385 | 16591 | 54214 | 12407 | 10043 | 11596 | 34047 | - - - | - - - | - - - | - - - | 12407 | 10043 | 11596 | 34047 | 23360 | 21397 | 20731 | 65487 | # # # | # # # | # # # | # # # | 0.824 | 0.859 | 0.8 | 0.828 | # # # | # # # | # # # | - - - | 0.839 | 0.876 | 0.819 | 0.845 | - - - | 0.628 | 1.71 | 1.57 | 1.49 | 1.53 | 1.5 | 1.53 | 18.93 | 19.13 | 20.81 | 0 | - - - | - - - | - - - | - - - | 23360 | 21397 | 20731 | 65487 | Over-range | 13237 | 10926 | 12415 | 36689 | 4510 | 4208 | 4337 | 13391 | 19252 | 18354 | 16652 | 54258 | 19252 | 18354 | 16652 | 54258 | - - - | - - - | - - - | - - -
5/5/2026 | 3:00:00 AM | 286.45 | 283.93 | 282.52 | 495.35 | 489.06 | 492.83 | 81.8752 | 75.8349 | 73.6422 | 0.2533 | 1.427 | 1.423 | 1.421 | 1.839 | 1.855 | 1.988 | Over-range | 59.99 | 19175 | 18380 | 16541 | 54095 | - - - | - - - | - - - | - - - | 19175 | 18380 | 16541 | 54095 | 12493 | 10101 | 11624 | 34218 | - - - | - - - | - - - | - - - | 12493 | 10101 | 11624 | 34218 | 23315 | 21379 | 20674 | 65368 | # # # | # # # | # # # | # # # | 0.822 | 0.86 | 0.8 | 0.828 | # # # | # # # | # # # | - - - | 0.837 | 0.875 | 0.817 | 0.843 | - - - | 0.633 | 1.71 | 1.55 | 1.48 | 1.52 | 1.49 | 1.52 | 18.23 | 18.36 | 20.15 | 0 | - - - | - - - | - - - | - - - | 23315 | 21379 | 20674 | 65368 | Over-range | 13254 | 10906 | 12389 | 36663 | 4306 | 4003 | 4176 | 12838 | 19197 | 18345 | 16584 | 54127 | 19197 | 18345 | 16584 | 54127 | - - - | - - - | - - - | - - -
5/5/2026 | 3:15:00 AM | 286.43 | 283.99 | 282.51 | 495.43 | 489.11 | 492.79 | 79.8872 | 74.259 | 72.3116 | 0.2545 | 1.427 | 1.424 | 1.422 | 1.843 | 1.854 | 1.993 | Over-range | 59.98 | 18751 | 17992 | 16310 | 53053 | - - - | - - - | - - - | - - - | 18751 | 17992 | 16310 | 53053 | 12124 | 9970 | 11357 | 33451 | - - - | - - - | - - - | - - - | 12124 | 9970 | 11357 | 33451 | 22768 | 20966 | 20325 | 64059 | # # # | # # # | # # # | # # # | 0.824 | 0.858 | 0.803 | 0.828 | # # # | # # # | # # # | - - - | 0.839 | 0.874 | 0.82 | 0.844 | - - - | 0.63 | 1.72 | 1.57 | 1.49 | 1.54 | 1.5 | 1.54 | 18.6 | 18.46 | 20.32 | 0 | - - - | - - - | - - - | - - - | 22768 | 20966 | 20325 | 64059 | Over-range | 12908 | 10751 | 12117 | 35874 | 4337 | 3931 | 4137 | 12701 | 18746 | 18013 | 16333 | 53091 | 18746 | 18013 | 16333 | 53091 | - - - | - - - | - - - | - - -
5/5/2026 | 3:30:00 AM | 286.56 | 284.1 | 282.7 | 495.57 | 489.4 | 493.07 | 80.5797 | 74.6119 | 72.5207 | 0.2589 | 1.427 | 1.424 | 1.422 | 1.837 | 1.86 | 1.989 | Over-range | 59.99 | 18899 | 18098 | 16310 | 53307 | - - - | - - - | - - - | - - - | 18899 | 18098 | 16310 | 53307 | 12227 | 9913 | 11378 | 33518 | - - - | - - - | - - - | - - - | 12227 | 9913 | 11378 | 33518 | 22940 | 21035 | 20362 | 64337 | # # # | # # # | # # # | # # # | 0.824 | 0.86 | 0.801 | 0.829 | # # # | # # # | # # # | - - - | 0.839 | 0.875 | 0.818 | 0.844 | - - - | 0.629 | 1.71 | 1.56 | 1.53 | 1.54 | 1.51 | 1.54 | 18.39 | 18.57 | 20.39 | 0 | - - - | - - - | - - - | - - - | 22940 | 21035 | 20362 | 64337 | Over-range | 12995 | 10706 | 12177 | 35989 | 4279 | 3932 | 4227 | 12777 | 18964 | 18099 | 16284 | 53347 | 18964 | 18099 | 16284 | 53347 | - - - | - - - | - - - | - - -
5/5/2026 | 3:45:00 AM | 286.65 | 284.26 | 282.75 | 495.81 | 489.61 | 493.15 | 81.0736 | 75.5489 | 73.404 | 0.2573 | 1.427 | 1.423 | 1.422 | 1.851 | 1.865 | 1.987 | Over-range | 59.99 | 18983 | 18259 | 16527 | 53769 | - - - | - - - | - - - | - - - | 18983 | 18259 | 16527 | 53769 | 12363 | 10144 | 11508 | 34016 | - - - | - - - | - - - | - - - | 12363 | 10144 | 11508 | 34016 | 23106 | 21327 | 20630 | 65063 | # # # | # # # | # # # | # # # | 0.822 | 0.856 | 0.801 | 0.826 | # # # | # # # | # # # | - - - | 0.838 | 0.872 | 0.819 | 0.843 | - - - | 0.633 | 1.71 | 1.55 | 1.49 | 1.53 | 1.5 | 1.53 | 18.79 | 19.09 | 20.66 | 0 | - - - | - - - | - - - | - - - | 23106 | 21327 | 20630 | 65063 | Over-range | 13160 | 11000 | 12331 | 36588 | 4392 | 4144 | 4329 | 13161 | 19050 | 18218 | 16541 | 53810 | 19050 | 18218 | 16541 | 53810 | - - - | - - - | - - - | - - -
5/5/2026 | 4:00:00 AM | 286.58 | 284.18 | 282.77 | 495.68 | 489.54 | 493.12 | 81.3154 | 75.7705 | 73.6412 | 0.2519 | 1.427 | 1.423 | 1.422 | 1.843 | 1.865 | 1.977 | Over-range | 60 | 19111 | 18385 | 16651 | 54146 | - - - | - - - | - - - | - - - | 19111 | 18385 | 16651 | 54146 | 12292 | 10107 | 11500 | 33898 | - - - | - - - | - - - | - - - | 12292 | 10107 | 11500 | 33898 | 23187 | 21409 | 20711 | 65307 | # # # | # # # | # # # | # # # | 0.824 | 0.859 | 0.804 | 0.829 | # # # | # # # | # # # | - - - | 0.84 | 0.875 | 0.822 | 0.846 | - - - | 0.626 | 1.73 | 1.6 | 1.54 | 1.55 | 1.53 | 1.57 | 18.78 | 19.04 | 20.69 | 0 | - - - | - - - | - - - | - - - | 23187 | 21409 | 20711 | 65307 | Over-range | 13124 | 10960 | 12306 | 36487 | 4506 | 4147 | 4289 | 13231 | 19085 | 18431 | 16675 | 54190 | 19085 | 18431 | 16675 | 54190 | - - - | - - - | - - - | - - -
5/5/2026 | 4:15:00 AM | 286.44 | 284.14 | 282.65 | 495.55 | 489.45 | 492.84 | 82.8737 | 77.2229 | 75.0173 | 0.2577 | 1.426 | 1.423 | 1.422 | 1.838 | 1.863 | 1.971 | Over-range | 59.98 | 19457 | 18716 | 16941 | 55114 | - - - | - - - | - - - | - - - | 19457 | 18716 | 16941 | 55114 | 12557 | 10346 | 11742 | 34645 | - - - | - - - | - - - | - - - | 12557 | 10346 | 11742 | 34645 | 23610 | 21804 | 21084 | 66498 | # # # | # # # | # # # | # # # | 0.824 | 0.858 | 0.804 | 0.829 | # # # | # # # | # # # | - - - | 0.839 | 0.875 | 0.82 | 0.845 | - - - | 0.629 | 1.73 | 1.57 | 1.53 | 1.54 | 1.52 | 1.55 | 18.49 | 18.94 | 20.39 | 0 | - - - | - - - | - - - | - - - | 23610 | 21804 | 21084 | 66498 | Over-range | 13367 | 11174 | 12543 | 37183 | 4487 | 4134 | 4324 | 13243 | 19462 | 18776 | 16917 | 55155 | 19462 | 18776 | 16917 | 55155 | - - - | - - - | - - - | - - -
5/5/2026 | 4:30:00 AM | 286.38 | 284.02 | 282.59 | 495.35 | 489.29 | 492.77 | 80.1253 | 74.5697 | 73.0127 | 0.2568 | 1.427 | 1.423 | 1.422 | 1.849 | 1.876 | 1.977 | Over-range | 59.99 | 18814 | 17989 | 16439 | 53243 | - - - | - - - | - - - | - - - | 18814 | 17989 | 16439 | 53243 | 12080 | 10038 | 11403 | 33521 | - - - | - - - | - - - | - - - | 12080 | 10038 | 11403 | 33521 | 22814 | 21035 | 20506 | 64355 | # # # | # # # | # # # | # # # | 0.825 | 0.855 | 0.802 | 0.827 | # # # | # # # | # # # | - - - | 0.841 | 0.872 | 0.82 | 0.844 | - - - | 0.63 | 1.71 | 1.58 | 1.54 | 1.54 | 1.52 | 1.56 | 18.99 | 19.48 | 20.93 | 0 | - - - | - - - | - - - | - - - | 22814 | 21035 | 20506 | 64355 | Over-range | 12896 | 10890 | 12244 | 36118 | 4408 | 4129 | 4366 | 13164 | 18880 | 17998 | 16408 | 53286 | 18880 | 17998 | 16408 | 53286 | - - - | - - - | - - - | - - -
5/5/2026 | 4:45:00 AM | 285.83 | 283.44 | 282.02 | 494.4 | 488.22 | 491.82 | 82.7215 | 77.264 | 74.7561 | 0.2594 | 1.426 | 1.423 | 1.422 | 1.849 | 1.88 | 1.979 | Over-range | 59.99 | 19402 | 18711 | 16898 | 55011 | - - - | - - - | - - - | - - - | 19402 | 18711 | 16898 | 55011 | 12334 | 10087 | 11435 | 33855 | - - - | - - - | - - - | - - - | 12334 | 10087 | 11435 | 33855 | 23488 | 21730 | 20935 | 66153 | # # # | # # # | # # # | # # # | 0.826 | 0.861 | 0.807 | 0.832 | # # # | # # # | # # # | - - - | 0.843 | 0.879 | 0.826 | 0.849 | - - - | 0.615 | 1.72 | 1.57 | 1.54 | 1.53 | 1.53 | 1.56 | 19.29 | 19.91 | 21.46 | 0 | - - - | - - - | - - - | - - - | 23488 | 21730 | 20935 | 66153 | Over-range | 13222 | 11028 | 12342 | 36691 | 4659 | 4359 | 4548 | 13857 | 19441 | 18750 | 16867 | 55059 | 19441 | 18750 | 16867 | 55059 | - - - | - - - | - - - | - - -
5/5/2026 | 5:00:00 AM | 285.82 | 283.42 | 282 | 494.37 | 488.19 | 491.81 | 81.3471 | 76.028 | 73.8111 | 0.256 | 1.426 | 1.424 | 1.422 | 1.866 | 1.9 | 1.995 | Over-range | 59.99 | 19133 | 18425 | 16721 | 54278 | - - - | - - - | - - - | - - - | 19133 | 18425 | 16721 | 54278 | 12087 | 9947 | 11255 | 33289 | - - - | - - - | - - - | - - - | 12087 | 9947 | 11255 | 33289 | 23137 | 21422 | 20704 | 65263 | # # # | # # # | # # # | # # # | 0.827 | 0.86 | 0.808 | 0.832 | # # # | # # # | # # # | - - - | 0.845 | 0.879 | 0.828 | 0.851 | - - - | 0.613 | 1.73 | 1.6 | 1.53 | 1.54 | 1.53 | 1.57 | 19.96 | 20.66 | 22.21 | 0 | - - - | - - - | - - - | - - - | 23137 | 21422 | 20704 | 65263 | Over-range | 13003 | 10919 | 12198 | 36211 | 4709 | 4424 | 4628 | 14018 | 19190 | 18452 | 16689 | 54330 | 19190 | 18452 | 16689 | 54330 | - - - | - - - | - - - | - - -
5/5/2026 | 5:15:00 AM | 285.2 | 282.67 | 281.26 | 493.23 | 486.82 | 490.67 | 82.7107 | 77.3814 | 74.8449 | 0.259 | 1.426 | 1.424 | 1.423 | 1.86 | 1.89 | 1.97 | Over-range | 60.01 | 19431 | 18741 | 16961 | 55133 | - - - | - - - | - - - | - - - | 19431 | 18741 | 16961 | 55133 | 12231 | 9993 | 11330 | 33554 | - - - | - - - | - - - | - - - | 12231 | 9993 | 11330 | 33554 | 23446 | 21719 | 20919 | 66084 | # # # | # # # | # # # | # # # | 0.829 | 0.863 | 0.811 | 0.834 | # # # | # # # | # # # | - - - | 0.845 | 0.881 | 0.83 | 0.852 | - - - | 0.609 | 1.7 | 1.6 | 1.56 | 1.53 | 1.55 | 1.58 | 19.44 | 20.22 | 21.54 | 0 | - - - | - - - | - - - | - - - | 23446 | 21719 | 20919 | 66084 | Over-range | 13115 | 10965 | 12232 | 36406 | 4645 | 4432 | 4529 | 13884 | 19468 | 18738 | 16986 | 55192 | 19468 | 18738 | 16986 | 55192 | - - - | - - - | - - - | - - -
5/5/2026 | 5:30:00 AM | 284.66 | 281.98 | 280.53 | 492.26 | 485.45 | 489.62 | 83.5462 | 77.9043 | 74.6758 | 0.2642 | 1.426 | 1.424 | 1.424 | 1.859 | 1.877 | 1.973 | Over-range | 60.01 | 19644 | 18986 | 16949 | 55579 | - - - | - - - | - - - | - - - | 19644 | 18986 | 16949 | 55579 | 12323 | 9802 | 11207 | 33332 | - - - | - - - | - - - | - - - | 12323 | 9802 | 11207 | 33332 | 23668 | 21843 | 20840 | 66352 | # # # | # # # | # # # | # # # | 0.83 | 0.869 | 0.813 | 0.838 | # # # | # # # | # # # | - - - | 0.847 | 0.887 | 0.833 | 0.856 | - - - | 0.6 | 1.7 | 1.61 | 1.54 | 1.53 | 1.55 | 1.57 | 19.29 | 20 | 21.5 | 0 | - - - | - - - | - - - | - - - | 23668 | 21843 | 20840 | 66352 | Over-range | 13197 | 10790 | 12116 | 36218 | 4639 | 4436 | 4528 | 13942 | 19712 | 18946 | 16981 | 55639 | 19712 | 18946 | 16981 | 55639 | - - - | - - - | - - - | - - -
5/5/2026 | 5:45:00 AM | 284.5 | 281.68 | 280.3 | 491.84 | 484.97 | 489.32 | 81.2714 | 75.3846 | 73.1967 | 0.2644 | 1.426 | 1.425 | 1.423 | 1.873 | 1.89 | 1.983 | Over-range | 60 | 18982 | 18136 | 16391 | 53508 | - - - | - - - | - - - | - - - | 18982 | 18136 | 16391 | 53508 | 11933 | 9672 | 11106 | 32710 | - - - | - - - | - - - | - - - | 11933 | 9672 | 11106 | 32710 | 22943 | 21045 | 20351 | 64338 | # # # | # # # | # # # | # # # | 0.827 | 0.862 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.845 | 0.881 | 0.825 | 0.851 | - - - | 0.611 | 1.71 | 1.62 | 1.58 | 1.54 | 1.57 | 1.59 | 19.9 | 20.6 | 22.11 | 0 | - - - | - - - | - - - | - - - | 22943 | 21045 | 20351 | 64338 | Over-range | 12869 | 10651 | 12043 | 35667 | 4695 | 4347 | 4547 | 13886 | 19021 | 18183 | 16356 | 53560 | 19021 | 18183 | 16356 | 53560 | - - - | - - - | - - - | - - -
5/5/2026 | 6:00:00 AM | 284.28 | 281.74 | 280.34 | 491.65 | 485.19 | 489.08 | 82.1039 | 76.2787 | 74.0139 | 0.2578 | 1.426 | 1.425 | 1.423 | 1.849 | 1.862 | 1.951 | Over-range | 60.01 | 19271 | 18470 | 16695 | 54436 | - - - | - - - | - - - | - - - | 19271 | 18470 | 16695 | 54436 | 12137 | 9846 | 11276 | 33259 | - - - | - - - | - - - | - - - | 12137 | 9846 | 11276 | 33259 | 23217 | 21363 | 20631 | 65212 | # # # | # # # | # # # | # # # | 0.83 | 0.865 | 0.809 | 0.835 | # # # | # # # | # # # | - - - | 0.846 | 0.881 | 0.827 | 0.851 | - - - | 0.611 | 1.73 | 1.65 | 1.6 | 1.56 | 1.58 | 1.62 | 18.54 | 19.28 | 20.62 | 0 | - - - | - - - | - - - | - - - | 23217 | 21363 | 20631 | 65212 | Over-range | 12943 | 10725 | 12112 | 35884 | 4407 | 4174 | 4342 | 13234 | 19352 | 18472 | 16673 | 54498 | 19352 | 18472 | 16673 | 54498 | - - - | - - - | - - - | - - -
5/5/2026 | 6:15:00 AM | 283.68 | 281.26 | 279.82 | 490.69 | 484.34 | 488.13 | 81.1482 | 75.581 | 72.9581 | 0.2603 | 1.427 | 1.427 | 1.425 | 1.86 | 1.862 | 1.949 | Over-range | 60 | 18984 | 18277 | 16452 | 53713 | - - - | - - - | - - - | - - - | 18984 | 18277 | 16452 | 53713 | 11899 | 9610 | 10971 | 32479 | - - - | - - - | - - - | - - - | 11899 | 9610 | 10971 | 32479 | 22871 | 21097 | 20274 | 64242 | # # # | # # # | # # # | # # # | 0.83 | 0.866 | 0.811 | 0.836 | # # # | # # # | # # # | - - - | 0.847 | 0.884 | 0.83 | 0.854 | - - - | 0.605 | 1.84 | 1.78 | 1.76 | 1.67 | 1.7 | 1.76 | 18.99 | 19.62 | 21.04 | 0 | - - - | - - - | - - - | - - - | 22871 | 21097 | 20274 | 64242 | Over-range | 12746 | 10522 | 11836 | 35207 | 4464 | 4191 | 4350 | 13310 | 19063 | 18298 | 16419 | 53780 | 19063 | 18298 | 16419 | 53780 | - - - | - - - | - - - | - - -
5/5/2026 | 6:30:00 AM | 283.24 | 280.9 | 279.33 | 490.02 | 483.63 | 487.26 | 80.8476 | 75.6535 | 73.1905 | 0.2646 | 1.426 | 1.427 | 1.425 | 1.858 | 1.854 | 1.933 | Over-range | 60 | 18945 | 18276 | 16563 | 53784 | - - - | - - - | - - - | - - - | 18945 | 18276 | 16563 | 53784 | 11835 | 9720 | 10965 | 32520 | - - - | - - - | - - - | - - - | 11835 | 9720 | 10965 | 32520 | 22787 | 21130 | 20340 | 64257 | # # # | # # # | # # # | # # # | 0.831 | 0.865 | 0.814 | 0.837 | # # # | # # # | # # # | - - - | 0.848 | 0.882 | 0.832 | 0.854 | - - - | 0.605 | 1.88 | 1.78 | 1.77 | 1.68 | 1.72 | 1.78 | 18.67 | 19.3 | 20.55 | 0 | - - - | - - - | - - - | - - - | 22787 | 21130 | 20340 | 64257 | Over-range | 12656 | 10593 | 11797 | 35134 | 4406 | 4143 | 4284 | 13094 | 19022 | 18305 | 16529 | 53855 | 19022 | 18305 | 16529 | 53855 | - - - | - - - | - - - | - - -
5/5/2026 | 6:45:00 AM | 283.49 | 281.15 | 279.64 | 490.42 | 484.09 | 487.81 | 80.0739 | 74.8344 | 71.8631 | 0.2528 | 1.426 | 1.427 | 1.424 | 1.823 | 1.821 | 1.919 | Over-range | 60.01 | 18656 | 18083 | 16196 | 52936 | - - - | - - - | - - - | - - - | 18656 | 18083 | 16196 | 52936 | 11896 | 9609 | 10864 | 32369 | - - - | - - - | - - - | - - - | 11896 | 9609 | 10864 | 32369 | 22539 | 20869 | 19944 | 63352 | # # # | # # # | # # # | # # # | 0.828 | 0.867 | 0.812 | 0.836 | # # # | # # # | # # # | - - - | 0.843 | 0.881 | 0.828 | 0.851 | - - - | 0.612 | 1.84 | 1.8 | 1.74 | 1.67 | 1.69 | 1.76 | 17.5 | 17.88 | 19.43 | 0 | - - - | - - - | - - - | - - - | 22539 | 20869 | 19944 | 63352 | Over-range | 12629 | 10392 | 11619 | 34744 | 4111 | 3831 | 3998 | 12268 | 18730 | 18104 | 16167 | 53002 | 18730 | 18104 | 16167 | 53002 | - - - | - - - | - - - | - - -
5/5/2026 | 7:00:00 AM | 283.41 | 281.09 | 279.53 | 490.36 | 483.86 | 487.68 | 79.167 | 74.4817 | 71.4835 | 0.2497 | 1.426 | 1.427 | 1.422 | 1.831 | 1.816 | 1.93 | Over-range | 60.02 | 18406 | 17947 | 16149 | 52501 | - - - | - - - | - - - | - - - | 18406 | 17947 | 16149 | 52501 | 11871 | 9719 | 10828 | 32417 | - - - | - - - | - - - | - - - | 11871 | 9719 | 10828 | 32417 | 22300 | 20788 | 19854 | 62942 | # # # | # # # | # # # | # # # | 0.825 | 0.863 | 0.813 | 0.834 | # # # | # # # | # # # | - - - | 0.84 | 0.878 | 0.83 | 0.849 | - - - | 0.618 | 1.84 | 1.79 | 1.73 | 1.65 | 1.69 | 1.76 | 17.71 | 17.75 | 19.34 | 0 | - - - | - - - | - - - | - - - | 22300 | 20788 | 19854 | 62942 | Over-range | 12583 | 10479 | 11537 | 34688 | 4072 | 3830 | 3889 | 12070 | 18453 | 17915 | 16194 | 52562 | 18453 | 17915 | 16194 | 52562 | - - - | - - - | - - - | - - -
5/5/2026 | 7:15:00 AM | 283.04 | 280.69 | 279.24 | 489.59 | 483.29 | 487.17 | 78.9194 | 74.0625 | 71.1299 | 0.2598 | 1.425 | 1.426 | 1.422 | 1.818 | 1.813 | 1.917 | Over-range | 59.99 | 18393 | 17889 | 16093 | 52376 | - - - | - - - | - - - | - - - | 18393 | 17889 | 16093 | 52376 | 11724 | 9565 | 10745 | 32034 | - - - | - - - | - - - | - - - | 11724 | 9565 | 10745 | 32034 | 22214 | 20655 | 19748 | 62617 | # # # | # # # | # # # | # # # | 0.828 | 0.866 | 0.815 | 0.836 | # # # | # # # | # # # | - - - | 0.842 | 0.881 | 0.831 | 0.851 | - - - | 0.612 | 1.86 | 1.81 | 1.74 | 1.66 | 1.7 | 1.77 | 17.41 | 17.49 | 19.17 | 0 | - - - | - - - | - - - | - - - | 22214 | 20655 | 19748 | 62617 | Over-range | 12450 | 10311 | 11435 | 34291 | 4092 | 3759 | 3817 | 11961 | 18382 | 17927 | 16130 | 52439 | 18382 | 17927 | 16130 | 52439 | - - - | - - - | - - - | - - -
5/5/2026 | 7:30:00 AM | 283.03 | 280.6 | 279.14 | 489.52 | 483.06 | 487.12 | 81.2789 | 76.0881 | 73.0954 | 0.2586 | 1.425 | 1.426 | 1.421 | 1.83 | 1.827 | 1.927 | Over-range | 60.02 | 18958 | 18395 | 16529 | 53882 | - - - | - - - | - - - | - - - | 18958 | 18395 | 16529 | 53882 | 12028 | 9778 | 11013 | 32818 | - - - | - - - | - - - | - - - | 12028 | 9778 | 11013 | 32818 | 22878 | 21213 | 20287 | 64379 | # # # | # # # | # # # | # # # | 0.829 | 0.867 | 0.815 | 0.837 | # # # | # # # | # # # | - - - | 0.843 | 0.882 | 0.831 | 0.852 | - - - | 0.609 | 1.85 | 1.82 | 1.77 | 1.67 | 1.72 | 1.78 | 17.8 | 17.91 | 19.55 | 0 | - - - | - - - | - - - | - - - | 22878 | 21213 | 20287 | 64379 | Over-range | 12800 | 10554 | 11752 | 35206 | 4293 | 3891 | 4019 | 12506 | 18970 | 18463 | 16514 | 53947 | 18970 | 18463 | 16514 | 53947 | - - - | - - - | - - - | - - -
5/5/2026 | 7:45:00 AM | 283.05 | 280.55 | 279.21 | 489.43 | 483.07 | 487.27 | 80.2247 | 75.1364 | 72.7392 | 0.2537 | 1.425 | 1.426 | 1.421 | 1.86 | 1.863 | 1.948 | Over-range | 60.01 | 18710 | 18060 | 16412 | 53182 | - - - | - - - | - - - | - - - | 18710 | 18060 | 16412 | 53182 | 11663 | 9569 | 10831 | 32063 | - - - | - - - | - - - | - - - | 11663 | 9569 | 10831 | 32063 | 22540 | 20900 | 20150 | 63590 | # # # | # # # | # # # | # # # | 0.83 | 0.864 | 0.815 | 0.836 | # # # | # # # | # # # | - - - | 0.847 | 0.882 | 0.834 | 0.854 | - - - | 0.603 | 1.86 | 1.82 | 1.78 | 1.67 | 1.73 | 1.78 | 19.29 | 19.6 | 21.09 | 0 | - - - | - - - | - - - | - - - | 22540 | 20900 | 20150 | 63590 | Over-range | 12554 | 10497 | 11674 | 34810 | 4547 | 4224 | 4260 | 13282 | 18699 | 18107 | 16455 | 53262 | 18699 | 18107 | 16455 | 53262 | - - - | - - - | - - - | - - -
5/5/2026 | 8:00:00 AM | 282.78 | 280.3 | 279 | 488.95 | 482.74 | 486.82 | 82.479 | 77.2992 | 74.3144 | 0.2727 | 1.425 | 1.426 | 1.421 | 1.869 | 1.87 | 1.944 | Over-range | 60.01 | 19307 | 18708 | 16871 | 54886 | - - - | - - - | - - - | - - - | 19307 | 18708 | 16871 | 54886 | 11938 | 9681 | 10970 | 32589 | - - - | - - - | - - - | - - - | 11938 | 9681 | 10970 | 32589 | 23205 | 21542 | 20625 | 65372 | # # # | # # # | # # # | # # # | 0.832 | 0.868 | 0.818 | 0.84 | # # # | # # # | # # # | - - - | 0.849 | 0.887 | 0.837 | 0.858 | - - - | 0.594 | 1.85 | 1.81 | 1.76 | 1.65 | 1.71 | 1.77 | 19.32 | 19.93 | 21.25 | 0 | - - - | - - - | - - - | - - - | 23205 | 21542 | 20625 | 65372 | Over-range | 12865 | 10666 | 11853 | 35481 | 4702 | 4391 | 4397 | 13767 | 19297 | 18781 | 16886 | 54965 | 19297 | 18781 | 16886 | 54965 | - - - | - - - | - - - | - - -
5/5/2026 | 8:15:00 AM | 282.56 | 279.89 | 278.81 | 488.35 | 482.14 | 486.58 | 82.4089 | 76.8843 | 74.603 | 0.2581 | 1.426 | 1.428 | 1.422 | 1.878 | 1.882 | 1.954 | Over-range | 60.01 | 19298 | 18540 | 16875 | 54713 | - - - | - - - | - - - | - - - | 19298 | 18540 | 16875 | 54713 | 11861 | 9682 | 11053 | 32596 | - - - | - - - | - - - | - - - | 11861 | 9682 | 11053 | 32596 | 23173 | 21402 | 20694 | 65270 | # # # | # # # | # # # | # # # | 0.833 | 0.866 | 0.816 | 0.838 | # # # | # # # | # # # | - - - | 0.851 | 0.886 | 0.836 | 0.858 | - - - | 0.596 | 1.83 | 1.82 | 1.75 | 1.64 | 1.71 | 1.76 | 19.88 | 20.47 | 21.9 | 0 | - - - | - - - | - - - | - - - | 23173 | 21402 | 20694 | 65270 | Over-range | 12822 | 10682 | 11969 | 35565 | 4798 | 4444 | 4524 | 14022 | 19301 | 18624 | 16876 | 54801 | 19301 | 18624 | 16876 | 54801 | - - - | - - - | - - - | - - -
5/5/2026 | 8:30:00 AM | 282.58 | 279.82 | 278.78 | 488.34 | 482.01 | 486.6 | 81.503 | 75.9524 | 73.3897 | 0.2699 | 1.426 | 1.427 | 1.422 | 1.867 | 1.877 | 1.958 | Over-range | 60.01 | 19093 | 18367 | 16612 | 54072 | - - - | - - - | - - - | - - - | 19093 | 18367 | 16612 | 54072 | 11743 | 9418 | 10820 | 31980 | - - - | - - - | - - - | - - - | 11743 | 9418 | 10820 | 31980 | 22924 | 21141 | 20357 | 64421 | # # # | # # # | # # # | # # # | 0.833 | 0.869 | 0.816 | 0.839 | # # # | # # # | # # # | - - - | 0.851 | 0.888 | 0.837 | 0.859 | - - - | 0.591 | 1.78 | 1.76 | 1.68 | 1.59 | 1.66 | 1.7 | 19.83 | 20.45 | 21.98 | 0 | - - - | - - - | - - - | - - - | 22924 | 21141 | 20357 | 64421 | Over-range | 12678 | 10456 | 11755 | 34989 | 4697 | 4467 | 4514 | 13964 | 19136 | 18343 | 16671 | 54150 | 19136 | 18343 | 16671 | 54150 | - - - | - - - | - - - | - - -
5/5/2026 | 8:45:00 AM | 281.84 | 279.11 | 278.03 | 487.03 | 480.79 | 485.32 | 82.5976 | 77.1949 | 74.4475 | 0.2562 | 1.426 | 1.428 | 1.422 | 1.878 | 1.885 | 1.954 | Over-range | 60.01 | 19295 | 18606 | 16829 | 54730 | - - - | - - - | - - - | - - - | 19295 | 18606 | 16829 | 54730 | 11826 | 9522 | 10853 | 32201 | - - - | - - - | - - - | - - - | 11826 | 9522 | 10853 | 32201 | 23162 | 21418 | 20587 | 65168 | # # # | # # # | # # # | # # # | 0.833 | 0.869 | 0.817 | 0.84 | # # # | # # # | # # # | - - - | 0.852 | 0.889 | 0.838 | 0.86 | - - - | 0.588 | 1.76 | 1.75 | 1.67 | 1.58 | 1.64 | 1.68 | 19.98 | 20.73 | 22.16 | 0 | - - - | - - - | - - - | - - - | 23162 | 21418 | 20587 | 65168 | Over-range | 12798 | 10586 | 11841 | 35322 | 4804 | 4547 | 4656 | 14283 | 19383 | 18622 | 16807 | 54812 | 19383 | 18622 | 16807 | 54812 | - - - | - - - | - - - | - - -
5/5/2026 | 9:00:00 AM | 281.59 | 278.84 | 277.76 | 486.63 | 480.29 | 484.86 | 82.1944 | 77.1143 | 74.4859 | 0.2707 | 1.427 | 1.428 | 1.423 | 1.904 | 1.911 | 1.973 | Over-range | 60 | 19258 | 18581 | 16919 | 54758 | - - - | - - - | - - - | - - - | 19258 | 18581 | 16919 | 54758 | 11546 | 9396 | 10632 | 31574 | - - - | - - - | - - - | - - - | 11546 | 9396 | 10632 | 31574 | 23010 | 21361 | 20565 | 64936 | # # # | # # # | # # # | # # # | 0.837 | 0.87 | 0.823 | 0.843 | # # # | # # # | # # # | - - - | 0.858 | 0.892 | 0.846 | 0.865 | - - - | 0.577 | 1.77 | 1.75 | 1.68 | 1.58 | 1.65 | 1.69 | 21.04 | 21.83 | 23.19 | 0 | - - - | - - - | - - - | - - - | 23010 | 21361 | 20565 | 64936 | Over-range | 12586 | 10524 | 11681 | 34875 | 4942 | 4680 | 4777 | 14628 | 19346 | 18609 | 16894 | 54849 | 19346 | 18609 | 16894 | 54849 | - - - | - - - | - - - | - - -
5/5/2026 | 9:15:00 AM | 281.09 | 278.23 | 277.22 | 485.62 | 479.3 | 484 | 83.3642 | 77.8196 | 74.8534 | 0.2706 | 1.427 | 1.429 | 1.424 | 1.901 | 1.903 | 1.964 | Over-range | 60 | 19525 | 18802 | 16971 | 55298 | - - - | - - - | - - - | - - - | 19525 | 18802 | 16971 | 55298 | 11661 | 9277 | 10664 | 31602 | - - - | - - - | - - - | - - - | 11661 | 9277 | 10664 | 31602 | 23301 | 21514 | 20629 | 65444 | # # # | # # # | # # # | # # # | 0.838 | 0.874 | 0.823 | 0.845 | # # # | # # # | # # # | - - - | 0.859 | 0.896 | 0.845 | 0.867 | - - - | 0.572 | 1.77 | 1.76 | 1.71 | 1.59 | 1.68 | 1.7 | 20.8 | 21.78 | 23.01 | 0 | - - - | - - - | - - - | - - - | 23301 | 21514 | 20629 | 65444 | Over-range | 12710 | 10445 | 11717 | 34973 | 4972 | 4728 | 4781 | 14761 | 19618 | 18824 | 16952 | 55394 | 19618 | 18824 | 16952 | 55394 | - - - | - - - | - - - | - - -
5/5/2026 | 9:30:00 AM | 281.27 | 278.34 | 277.41 | 485.81 | 479.6 | 484.33 | 82.8611 | 77.3409 | 75.2614 | 0.2698 | 1.427 | 1.429 | 1.424 | 1.941 | 1.938 | 1.984 | Over-range | 60.01 | 19399 | 18540 | 17000 | 54939 | - - - | - - - | - - - | - - - | 19399 | 18540 | 17000 | 54939 | 11409 | 9285 | 10671 | 31365 | - - - | - - - | - - - | - - - | 11409 | 9285 | 10671 | 31365 | 23157 | 21375 | 20743 | 65275 | # # # | # # # | # # # | # # # | 0.838 | 0.867 | 0.82 | 0.842 | # # # | # # # | # # # | - - - | 0.861 | 0.893 | 0.845 | 0.867 | - - - | 0.571 | 1.8 | 1.82 | 1.75 | 1.63 | 1.72 | 1.75 | 22.52 | 23.67 | 24.68 | 0 | - - - | - - - | - - - | - - - | 23157 | 21375 | 20743 | 65275 | Over-range | 12638 | 10622 | 11872 | 35213 | 5329 | 5061 | 5103 | 15712 | 19469 | 18598 | 16972 | 55039 | 19469 | 18598 | 16972 | 55039 | - - - | - - - | - - - | - - -
5/5/2026 | 9:45:00 AM | 280.85 | 277.97 | 276.96 | 485.18 | 478.88 | 483.56 | 84.8523 | 79.2647 | 76.5382 | 0.2707 | 1.428 | 1.43 | 1.426 | 1.933 | 1.921 | 1.97 | Over-range | 60.01 | 19894 | 19096 | 17347 | 56337 | - - - | - - - | - - - | - - - | 19894 | 19096 | 17347 | 56337 | 11690 | 9372 | 10788 | 31850 | - - - | - - - | - - - | - - - | 11690 | 9372 | 10788 | 31850 | 23712 | 21903 | 21085 | 66699 | # # # | # # # | # # # | # # # | 0.839 | 0.872 | 0.823 | 0.845 | # # # | # # # | # # # | - - - | 0.862 | 0.897 | 0.847 | 0.869 | - - - | 0.565 | 1.83 | 1.84 | 1.79 | 1.66 | 1.75 | 1.78 | 21.84 | 22.98 | 23.96 | 0 | - - - | - - - | - - - | - - - | 23712 | 21903 | 21085 | 66699 | Over-range | 12888 | 10705 | 11967 | 35654 | 5351 | 5102 | 5110 | 15817 | 19982 | 19154 | 17317 | 56453 | 19982 | 19154 | 17317 | 56453 | - - - | - - - | - - - | - - -
5/5/2026 | 10:00:00 AM | 280.55 | 277.69 | 276.75 | 484.64 | 478.44 | 483.14 | 82.6321 | 76.8316 | 74.3439 | 0.2654 | 1.428 | 1.43 | 1.426 | 1.915 | 1.906 | 1.961 | Over-range | 60 | 19319 | 18490 | 16772 | 54580 | - - - | - - - | - - - | - - - | 19319 | 18490 | 16772 | 54580 | 11514 | 9203 | 10662 | 31380 | - - - | - - - | - - - | - - - | 11514 | 9203 | 10662 | 31380 | 23074 | 21219 | 20472 | 64764 | # # # | # # # | # # # | # # # | 0.837 | 0.871 | 0.819 | 0.843 | # # # | # # # | # # # | - - - | 0.859 | 0.894 | 0.842 | 0.865 | - - - | 0.575 | 1.84 | 1.86 | 1.76 | 1.67 | 1.74 | 1.78 | 21.22 | 22.25 | 23.34 | 0 | - - - | - - - | - - - | - - - | 23074 | 21219 | 20472 | 64764 | Over-range | 12610 | 10401 | 11728 | 34837 | 5069 | 4781 | 4817 | 14935 | 19384 | 18551 | 16745 | 54679 | 19384 | 18551 | 16745 | 54679 | - - - | - - - | - - - | - - -
5/5/2026 | 10:15:00 AM | 280.32 | 277.56 | 276.46 | 484.36 | 478.12 | 482.62 | 82.7729 | 77.4995 | 74.7323 | 0.2641 | 1.429 | 1.431 | 1.427 | 1.91 | 1.895 | 1.952 | Over-range | 60.02 | 19383 | 18680 | 16963 | 55027 | - - - | - - - | - - - | - - - | 19383 | 18680 | 16963 | 55027 | 11481 | 9269 | 10606 | 31356 | - - - | - - - | - - - | - - - | 11481 | 9269 | 10606 | 31356 | 23083 | 21385 | 20552 | 65020 | # # # | # # # | # # # | # # # | 0.84 | 0.874 | 0.825 | 0.846 | # # # | # # # | # # # | - - - | 0.859 | 0.895 | 0.847 | 0.867 | - - - | 0.57 | 1.86 | 1.87 | 1.83 | 1.69 | 1.78 | 1.81 | 20.57 | 21.32 | 22.36 | 0 | - - - | - - - | - - - | - - - | 23083 | 21385 | 20552 | 65020 | Over-range | 12528 | 10398 | 11592 | 34609 | 4939 | 4644 | 4609 | 14445 | 19392 | 18755 | 16978 | 55125 | 19392 | 18755 | 16978 | 55125 | - - - | - - - | - - - | - - -
5/5/2026 | 10:30:00 AM | 280.08 | 277.28 | 276.22 | 483.91 | 477.67 | 482.2 | 83.2354 | 77.7201 | 74.7439 | 0.2626 | 1.427 | 1.429 | 1.426 | 1.92 | 1.916 | 1.98 | Over-range | 60.01 | 19439 | 18717 | 16897 | 55053 | - - - | - - - | - - - | - - - | 19439 | 18717 | 16897 | 55053 | 11501 | 9118 | 10553 | 31172 | - - - | - - - | - - - | - - - | 11501 | 9118 | 10553 | 31172 | 23179 | 21409 | 20523 | 65112 | # # # | # # # | # # # | # # # | 0.839 | 0.874 | 0.823 | 0.846 | # # # | # # # | # # # | - - - | 0.86 | 0.898 | 0.848 | 0.869 | - - - | 0.566 | 1.83 | 1.83 | 1.8 | 1.67 | 1.76 | 1.78 | 21.58 | 22.57 | 23.66 | 0 | - - - | - - - | - - - | - - - | 23179 | 21409 | 20523 | 65112 | Over-range | 12619 | 10381 | 11637 | 34737 | 5116 | 4895 | 4833 | 15120 | 19478 | 18722 | 16957 | 55157 | 19478 | 18722 | 16957 | 55157 | - - - | - - - | - - - | - - -
5/5/2026 | 10:45:00 AM | 279.76 | 276.88 | 275.82 | 483.33 | 476.93 | 481.6 | 81.8311 | 76.6405 | 74.0381 | 0.2607 | 1.428 | 1.431 | 1.426 | 1.943 | 1.938 | 1.998 | Over-range | 60.02 | 19096 | 18359 | 16718 | 54174 | - - - | - - - | - - - | - - - | 19096 | 18359 | 16718 | 54174 | 11083 | 8916 | 10255 | 30254 | - - - | - - - | - - - | - - - | 11083 | 8916 | 10255 | 30254 | 22752 | 21071 | 20287 | 64110 | # # # | # # # | # # # | # # # | 0.839 | 0.871 | 0.824 | 0.845 | # # # | # # # | # # # | - - - | 0.863 | 0.898 | 0.851 | 0.871 | - - - | 0.559 | 1.85 | 1.87 | 1.82 | 1.69 | 1.78 | 1.8 | 22.87 | 23.86 | 25 | 0 | - - - | - - - | - - - | - - - | 22752 | 21071 | 20287 | 64110 | Over-range | 12349 | 10313 | 11471 | 34217 | 5363 | 5107 | 5059 | 15753 | 19117 | 18404 | 16761 | 54281 | 19117 | 18404 | 16761 | 54281 | - - - | - - - | - - - | - - -
5/5/2026 | 11:00:00 AM | 279.42 | 276.58 | 275.43 | 482.81 | 476.34 | 480.93 | 85.5479 | 79.8508 | 76.8076 | 0.306 | 1.428 | 1.43 | 1.426 | 1.909 | 1.902 | 1.965 | Over-range | 60 | 20052 | 19281 | 17421 | 56754 | - - - | - - - | - - - | - - - | 20052 | 19281 | 17421 | 56754 | 11706 | 9268 | 10723 | 31697 | - - - | - - - | - - - | - - - | 11706 | 9268 | 10723 | 31697 | 23795 | 21972 | 21052 | 66819 | # # # | # # # | # # # | # # # | 0.843 | 0.877 | 0.828 | 0.849 | # # # | # # # | # # # | - - - | 0.864 | 0.9 | 0.851 | 0.872 | - - - | 0.559 | 1.84 | 1.88 | 1.82 | 1.7 | 1.79 | 1.81 | 21.02 | 22.01 | 23.11 | 0 | - - - | - - - | - - - | - - - | 23795 | 21972 | 21052 | 66819 | Over-range | 12805 | 10525 | 11808 | 35242 | 5127 | 4933 | 4883 | 15231 | 20134 | 19267 | 17460 | 56861 | 20134 | 19267 | 17460 | 56861 | - - - | - - - | - - - | - - -
5/5/2026 | 11:15:00 AM | 278.87 | 276.14 | 274.91 | 481.87 | 475.62 | 479.97 | 84.147 | 78.9129 | 75.9678 | 0.5905 | 1.428 | 1.429 | 1.426 | 2.062 | 2.032 | 2.106 | Over-range | 60 | 19615 | 18864 | 17161 | 55640 | - - - | - - - | - - - | - - - | 19615 | 18864 | 17161 | 55640 | 11159 | 8995 | 10233 | 30387 | - - - | - - - | - - - | - - - | 11159 | 8995 | 10233 | 30387 | 23354 | 21677 | 20778 | 65809 | # # # | # # # | # # # | # # # | 0.84 | 0.87 | 0.826 | 0.846 | # # # | # # # | # # # | - - - | 0.869 | 0.902 | 0.857 | 0.876 | - - - | 0.546 | 1.6 | 1.6 | 1.54 | 1.42 | 1.46 | 1.52 | 25.18 | 26.27 | 27.47 | 0 | - - - | - - - | - - - | - - - | 23354 | 21677 | 20778 | 65809 | Over-range | 12668 | 10667 | 11705 | 35116 | 5932 | 5674 | 5623 | 17421 | 19678 | 18917 | 17143 | 55739 | 19678 | 18917 | 17143 | 55739 | - - - | - - - | - - - | - - -
5/5/2026 | 11:30:00 AM | 279.07 | 276.43 | 275.18 | 482.35 | 476.04 | 480.36 | 86.7338 | 81.2615 | 78.3415 | 0.6092 | 1.428 | 1.429 | 1.426 | 2.077 | 2.051 | 2.132 | Over-range | 60 | 20351 | 19506 | 17806 | 57662 | - - - | - - - | - - - | - - - | 20351 | 19506 | 17806 | 57662 | 11191 | 9014 | 10339 | 30544 | - - - | - - - | - - - | - - - | 11191 | 9014 | 10339 | 30544 | 24061 | 22311 | 21427 | 67799 | # # # | # # # | # # # | # # # | 0.846 | 0.874 | 0.831 | 0.851 | # # # | # # # | # # # | - - - | 0.875 | 0.907 | 0.863 | 0.882 | - - - | 0.53 | 1.62 | 1.55 | 1.54 | 1.42 | 1.45 | 1.51 | 25.7 | 26.95 | 27.99 | 0 | - - - | - - - | - - - | - - - | 24061 | 22311 | 21427 | 67799 | Over-range | 12827 | 10817 | 11908 | 35632 | 6198 | 5921 | 5847 | 18165 | 20390 | 19589 | 17792 | 57771 | 20390 | 19589 | 17792 | 57771 | - - - | - - - | - - - | - - -
5/5/2026 | 11:45:00 AM | 278.83 | 276.22 | 275.04 | 481.94 | 475.73 | 480.07 | 85.1591 | 80.1893 | 76.86 | 0.6013 | 1.428 | 1.429 | 1.426 | 2.088 | 2.061 | 2.143 | Over-range | 60 | 19803 | 19144 | 17368 | 56315 | - - - | - - - | - - - | - - - | 19803 | 19144 | 17368 | 56315 | 11216 | 9025 | 10222 | 30464 | - - - | - - - | - - - | - - - | 11216 | 9025 | 10222 | 30464 | 23618 | 22014 | 21016 | 66647 | # # # | # # # | # # # | # # # | 0.839 | 0.87 | 0.826 | 0.845 | # # # | # # # | # # # | - - - | 0.869 | 0.903 | 0.861 | 0.878 | - - - | 0.541 | 1.58 | 1.54 | 1.51 | 1.4 | 1.44 | 1.49 | 26.06 | 27.13 | 28.43 | 0 | - - - | - - - | - - - | - - - | 23618 | 22014 | 21016 | 66647 | Over-range | 12851 | 10842 | 11811 | 35578 | 6200 | 5942 | 5850 | 18181 | 19824 | 19202 | 17392 | 56418 | 19824 | 19202 | 17392 | 56418 | - - - | - - - | - - - | - - -
5/5/2026 | 12:00:00 PM | 278.55 | 276.03 | 274.76 | 481.51 | 475.43 | 479.51 | 85.3178 | 80.6781 | 77.2402 | 0.6026 | 1.428 | 1.429 | 1.426 | 2.09 | 2.061 | 2.142 | Over-range | 60.01 | 19921 | 19328 | 17564 | 56813 | - - - | - - - | - - - | - - - | 19921 | 19328 | 17564 | 56813 | 11148 | 9027 | 10125 | 30300 | - - - | - - - | - - - | - - - | 11148 | 9027 | 10125 | 30300 | 23668 | 22165 | 21130 | 66963 | # # # | # # # | # # # | # # # | 0.842 | 0.872 | 0.831 | 0.848 | # # # | # # # | # # # | - - - | 0.872 | 0.906 | 0.865 | 0.881 | - - - | 0.533 | 1.54 | 1.55 | 1.49 | 1.38 | 1.41 | 1.46 | 26.03 | 27.09 | 28.47 | 0 | - - - | - - - | - - - | - - - | 23668 | 22165 | 21130 | 66963 | Over-range | 12774 | 10837 | 11736 | 35417 | 6185 | 5950 | 5887 | 18196 | 19980 | 19390 | 17550 | 56919 | 19980 | 19390 | 17550 | 56919 | - - - | - - - | - - - | - - -
5/5/2026 | 12:15:00 PM | 278.48 | 275.88 | 274.67 | 481.34 | 475.17 | 479.39 | 85.7193 | 80.8078 | 77.2451 | 0.5966 | 1.428 | 1.429 | 1.426 | 2.09 | 2.052 | 2.143 | Over-range | 59.99 | 19959 | 19343 | 17509 | 56811 | - - - | - - - | - - - | - - - | 19959 | 19343 | 17509 | 56811 | 11266 | 9007 | 10184 | 30456 | - - - | - - - | - - - | - - - | 11266 | 9007 | 10184 | 30456 | 23755 | 22171 | 21111 | 67037 | # # # | # # # | # # # | # # # | 0.84 | 0.872 | 0.829 | 0.848 | # # # | # # # | # # # | - - - | 0.871 | 0.905 | 0.864 | 0.88 | - - - | 0.536 | 1.57 | 1.56 | 1.5 | 1.4 | 1.43 | 1.49 | 26.01 | 27 | 28.4 | 0 | - - - | - - - | - - - | - - - | 23755 | 22171 | 21111 | 67037 | Over-range | 12875 | 10824 | 11783 | 35559 | 6173 | 5949 | 5874 | 18192 | 20048 | 19327 | 17539 | 56913 | 20048 | 19327 | 17539 | 56913 | - - - | - - - | - - - | - - -
5/5/2026 | 12:30:00 PM | 278.65 | 276.06 | 274.85 | 481.64 | 475.45 | 479.73 | 85.7357 | 80.8524 | 77.6533 | 0.5983 | 1.429 | 1.431 | 1.428 | 2.095 | 2.051 | 2.136 | Over-range | 60 | 20047 | 19370 | 17667 | 57084 | - - - | - - - | - - - | - - - | 20047 | 19370 | 17667 | 57084 | 11131 | 9020 | 10188 | 30339 | - - - | - - - | - - - | - - - | 11131 | 9020 | 10188 | 30339 | 23768 | 22192 | 21231 | 67191 | # # # | # # # | # # # | # # # | 0.843 | 0.873 | 0.832 | 0.85 | # # # | # # # | # # # | - - - | 0.874 | 0.906 | 0.865 | 0.882 | - - - | 0.532 | 1.65 | 1.61 | 1.56 | 1.45 | 1.48 | 1.55 | 25.97 | 26.96 | 28.14 | 0 | - - - | - - - | - - - | - - - | 23768 | 22192 | 21231 | 67191 | Over-range | 12763 | 10818 | 11765 | 35416 | 6189 | 5923 | 5836 | 18122 | 20091 | 19429 | 17681 | 57201 | 20091 | 19429 | 17681 | 57201 | - - - | - - - | - - - | - - -
5/5/2026 | 12:45:00 PM | 280.2 | 277.63 | 276.38 | 484.34 | 478.21 | 482.33 | 87.3333 | 82.2275 | 78.8658 | 0.6025 | 1.429 | 1.43 | 1.428 | 2.085 | 2.041 | 2.117 | Over-range | 60.02 | 20418 | 19729 | 17910 | 58056 | - - - | - - - | - - - | - - - | 20418 | 19729 | 17910 | 58056 | 11643 | 9410 | 10640 | 31693 | - - - | - - - | - - - | - - - | 11643 | 9410 | 10640 | 31693 | 24345 | 22694 | 21677 | 68717 | # # # | # # # | # # # | # # # | 0.839 | 0.869 | 0.826 | 0.845 | # # # | # # # | # # # | - - - | 0.868 | 0.901 | 0.858 | 0.876 | - - - | 0.546 | 1.63 | 1.59 | 1.59 | 1.45 | 1.48 | 1.54 | 25.27 | 26.43 | 27.46 | 0 | - - - | - - - | - - - | - - - | 24345 | 22694 | 21677 | 68717 | Over-range | 13243 | 11193 | 12195 | 36707 | 6238 | 5996 | 5893 | 18325 | 20466 | 19801 | 17898 | 58165 | 20466 | 19801 | 17898 | 58165 | - - - | - - - | - - - | - - -
5/5/2026 | 1:00:00 PM | 279.75 | 276.96 | 275.78 | 483.38 | 476.98 | 481.55 | 84.677 | 79.6718 | 76.6479 | 0.5971 | 1.429 | 1.43 | 1.428 | 2.118 | 2.064 | 2.146 | Over-range | 60.01 | 19749 | 19021 | 17353 | 56123 | - - - | - - - | - - - | - - - | 19749 | 19021 | 17353 | 56123 | 11100 | 8957 | 10158 | 30216 | - - - | - - - | - - - | - - - | 11100 | 8957 | 10158 | 30216 | 23518 | 21892 | 20984 | 66394 | # # # | # # # | # # # | # # # | 0.84 | 0.869 | 0.827 | 0.845 | # # # | # # # | # # # | - - - | 0.871 | 0.903 | 0.862 | 0.879 | - - - | 0.538 | 1.65 | 1.63 | 1.58 | 1.45 | 1.52 | 1.56 | 26.64 | 27.84 | 28.96 | 0 | - - - | - - - | - - - | - - - | 23518 | 21892 | 20984 | 66394 | Over-range | 12760 | 10820 | 11785 | 35434 | 6213 | 6000 | 5903 | 18293 | 19826 | 19013 | 17398 | 56236 | 19826 | 19013 | 17398 | 56236 | - - - | - - - | - - - | - - -
5/5/2026 | 1:15:00 PM | 280.07 | 277.35 | 276.08 | 484.06 | 477.55 | 482.04 | 88.0834 | 82.8195 | 78.7712 | 0.6095 | 1.429 | 1.43 | 1.428 | 2.076 | 2.031 | 2.117 | Over-range | 60.01 | 20616 | 19989 | 17939 | 58544 | - - - | - - - | - - - | - - - | 20616 | 19989 | 17939 | 58544 | 11817 | 9321 | 10579 | 31718 | - - - | - - - | - - - | - - - | 11817 | 9321 | 10579 | 31718 | 24572 | 22866 | 21654 | 69093 | # # # | # # # | # # # | # # # | 0.839 | 0.874 | 0.829 | 0.847 | # # # | # # # | # # # | - - - | 0.868 | 0.905 | 0.86 | 0.878 | - - - | 0.542 | 1.64 | 1.6 | 1.57 | 1.44 | 1.5 | 1.54 | 25.09 | 26.23 | 27.5 | 0 | - - - | - - - | - - - | - - - | 24572 | 22866 | 21654 | 69093 | Over-range | 13365 | 11096 | 12118 | 36670 | 6194 | 5974 | 5862 | 18264 | 20718 | 19990 | 17947 | 58655 | 20718 | 19990 | 17947 | 58655 | - - - | - - - | - - - | - - -
5/5/2026 | 1:30:00 PM | 280.11 | 277.35 | 276.05 | 484.12 | 477.5 | 482.03 | 84.0023 | 79.1263 | 75.7531 | 0.5978 | 1.429 | 1.43 | 1.428 | 2.111 | 2.062 | 2.154 | Over-range | 60 | 19523 | 18880 | 17108 | 55511 | - - - | - - - | - - - | - - - | 19523 | 18880 | 17108 | 55511 | 11165 | 8983 | 10135 | 30282 | - - - | - - - | - - - | - - - | 11165 | 8983 | 10135 | 30282 | 23359 | 21769 | 20756 | 65883 | # # # | # # # | # # # | # # # | 0.836 | 0.867 | 0.824 | 0.843 | # # # | # # # | # # # | - - - | 0.868 | 0.902 | 0.86 | 0.877 | - - - | 0.546 | 1.63 | 1.59 | 1.54 | 1.42 | 1.48 | 1.52 | 26.79 | 27.86 | 29.13 | 0 | - - - | - - - | - - - | - - - | 23359 | 21769 | 20756 | 65883 | Over-range | 12817 | 10822 | 11740 | 35451 | 6218 | 5968 | 5858 | 18226 | 19575 | 18902 | 17148 | 55625 | 19575 | 18902 | 17148 | 55625 | - - - | - - - | - - - | - - -
5/5/2026 | 1:45:00 PM | 280.23 | 277.44 | 276.22 | 484.23 | 477.8 | 482.29 | 86.8398 | 81.6112 | 77.9309 | 0.5994 | 1.429 | 1.43 | 1.428 | 2.083 | 2.04 | 2.135 | Over-range | 60.01 | 20257 | 19588 | 17660 | 57505 | - - - | - - - | - - - | - - - | 20257 | 19588 | 17660 | 57505 | 11566 | 9215 | 10482 | 31263 | - - - | - - - | - - - | - - - | 11566 | 9215 | 10482 | 31263 | 24182 | 22484 | 21385 | 68052 | # # # | # # # | # # # | # # # | 0.838 | 0.871 | 0.826 | 0.845 | # # # | # # # | # # # | - - - | 0.867 | 0.904 | 0.858 | 0.876 | - - - | 0.544 | 1.63 | 1.59 | 1.55 | 1.43 | 1.48 | 1.52 | 25.66 | 26.68 | 27.99 | 0 | - - - | - - - | - - - | - - - | 24182 | 22484 | 21385 | 68052 | Over-range | 13193 | 11017 | 12043 | 36339 | 6266 | 5966 | 5856 | 18306 | 20266 | 19673 | 17675 | 57614 | 20266 | 19673 | 17675 | 57614 | - - - | - - - | - - - | - - -
5/5/2026 | 2:00:00 PM | 280.38 | 277.7 | 276.44 | 484.62 | 478.19 | 482.6 | 85.39 | 80.1343 | 76.7013 | 0.5962 | 1.43 | 1.431 | 1.428 | 2.094 | 2.05 | 2.145 | Over-range | 60.01 | 19914 | 19223 | 17359 | 56496 | - - - | - - - | - - - | - - - | 19914 | 19223 | 17359 | 56496 | 11432 | 9142 | 10406 | 30980 | - - - | - - - | - - - | - - - | 11432 | 9142 | 10406 | 30980 | 23817 | 22123 | 21087 | 67027 | # # # | # # # | # # # | # # # | 0.836 | 0.869 | 0.823 | 0.843 | # # # | # # # | # # # | - - - | 0.866 | 0.903 | 0.857 | 0.875 | - - - | 0.548 | 1.63 | 1.59 | 1.56 | 1.44 | 1.48 | 1.53 | 26.07 | 27.12 | 28.4 | 0 | - - - | - - - | - - - | - - - | 23817 | 22123 | 21087 | 67027 | Over-range | 13058 | 10936 | 11959 | 36035 | 6241 | 5938 | 5832 | 18217 | 19932 | 19306 | 17375 | 56614 | 19932 | 19306 | 17375 | 56614 | - - - | - - - | - - - | - - -
5/5/2026 | 2:15:00 PM | 280.38 | 277.61 | 276.41 | 484.55 | 478.04 | 482.61 | 86.827 | 81.5436 | 77.8794 | 0.5963 | 1.43 | 1.431 | 1.428 | 2.083 | 2.039 | 2.129 | Over-range | 60.02 | 20307 | 19621 | 17703 | 57631 | - - - | - - - | - - - | - - - | 20307 | 19621 | 17703 | 57631 | 11572 | 9196 | 10444 | 31211 | - - - | - - - | - - - | - - - | 11572 | 9196 | 10444 | 31211 | 24204 | 22491 | 21400 | 68095 | # # # | # # # | # # # | # # # | 0.839 | 0.872 | 0.827 | 0.846 | # # # | # # # | # # # | - - - | 0.869 | 0.905 | 0.86 | 0.878 | - - - | 0.542 | 1.62 | 1.62 | 1.56 | 1.44 | 1.47 | 1.53 | 25.62 | 26.67 | 27.97 | 0 | - - - | - - - | - - - | - - - | 24204 | 22491 | 21400 | 68095 | Over-range | 13163 | 10979 | 12011 | 36240 | 6208 | 5941 | 5875 | 18239 | 20409 | 19651 | 17688 | 57748 | 20409 | 19651 | 17688 | 57748 | - - - | - - - | - - - | - - -
5/5/2026 | 2:30:00 PM | 280.29 | 277.56 | 276.33 | 484.36 | 478 | 482.44 | 87.8194 | 82.2489 | 78.9039 | 0.6002 | 1.429 | 1.431 | 1.428 | 2.075 | 2.032 | 2.115 | Over-range | 60.01 | 20539 | 19768 | 17889 | 58196 | - - - | - - - | - - - | - - - | 20539 | 19768 | 17889 | 58196 | 11798 | 9397 | 10756 | 31951 | - - - | - - - | - - - | - - - | 11798 | 9397 | 10756 | 31951 | 24495 | 22701 | 21692 | 68888 | # # # | # # # | # # # | # # # | 0.839 | 0.871 | 0.825 | 0.845 | # # # | # # # | # # # | - - - | 0.867 | 0.902 | 0.857 | 0.875 | - - - | 0.549 | 1.61 | 1.59 | 1.55 | 1.42 | 1.46 | 1.52 | 25.07 | 26.28 | 27.31 | 0 | - - - | - - - | - - - | - - - | 24495 | 22701 | 21692 | 68888 | Over-range | 13340 | 11148 | 12257 | 36832 | 6157 | 5937 | 5817 | 18138 | 20621 | 19760 | 17928 | 58309 | 20621 | 19760 | 17928 | 58309 | - - - | - - - | - - - | - - -
5/5/2026 | 2:45:00 PM | 280.18 | 277.55 | 276.27 | 484.27 | 477.97 | 482.28 | 84.8301 | 79.681 | 76.5361 | 0.6 | 1.43 | 1.431 | 1.428 | 2.058 | 2.023 | 2.115 | Over-range | 60.01 | 19821 | 19120 | 17356 | 56296 | - - - | - - - | - - - | - - - | 19821 | 19120 | 17356 | 56296 | 11394 | 9202 | 10427 | 31024 | - - - | - - - | - - - | - - - | 11394 | 9202 | 10427 | 31024 | 23645 | 21984 | 21026 | 66655 | # # # | # # # | # # # | # # # | 0.838 | 0.87 | 0.825 | 0.845 | # # # | # # # | # # # | - - - | 0.866 | 0.9 | 0.855 | 0.874 | - - - | 0.551 | 1.61 | 1.59 | 1.54 | 1.43 | 1.47 | 1.51 | 24.59 | 25.5 | 26.68 | 0 | - - - | - - - | - - - | - - - | 23645 | 21984 | 21026 | 66655 | Over-range | 12874 | 10826 | 11850 | 35629 | 5920 | 5635 | 5562 | 17318 | 19855 | 19182 | 17368 | 56405 | 19855 | 19182 | 17368 | 56405 | - - - | - - - | - - - | - - -
5/5/2026 | 3:00:00 PM | 279.92 | 277.21 | 276 | 483.77 | 477.38 | 481.86 | 85.236 | 79.6546 | 76.0564 | 0.5978 | 1.429 | 1.431 | 1.428 | 2.019 | 1.989 | 2.097 | Over-range | 60 | 19849 | 19165 | 17180 | 56194 | - - - | - - - | - - - | - - - | 19849 | 19165 | 17180 | 56194 | 11717 | 9278 | 10615 | 31610 | - - - | - - - | - - - | - - - | 11717 | 9278 | 10615 | 31610 | 23742 | 21955 | 20878 | 66575 | # # # | # # # | # # # | # # # | 0.836 | 0.873 | 0.823 | 0.844 | # # # | # # # | # # # | - - - | 0.86 | 0.9 | 0.85 | 0.87 | - - - | 0.563 | 1.63 | 1.6 | 1.54 | 1.43 | 1.47 | 1.52 | 23.09 | 23.8 | 25.29 | 0 | - - - | - - - | - - - | - - - | 23742 | 21955 | 20878 | 66575 | Over-range | 13019 | 10699 | 11853 | 35671 | 5611 | 5269 | 5213 | 16353 | 19845 | 19235 | 17214 | 56294 | 19845 | 19235 | 17214 | 56294 | - - - | - - - | - - - | - - -
5/5/2026 | 3:15:00 PM | 280.01 | 277.42 | 276.09 | 484.01 | 477.71 | 481.94 | 83.3242 | 78.3715 | 75.1108 | 0.5992 | 1.43 | 1.432 | 1.429 | 2.07 | 2.03 | 2.13 | Over-range | 60.03 | 19383 | 18742 | 16978 | 55103 | - - - | - - - | - - - | - - - | 19383 | 18742 | 16978 | 55103 | 11194 | 9033 | 10215 | 30442 | - - - | - - - | - - - | - - - | 11194 | 9033 | 10215 | 30442 | 23164 | 21568 | 20584 | 65316 | # # # | # # # | # # # | # # # | 0.837 | 0.869 | 0.825 | 0.844 | # # # | # # # | # # # | - - - | 0.865 | 0.9 | 0.856 | 0.874 | - - - | 0.553 | 1.66 | 1.59 | 1.57 | 1.46 | 1.48 | 1.54 | 25.16 | 26.04 | 27.2 | 0 | - - - | - - - | - - - | - - - | 23164 | 21568 | 20584 | 65316 | Over-range | 12676 | 10658 | 11626 | 35035 | 5869 | 5585 | 5477 | 17124 | 19397 | 18792 | 17026 | 55215 | 19397 | 18792 | 17026 | 55215 | - - - | - - - | - - - | - - -
5/5/2026 | 3:30:00 PM | 279.99 | 277.41 | 276.15 | 483.95 | 477.8 | 481.98 | 85.4018 | 80.0434 | 76.3585 | 0.6032 | 1.43 | 1.431 | 1.429 | 2.007 | 1.99 | 2.09 | Over-range | 60 | 19945 | 19319 | 17328 | 56593 | - - - | - - - | - - - | - - - | 19945 | 19319 | 17328 | 56593 | 11743 | 9345 | 10609 | 31697 | - - - | - - - | - - - | - - - | 11743 | 9345 | 10609 | 31697 | 23824 | 22113 | 21001 | 66938 | # # # | # # # | # # # | # # # | 0.837 | 0.874 | 0.825 | 0.845 | # # # | # # # | # # # | - - - | 0.861 | 0.9 | 0.852 | 0.871 | - - - | 0.56 | 1.64 | 1.58 | 1.55 | 1.44 | 1.47 | 1.53 | 22.89 | 23.67 | 25.18 | 0 | - - - | - - - | - - - | - - - | 23824 | 22113 | 21001 | 66938 | Over-range | 13025 | 10750 | 11858 | 35730 | 5584 | 5266 | 5246 | 16344 | 19980 | 19399 | 17316 | 56694 | 19980 | 19399 | 17316 | 56694 | - - - | - - - | - - - | - - -
5/5/2026 | 3:45:00 PM | 280.09 | 277.44 | 276.18 | 484.11 | 477.74 | 482.15 | 83.0067 | 77.9219 | 74.7896 | 0.6048 | 1.431 | 1.432 | 1.429 | 2.066 | 2.027 | 2.127 | Over-range | 59.99 | 19294 | 18618 | 16867 | 54779 | - - - | - - - | - - - | - - - | 19294 | 18618 | 16867 | 54779 | 11256 | 9099 | 10269 | 30624 | - - - | - - - | - - - | - - - | 11256 | 9099 | 10269 | 30624 | 23126 | 21486 | 20536 | 65148 | # # # | # # # | # # # | # # # | 0.834 | 0.867 | 0.821 | 0.841 | # # # | # # # | # # # | - - - | 0.863 | 0.897 | 0.852 | 0.871 | - - - | 0.559 | 1.66 | 1.64 | 1.58 | 1.47 | 1.51 | 1.57 | 24.93 | 25.76 | 27.13 | 0 | - - - | - - - | - - - | - - - | 23126 | 21486 | 20536 | 65148 | Over-range | 12735 | 10701 | 11697 | 35210 | 5874 | 5551 | 5521 | 17141 | 19353 | 18698 | 16850 | 54901 | 19353 | 18698 | 16850 | 54901 | - - - | - - - | - - - | - - -
5/5/2026 | 4:00:00 PM | 279.66 | 277 | 275.72 | 483.39 | 476.93 | 481.38 | 86.1675 | 80.7708 | 77.0356 | 0.6062 | 1.43 | 1.432 | 1.429 | 2.047 | 2.01 | 2.104 | Over-range | 60.01 | 20115 | 19455 | 17476 | 57046 | - - - | - - - | - - - | - - - | 20115 | 19455 | 17476 | 57046 | 11685 | 9240 | 10512 | 31437 | - - - | - - - | - - - | - - - | 11685 | 9240 | 10512 | 31437 | 24003 | 22274 | 21153 | 67430 | # # # | # # # | # # # | # # # | 0.838 | 0.874 | 0.826 | 0.846 | # # # | # # # | # # # | - - - | 0.865 | 0.902 | 0.856 | 0.874 | - - - | 0.551 | 1.66 | 1.64 | 1.56 | 1.46 | 1.51 | 1.56 | 24.04 | 24.96 | 26.3 | 0 | - - - | - - - | - - - | - - - | 24003 | 22274 | 21153 | 67430 | Over-range | 13091 | 10834 | 11908 | 35926 | 5844 | 5605 | 5540 | 17230 | 20221 | 19446 | 17490 | 57157 | 20221 | 19446 | 17490 | 57157 | - - - | - - - | - - - | - - -
5/5/2026 | 4:15:00 PM | 279.73 | 277.08 | 275.84 | 483.45 | 477.19 | 481.54 | 82.5738 | 77.172 | 74.465 | 0.6061 | 1.431 | 1.432 | 1.429 | 2.001 | 1.983 | 2.082 | Over-range | 60.01 | 19239 | 18479 | 16799 | 54517 | - - - | - - - | - - - | - - - | 19239 | 18479 | 16799 | 54517 | 11368 | 9185 | 10461 | 31013 | - - - | - - - | - - - | - - - | 11368 | 9185 | 10461 | 31013 | 22986 | 21262 | 20432 | 64679 | # # # | # # # | # # # | # # # | 0.837 | 0.869 | 0.822 | 0.843 | # # # | # # # | # # # | - - - | 0.86 | 0.894 | 0.848 | 0.868 | - - - | 0.569 | 1.68 | 1.63 | 1.56 | 1.47 | 1.5 | 1.56 | 22.56 | 23.25 | 24.49 | 0 | - - - | - - - | - - - | - - - | 22986 | 21262 | 20432 | 64679 | Over-range | 12570 | 10506 | 11620 | 34778 | 5296 | 5037 | 4993 | 15544 | 19297 | 18459 | 16860 | 54615 | 19297 | 18459 | 16860 | 54615 | - - - | - - - | - - - | - - -
5/5/2026 | 4:30:00 PM | 279.48 | 276.92 | 275.51 | 483.2 | 476.68 | 481.02 | 86.4893 | 81.1755 | 77.5241 | 0.6074 | 1.431 | 1.433 | 1.43 | 2.011 | 1.973 | 2.07 | Over-range | 60.01 | 20190 | 19544 | 17602 | 57336 | - - - | - - - | - - - | - - - | 20190 | 19544 | 17602 | 57336 | 11775 | 9410 | 10631 | 31816 | - - - | - - - | - - - | - - - | 11775 | 9410 | 10631 | 31816 | 24041 | 22340 | 21237 | 67618 | # # # | # # # | # # # | # # # | 0.84 | 0.875 | 0.829 | 0.848 | # # # | # # # | # # # | - - - | 0.864 | 0.9 | 0.855 | 0.873 | - - - | 0.555 | 1.71 | 1.64 | 1.6 | 1.49 | 1.52 | 1.59 | 22.63 | 23.32 | 24.58 | 0 | - - - | - - - | - - - | - - - | 24041 | 22340 | 21237 | 67618 | Over-range | 13045 | 10811 | 11871 | 35817 | 5532 | 5250 | 5209 | 16231 | 20286 | 19555 | 17604 | 57445 | 20286 | 19555 | 17604 | 57445 | - - - | - - - | - - - | - - -
5/5/2026 | 4:45:00 PM | 279.15 | 276.43 | 275.06 | 482.5 | 475.8 | 480.39 | 83.9343 | 78.7559 | 75.1576 | 0.6026 | 1.431 | 1.433 | 1.43 | 2.058 | 2.008 | 2.105 | Over-range | 60 | 19476 | 18837 | 16939 | 55252 | - - - | - - - | - - - | - - - | 19476 | 18837 | 16939 | 55252 | 11328 | 9037 | 10230 | 30595 | - - - | - - - | - - - | - - - | 11328 | 9037 | 10230 | 30595 | 23293 | 21624 | 20542 | 65459 | # # # | # # # | # # # | # # # | 0.836 | 0.871 | 0.825 | 0.844 | # # # | # # # | # # # | - - - | 0.863 | 0.9 | 0.854 | 0.873 | - - - | 0.554 | 1.69 | 1.64 | 1.6 | 1.49 | 1.54 | 1.59 | 24.36 | 25.12 | 26.47 | 0 | - - - | - - - | - - - | - - - | 23293 | 21624 | 20542 | 65459 | Over-range | 12759 | 10593 | 11601 | 35040 | 5787 | 5445 | 5392 | 16843 | 19513 | 18913 | 16939 | 55365 | 19513 | 18913 | 16939 | 55365 | - - - | - - - | - - - | - - -
5/5/2026 | 5:00:00 PM | 279.13 | 276.2 | 274.94 | 482.27 | 475.43 | 480.33 | 85.5365 | 80.068 | 76.4528 | 0.6062 | 1.431 | 1.434 | 1.431 | 2.053 | 2.008 | 2.104 | Over-range | 60.01 | 19946 | 19237 | 17307 | 56490 | - - - | - - - | - - - | - - - | 19946 | 19237 | 17307 | 56490 | 11440 | 9069 | 10328 | 30837 | - - - | - - - | - - - | - - - | 11440 | 9069 | 10328 | 30837 | 23754 | 21991 | 20906 | 66651 | # # # | # # # | # # # | # # # | 0.84 | 0.875 | 0.828 | 0.848 | # # # | # # # | # # # | - - - | 0.867 | 0.904 | 0.857 | 0.876 | - - - | 0.546 | 1.7 | 1.68 | 1.62 | 1.5 | 1.57 | 1.61 | 24.26 | 24.98 | 26.36 | 0 | - - - | - - - | - - - | - - - | 23754 | 21991 | 20906 | 66651 | Over-range | 12893 | 10642 | 11719 | 35346 | 5877 | 5505 | 5469 | 17080 | 19989 | 19327 | 17290 | 56606 | 19989 | 19327 | 17290 | 56606 | - - - | - - - | - - - | - - -
5/5/2026 | 5:15:00 PM | 280.46 | 277.65 | 276.32 | 484.65 | 478.02 | 482.61 | 84.9497 | 79.5159 | 75.8953 | 0.6062 | 1.431 | 1.434 | 1.431 | 2.011 | 1.984 | 2.08 | Over-range | 60.02 | 19824 | 19157 | 17190 | 56171 | - - - | - - - | - - - | - - - | 19824 | 19157 | 17190 | 56171 | 11698 | 9298 | 10561 | 31556 | - - - | - - - | - - - | - - - | 11698 | 9298 | 10561 | 31556 | 23702 | 21951 | 20858 | 66511 | # # # | # # # | # # # | # # # | 0.836 | 0.873 | 0.824 | 0.845 | # # # | # # # | # # # | - - - | 0.861 | 0.899 | 0.851 | 0.871 | - - - | 0.562 | 1.68 | 1.65 | 1.61 | 1.5 | 1.54 | 1.6 | 23.03 | 23.75 | 25.09 | 0 | - - - | - - - | - - - | - - - | 23702 | 21951 | 20858 | 66511 | Over-range | 12985 | 10706 | 11802 | 35589 | 5572 | 5250 | 5212 | 16282 | 19876 | 19209 | 17198 | 56284 | 19876 | 19209 | 17198 | 56284 | - - - | - - - | - - - | - - -
5/5/2026 | 5:30:00 PM | 280.42 | 277.53 | 276.29 | 484.54 | 477.84 | 482.56 | 81.9462 | 76.5741 | 73.3773 | 0.6024 | 1.432 | 1.434 | 1.432 | 1.986 | 1.968 | 2.074 | Over-range | 60.01 | 19114 | 18414 | 16582 | 54109 | - - - | - - - | - - - | - - - | 19114 | 18414 | 16582 | 54109 | 11352 | 9090 | 10342 | 30785 | - - - | - - - | - - - | - - - | 11352 | 9090 | 10342 | 30785 | 22870 | 21136 | 20166 | 64172 | # # # | # # # | # # # | # # # | 0.836 | 0.871 | 0.822 | 0.843 | # # # | # # # | # # # | - - - | 0.859 | 0.896 | 0.848 | 0.868 | - - - | 0.569 | 1.65 | 1.64 | 1.6 | 1.48 | 1.53 | 1.58 | 22.4 | 22.91 | 24.32 | 0 | - - - | - - - | - - - | - - - | 22870 | 21136 | 20166 | 64172 | Over-range | 12550 | 10365 | 11466 | 34472 | 5283 | 4916 | 4884 | 15318 | 19107 | 18493 | 16618 | 54217 | 19107 | 18493 | 16618 | 54217 | - - - | - - - | - - - | - - -
5/5/2026 | 5:45:00 PM | 281.1 | 278.26 | 276.94 | 485.79 | 479.05 | 483.67 | 83.6748 | 77.8291 | 74.1961 | 0.6004 | 1.432 | 1.434 | 1.433 | 1.938 | 1.94 | 2.058 | Over-range | 60 | 19455 | 18749 | 16685 | 54889 | - - - | - - - | - - - | - - - | 19455 | 18749 | 16685 | 54889 | 11835 | 9301 | 10698 | 31835 | - - - | - - - | - - - | - - - | 11835 | 9301 | 10698 | 31835 | 23374 | 21500 | 20408 | 65282 | # # # | # # # | # # # | # # # | 0.832 | 0.872 | 0.818 | 0.841 | # # # | # # # | # # # | - - - | 0.853 | 0.895 | 0.841 | 0.863 | - - - | 0.58 | 1.68 | 1.59 | 1.58 | 1.48 | 1.52 | 1.58 | 21.1 | 21.67 | 23.06 | 0 | - - - | - - - | - - - | - - - | 23374 | 21500 | 20408 | 65282 | Over-range | 12942 | 10500 | 11734 | 35289 | 5146 | 4789 | 4736 | 14983 | 19442 | 18803 | 16748 | 54994 | 19442 | 18803 | 16748 | 54994 | - - - | - - - | - - - | - - -
5/5/2026 | 6:00:00 PM | 281.27 | 278.47 | 277.12 | 486.09 | 479.4 | 483.98 | 82.3298 | 76.7644 | 73.7262 | 0.5984 | 1.432 | 1.434 | 1.433 | 1.926 | 1.942 | 2.058 | Over-range | 60.01 | 19179 | 18446 | 16611 | 54236 | - - - | - - - | - - - | - - - | 19179 | 18446 | 16611 | 54236 | 11641 | 9362 | 10649 | 31651 | - - - | - - - | - - - | - - - | 11641 | 9362 | 10649 | 31651 | 23000 | 21213 | 20291 | 64504 | # # # | # # # | # # # | # # # | 0.834 | 0.87 | 0.819 | 0.841 | # # # | # # # | # # # | - - - | 0.854 | 0.891 | 0.841 | 0.862 | - - - | 0.584 | 1.64 | 1.59 | 1.54 | 1.44 | 1.47 | 1.54 | 20.88 | 21.31 | 22.82 | 0 | - - - | - - - | - - - | - - - | 23000 | 21213 | 20291 | 64504 | Over-range | 12688 | 10461 | 11641 | 34886 | 4961 | 4594 | 4627 | 14444 | 19182 | 18510 | 16646 | 54338 | 19182 | 18510 | 16646 | 54338 | - - - | - - - | - - - | - - -
5/5/2026 | 6:15:00 PM | 282.1 | 279.33 | 278.05 | 487.57 | 480.97 | 485.48 | 83.7241 | 77.4868 | 74.4331 | 0.5996 | 1.432 | 1.432 | 1.432 | 1.882 | 1.912 | 2.046 | Over-range | 60.01 | 19586 | 18760 | 16778 | 55124 | - - - | - - - | - - - | - - - | 19586 | 18760 | 16778 | 55124 | 12089 | 9543 | 11032 | 32664 | - - - | - - - | - - - | - - - | 12089 | 9543 | 11032 | 32664 | 23511 | 21528 | 20592 | 65630 | # # # | # # # | # # # | # # # | 0.833 | 0.871 | 0.815 | 0.84 | # # # | # # # | # # # | - - - | 0.851 | 0.89 | 0.835 | 0.859 | - - - | 0.593 | 1.54 | 1.48 | 1.4 | 1.37 | 1.35 | 1.42 | 19.38 | 19.84 | 21.38 | 0 | - - - | - - - | - - - | - - - | 23511 | 21528 | 20592 | 65630 | Over-range | 13000 | 10548 | 11927 | 35592 | 4705 | 4422 | 4457 | 13923 | 19624 | 18747 | 16844 | 55215 | 19624 | 18747 | 16844 | 55215 | - - - | - - - | - - - | - - -
5/5/2026 | 6:30:00 PM | 282.12 | 279.37 | 277.98 | 487.65 | 480.95 | 485.4 | 81.3223 | 75.4363 | 72.832 | 0.6009 | 1.432 | 1.431 | 1.432 | 1.912 | 1.935 | 2.065 | Over-range | 60 | 18967 | 18143 | 16357 | 53468 | - - - | - - - | - - - | - - - | 18967 | 18143 | 16357 | 53468 | 11745 | 9436 | 10781 | 31963 | - - - | - - - | - - - | - - - | 11745 | 9436 | 10781 | 31963 | 22832 | 20956 | 20139 | 63926 | # # # | # # # | # # # | # # # | 0.831 | 0.866 | 0.812 | 0.836 | # # # | # # # | # # # | - - - | 0.85 | 0.886 | 0.834 | 0.857 | - - - | 0.598 | 1.52 | 1.45 | 1.37 | 1.35 | 1.33 | 1.39 | 20.41 | 20.94 | 22.35 | 0 | - - - | - - - | - - - | - - - | 22832 | 20956 | 20139 | 63926 | Over-range | 12704 | 10478 | 11739 | 35019 | 4770 | 4493 | 4579 | 14117 | 19056 | 18126 | 16376 | 53558 | 19056 | 18126 | 16376 | 53558 | - - - | - - - | - - - | - - -
5/5/2026 | 6:45:00 PM | 282.33 | 279.59 | 278.18 | 488.02 | 481.32 | 485.75 | 82.9667 | 77.0507 | 73.7006 | 0.6027 | 1.432 | 1.431 | 1.431 | 1.86 | 1.899 | 2.044 | Over-range | 59.99 | 19293 | 18576 | 16548 | 54417 | - - - | - - - | - - - | - - - | 19293 | 18576 | 16548 | 54417 | 12090 | 9602 | 10938 | 32630 | - - - | - - - | - - - | - - - | 12090 | 9602 | 10938 | 32630 | 23259 | 21365 | 20348 | 64972 | # # # | # # # | # # # | # # # | 0.83 | 0.87 | 0.813 | 0.838 | # # # | # # # | # # # | - - - | 0.847 | 0.887 | 0.832 | 0.855 | - - - | 0.6 | 1.5 | 1.44 | 1.36 | 1.34 | 1.32 | 1.38 | 18.97 | 19.17 | 20.91 | 0 | - - - | - - - | - - - | - - - | 23259 | 21365 | 20348 | 64972 | Over-range | 12976 | 10529 | 11822 | 35442 | 4600 | 4213 | 4381 | 13530 | 19356 | 18616 | 16521 | 54493 | 19356 | 18616 | 16521 | 54493 | - - - | - - - | - - - | - - -
5/5/2026 | 7:00:00 PM | 282.68 | 279.97 | 278.51 | 488.65 | 481.93 | 486.34 | 81.5706 | 75.5468 | 72.6216 | 0.6039 | 1.432 | 1.43 | 1.43 | 1.868 | 1.911 | 2.056 | Over-range | 60 | 18973 | 18203 | 16269 | 53445 | - - - | - - - | - - - | - - - | 18973 | 18203 | 16269 | 53445 | 11997 | 9608 | 10959 | 32564 | - - - | - - - | - - - | - - - | 11997 | 9608 | 10959 | 32564 | 22944 | 21028 | 20114 | 64086 | # # # | # # # | # # # | # # # | 0.827 | 0.866 | 0.809 | 0.834 | # # # | # # # | # # # | - - - | 0.844 | 0.884 | 0.828 | 0.852 | - - - | 0.609 | 1.49 | 1.41 | 1.29 | 1.31 | 1.27 | 1.34 | 19.46 | 19.62 | 21.29 | 0 | - - - | - - - | - - - | - - - | 22944 | 21028 | 20114 | 64086 | Over-range | 12895 | 10517 | 11818 | 35340 | 4642 | 4194 | 4343 | 13488 | 18998 | 18280 | 16245 | 53524 | 18998 | 18280 | 16245 | 53524 | - - - | - - - | - - - | - - -
5/5/2026 | 7:15:00 PM | 282.56 | 279.97 | 278.41 | 488.64 | 481.84 | 486.05 | 82.6121 | 77.024 | 73.4644 | 0.6018 | 1.432 | 1.431 | 1.431 | 1.869 | 1.909 | 2.045 | Over-range | 60 | 19232 | 18611 | 16562 | 54405 | - - - | - - - | - - - | - - - | 19232 | 18611 | 16562 | 54405 | 12127 | 9703 | 10937 | 32766 | - - - | - - - | - - - | - - - | 12127 | 9703 | 10937 | 32766 | 23216 | 21431 | 20337 | 64984 | # # # | # # # | # # # | # # # | 0.828 | 0.868 | 0.814 | 0.837 | # # # | # # # | # # # | - - - | 0.845 | 0.886 | 0.833 | 0.855 | - - - | 0.602 | 1.47 | 1.39 | 1.27 | 1.3 | 1.24 | 1.31 | 19.11 | 19.33 | 20.94 | 0 | - - - | - - - | - - - | - - - | 23216 | 21431 | 20337 | 64984 | Over-range | 12998 | 10613 | 11789 | 35509 | 4597 | 4224 | 4323 | 13457 | 19276 | 18660 | 16550 | 54485 | 19276 | 18660 | 16550 | 54485 | - - - | - - - | - - - | - - -
5/5/2026 | 7:30:00 PM | 282.95 | 280.44 | 278.83 | 489.39 | 482.61 | 486.74 | 81.4983 | 75.8341 | 72.2504 | 0.5974 | 1.431 | 1.43 | 1.43 | 1.855 | 1.902 | 2.05 | Over-range | 60 | 18851 | 18253 | 16161 | 53265 | - - - | - - - | - - - | - - - | 18851 | 18253 | 16161 | 53265 | 12180 | 9724 | 10957 | 32861 | - - - | - - - | - - - | - - - | 12180 | 9724 | 10957 | 32861 | 22912 | 21103 | 20006 | 64020 | # # # | # # # | # # # | # # # | 0.823 | 0.865 | 0.808 | 0.832 | # # # | # # # | # # # | - - - | 0.839 | 0.882 | 0.826 | 0.849 | - - - | 0.617 | 1.46 | 1.33 | 1.24 | 1.27 | 1.21 | 1.28 | 18.84 | 18.97 | 20.72 | 0 | - - - | - - - | - - - | - - - | 22912 | 21103 | 20006 | 64020 | Over-range | 13015 | 10577 | 11778 | 35484 | 4484 | 4064 | 4228 | 13109 | 18899 | 18307 | 16129 | 53334 | 18899 | 18307 | 16129 | 53334 | - - - | - - - | - - - | - - -
5/5/2026 | 7:45:00 PM | 283.12 | 280.73 | 279.07 | 489.76 | 483.2 | 487.02 | 81.7337 | 76.8532 | 73.1547 | 0.5918 | 1.432 | 1.43 | 1.43 | 1.893 | 1.938 | 2.071 | Over-range | 59.99 | 18983 | 18507 | 16512 | 54003 | - - - | - - - | - - - | - - - | 18983 | 18507 | 16512 | 54003 | 11979 | 9727 | 10799 | 32504 | - - - | - - - | - - - | - - - | 11979 | 9727 | 10799 | 32504 | 22987 | 21407 | 20269 | 64663 | # # # | # # # | # # # | # # # | 0.826 | 0.865 | 0.815 | 0.835 | # # # | # # # | # # # | - - - | 0.845 | 0.885 | 0.835 | 0.855 | - - - | 0.602 | 1.46 | 1.35 | 1.26 | 1.28 | 1.21 | 1.28 | 20.23 | 20.54 | 22.09 | 0 | - - - | - - - | - - - | - - - | 22987 | 21407 | 20269 | 64663 | Over-range | 12951 | 10736 | 11737 | 35518 | 4821 | 4449 | 4506 | 14044 | 18991 | 18591 | 16504 | 54086 | 18991 | 18591 | 16504 | 54086 | - - - | - - - | - - - | - - -
5/5/2026 | 8:00:00 PM | 283.58 | 281.21 | 279.5 | 490.61 | 483.95 | 487.79 | 82.9559 | 77.658 | 73.9542 | 0.5921 | 1.431 | 1.429 | 1.43 | 1.883 | 1.93 | 2.077 | Over-range | 60 | 19273 | 18746 | 16664 | 54684 | - - - | - - - | - - - | - - - | 19273 | 18746 | 16664 | 54684 | 12301 | 9919 | 11077 | 33297 | - - - | - - - | - - - | - - - | 12301 | 9919 | 11077 | 33297 | 23396 | 21699 | 20549 | 65644 | # # # | # # # | # # # | # # # | 0.824 | 0.864 | 0.811 | 0.833 | # # # | # # # | # # # | - - - | 0.842 | 0.883 | 0.831 | 0.852 | - - - | 0.609 | 1.43 | 1.32 | 1.22 | 1.26 | 1.18 | 1.25 | 20.08 | 20.34 | 22.01 | 0 | - - - | - - - | - - - | - - - | 23396 | 21699 | 20549 | 65644 | Over-range | 13257 | 10916 | 12013 | 36289 | 4857 | 4476 | 4567 | 14188 | 19300 | 18813 | 16643 | 54756 | 19300 | 18813 | 16643 | 54756 | - - - | - - - | - - - | - - -
5/5/2026 | 8:15:00 PM | 283.96 | 281.56 | 279.83 | 491.24 | 484.55 | 488.39 | 79.9477 | 74.9554 | 71.7698 | 0.5846 | 1.431 | 1.43 | 1.43 | 1.897 | 1.947 | 2.099 | Over-range | 60 | 18540 | 17995 | 16128 | 52664 | - - - | - - - | - - - | - - - | 18540 | 17995 | 16128 | 52664 | 11838 | 9656 | 10717 | 32212 | - - - | - - - | - - - | - - - | 11838 | 9656 | 10717 | 32212 | 22523 | 20914 | 19918 | 63355 | # # # | # # # | # # # | # # # | 0.823 | 0.861 | 0.81 | 0.831 | # # # | # # # | # # # | - - - | 0.843 | 0.88 | 0.831 | 0.852 | - - - | 0.612 | 1.43 | 1.33 | 1.2 | 1.25 | 1.17 | 1.24 | 20.63 | 20.77 | 22.6 | 0 | - - - | - - - | - - - | - - - | 22523 | 20914 | 19918 | 63355 | Over-range | 12781 | 10641 | 11674 | 35184 | 4713 | 4376 | 4538 | 13873 | 18624 | 18005 | 16108 | 52737 | 18624 | 18005 | 16108 | 52737 | - - - | - - - | - - - | - - -
5/5/2026 | 8:30:00 PM | 283.25 | 280.89 | 279.03 | 490.09 | 483.29 | 487.01 | 83.3023 | 77.9541 | 73.9771 | 0.587 | 1.43 | 1.429 | 1.429 | 1.866 | 1.91 | 2.05 | Over-range | 60 | 19393 | 18907 | 16713 | 55013 | - - - | - - - | - - - | - - - | 19393 | 18907 | 16713 | 55013 | 12407 | 9941 | 11094 | 33442 | - - - | - - - | - - - | - - - | 12407 | 9941 | 11094 | 33442 | 23499 | 21793 | 20545 | 65837 | # # # | # # # | # # # | # # # | 0.825 | 0.868 | 0.814 | 0.836 | # # # | # # # | # # # | - - - | 0.842 | 0.885 | 0.832 | 0.853 | - - - | 0.608 | 1.39 | 1.27 | 1.19 | 1.23 | 1.15 | 1.22 | 19.04 | 19.12 | 20.84 | 0 | - - - | - - - | - - - | - - - | 23499 | 21793 | 20545 | 65837 | Over-range | 13265 | 10828 | 11939 | 36143 | 4629 | 4229 | 4348 | 13527 | 19434 | 18968 | 16681 | 55084 | 19434 | 18968 | 16681 | 55084 | - - - | - - - | - - - | - - -
5/5/2026 | 8:45:00 PM | 283.19 | 280.74 | 278.95 | 489.88 | 483.1 | 486.91 | 81.4023 | 75.9458 | 73.1139 | 0.5838 | 1.431 | 1.429 | 1.429 | 1.89 | 1.944 | 2.071 | Over-range | 60 | 19003 | 18300 | 16465 | 53768 | - - - | - - - | - - - | - - - | 19003 | 18300 | 16465 | 53768 | 11882 | 9680 | 10891 | 32454 | - - - | - - - | - - - | - - - | 11882 | 9680 | 10891 | 32454 | 22952 | 21208 | 20296 | 64456 | # # # | # # # | # # # | # # # | 0.828 | 0.863 | 0.811 | 0.834 | # # # | # # # | # # # | - - - | 0.847 | 0.883 | 0.832 | 0.854 | - - - | 0.604 | 1.42 | 1.3 | 1.18 | 1.24 | 1.16 | 1.23 | 20.12 | 20.44 | 22.02 | 0 | - - - | - - - | - - - | - - - | 22952 | 21208 | 20296 | 64456 | Over-range | 12856 | 10692 | 11849 | 35491 | 4807 | 4446 | 4577 | 14088 | 19059 | 18346 | 16435 | 53840 | 19059 | 18346 | 16435 | 53840 | - - - | - - - | - - - | - - -
5/5/2026 | 9:00:00 PM | 283.57 | 281.13 | 279.28 | 490.61 | 483.68 | 487.52 | 83.7191 | 78.1415 | 74.5417 | 0.5823 | 1.431 | 1.43 | 1.429 | 1.879 | 1.93 | 2.065 | Over-range | 60.01 | 19614 | 18992 | 16903 | 55508 | - - - | - - - | - - - | - - - | 19614 | 18992 | 16903 | 55508 | 12223 | 9806 | 11049 | 33078 | - - - | - - - | - - - | - - - | 12223 | 9806 | 11049 | 33078 | 23634 | 21854 | 20721 | 66208 | # # # | # # # | # # # | # # # | 0.83 | 0.869 | 0.816 | 0.838 | # # # | # # # | # # # | - - - | 0.848 | 0.888 | 0.835 | 0.857 | - - - | 0.596 | 1.43 | 1.33 | 1.2 | 1.27 | 1.18 | 1.26 | 19.81 | 20.09 | 21.72 | 0 | - - - | - - - | - - - | - - - | 23634 | 21854 | 20721 | 66208 | Over-range | 13179 | 10802 | 11976 | 36065 | 4852 | 4460 | 4549 | 14163 | 19649 | 19063 | 16876 | 55587 | 19649 | 19063 | 16876 | 55587 | - - - | - - - | - - - | - - -
5/5/2026 | 9:15:00 PM | 283.7 | 281.34 | 279.47 | 490.87 | 484.1 | 487.76 | 81.251 | 75.971 | 72.6066 | 0.5763 | 1.43 | 1.428 | 1.428 | 1.892 | 1.932 | 2.071 | Over-range | 60 | 18917 | 18348 | 16358 | 53623 | - - - | - - - | - - - | - - - | 18917 | 18348 | 16358 | 53623 | 12041 | 9724 | 10932 | 32697 | - - - | - - - | - - - | - - - | 12041 | 9724 | 10932 | 32697 | 22929 | 21239 | 20174 | 64343 | # # # | # # # | # # # | # # # | 0.825 | 0.864 | 0.811 | 0.833 | # # # | # # # | # # # | - - - | 0.842 | 0.883 | 0.831 | 0.852 | - - - | 0.61 | 1.44 | 1.31 | 1.18 | 1.25 | 1.16 | 1.24 | 19.82 | 19.98 | 21.62 | 0 | - - - | - - - | - - - | - - - | 22929 | 21239 | 20174 | 64343 | Over-range | 12951 | 10688 | 11796 | 35535 | 4688 | 4360 | 4353 | 13687 | 18907 | 18360 | 16423 | 53690 | 18907 | 18360 | 16423 | 53690 | - - - | - - - | - - - | - - -
5/5/2026 | 9:30:00 PM | 284.03 | 281.63 | 279.86 | 491.32 | 484.72 | 488.41 | 82.0048 | 76.5761 | 73.2622 | 0.5774 | 1.431 | 1.429 | 1.428 | 1.873 | 1.917 | 2.061 | Over-range | 60.01 | 19148 | 18541 | 16549 | 54238 | - - - | - - - | - - - | - - - | 19148 | 18541 | 16549 | 54238 | 12134 | 9781 | 11045 | 32960 | - - - | - - - | - - - | - - - | 12134 | 9781 | 11045 | 32960 | 23151 | 21414 | 20372 | 64937 | # # # | # # # | # # # | # # # | 0.827 | 0.866 | 0.812 | 0.835 | # # # | # # # | # # # | - - - | 0.843 | 0.883 | 0.832 | 0.853 | - - - | 0.608 | 1.43 | 1.3 | 1.18 | 1.25 | 1.16 | 1.23 | 19.23 | 19.37 | 21.01 | 0 | - - - | - - - | - - - | - - - | 23151 | 21414 | 20372 | 64937 | Over-range | 13005 | 10699 | 11869 | 35676 | 4596 | 4259 | 4265 | 13425 | 19131 | 18566 | 16613 | 54310 | 19131 | 18566 | 16613 | 54310 | - - - | - - - | - - - | - - -
5/5/2026 | 9:45:00 PM | 284.41 | 282.06 | 280.29 | 492.08 | 485.45 | 489.09 | 81.9413 | 76.2685 | 73.0693 | 0.5786 | 1.43 | 1.427 | 1.427 | 1.859 | 1.896 | 2.05 | Over-range | 60.01 | 19083 | 18442 | 16427 | 53953 | - - - | - - - | - - - | - - - | 19083 | 18442 | 16427 | 53953 | 12316 | 9907 | 11191 | 33414 | - - - | - - - | - - - | - - - | 12316 | 9907 | 11191 | 33414 | 23178 | 21373 | 20358 | 64909 | # # # | # # # | # # # | # # # | 0.823 | 0.863 | 0.807 | 0.831 | # # # | # # # | # # # | - - - | 0.839 | 0.879 | 0.825 | 0.848 | - - - | 0.619 | 1.45 | 1.31 | 1.17 | 1.25 | 1.16 | 1.23 | 18.63 | 18.73 | 20.44 | 0 | - - - | - - - | - - - | - - - | 23178 | 21373 | 20358 | 64909 | Over-range | 13141 | 10783 | 12010 | 36043 | 4471 | 4154 | 4255 | 13209 | 19129 | 18428 | 16453 | 54010 | 19129 | 18428 | 16453 | 54010 | - - - | - - - | - - - | - - -
5/5/2026 | 10:00:00 PM | 284.55 | 282.18 | 280.45 | 492.26 | 485.72 | 489.38 | 79.5046 | 73.7785 | 71.0742 | 0.5736 | 1.431 | 1.428 | 1.428 | 1.848 | 1.89 | 2.042 | Over-range | 60.01 | 18534 | 17823 | 15953 | 52309 | - - - | - - - | - - - | - - - | 18534 | 17823 | 15953 | 52309 | 11994 | 9700 | 10986 | 32680 | - - - | - - - | - - - | - - - | 11994 | 9700 | 10986 | 32680 | 22494 | 20678 | 19809 | 62981 | # # # | # # # | # # # | # # # | 0.824 | 0.862 | 0.805 | 0.831 | # # # | # # # | # # # | - - - | 0.839 | 0.877 | 0.822 | 0.846 | - - - | 0.625 | 1.45 | 1.3 | 1.2 | 1.26 | 1.18 | 1.24 | 18.24 | 18.23 | 19.97 | 0 | - - - | - - - | - - - | - - - | 22494 | 20678 | 19809 | 62981 | Over-range | 12740 | 10473 | 11733 | 35050 | 4206 | 3866 | 4032 | 12419 | 18595 | 17814 | 15957 | 52366 | 18595 | 17814 | 15957 | 52366 | - - - | - - - | - - - | - - -
5/5/2026 | 10:15:00 PM | 284.52 | 282.08 | 280.28 | 492.2 | 485.41 | 489.22 | 81.6035 | 75.4584 | 72.1401 | 0.5769 | 1.431 | 1.428 | 1.429 | 1.842 | 1.88 | 2.024 | Over-range | 60.01 | 19003 | 18305 | 16166 | 53474 | - - - | - - - | - - - | - - - | 19003 | 18305 | 16166 | 53474 | 12340 | 9768 | 11203 | 33311 | - - - | - - - | - - - | - - - | 12340 | 9768 | 11203 | 33311 | 23088 | 21144 | 20093 | 64325 | # # # | # # # | # # # | # # # | 0.823 | 0.866 | 0.805 | 0.831 | # # # | # # # | # # # | - - - | 0.837 | 0.881 | 0.821 | 0.847 | - - - | 0.623 | 1.48 | 1.3 | 1.24 | 1.29 | 1.21 | 1.28 | 17.89 | 18 | 19.64 | 0 | - - - | - - - | - - - | - - - | 23088 | 21144 | 20093 | 64325 | Over-range | 13106 | 10570 | 11922 | 35724 | 4309 | 3940 | 3973 | 12615 | 18989 | 18324 | 16219 | 53532 | 18989 | 18324 | 16219 | 53532 | - - - | - - - | - - - | - - -
5/5/2026 | 10:30:00 PM | 284.63 | 282.14 | 280.35 | 492.35 | 485.47 | 489.42 | 79.743 | 73.7228 | 71.1635 | 0.5766 | 1.431 | 1.428 | 1.428 | 1.85 | 1.9 | 2.048 | Over-range | 60 | 18529 | 17736 | 15872 | 52138 | - - - | - - - | - - - | - - - | 18529 | 17736 | 15872 | 52138 | 11992 | 9698 | 11035 | 32725 | - - - | - - - | - - - | - - - | 11992 | 9698 | 11035 | 32725 | 22514 | 20602 | 19782 | 62898 | # # # | # # # | # # # | # # # | 0.823 | 0.861 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.839 | 0.877 | 0.819 | 0.845 | - - - | 0.628 | 1.46 | 1.31 | 1.21 | 1.27 | 1.19 | 1.26 | 18.77 | 18.68 | 20.48 | 0 | - - - | - - - | - - - | - - - | 22514 | 20602 | 19782 | 62898 | Over-range | 12782 | 10470 | 11794 | 35153 | 4330 | 3858 | 4075 | 12582 | 18561 | 17789 | 15846 | 52196 | 18561 | 17789 | 15846 | 52196 | - - - | - - - | - - - | - - -
5/5/2026 | 10:45:00 PM | 284.66 | 281.99 | 280.3 | 492.27 | 485.23 | 489.45 | 82.6112 | 76.1598 | 72.9278 | 0.5808 | 1.431 | 1.428 | 1.429 | 1.818 | 1.862 | 2.021 | Over-range | 60 | 19276 | 18504 | 16350 | 54131 | - - - | - - - | - - - | - - - | 19276 | 18504 | 16350 | 54131 | 12490 | 9863 | 11303 | 33655 | - - - | - - - | - - - | - - - | 12490 | 9863 | 11303 | 33655 | 23397 | 21346 | 20325 | 65068 | # # # | # # # | # # # | # # # | 0.824 | 0.867 | 0.804 | 0.832 | # # # | # # # | # # # | - - - | 0.838 | 0.881 | 0.82 | 0.847 | - - - | 0.622 | 1.45 | 1.32 | 1.23 | 1.27 | 1.2 | 1.27 | 17.44 | 17.26 | 19.27 | 0 | - - - | - - - | - - - | - - - | 23397 | 21346 | 20325 | 65068 | Over-range | 13244 | 10618 | 12057 | 36053 | 4281 | 3812 | 4082 | 12589 | 19338 | 18533 | 16309 | 54180 | 19338 | 18533 | 16309 | 54180 | - - - | - - - | - - - | - - -
5/5/2026 | 11:00:00 PM | 285.28 | 282.62 | 280.9 | 493.37 | 486.29 | 490.49 | 80.4822 | 74.2172 | 71.2646 | 0.5821 | 1.431 | 1.428 | 1.428 | 1.836 | 1.874 | 2.049 | Over-range | 60.01 | 18744 | 17979 | 15936 | 52659 | - - - | - - - | - - - | - - - | 18744 | 17979 | 15936 | 52659 | 12245 | 9767 | 11155 | 33167 | - - - | - - - | - - - | - - - | 12245 | 9767 | 11155 | 33167 | 22830 | 20833 | 19893 | 63557 | # # # | # # # | # # # | # # # | 0.821 | 0.863 | 0.801 | 0.829 | # # # | # # # | # # # | - - - | 0.836 | 0.878 | 0.817 | 0.844 | - - - | 0.63 | 1.45 | 1.33 | 1.23 | 1.28 | 1.21 | 1.28 | 18.33 | 17.98 | 20.04 | 0 | - - - | - - - | - - - | - - - | 22830 | 20833 | 19893 | 63557 | Over-range | 13027 | 10515 | 11897 | 35562 | 4355 | 3803 | 4046 | 12573 | 18760 | 18043 | 15908 | 52711 | 18760 | 18043 | 15908 | 52711 | - - - | - - - | - - - | - - -
5/5/2026 | 11:15:00 PM | 285.13 | 282.35 | 280.73 | 492.93 | 485.93 | 490.28 | 81.3026 | 74.8366 | 71.7905 | 0.5858 | 1.431 | 1.428 | 1.429 | 1.838 | 1.887 | 2.051 | Over-range | 60 | 18969 | 18169 | 16067 | 53205 | - - - | - - - | - - - | - - - | 18969 | 18169 | 16067 | 53205 | 12300 | 9695 | 11159 | 33154 | - - - | - - - | - - - | - - - | 12300 | 9695 | 11159 | 33154 | 23052 | 20988 | 20027 | 64066 | # # # | # # # | # # # | # # # | 0.823 | 0.866 | 0.802 | 0.831 | # # # | # # # | # # # | - - - | 0.838 | 0.881 | 0.819 | 0.847 | - - - | 0.623 | 1.47 | 1.35 | 1.25 | 1.29 | 1.23 | 1.29 | 18.36 | 18.28 | 20.35 | 0 | - - - | - - - | - - - | - - - | 23052 | 20988 | 20027 | 64066 | Over-range | 13091 | 10494 | 11944 | 35661 | 4381 | 3920 | 4162 | 12856 | 19015 | 18195 | 16047 | 53257 | 19015 | 18195 | 16047 | 53257 | - - - | - - - | - - - | - - -
5/5/2026 | 11:30:00 PM | 285.43 | 282.45 | 280.85 | 493.39 | 485.94 | 490.7 | 80.9609 | 74.0795 | 71.2057 | 0.4638 | 1.431 | 1.429 | 1.427 | 1.824 | 1.838 | 2.01 | Over-range | 60 | 18866 | 17991 | 15853 | 52709 | - - - | - - - | - - - | - - - | 18866 | 17991 | 15853 | 52709 | 12383 | 9638 | 11246 | 33266 | - - - | - - - | - - - | - - - | 12383 | 9638 | 11246 | 33266 | 22981 | 20783 | 19879 | 63644 | # # # | # # # | # # # | # # # | 0.821 | 0.866 | 0.798 | 0.828 | # # # | # # # | # # # | - - - | 0.836 | 0.88 | 0.815 | 0.844 | - - - | 0.631 | 1.58 | 1.46 | 1.37 | 1.4 | 1.38 | 1.42 | 18.03 | 17.9 | 19.93 | 0 | - - - | - - - | - - - | - - - | 22981 | 20783 | 19879 | 63644 | Over-range | 13118 | 10395 | 11984 | 35645 | 4229 | 3807 | 4055 | 12544 | 18934 | 17961 | 15867 | 52763 | 18934 | 17961 | 15867 | 52763 | - - - | - - - | - - - | - - -
5/5/2026 | 11:45:00 PM | 285.36 | 282.37 | 280.76 | 493.27 | 485.79 | 490.55 | 81.4924 | 75.0363 | 72.3275 | 0.249 | 1.432 | 1.431 | 1.427 | 1.83 | 1.834 | 1.965 | Over-range | 60.01 | 19030 | 18198 | 16165 | 53393 | - - - | - - - | - - - | - - - | 19030 | 18198 | 16165 | 53393 | 12340 | 9715 | 11288 | 33344 | - - - | - - - | - - - | - - - | 12340 | 9715 | 11288 | 33344 | 23127 | 21051 | 20189 | 64367 | # # # | # # # | # # # | # # # | 0.823 | 0.865 | 0.801 | 0.83 | # # # | # # # | # # # | - - - | 0.838 | 0.88 | 0.819 | 0.846 | - - - | 0.625 | 1.7 | 1.61 | 1.52 | 1.54 | 1.53 | 1.55 | 18.26 | 18.45 | 20.24 | 0 | - - - | - - - | - - - | - - - | 23127 | 21051 | 20189 | 64367 | Over-range | 13127 | 10556 | 12079 | 35896 | 4350 | 4016 | 4182 | 12962 | 19080 | 18172 | 16203 | 53454 | 19080 | 18172 | 16203 | 53454 | - - - | - - - | - - - | - - -
5/6/2026 | 12:00:00 AM | 285.21 | 282.24 | 280.63 | 492.99 | 485.62 | 490.3 | 83.0346 | 76.4609 | 73.3857 | 0.2503 | 1.431 | 1.431 | 1.426 | 1.823 | 1.829 | 1.949 | Over-range | 60.02 | 19402 | 18604 | 16427 | 54433 | - - - | - - - | - - - | - - - | 19402 | 18604 | 16427 | 54433 | 12623 | 9860 | 11491 | 33973 | - - - | - - - | - - - | - - - | 12623 | 9860 | 11491 | 33973 | 23573 | 21457 | 20487 | 65517 | # # # | # # # | # # # | # # # | 0.823 | 0.867 | 0.802 | 0.831 | # # # | # # # | # # # | - - - | 0.837 | 0.882 | 0.819 | 0.846 | - - - | 0.624 | 1.68 | 1.6 | 1.52 | 1.53 | 1.52 | 1.55 | 17.76 | 18.02 | 19.68 | 0 | - - - | - - - | - - - | - - - | 23573 | 21457 | 20487 | 65517 | Over-range | 13382 | 10677 | 12231 | 36434 | 4340 | 4006 | 4094 | 12887 | 19417 | 18591 | 16482 | 54490 | 19417 | 18591 | 16482 | 54490 | - - - | - - - | - - - | - - -
5/6/2026 | 12:15:00 AM | 285.21 | 282.13 | 280.48 | 492.97 | 485.3 | 490.2 | 80.2351 | 73.6297 | 71.2702 | 0.2468 | 1.43 | 1.429 | 1.425 | 1.843 | 1.843 | 1.985 | Over-range | 59.98 | 18686 | 17779 | 15837 | 52302 | - - - | - - - | - - - | - - - | 18686 | 17779 | 15837 | 52302 | 12093 | 9542 | 11151 | 32786 | - - - | - - - | - - - | - - - | 12093 | 9542 | 11151 | 32786 | 22712 | 20591 | 19836 | 63139 | # # # | # # # | # # # | # # # | 0.823 | 0.864 | 0.798 | 0.828 | # # # | # # # | # # # | - - - | 0.839 | 0.88 | 0.817 | 0.845 | - - - | 0.627 | 1.7 | 1.59 | 1.49 | 1.53 | 1.52 | 1.54 | 18.86 | 18.86 | 20.73 | 0 | - - - | - - - | - - - | - - - | 22712 | 20591 | 19836 | 63139 | Over-range | 12903 | 10371 | 11931 | 35337 | 4382 | 3958 | 4138 | 12871 | 18702 | 17775 | 15881 | 52358 | 18702 | 17775 | 15881 | 52358 | - - - | - - - | - - - | - - -
5/6/2026 | 12:30:00 AM | 285.49 | 282.34 | 280.8 | 493.36 | 485.78 | 490.73 | 83.5431 | 76.2936 | 73.7136 | 0.2521 | 1.43 | 1.429 | 1.425 | 1.822 | 1.82 | 1.959 | Over-range | 60 | 19568 | 18574 | 16442 | 54583 | - - - | - - - | - - - | - - - | 19568 | 18574 | 16442 | 54583 | 12638 | 9857 | 11623 | 34118 | - - - | - - - | - - - | - - - | 12638 | 9857 | 11623 | 34118 | 23720 | 21396 | 20575 | 65690 | # # # | # # # | # # # | # # # | 0.825 | 0.868 | 0.799 | 0.831 | # # # | # # # | # # # | - - - | 0.839 | 0.883 | 0.815 | 0.846 | - - - | 0.625 | 1.68 | 1.59 | 1.52 | 1.53 | 1.53 | 1.54 | 17.7 | 17.74 | 19.58 | 0 | - - - | - - - | - - - | - - - | 23720 | 21396 | 20575 | 65690 | Over-range | 13400 | 10610 | 12358 | 36524 | 4360 | 3833 | 4109 | 12777 | 19585 | 18636 | 16415 | 54636 | 19585 | 18636 | 16415 | 54636 | - - - | - - - | - - - | - - -
5/6/2026 | 12:45:00 AM | 285.9 | 282.88 | 281.26 | 494.18 | 486.71 | 491.42 | 81.1487 | 74.617 | 72.4641 | 0.2503 | 1.43 | 1.429 | 1.425 | 1.851 | 1.848 | 1.978 | Over-range | 60.01 | 18936 | 18007 | 16131 | 53074 | - - - | - - - | - - - | - - - | 18936 | 18007 | 16131 | 53074 | 12256 | 9801 | 11405 | 33463 | - - - | - - - | - - - | - - - | 12256 | 9801 | 11405 | 33463 | 23037 | 20930 | 20231 | 64198 | # # # | # # # | # # # | # # # | 0.822 | 0.86 | 0.797 | 0.827 | # # # | # # # | # # # | - - - | 0.838 | 0.877 | 0.815 | 0.844 | - - - | 0.63 | 1.73 | 1.61 | 1.51 | 1.55 | 1.54 | 1.56 | 18.85 | 18.93 | 20.59 | 0 | - - - | - - - | - - - | - - - | 23037 | 20930 | 20231 | 64198 | Over-range | 13106 | 10648 | 12195 | 36072 | 4521 | 4049 | 4201 | 13141 | 18914 | 18057 | 16157 | 53129 | 18914 | 18057 | 16157 | 53129 | - - - | - - - | - - - | - - -
5/6/2026 | 1:00:00 AM | 285.8 | 282.73 | 281.09 | 493.97 | 486.42 | 491.19 | 82.3262 | 75.747 | 72.8997 | 0.25 | 1.431 | 1.43 | 1.425 | 1.842 | 1.832 | 1.972 | Over-range | 60 | 19276 | 18433 | 16333 | 54042 | - - - | - - - | - - - | - - - | 19276 | 18433 | 16333 | 54042 | 12438 | 9744 | 11370 | 33552 | - - - | - - - | - - - | - - - | 12438 | 9744 | 11370 | 33552 | 23389 | 21266 | 20363 | 65017 | # # # | # # # | # # # | # # # | 0.824 | 0.867 | 0.802 | 0.831 | # # # | # # # | # # # | - - - | 0.839 | 0.882 | 0.82 | 0.847 | - - - | 0.621 | 1.72 | 1.6 | 1.53 | 1.56 | 1.53 | 1.56 | 18.45 | 18.56 | 20.24 | 0 | - - - | - - - | - - - | - - - | 23389 | 21266 | 20363 | 65017 | Over-range | 13238 | 10590 | 12148 | 36116 | 4424 | 4050 | 4177 | 13075 | 19299 | 18415 | 16383 | 54096 | 19299 | 18415 | 16383 | 54096 | - - - | - - - | - - - | - - -
5/6/2026 | 1:15:00 AM | 285.58 | 282.57 | 281.09 | 493.57 | 486.3 | 491.04 | 81.2823 | 74.6958 | 72.3155 | 0.2485 | 1.431 | 1.43 | 1.426 | 1.837 | 1.844 | 1.973 | Over-range | 59.98 | 18981 | 18091 | 16129 | 53201 | - - - | - - - | - - - | - - - | 18981 | 18091 | 16129 | 53201 | 12366 | 9772 | 11384 | 33522 | - - - | - - - | - - - | - - - | 12366 | 9772 | 11384 | 33522 | 23083 | 20963 | 20205 | 64251 | # # # | # # # | # # # | # # # | 0.822 | 0.863 | 0.798 | 0.828 | # # # | # # # | # # # | - - - | 0.837 | 0.878 | 0.816 | 0.844 | - - - | 0.63 | 1.72 | 1.61 | 1.51 | 1.56 | 1.53 | 1.56 | 18.33 | 18.5 | 20.3 | 0 | - - - | - - - | - - - | - - - | 23083 | 20963 | 20205 | 64251 | Over-range | 13128 | 10578 | 12158 | 35997 | 4304 | 3959 | 4176 | 12844 | 19039 | 18051 | 16160 | 53250 | 19039 | 18051 | 16160 | 53250 | - - - | - - - | - - - | - - -
5/6/2026 | 1:30:00 AM | 285.64 | 282.54 | 281.08 | 493.62 | 486.23 | 491.1 | 81.1722 | 74.4767 | 72.2184 | 0.2485 | 1.43 | 1.429 | 1.425 | 1.831 | 1.833 | 1.975 | Over-range | 60.01 | 18990 | 18055 | 16124 | 53170 | - - - | - - - | - - - | - - - | 18990 | 18055 | 16124 | 53170 | 12259 | 9697 | 11363 | 33318 | - - - | - - - | - - - | - - - | 12259 | 9697 | 11363 | 33318 | 23035 | 20881 | 20162 | 64078 | # # # | # # # | # # # | # # # | 0.824 | 0.865 | 0.8 | 0.83 | # # # | # # # | # # # | - - - | 0.839 | 0.88 | 0.817 | 0.846 | - - - | 0.627 | 1.72 | 1.59 | 1.52 | 1.55 | 1.53 | 1.55 | 18.27 | 18.23 | 20.11 | 0 | - - - | - - - | - - - | - - - | 23035 | 20881 | 20162 | 64078 | Over-range | 13031 | 10478 | 12095 | 35738 | 4324 | 3881 | 4055 | 12668 | 18970 | 18068 | 16184 | 53222 | 18970 | 18068 | 16184 | 53222 | - - - | - - - | - - - | - - -
5/6/2026 | 1:45:00 AM | 285.9 | 282.7 | 281.29 | 493.95 | 486.56 | 491.52 | 81.8123 | 74.7496 | 72.3822 | 0.2501 | 1.43 | 1.429 | 1.425 | 1.82 | 1.829 | 1.964 | Over-range | 60.01 | 19085 | 18110 | 16064 | 53259 | - - - | - - - | - - - | - - - | 19085 | 18110 | 16064 | 53259 | 12473 | 9762 | 11530 | 33765 | - - - | - - - | - - - | - - - | 12473 | 9762 | 11530 | 33765 | 23240 | 20967 | 20218 | 64425 | # # # | # # # | # # # | # # # | 0.821 | 0.864 | 0.795 | 0.827 | # # # | # # # | # # # | - - - | 0.835 | 0.879 | 0.811 | 0.842 | - - - | 0.634 | 1.75 | 1.62 | 1.54 | 1.57 | 1.56 | 1.58 | 17.81 | 17.93 | 19.82 | 0 | - - - | - - - | - - - | - - - | 23240 | 20967 | 20218 | 64425 | Over-range | 13248 | 10544 | 12261 | 36203 | 4334 | 3863 | 4047 | 12711 | 19053 | 18148 | 16104 | 53305 | 19053 | 18148 | 16104 | 53305 | - - - | - - - | - - - | - - -
5/6/2026 | 2:00:00 AM | 285.92 | 282.76 | 281.32 | 494.09 | 486.59 | 491.56 | 80.7699 | 73.6977 | 71.7593 | 0.2474 | 1.431 | 1.43 | 1.426 | 1.821 | 1.825 | 1.964 | Over-range | 60.01 | 18892 | 17866 | 15952 | 52710 | - - - | - - - | - - - | - - - | 18892 | 17866 | 15952 | 52710 | 12364 | 9758 | 11459 | 33581 | - - - | - - - | - - - | - - - | 12364 | 9758 | 11459 | 33581 | 22980 | 20720 | 20082 | 63783 | # # # | # # # | # # # | # # # | 0.822 | 0.862 | 0.794 | 0.826 | # # # | # # # | # # # | - - - | 0.837 | 0.876 | 0.811 | 0.841 | - - - | 0.637 | 1.77 | 1.63 | 1.56 | 1.59 | 1.58 | 1.6 | 17.76 | 17.8 | 19.72 | 0 | - - - | - - - | - - - | - - - | 22980 | 20720 | 20082 | 63783 | Over-range | 13078 | 10483 | 12191 | 35892 | 4166 | 3745 | 4077 | 12419 | 18966 | 17852 | 15942 | 52760 | 18966 | 17852 | 15942 | 52760 | - - - | - - - | - - - | - - -
5/6/2026 | 2:15:00 AM | 285.94 | 282.8 | 281.29 | 494.16 | 486.58 | 491.54 | 83.0096 | 75.8038 | 73.033 | 0.2493 | 1.431 | 1.431 | 1.427 | 1.802 | 1.807 | 1.948 | Over-range | 60 | 19421 | 18479 | 16281 | 54181 | - - - | - - - | - - - | - - - | 19421 | 18479 | 16281 | 54181 | 12694 | 9861 | 11602 | 34158 | - - - | - - - | - - - | - - - | 12694 | 9861 | 11602 | 34158 | 23606 | 21294 | 20420 | 65320 | # # # | # # # | # # # | # # # | 0.823 | 0.868 | 0.797 | 0.83 | # # # | # # # | # # # | - - - | 0.836 | 0.881 | 0.812 | 0.843 | - - - | 0.63 | 1.76 | 1.66 | 1.63 | 1.62 | 1.62 | 1.64 | 17.19 | 17.18 | 19.14 | 0 | - - - | - - - | - - - | - - - | 23606 | 21294 | 20420 | 65320 | Over-range | 13412 | 10570 | 12313 | 36457 | 4222 | 3704 | 4028 | 12457 | 19457 | 18525 | 16241 | 54224 | 19457 | 18525 | 16241 | 54224 | - - - | - - - | - - - | - - -
5/6/2026 | 2:30:00 AM | 286.05 | 282.84 | 281.41 | 494.21 | 486.76 | 491.78 | 80.8193 | 73.6182 | 71.9478 | 0.2464 | 1.431 | 1.43 | 1.427 | 1.821 | 1.839 | 1.969 | Over-range | 60 | 18860 | 17763 | 15914 | 52537 | - - - | - - - | - - - | - - - | 18860 | 17763 | 15914 | 52537 | 12319 | 9744 | 11497 | 33561 | - - - | - - - | - - - | - - - | 12319 | 9744 | 11497 | 33561 | 22948 | 20641 | 20094 | 63683 | # # # | # # # | # # # | # # # | 0.822 | 0.861 | 0.792 | 0.825 | # # # | # # # | # # # | - - - | 0.837 | 0.875 | 0.809 | 0.841 | - - - | 0.639 | 1.76 | 1.67 | 1.62 | 1.61 | 1.62 | 1.64 | 18.1 | 18.25 | 20.16 | 0 | - - - | - - - | - - - | - - - | 22948 | 20641 | 20094 | 63683 | Over-range | 13066 | 10500 | 12256 | 35961 | 4235 | 3805 | 4138 | 12605 | 18922 | 17760 | 15903 | 52585 | 18922 | 17760 | 15903 | 52585 | - - - | - - - | - - - | - - -
5/6/2026 | 2:45:00 AM | 286.09 | 282.89 | 281.41 | 494.33 | 486.79 | 491.8 | 82.3063 | 75.095 | 72.5085 | 0.2485 | 1.431 | 1.43 | 1.427 | 1.81 | 1.815 | 1.964 | Over-range | 60.01 | 19233 | 18259 | 16126 | 53618 | - - - | - - - | - - - | - - - | 19233 | 18259 | 16126 | 53618 | 12538 | 9749 | 11500 | 33788 | - - - | - - - | - - - | - - - | 12538 | 9749 | 11500 | 33788 | 23390 | 21073 | 20261 | 64724 | # # # | # # # | # # # | # # # | 0.822 | 0.867 | 0.796 | 0.828 | # # # | # # # | # # # | - - - | 0.836 | 0.881 | 0.812 | 0.843 | - - - | 0.63 | 1.79 | 1.7 | 1.66 | 1.64 | 1.66 | 1.67 | 17.63 | 17.6 | 19.62 | 0 | - - - | - - - | - - - | - - - | 23390 | 21073 | 20261 | 64724 | Over-range | 13297 | 10499 | 12252 | 36207 | 4305 | 3781 | 4108 | 12684 | 19267 | 18305 | 16094 | 53665 | 19267 | 18305 | 16094 | 53665 | - - - | - - - | - - - | - - -
5/6/2026 | 3:00:00 AM | 286.14 | 282.88 | 281.47 | 494.36 | 486.8 | 491.93 | 81.6342 | 74.2207 | 71.9827 | 0.2466 | 1.431 | 1.431 | 1.427 | 1.79 | 1.8 | 1.959 | Over-range | 60.01 | 19048 | 18028 | 15946 | 53022 | - - - | - - - | - - - | - - - | 19048 | 18028 | 15946 | 53022 | 12661 | 9867 | 11641 | 34169 | - - - | - - - | - - - | - - - | 12661 | 9867 | 11641 | 34169 | 23244 | 20872 | 20152 | 64268 | # # # | # # # | # # # | # # # | 0.82 | 0.864 | 0.791 | 0.825 | # # # | # # # | # # # | - - - | 0.833 | 0.876 | 0.806 | 0.839 | - - - | 0.644 | 1.81 | 1.73 | 1.67 | 1.65 | 1.68 | 1.69 | 16.94 | 16.74 | 18.9 | 0 | - - - | - - - | - - - | - - - | 23244 | 20872 | 20152 | 64268 | Over-range | 13315 | 10507 | 12311 | 36293 | 4033 | 3530 | 3928 | 12002 | 19117 | 18032 | 15921 | 53069 | 19117 | 18032 | 15921 | 53069 | - - - | - - - | - - - | - - -
5/6/2026 | 3:15:00 AM | 285.78 | 282.55 | 281.1 | 493.74 | 486.22 | 491.28 | 81.2491 | 74.0096 | 71.5079 | 0.2444 | 1.431 | 1.43 | 1.428 | 1.802 | 1.803 | 1.966 | Over-range | 60 | 18955 | 17989 | 15867 | 52811 | - - - | - - - | - - - | - - - | 18955 | 17989 | 15867 | 52811 | 12512 | 9707 | 11448 | 33666 | - - - | - - - | - - - | - - - | 12512 | 9707 | 11448 | 33666 | 23092 | 20773 | 19981 | 63846 | # # # | # # # | # # # | # # # | 0.821 | 0.866 | 0.794 | 0.827 | # # # | # # # | # # # | - - - | 0.835 | 0.879 | 0.809 | 0.841 | - - - | 0.637 | 1.79 | 1.74 | 1.69 | 1.65 | 1.69 | 1.69 | 17.11 | 16.88 | 19.03 | 0 | - - - | - - - | - - - | - - - | 23092 | 20773 | 19981 | 63846 | Over-range | 13182 | 10373 | 12133 | 35849 | 4052 | 3568 | 3932 | 12062 | 19021 | 17992 | 15839 | 52852 | 19021 | 17992 | 15839 | 52852 | - - - | - - - | - - - | - - -
5/6/2026 | 3:30:00 AM | 286.1 | 282.9 | 281.46 | 494.3 | 486.87 | 491.86 | 81.2708 | 74.0572 | 71.5335 | 0.2456 | 1.431 | 1.431 | 1.428 | 1.795 | 1.802 | 1.958 | Over-range | 60.01 | 18925 | 17975 | 15845 | 52745 | - - - | - - - | - - - | - - - | 18925 | 17975 | 15845 | 52745 | 12589 | 9760 | 11508 | 33857 | - - - | - - - | - - - | - - - | 12589 | 9760 | 11508 | 33857 | 23102 | 20790 | 19997 | 63889 | # # # | # # # | # # # | # # # | 0.819 | 0.865 | 0.792 | 0.826 | # # # | # # # | # # # | - - - | 0.833 | 0.877 | 0.808 | 0.839 | - - - | 0.642 | 1.84 | 1.75 | 1.72 | 1.67 | 1.72 | 1.73 | 16.91 | 16.81 | 18.86 | 0 | - - - | - - - | - - - | - - - | 23102 | 20790 | 19997 | 63889 | Over-range | 13242 | 10433 | 12186 | 36022 | 3984 | 3576 | 3903 | 11983 | 19002 | 17942 | 15842 | 52786 | 19002 | 17942 | 15842 | 52786 | - - - | - - - | - - - | - - -
5/6/2026 | 3:45:00 AM | 286.24 | 283.04 | 281.66 | 494.53 | 487.15 | 492.18 | 81.7702 | 74.8817 | 72.359 | 0.2463 | 1.431 | 1.431 | 1.429 | 1.802 | 1.816 | 1.955 | Over-range | 60 | 19126 | 18205 | 16144 | 53474 | - - - | - - - | - - - | - - - | 19126 | 18205 | 16144 | 53474 | 12566 | 9828 | 11528 | 33921 | - - - | - - - | - - - | - - - | 12566 | 9828 | 11528 | 33921 | 23281 | 21053 | 20262 | 64596 | # # # | # # # | # # # | # # # | 0.822 | 0.865 | 0.797 | 0.828 | # # # | # # # | # # # | - - - | 0.835 | 0.878 | 0.813 | 0.842 | - - - | 0.634 | 1.86 | 1.77 | 1.71 | 1.68 | 1.73 | 1.73 | 17.2 | 17.18 | 19.17 | 0 | - - - | - - - | - - - | - - - | 23281 | 21053 | 20262 | 64596 | Over-range | 13260 | 10550 | 12228 | 36186 | 4124 | 3739 | 3983 | 12321 | 19166 | 18178 | 16177 | 53521 | 19166 | 18178 | 16177 | 53521 | - - - | - - - | - - - | - - -
5/6/2026 | 4:00:00 AM | 286.23 | 283.09 | 281.64 | 494.58 | 487.19 | 492.13 | 82.5909 | 75.4283 | 72.9299 | 0.2467 | 1.431 | 1.43 | 1.429 | 1.808 | 1.83 | 1.959 | Over-range | 60.01 | 19284 | 18320 | 16208 | 53812 | - - - | - - - | - - - | - - - | 19284 | 18320 | 16208 | 53812 | 12698 | 9889 | 11687 | 34274 | - - - | - - - | - - - | - - - | 12698 | 9889 | 11687 | 34274 | 23502 | 21205 | 20414 | 65121 | # # # | # # # | # # # | # # # | 0.821 | 0.864 | 0.794 | 0.826 | # # # | # # # | # # # | - - - | 0.834 | 0.878 | 0.811 | 0.841 | - - - | 0.637 | 1.85 | 1.75 | 1.75 | 1.68 | 1.73 | 1.74 | 17.54 | 17.81 | 19.56 | 0 | - - - | - - - | - - - | - - - | 23502 | 21205 | 20414 | 65121 | Over-range | 13427 | 10666 | 12400 | 36647 | 4255 | 3897 | 4038 | 12676 | 19281 | 18305 | 16268 | 53854 | 19281 | 18305 | 16268 | 53854 | - - - | - - - | - - - | - - -
5/6/2026 | 4:15:00 AM | 286.01 | 282.91 | 281.49 | 494.17 | 486.99 | 491.78 | 81.3016 | 74.574 | 72.6738 | 0.2473 | 1.431 | 1.432 | 1.43 | 1.796 | 1.829 | 1.949 | Over-range | 60 | 19024 | 18028 | 16190 | 53243 | - - - | - - - | - - - | - - - | 19024 | 18028 | 16190 | 53243 | 12343 | 9837 | 11492 | 33672 | - - - | - - - | - - - | - - - | 12343 | 9837 | 11492 | 33672 | 23077 | 20910 | 20295 | 64282 | # # # | # # # | # # # | # # # | 0.824 | 0.862 | 0.798 | 0.828 | # # # | # # # | # # # | - - - | 0.839 | 0.876 | 0.814 | 0.843 | - - - | 0.632 | 1.91 | 1.83 | 1.82 | 1.74 | 1.81 | 1.82 | 17.52 | 17.89 | 19.66 | 0 | - - - | - - - | - - - | - - - | 23077 | 20910 | 20295 | 64282 | Over-range | 13054 | 10578 | 12225 | 35986 | 4135 | 3789 | 4069 | 12397 | 19081 | 18026 | 16190 | 53296 | 19081 | 18026 | 16190 | 53296 | - - - | - - - | - - - | - - -
5/6/2026 | 4:30:00 AM | 285.8 | 282.7 | 281.23 | 493.87 | 486.52 | 491.39 | 83.1089 | 76.0662 | 73.3087 | 0.2464 | 1.431 | 1.431 | 1.43 | 1.788 | 1.812 | 1.937 | Over-range | 60.01 | 19460 | 18542 | 16376 | 54378 | - - - | - - - | - - - | - - - | 19460 | 18542 | 16376 | 54378 | 12699 | 9879 | 11648 | 34225 | - - - | - - - | - - - | - - - | 12699 | 9879 | 11648 | 34225 | 23638 | 21379 | 20508 | 65525 | # # # | # # # | # # # | # # # | 0.823 | 0.867 | 0.799 | 0.83 | # # # | # # # | # # # | - - - | 0.836 | 0.881 | 0.814 | 0.844 | - - - | 0.629 | 1.9 | 1.81 | 1.8 | 1.72 | 1.79 | 1.81 | 17.02 | 17.41 | 19.09 | 0 | - - - | - - - | - - - | - - - | 23638 | 21379 | 20508 | 65525 | Over-range | 13412 | 10633 | 12336 | 36536 | 4209 | 3838 | 3964 | 12504 | 19447 | 18559 | 16427 | 54432 | 19447 | 18559 | 16427 | 54432 | - - - | - - - | - - - | - - -
5/6/2026 | 4:45:00 AM | 285.88 | 282.78 | 281.38 | 493.97 | 486.73 | 491.59 | 80.7553 | 74.3184 | 72.0394 | 0.2431 | 1.431 | 1.432 | 1.431 | 1.809 | 1.844 | 1.944 | Over-range | 60.01 | 18851 | 17958 | 16055 | 52864 | - - - | - - - | - - - | - - - | 18851 | 17958 | 16055 | 52864 | 12289 | 9742 | 11345 | 33376 | - - - | - - - | - - - | - - - | 12289 | 9742 | 11345 | 33376 | 22947 | 20864 | 20138 | 63949 | # # # | # # # | # # # | # # # | 0.822 | 0.861 | 0.797 | 0.827 | # # # | # # # | # # # | - - - | 0.837 | 0.877 | 0.816 | 0.843 | - - - | 0.631 | 1.91 | 1.83 | 1.82 | 1.74 | 1.81 | 1.83 | 18.15 | 18.77 | 20.34 | 0 | - - - | - - - | - - - | - - - | 22947 | 20864 | 20138 | 63949 | Over-range | 13068 | 10600 | 12142 | 35935 | 4324 | 4069 | 4216 | 12998 | 18895 | 17927 | 16100 | 52921 | 18895 | 17927 | 16100 | 52921 | - - - | - - - | - - - | - - -
5/6/2026 | 5:00:00 AM | 285.69 | 282.61 | 281.21 | 493.62 | 486.5 | 491.26 | 82.4977 | 76.1791 | 73.2036 | 0.2464 | 1.432 | 1.432 | 1.431 | 1.818 | 1.855 | 1.948 | Over-range | 60.01 | 19315 | 18516 | 16429 | 54261 | - - - | - - - | - - - | - - - | 19315 | 18516 | 16429 | 54261 | 12375 | 9698 | 11312 | 33385 | - - - | - - - | - - - | - - - | 12375 | 9698 | 11312 | 33385 | 23398 | 21350 | 20429 | 65177 | # # # | # # # | # # # | # # # | 0.826 | 0.867 | 0.804 | 0.833 | # # # | # # # | # # # | - - - | 0.841 | 0.885 | 0.823 | 0.85 | - - - | 0.615 | 1.93 | 1.85 | 1.87 | 1.76 | 1.84 | 1.86 | 18.56 | 19.34 | 20.88 | 0 | - - - | - - - | - - - | - - - | 23398 | 21350 | 20429 | 65177 | Over-range | 13200 | 10614 | 12130 | 36079 | 4481 | 4216 | 4279 | 13387 | 19312 | 18524 | 16489 | 54325 | 19312 | 18524 | 16489 | 54325 | - - - | - - - | - - - | - - -
5/6/2026 | 5:15:00 AM | 285.64 | 282.58 | 281.11 | 493.62 | 486.33 | 491.12 | 82.0217 | 75.7981 | 72.9444 | 0.2469 | 1.432 | 1.432 | 1.432 | 1.817 | 1.85 | 1.923 | Over-range | 60 | 19187 | 18381 | 16354 | 53923 | - - - | - - - | - - - | - - - | 19187 | 18381 | 16354 | 53923 | 12386 | 9772 | 11335 | 33493 | - - - | - - - | - - - | - - - | 12386 | 9772 | 11335 | 33493 | 23276 | 21255 | 20365 | 64896 | # # # | # # # | # # # | # # # | 0.824 | 0.865 | 0.803 | 0.831 | # # # | # # # | # # # | - - - | 0.84 | 0.882 | 0.822 | 0.848 | - - - | 0.621 | 1.94 | 1.86 | 1.88 | 1.77 | 1.85 | 1.88 | 18.25 | 19.19 | 20.44 | 0 | - - - | - - - | - - - | - - - | 23276 | 21255 | 20365 | 64896 | Over-range | 13169 | 10658 | 12123 | 36077 | 4374 | 4168 | 4211 | 13146 | 19217 | 18371 | 16404 | 53992 | 19217 | 18371 | 16404 | 53992 | - - - | - - - | - - - | - - -
5/6/2026 | 5:30:00 AM | 285.34 | 282.24 | 280.9 | 493.03 | 485.84 | 490.74 | 83.4453 | 77.0826 | 74.2848 | 0.2488 | 1.432 | 1.433 | 1.432 | 1.825 | 1.855 | 1.911 | Over-range | 60.01 | 19655 | 18796 | 16776 | 55227 | - - - | - - - | - - - | - - - | 19655 | 18796 | 16776 | 55227 | 12444 | 9803 | 11384 | 33631 | - - - | - - - | - - - | - - - | 12444 | 9803 | 11384 | 33631 | 23716 | 21655 | 20776 | 66146 | # # # | # # # | # # # | # # # | 0.829 | 0.868 | 0.808 | 0.835 | # # # | # # # | # # # | - - - | 0.845 | 0.885 | 0.826 | 0.852 | - - - | 0.609 | 1.95 | 1.89 | 1.89 | 1.78 | 1.87 | 1.89 | 18.42 | 19.6 | 20.8 | 0 | - - - | - - - | - - - | - - - | 23716 | 21655 | 20776 | 66146 | Over-range | 13264 | 10744 | 12248 | 36383 | 4516 | 4328 | 4447 | 13674 | 19745 | 18792 | 16769 | 55306 | 19745 | 18792 | 16769 | 55306 | - - - | - - - | - - - | - - -
5/6/2026 | 5:45:00 AM | 285.15 | 282.18 | 280.76 | 492.79 | 485.72 | 490.39 | 82.8366 | 76.4566 | 73.7883 | 0.2482 | 1.433 | 1.433 | 1.433 | 1.835 | 1.851 | 1.905 | Over-range | 60 | 19419 | 18540 | 16563 | 54522 | - - - | - - - | - - - | - - - | 19419 | 18540 | 16563 | 54522 | 12296 | 9739 | 11336 | 33371 | - - - | - - - | - - - | - - - | 12296 | 9739 | 11336 | 33371 | 23478 | 21422 | 20585 | 65485 | # # # | # # # | # # # | # # # | 0.827 | 0.866 | 0.805 | 0.833 | # # # | # # # | # # # | - - - | 0.844 | 0.884 | 0.823 | 0.851 | - - - | 0.612 | 1.99 | 1.93 | 1.96 | 1.82 | 1.91 | 1.94 | 18.74 | 19.92 | 20.94 | 0 | - - - | - - - | - - - | - - - | 23478 | 21422 | 20585 | 65485 | Over-range | 13181 | 10711 | 12208 | 36224 | 4645 | 4366 | 4434 | 13817 | 19449 | 18606 | 16545 | 54600 | 19449 | 18606 | 16545 | 54600 | - - - | - - - | - - - | - - -
5/6/2026 | 6:00:00 AM | 284.69 | 281.73 | 280.35 | 492 | 485 | 489.64 | 82.2752 | 75.9714 | 73.5799 | 0.2471 | 1.433 | 1.434 | 1.433 | 1.841 | 1.842 | 1.881 | Over-range | 60.01 | 19364 | 18452 | 16581 | 54397 | - - - | - - - | - - - | - - - | 19364 | 18452 | 16581 | 54397 | 12085 | 9635 | 11223 | 32943 | - - - | - - - | - - - | - - - | 12085 | 9635 | 11223 | 32943 | 23305 | 21280 | 20515 | 65100 | # # # | # # # | # # # | # # # | 0.831 | 0.867 | 0.808 | 0.836 | # # # | # # # | # # # | - - - | 0.847 | 0.886 | 0.827 | 0.853 | - - - | 0.606 | 2.05 | 2.02 | 2.04 | 1.88 | 1.99 | 2.03 | 18.68 | 19.88 | 20.8 | 0 | - - - | - - - | - - - | - - - | 23305 | 21280 | 20515 | 65100 | Over-range | 12960 | 10587 | 12069 | 35734 | 4586 | 4301 | 4344 | 13577 | 19375 | 18536 | 16575 | 54486 | 19375 | 18536 | 16575 | 54486 | - - - | - - - | - - - | - - -
5/6/2026 | 6:15:00 AM | 284.01 | 281.19 | 279.66 | 490.98 | 483.95 | 488.39 | 82.814 | 76.6116 | 73.4045 | 0.2467 | 1.434 | 1.436 | 1.435 | 1.86 | 1.827 | 1.857 | Over-range | 59.99 | 19388 | 18611 | 16516 | 54516 | - - - | - - - | - - - | - - - | 19388 | 18611 | 16516 | 54516 | 12221 | 9579 | 11176 | 32975 | - - - | - - - | - - - | - - - | 12221 | 9579 | 11176 | 32975 | 23382 | 21393 | 20399 | 65174 | # # # | # # # | # # # | # # # | 0.829 | 0.87 | 0.81 | 0.837 | # # # | # # # | # # # | - - - | 0.845 | 0.889 | 0.828 | 0.854 | - - - | 0.605 | 2.19 | 2.18 | 2.22 | 2.02 | 2.15 | 2.2 | 18.47 | 19.61 | 20.3 | 0 | - - - | - - - | - - - | - - - | 23382 | 21393 | 20399 | 65174 | Over-range | 13064 | 10538 | 11963 | 35693 | 4538 | 4322 | 4193 | 13448 | 19386 | 18651 | 16575 | 54612 | 19386 | 18651 | 16575 | 54612 | - - - | - - - | - - - | - - -
5/6/2026 | 6:30:00 AM | 284.12 | 281.3 | 279.75 | 491.18 | 484.12 | 488.56 | 81.6474 | 76.0477 | 72.9656 | 0.2453 | 1.435 | 1.438 | 1.436 | 1.891 | 1.854 | 1.885 | Over-range | 59.99 | 19110 | 18402 | 16466 | 53978 | - - - | - - - | - - - | - - - | 19110 | 18402 | 16466 | 53978 | 11909 | 9468 | 10906 | 32283 | - - - | - - - | - - - | - - - | 11909 | 9468 | 10906 | 32283 | 23028 | 21212 | 20261 | 64501 | # # # | # # # | # # # | # # # | 0.83 | 0.868 | 0.813 | 0.837 | # # # | # # # | # # # | - - - | 0.848 | 0.888 | 0.834 | 0.857 | - - - | 0.598 | 2.26 | 2.23 | 2.26 | 2.07 | 2.19 | 2.25 | 19.65 | 20.78 | 21.45 | 0 | - - - | - - - | - - - | - - - | 23028 | 21212 | 20261 | 64501 | Over-range | 12841 | 10534 | 11790 | 35271 | 4694 | 4524 | 4382 | 13923 | 19132 | 18405 | 16543 | 54080 | 19132 | 18405 | 16543 | 54080 | - - - | - - - | - - - | - - -
5/6/2026 | 6:45:00 AM | 284.08 | 281.36 | 279.86 | 491.11 | 484.34 | 488.63 | 83.8054 | 78.0164 | 74.5174 | 0.2491 | 1.435 | 1.437 | 1.435 | 1.87 | 1.844 | 1.882 | Over-range | 60 | 19657 | 18989 | 16868 | 55513 | - - - | - - - | - - - | - - - | 19657 | 18989 | 16868 | 55513 | 12220 | 9606 | 11115 | 32941 | - - - | - - - | - - - | - - - | 12220 | 9606 | 11115 | 32941 | 23675 | 21807 | 20724 | 66206 | # # # | # # # | # # # | # # # | 0.83 | 0.871 | 0.814 | 0.839 | # # # | # # # | # # # | - - - | 0.848 | 0.891 | 0.834 | 0.858 | - - - | 0.593 | 2.21 | 2.15 | 2.19 | 2.01 | 2.11 | 2.18 | 19.33 | 20.53 | 21.35 | 0 | - - - | - - - | - - - | - - - | 23675 | 21807 | 20724 | 66206 | Over-range | 13181 | 10700 | 12021 | 36024 | 4845 | 4624 | 4483 | 14314 | 19654 | 19045 | 16923 | 55623 | 19654 | 19045 | 16923 | 55623 | - - - | - - - | - - - | - - -
5/6/2026 | 7:00:00 AM | 284.05 | 281.33 | 279.76 | 491.16 | 484.13 | 488.53 | 80.5402 | 75.418 | 72.2187 | 0.2463 | 1.435 | 1.438 | 1.434 | 1.881 | 1.849 | 1.895 | Over-range | 60.02 | 18815 | 18246 | 16331 | 53391 | - - - | - - - | - - - | - - - | 18815 | 18246 | 16331 | 53391 | 11838 | 9541 | 10772 | 32151 | - - - | - - - | - - - | - - - | 11838 | 9541 | 10772 | 32151 | 22771 | 21105 | 20100 | 63976 | # # # | # # # | # # # | # # # | 0.826 | 0.865 | 0.813 | 0.835 | # # # | # # # | # # # | - - - | 0.846 | 0.886 | 0.833 | 0.855 | - - - | 0.602 | 2.18 | 2.13 | 2.17 | 1.98 | 2.08 | 2.15 | 20.17 | 21.01 | 22.05 | 0 | - - - | - - - | - - - | - - - | 22771 | 21105 | 20100 | 63976 | Over-range | 12818 | 10596 | 11709 | 35219 | 4833 | 4533 | 4510 | 14147 | 18849 | 18328 | 16321 | 53498 | 18849 | 18328 | 16321 | 53498 | - - - | - - - | - - - | - - -
5/6/2026 | 7:15:00 AM | 284.02 | 281.32 | 279.74 | 491.07 | 484.14 | 488.5 | 83.5776 | 78.3429 | 74.536 | 0.2499 | 1.434 | 1.438 | 1.434 | 1.883 | 1.853 | 1.892 | Over-range | 59.99 | 19584 | 19060 | 16949 | 55593 | - - - | - - - | - - - | - - - | 19584 | 19060 | 16949 | 55593 | 12201 | 9707 | 11003 | 32911 | - - - | - - - | - - - | - - - | 12201 | 9707 | 11003 | 32911 | 23623 | 21920 | 20744 | 66287 | # # # | # # # | # # # | # # # | 0.829 | 0.87 | 0.817 | 0.839 | # # # | # # # | # # # | - - - | 0.848 | 0.891 | 0.838 | 0.859 | - - - | 0.592 | 2.19 | 2.15 | 2.16 | 1.99 | 2.08 | 2.16 | 19.99 | 20.96 | 21.94 | 0 | - - - | - - - | - - - | - - - | 23623 | 21920 | 20744 | 66287 | Over-range | 13203 | 10815 | 11952 | 36078 | 4969 | 4698 | 4595 | 14571 | 19601 | 19151 | 16958 | 55709 | 19601 | 19151 | 16958 | 55709 | - - - | - - - | - - - | - - -
5/6/2026 | 7:30:00 AM | 283.67 | 281 | 279.41 | 490.42 | 483.64 | 487.89 | 81.3681 | 76.3151 | 73.0648 | 0.2468 | 1.434 | 1.438 | 1.434 | 1.898 | 1.871 | 1.907 | Over-range | 60.01 | 19003 | 18440 | 16528 | 53972 | - - - | - - - | - - - | - - - | 19003 | 18440 | 16528 | 53972 | 11855 | 9557 | 10814 | 32226 | - - - | - - - | - - - | - - - | 11855 | 9557 | 10814 | 32226 | 22963 | 21317 | 20303 | 64582 | # # # | # # # | # # # | # # # | 0.828 | 0.865 | 0.814 | 0.836 | # # # | # # # | # # # | - - - | 0.848 | 0.888 | 0.836 | 0.857 | - - - | 0.597 | 2.19 | 2.17 | 2.18 | 2 | 2.1 | 2.17 | 20.6 | 21.6 | 22.53 | 0 | - - - | - - - | - - - | - - - | 22963 | 21317 | 20303 | 64582 | Over-range | 12883 | 10683 | 11780 | 35440 | 4968 | 4705 | 4601 | 14540 | 19010 | 18530 | 16543 | 54083 | 19010 | 18530 | 16543 | 54083 | - - - | - - - | - - - | - - -
5/6/2026 | 7:45:00 AM | 283.23 | 280.46 | 279.01 | 489.58 | 482.76 | 487.25 | 83.9108 | 78.6264 | 75.2629 | 0.2489 | 1.434 | 1.438 | 1.433 | 1.912 | 1.882 | 1.917 | Over-range | 60 | 19638 | 19008 | 17062 | 55708 | - - - | - - - | - - - | - - - | 19638 | 19008 | 17062 | 55708 | 11992 | 9577 | 10935 | 32504 | - - - | - - - | - - - | - - - | 11992 | 9577 | 10935 | 32504 | 23618 | 21893 | 20863 | 66373 | # # # | # # # | # # # | # # # | 0.832 | 0.868 | 0.818 | 0.839 | # # # | # # # | # # # | - - - | 0.852 | 0.892 | 0.841 | 0.862 | - - - | 0.584 | 2.18 | 2.13 | 2.17 | 1.98 | 2.09 | 2.15 | 21.08 | 22.25 | 22.98 | 0 | - - - | - - - | - - - | - - - | 23618 | 21893 | 20863 | 66373 | Over-range | 13106 | 10840 | 11989 | 36033 | 5199 | 4998 | 4835 | 15315 | 19656 | 19054 | 17119 | 55828 | 19656 | 19054 | 17119 | 55828 | - - - | - - - | - - - | - - -
5/6/2026 | 8:00:00 AM | 282.55 | 279.84 | 278.41 | 488.38 | 481.73 | 486.17 | 84.0749 | 78.8031 | 75.4691 | 0.2506 | 1.434 | 1.437 | 1.433 | 1.889 | 1.867 | 1.897 | Over-range | 60 | 19660 | 19049 | 17108 | 55817 | - - - | - - - | - - - | - - - | 19660 | 19049 | 17108 | 55817 | 12063 | 9667 | 10971 | 32700 | - - - | - - - | - - - | - - - | 12063 | 9667 | 10971 | 32700 | 23631 | 21919 | 20894 | 66444 | # # # | # # # | # # # | # # # | 0.832 | 0.869 | 0.819 | 0.84 | # # # | # # # | # # # | - - - | 0.852 | 0.891 | 0.84 | 0.861 | - - - | 0.586 | 2.11 | 2.09 | 2.08 | 1.93 | 2.02 | 2.08 | 20.33 | 21.46 | 22.32 | 0 | - - - | - - - | - - - | - - - | 23631 | 21919 | 20894 | 66444 | Over-range | 13103 | 10831 | 11985 | 36017 | 5023 | 4803 | 4738 | 14843 | 19731 | 19097 | 17098 | 55926 | 19731 | 19097 | 17098 | 55926 | - - - | - - - | - - - | - - -
5/6/2026 | 8:15:00 AM | 282.15 | 279.38 | 278.02 | 487.59 | 481.03 | 485.51 | 82.3965 | 76.8722 | 74.4078 | 0.2471 | 1.435 | 1.438 | 1.434 | 1.899 | 1.877 | 1.914 | Over-range | 60.01 | 19359 | 18573 | 16872 | 54804 | - - - | - - - | - - - | - - - | 19359 | 18573 | 16872 | 54804 | 11588 | 9332 | 10766 | 31686 | - - - | - - - | - - - | - - - | 11588 | 9332 | 10766 | 31686 | 23117 | 21344 | 20560 | 65021 | # # # | # # # | # # # | # # # | 0.837 | 0.87 | 0.821 | 0.843 | # # # | # # # | # # # | - - - | 0.857 | 0.893 | 0.843 | 0.865 | - - - | 0.578 | 2.14 | 2.12 | 2.14 | 1.96 | 2.07 | 2.13 | 20.55 | 21.71 | 22.32 | 0 | - - - | - - - | - - - | - - - | 23117 | 21344 | 20560 | 65021 | Over-range | 12624 | 10504 | 11738 | 34959 | 4937 | 4758 | 4605 | 14567 | 19380 | 18593 | 16949 | 54922 | 19380 | 18593 | 16949 | 54922 | - - - | - - - | - - - | - - -
5/6/2026 | 8:30:00 AM | 281.97 | 279.16 | 277.84 | 487.26 | 480.61 | 485.24 | 82.6799 | 77.232 | 73.9469 | 0.2466 | 1.435 | 1.438 | 1.435 | 1.916 | 1.884 | 1.92 | Over-range | 60.01 | 19320 | 18660 | 16726 | 54706 | - - - | - - - | - - - | - - - | 19320 | 18660 | 16726 | 54706 | 11720 | 9297 | 10695 | 31712 | - - - | - - - | - - - | - - - | 11720 | 9297 | 10695 | 31712 | 23199 | 21437 | 20434 | 65069 | # # # | # # # | # # # | # # # | 0.833 | 0.871 | 0.819 | 0.841 | # # # | # # # | # # # | - - - | 0.854 | 0.895 | 0.842 | 0.863 | - - - | 0.58 | 2.16 | 2.14 | 2.15 | 1.97 | 2.08 | 2.15 | 21.16 | 22.31 | 23.04 | 0 | - - - | - - - | - - - | - - - | 23199 | 21437 | 20434 | 65069 | Over-range | 12835 | 10540 | 11728 | 35204 | 5155 | 4895 | 4736 | 15071 | 19322 | 18747 | 16758 | 54827 | 19322 | 18747 | 16758 | 54827 | - - - | - - - | - - - | - - -
5/6/2026 | 8:45:00 AM | 282.02 | 279.2 | 277.8 | 487.41 | 480.57 | 485.24 | 84.7335 | 79.677 | 76.2334 | 0.2504 | 1.434 | 1.438 | 1.435 | 1.94 | 1.913 | 1.94 | Over-range | 60.01 | 19824 | 19213 | 17318 | 56356 | - - - | - - - | - - - | - - - | 19824 | 19213 | 17318 | 56356 | 11793 | 9464 | 10754 | 32011 | - - - | - - - | - - - | - - - | 11793 | 9464 | 10754 | 32011 | 23746 | 22091 | 21039 | 66877 | # # # | # # # | # # # | # # # | 0.835 | 0.87 | 0.823 | 0.843 | # # # | # # # | # # # | - - - | 0.858 | 0.897 | 0.849 | 0.868 | - - - | 0.568 | 2.13 | 2.1 | 2.15 | 1.95 | 2.06 | 2.12 | 22.41 | 23.61 | 24.21 | 0 | - - - | - - - | - - - | - - - | 23746 | 22091 | 21039 | 66877 | Over-range | 13057 | 10880 | 11930 | 35954 | 5513 | 5286 | 5079 | 16125 | 19831 | 19304 | 17355 | 56490 | 19831 | 19304 | 17355 | 56490 | - - - | - - - | - - - | - - -
5/6/2026 | 9:00:00 AM | 281.66 | 278.76 | 277.4 | 486.68 | 479.84 | 484.61 | 85.2438 | 79.8215 | 76.2211 | 0.251 | 1.434 | 1.438 | 1.435 | 1.958 | 1.934 | 1.966 | Over-range | 60.01 | 19958 | 19286 | 17291 | 56535 | - - - | - - - | - - - | - - - | 19958 | 19286 | 17291 | 56535 | 11769 | 9281 | 10699 | 31749 | - - - | - - - | - - - | - - - | 11769 | 9281 | 10699 | 31749 | 23868 | 22103 | 21010 | 66980 | # # # | # # # | # # # | # # # | 0.836 | 0.873 | 0.823 | 0.844 | # # # | # # # | # # # | - - - | 0.86 | 0.901 | 0.85 | 0.87 | - - - | 0.562 | 2.14 | 2.15 | 2.19 | 1.98 | 2.11 | 2.15 | 22.84 | 24.25 | 24.82 | 0 | - - - | - - - | - - - | - - - | 23868 | 22103 | 21010 | 66980 | Over-range | 13082 | 10781 | 11922 | 35884 | 5631 | 5416 | 5185 | 16504 | 19963 | 19375 | 17335 | 56673 | 19963 | 19375 | 17335 | 56673 | - - - | - - - | - - - | - - -
5/6/2026 | 9:15:00 AM | 280.94 | 277.92 | 276.64 | 485.32 | 478.43 | 483.37 | 83.697 | 78.3658 | 75.4338 | 0.2491 | 1.434 | 1.439 | 1.436 | 1.968 | 1.952 | 1.991 | Over-range | 60.01 | 19606 | 18854 | 17093 | 55553 | - - - | - - - | - - - | - - - | 19606 | 18854 | 17093 | 55553 | 11389 | 9101 | 10440 | 30929 | - - - | - - - | - - - | - - - | 11389 | 9101 | 10440 | 30929 | 23392 | 21656 | 20754 | 65801 | # # # | # # # | # # # | # # # | 0.838 | 0.871 | 0.824 | 0.844 | # # # | # # # | # # # | - - - | 0.865 | 0.9 | 0.852 | 0.872 | - - - | 0.557 | 2.16 | 2.17 | 2.22 | 1.99 | 2.14 | 2.18 | 23.7 | 25.07 | 25.76 | 0 | - - - | - - - | - - - | - - - | 23392 | 21656 | 20754 | 65801 | Over-range | 12752 | 10642 | 11761 | 35240 | 5669 | 5457 | 5354 | 16704 | 19705 | 18909 | 17083 | 55697 | 19705 | 18909 | 17083 | 55697 | - - - | - - - | - - - | - - -
5/6/2026 | 9:30:00 AM | 280.63 | 277.5 | 276.35 | 484.69 | 477.73 | 482.94 | 87.0343 | 81.2945 | 77.4063 | 0.2527 | 1.435 | 1.439 | 1.436 | 1.942 | 1.938 | 1.982 | Over-range | 60 | 20406 | 19698 | 17587 | 57691 | - - - | - - - | - - - | - - - | 20406 | 19698 | 17587 | 57691 | 11891 | 9197 | 10702 | 31790 | - - - | - - - | - - - | - - - | 11891 | 9197 | 10702 | 31790 | 24320 | 22448 | 21292 | 68060 | # # # | # # # | # # # | # # # | 0.839 | 0.877 | 0.826 | 0.848 | # # # | # # # | # # # | - - - | 0.864 | 0.905 | 0.854 | 0.874 | - - - | 0.551 | 2.19 | 2.18 | 2.23 | 2 | 2.16 | 2.2 | 22.88 | 24.25 | 25.14 | 0 | - - - | - - - | - - - | - - - | 24320 | 22448 | 21292 | 68060 | Over-range | 13223 | 10755 | 11992 | 36084 | 5728 | 5526 | 5358 | 16917 | 20466 | 19727 | 17642 | 57835 | 20466 | 19727 | 17642 | 57835 | - - - | - - - | - - - | - - -
5/6/2026 | 9:45:00 AM | 279.85 | 276.7 | 275.48 | 483.33 | 476.3 | 481.47 | 83.562 | 78.1814 | 74.7577 | 0.3606 | 1.434 | 1.438 | 1.436 | 1.987 | 1.976 | 2.019 | Over-range | 60.01 | 19460 | 18739 | 16846 | 55045 | - - - | - - - | - - - | - - - | 19460 | 18739 | 16846 | 55045 | 11251 | 8833 | 10225 | 30309 | - - - | - - - | - - - | - - - | 11251 | 8833 | 10225 | 30309 | 23257 | 21497 | 20472 | 65226 | # # # | # # # | # # # | # # # | 0.837 | 0.872 | 0.823 | 0.844 | # # # | # # # | # # # | - - - | 0.864 | 0.903 | 0.854 | 0.874 | - - - | 0.551 | 2.11 | 2.1 | 2.15 | 1.92 | 2.08 | 2.12 | 24.47 | 25.89 | 26.68 | 0 | - - - | - - - | - - - | - - - | 23257 | 21497 | 20472 | 65226 | Over-range | 12720 | 10510 | 11614 | 34937 | 5848 | 5617 | 5426 | 17141 | 19467 | 18806 | 16912 | 55186 | 19467 | 18806 | 16912 | 55186 | - - - | - - - | - - - | - - -
5/6/2026 | 10:00:00 AM | 279.61 | 276.58 | 275.12 | 482.95 | 475.96 | 480.95 | 84.9235 | 79.7695 | 75.2999 | 0.7075 | 1.437 | 1.442 | 1.438 | 2.038 | 2.006 | 2.06 | Over-range | 60.01 | 19801 | 19187 | 17060 | 56047 | - - - | - - - | - - - | - - - | 19801 | 19187 | 17060 | 56047 | 11290 | 8728 | 9972 | 29990 | - - - | - - - | - - - | - - - | 11290 | 8728 | 9972 | 29990 | 23596 | 21911 | 20578 | 66085 | # # # | # # # | # # # | # # # | 0.839 | 0.876 | 0.829 | 0.848 | # # # | # # # | # # # | - - - | 0.869 | 0.909 | 0.863 | 0.88 | - - - | 0.535 | 2.02 | 1.96 | 2.04 | 1.82 | 1.93 | 2.01 | 25.37 | 27.07 | 27.98 | 0 | - - - | - - - | - - - | - - - | 23596 | 21911 | 20578 | 66085 | Over-range | 12826 | 10568 | 11496 | 34983 | 6021 | 5900 | 5659 | 17833 | 19882 | 19205 | 17092 | 56179 | 19882 | 19205 | 17092 | 56179 | - - - | - - - | - - - | - - -
5/6/2026 | 10:15:00 AM | 279.94 | 276.8 | 275.53 | 483.45 | 476.44 | 481.64 | 85.7626 | 80.301 | 76.0288 | 0.8088 | 1.434 | 1.439 | 1.433 | 2.019 | 2.024 | 2.082 | Over-range | 60.02 | 20027 | 19330 | 17214 | 56571 | - - - | - - - | - - - | - - - | 20027 | 19330 | 17214 | 56571 | 11479 | 8901 | 10177 | 30557 | - - - | - - - | - - - | - - - | 11479 | 8901 | 10177 | 30557 | 23877 | 22093 | 20825 | 66794 | # # # | # # # | # # # | # # # | 0.839 | 0.875 | 0.827 | 0.847 | # # # | # # # | # # # | - - - | 0.867 | 0.907 | 0.859 | 0.878 | - - - | 0.54 | 1.98 | 1.98 | 2.02 | 1.8 | 1.94 | 1.98 | 24.97 | 26.59 | 27.93 | 0 | - - - | - - - | - - - | - - - | 23877 | 22093 | 20825 | 66794 | Over-range | 12993 | 10686 | 11709 | 35485 | 6016 | 5848 | 5723 | 17843 | 20119 | 19362 | 17215 | 56696 | 20119 | 19362 | 17215 | 56696 | - - - | - - - | - - - | - - -
5/6/2026 | 10:30:00 AM | 280.9 | 277.86 | 276.63 | 485.16 | 478.36 | 483.4 | 85.5502 | 80.0831 | 76.0499 | 0.8162 | 1.433 | 1.436 | 1.431 | 2.006 | 2.051 | 2.106 | Over-range | 60.01 | 20019 | 19304 | 17245 | 56567 | - - - | - - - | - - - | - - - | 20019 | 19304 | 17245 | 56567 | 11504 | 8997 | 10313 | 30814 | - - - | - - - | - - - | - - - | 11504 | 8997 | 10313 | 30814 | 23884 | 22100 | 20903 | 66887 | # # # | # # # | # # # | # # # | 0.838 | 0.874 | 0.825 | 0.846 | # # # | # # # | # # # | - - - | 0.866 | 0.906 | 0.857 | 0.876 | - - - | 0.545 | 1.96 | 1.93 | 1.95 | 1.76 | 1.88 | 1.92 | 24.77 | 26.26 | 27.65 | 0 | - - - | - - - | - - - | - - - | 23884 | 22100 | 20903 | 66887 | Over-range | 13017 | 10742 | 11797 | 35652 | 6014 | 5800 | 5657 | 17722 | 20015 | 19384 | 17290 | 56689 | 20015 | 19384 | 17290 | 56689 | - - - | - - - | - - - | - - -
5/6/2026 | 10:45:00 AM | 282.08 | 279.04 | 277.93 | 487.13 | 480.58 | 485.56 | 84.8433 | 79.0675 | 75.4715 | 1.0706 | 1.433 | 1.436 | 1.432 | 1.968 | 2.027 | 2.087 | Over-range | 60.01 | 19841 | 19052 | 17052 | 55944 | - - - | - - - | - - - | - - - | 19841 | 19052 | 17052 | 55944 | 11708 | 9209 | 10589 | 31506 | - - - | - - - | - - - | - - - | 11708 | 9209 | 10589 | 31506 | 23777 | 21901 | 20829 | 66507 | # # # | # # # | # # # | # # # | 0.834 | 0.87 | 0.819 | 0.841 | # # # | # # # | # # # | - - - | 0.86 | 0.899 | 0.848 | 0.869 | - - - | 0.563 | 1.97 | 1.92 | 1.93 | 1.77 | 1.85 | 1.92 | 23.43 | 24.84 | 26.24 | 0 | - - - | - - - | - - - | - - - | 23777 | 21901 | 20829 | 66507 | Over-range | 13087 | 10776 | 11943 | 35905 | 5750 | 5510 | 5433 | 16960 | 19857 | 19136 | 17073 | 56066 | 19857 | 19136 | 17073 | 56066 | - - - | - - - | - - - | - - -
5/6/2026 | 11:00:00 AM | 282.02 | 279.05 | 277.87 | 487.15 | 480.49 | 485.44 | 85.5918 | 79.9117 | 75.8054 | 0.8198 | 1.433 | 1.436 | 1.432 | 1.965 | 2.019 | 2.083 | Over-range | 60 | 20103 | 19396 | 17248 | 56747 | - - - | - - - | - - - | - - - | 20103 | 19396 | 17248 | 56747 | 11836 | 9212 | 10587 | 31635 | - - - | - - - | - - - | - - - | 11836 | 9212 | 10587 | 31635 | 24018 | 22170 | 20948 | 67136 | # # # | # # # | # # # | # # # | 0.837 | 0.875 | 0.823 | 0.845 | # # # | # # # | # # # | - - - | 0.861 | 0.903 | 0.852 | 0.872 | - - - | 0.558 | 1.95 | 1.91 | 1.9 | 1.74 | 1.83 | 1.89 | 22.84 | 24.25 | 25.73 | 0 | - - - | - - - | - - - | - - - | 24018 | 22170 | 20948 | 67136 | Over-range | 13136 | 10726 | 11877 | 35847 | 5634 | 5437 | 5323 | 16685 | 20109 | 19451 | 17309 | 56870 | 20109 | 19451 | 17309 | 56870 | - - - | - - - | - - - | - - -
5/6/2026 | 11:15:00 AM | 282.51 | 279.55 | 278.35 | 488.02 | 481.34 | 486.23 | 83.7345 | 78.0721 | 75.0348 | 0.8165 | 1.433 | 1.435 | 1.432 | 1.958 | 2.021 | 2.083 | Over-range | 60.02 | 19684 | 18850 | 17031 | 55565 | - - - | - - - | - - - | - - - | 19684 | 18850 | 17031 | 55565 | 11616 | 9275 | 10623 | 31514 | - - - | - - - | - - - | - - - | 11616 | 9275 | 10623 | 31514 | 23531 | 21698 | 20769 | 65998 | # # # | # # # | # # # | # # # | 0.837 | 0.869 | 0.82 | 0.842 | # # # | # # # | # # # | - - - | 0.86 | 0.896 | 0.848 | 0.868 | - - - | 0.567 | 1.94 | 1.93 | 1.88 | 1.73 | 1.82 | 1.88 | 22.78 | 24.1 | 25.4 | 0 | - - - | - - - | - - - | - - - | 23531 | 21698 | 20769 | 65998 | Over-range | 12887 | 10733 | 11876 | 35584 | 5497 | 5325 | 5228 | 16291 | 19704 | 18867 | 17112 | 55684 | 19704 | 18867 | 17112 | 55684 | - - - | - - - | - - - | - - -
5/6/2026 | 11:30:00 AM | 282.26 | 279.31 | 278.1 | 487.56 | 481.01 | 485.77 | 83.6517 | 78.1443 | 74.8119 | 0.8176 | 1.433 | 1.435 | 1.432 | 1.912 | 1.982 | 2.052 | Over-range | 60 | 19609 | 18865 | 16969 | 55442 | - - - | - - - | - - - | - - - | 19609 | 18865 | 16969 | 55442 | 11774 | 9389 | 10673 | 31837 | - - - | - - - | - - - | - - - | 11774 | 9389 | 10673 | 31837 | 23445 | 21654 | 20648 | 65748 | # # # | # # # | # # # | # # # | 0.836 | 0.871 | 0.822 | 0.843 | # # # | # # # | # # # | - - - | 0.857 | 0.894 | 0.846 | 0.866 | - - - | 0.574 | 1.93 | 1.89 | 1.89 | 1.73 | 1.81 | 1.88 | 20.86 | 21.91 | 23.36 | 0 | - - - | - - - | - - - | - - - | 23445 | 21654 | 20648 | 65748 | Over-range | 12844 | 10617 | 11753 | 35307 | 5038 | 4876 | 4833 | 15013 | 19663 | 18852 | 17032 | 55547 | 19663 | 18852 | 17032 | 55547 | - - - | - - - | - - - | - - -
5/6/2026 | 11:45:00 AM | 281.62 | 278.71 | 277.48 | 486.52 | 479.92 | 484.68 | 85.447 | 79.7292 | 76.2082 | 0.8146 | 1.433 | 1.436 | 1.433 | 1.961 | 2.007 | 2.08 | Over-range | 59.99 | 20091 | 19290 | 17322 | 56704 | - - - | - - - | - - - | - - - | 20091 | 19290 | 17322 | 56704 | 11659 | 9172 | 10557 | 31387 | - - - | - - - | - - - | - - - | 11659 | 9172 | 10557 | 31387 | 23923 | 22074 | 21009 | 67006 | # # # | # # # | # # # | # # # | 0.84 | 0.874 | 0.825 | 0.846 | # # # | # # # | # # # | - - - | 0.864 | 0.902 | 0.853 | 0.873 | - - - | 0.554 | 1.93 | 1.91 | 1.9 | 1.73 | 1.82 | 1.88 | 22.84 | 24.27 | 25.62 | 0 | - - - | - - - | - - - | - - - | 23923 | 22074 | 21009 | 67006 | Over-range | 12967 | 10709 | 11871 | 35646 | 5596 | 5453 | 5350 | 16672 | 20145 | 19286 | 17391 | 56822 | 20145 | 19286 | 17391 | 56822 | - - - | - - - | - - - | - - -
5/6/2026 | 12:00:00 PM | 281.13 | 278.21 | 277.06 | 485.63 | 479.09 | 483.95 | 84.9866 | 79.6022 | 76.4799 | 0.8134 | 1.434 | 1.437 | 1.433 | 1.992 | 2.009 | 2.073 | Over-range | 59.99 | 19961 | 19159 | 17396 | 56517 | - - - | - - - | - - - | - - - | 19961 | 19159 | 17396 | 56517 | 11472 | 9226 | 10499 | 31197 | - - - | - - - | - - - | - - - | 11472 | 9226 | 10499 | 31197 | 23746 | 21994 | 21055 | 66795 | # # # | # # # | # # # | # # # | 0.841 | 0.871 | 0.826 | 0.846 | # # # | # # # | # # # | - - - | 0.866 | 0.9 | 0.856 | 0.874 | - - - | 0.552 | 1.96 | 1.92 | 1.94 | 1.76 | 1.85 | 1.91 | 23.61 | 24.9 | 26.05 | 0 | - - - | - - - | - - - | - - - | 23746 | 21994 | 21055 | 66795 | Over-range | 12855 | 10789 | 11849 | 35572 | 5717 | 5516 | 5417 | 16861 | 19990 | 19194 | 17454 | 56638 | 19990 | 19194 | 17454 | 56638 | - - - | - - - | - - - | - - -
5/6/2026 | 12:15:00 PM | 281.04 | 278.21 | 277 | 485.53 | 479.08 | 483.77 | 85.4846 | 80.1018 | 76.8578 | 0.8147 | 1.435 | 1.437 | 1.434 | 1.971 | 1.996 | 2.069 | Over-range | 60 | 20095 | 19330 | 17506 | 56932 | - - - | - - - | - - - | - - - | 20095 | 19330 | 17506 | 56932 | 11627 | 9362 | 10630 | 31620 | - - - | - - - | - - - | - - - | 11627 | 9362 | 10630 | 31620 | 23916 | 22169 | 21185 | 67271 | # # # | # # # | # # # | # # # | 0.84 | 0.872 | 0.826 | 0.846 | # # # | # # # | # # # | - - - | 0.864 | 0.899 | 0.854 | 0.873 | - - - | 0.555 | 1.94 | 1.89 | 1.9 | 1.74 | 1.82 | 1.89 | 22.83 | 23.96 | 25.28 | 0 | - - - | - - - | - - - | - - - | 23916 | 22169 | 21185 | 67271 | Over-range | 12960 | 10841 | 11919 | 35803 | 5652 | 5400 | 5324 | 16594 | 20091 | 19405 | 17558 | 57054 | 20091 | 19405 | 17558 | 57054 | - - - | - - - | - - - | - - -
5/6/2026 | 12:30:00 PM | 280.54 | 277.74 | 276.5 | 484.67 | 478.29 | 482.89 | 85.1225 | 79.4896 | 75.8318 | 0.8109 | 1.435 | 1.438 | 1.435 | 1.937 | 1.969 | 2.05 | Over-range | 60.01 | 19951 | 19209 | 17213 | 56373 | - - - | - - - | - - - | - - - | 19951 | 19209 | 17213 | 56373 | 11656 | 9191 | 10546 | 31392 | - - - | - - - | - - - | - - - | 11656 | 9191 | 10546 | 31392 | 23738 | 21927 | 20831 | 66496 | # # # | # # # | # # # | # # # | 0.84 | 0.876 | 0.826 | 0.848 | # # # | # # # | # # # | - - - | 0.862 | 0.901 | 0.852 | 0.872 | - - - | 0.557 | 1.99 | 1.95 | 1.94 | 1.79 | 1.86 | 1.93 | 21.72 | 22.89 | 24.25 | 0 | - - - | - - - | - - - | - - - | 23738 | 21927 | 20831 | 66496 | Over-range | 12855 | 10561 | 11718 | 35235 | 5333 | 5123 | 5025 | 15756 | 19962 | 19252 | 17276 | 56490 | 19962 | 19252 | 17276 | 56490 | - - - | - - - | - - - | - - -
5/6/2026 | 12:45:00 PM | 280.75 | 278.07 | 276.76 | 485.18 | 478.81 | 483.26 | 85.8931 | 80.709 | 77.6732 | 0.8072 | 1.436 | 1.439 | 1.436 | 1.971 | 1.977 | 2.045 | Over-range | 60 | 20182 | 19417 | 17693 | 57293 | - - - | - - - | - - - | - - - | 20182 | 19417 | 17693 | 57293 | 11659 | 9485 | 10703 | 31847 | - - - | - - - | - - - | - - - | 11659 | 9485 | 10703 | 31847 | 23995 | 22312 | 21380 | 67687 | # # # | # # # | # # # | # # # | 0.841 | 0.87 | 0.828 | 0.846 | # # # | # # # | # # # | - - - | 0.865 | 0.897 | 0.855 | 0.872 | - - - | 0.556 | 1.97 | 1.97 | 1.98 | 1.82 | 1.89 | 1.96 | 22.56 | 23.77 | 24.76 | 0 | - - - | - - - | - - - | - - - | 23995 | 22312 | 21380 | 67687 | Over-range | 12964 | 10973 | 11989 | 35998 | 5592 | 5449 | 5328 | 16573 | 20238 | 19418 | 17759 | 57415 | 20238 | 19418 | 17759 | 57415 | - - - | - - - | - - - | - - -
5/6/2026 | 1:00:00 PM | 280.71 | 278.11 | 276.73 | 485.18 | 478.85 | 483.17 | 85.7602 | 80.8222 | 76.914 | 0.8014 | 1.437 | 1.441 | 1.438 | 1.988 | 1.966 | 2.038 | Over-range | 60 | 20141 | 19541 | 17586 | 57268 | - - - | - - - | - - - | - - - | 20141 | 19541 | 17586 | 57268 | 11653 | 9328 | 10502 | 31483 | - - - | - - - | - - - | - - - | 11653 | 9328 | 10502 | 31483 | 23965 | 22362 | 21180 | 67508 | # # # | # # # | # # # | # # # | 0.84 | 0.874 | 0.83 | 0.848 | # # # | # # # | # # # | - - - | 0.865 | 0.902 | 0.858 | 0.875 | - - - | 0.55 | 2.06 | 2.01 | 2.02 | 1.86 | 1.92 | 2.01 | 22.81 | 24.06 | 25.02 | 0 | - - - | - - - | - - - | - - - | 23965 | 22362 | 21180 | 67508 | Over-range | 12979 | 10860 | 11793 | 35715 | 5644 | 5501 | 5300 | 16672 | 20172 | 19569 | 17660 | 57401 | 20172 | 19569 | 17660 | 57401 | - - - | - - - | - - - | - - -
5/6/2026 | 1:15:00 PM | 280.31 | 277.6 | 276.29 | 484.33 | 478.04 | 482.48 | 85.6195 | 80.5826 | 77.2269 | 0.8042 | 1.438 | 1.442 | 1.438 | 1.974 | 1.966 | 2.026 | Over-range | 60.01 | 20137 | 19439 | 17648 | 57224 | - - - | - - - | - - - | - - - | 20137 | 19439 | 17648 | 57224 | 11607 | 9407 | 10599 | 31613 | - - - | - - - | - - - | - - - | 11607 | 9407 | 10599 | 31613 | 23904 | 22270 | 21246 | 67420 | # # # | # # # | # # # | # # # | 0.842 | 0.873 | 0.831 | 0.849 | # # # | # # # | # # # | - - - | 0.866 | 0.9 | 0.857 | 0.874 | - - - | 0.552 | 2.07 | 1.99 | 2 | 1.86 | 1.92 | 2.01 | 22.33 | 23.62 | 24.44 | 0 | - - - | - - - | - - - | - - - | 23904 | 22270 | 21246 | 67420 | Over-range | 12875 | 10856 | 11822 | 35628 | 5520 | 5373 | 5187 | 16287 | 20157 | 19480 | 17722 | 57359 | 20157 | 19480 | 17722 | 57359 | - - - | - - - | - - - | - - -
5/6/2026 | 1:30:00 PM | 279.85 | 277.22 | 275.84 | 483.67 | 477.32 | 481.66 | 84.0674 | 79.1662 | 75.8226 | 0.7993 | 1.438 | 1.442 | 1.439 | 1.977 | 1.971 | 2.033 | Over-range | 59.99 | 19676 | 19013 | 17238 | 55927 | - - - | - - - | - - - | - - - | 19676 | 19013 | 17238 | 55927 | 11426 | 9260 | 10391 | 31077 | - - - | - - - | - - - | - - - | 11426 | 9260 | 10391 | 31077 | 23410 | 21822 | 20800 | 66032 | # # # | # # # | # # # | # # # | 0.841 | 0.871 | 0.829 | 0.847 | # # # | # # # | # # # | - - - | 0.864 | 0.898 | 0.856 | 0.873 | - - - | 0.556 | 2.07 | 2.02 | 2.03 | 1.88 | 1.94 | 2.03 | 22.47 | 23.74 | 24.65 | 0 | - - - | - - - | - - - | - - - | 23410 | 21822 | 20800 | 66032 | Over-range | 12676 | 10699 | 11630 | 35077 | 5423 | 5302 | 5161 | 16088 | 19748 | 19018 | 17286 | 56052 | 19748 | 19018 | 17286 | 56052 | - - - | - - - | - - - | - - -
5/6/2026 | 1:45:00 PM | 279.4 | 276.77 | 275.44 | 482.86 | 476.56 | 480.96 | 88.1483 | 83.1784 | 78.9189 | 0.8229 | 1.438 | 1.442 | 1.439 | 2.001 | 1.977 | 2.029 | Over-range | 60 | 20664 | 20071 | 18028 | 58763 | - - - | - - - | - - - | - - - | 20664 | 20071 | 18028 | 58763 | 11742 | 9332 | 10534 | 31609 | - - - | - - - | - - - | - - - | 11742 | 9332 | 10534 | 31609 | 24523 | 22908 | 21634 | 69065 | # # # | # # # | # # # | # # # | 0.843 | 0.876 | 0.833 | 0.851 | # # # | # # # | # # # | - - - | 0.868 | 0.906 | 0.863 | 0.879 | - - - | 0.538 | 2.06 | 2.04 | 2.02 | 1.88 | 1.94 | 2.03 | 23.5 | 24.87 | 25.83 | 0 | - - - | - - - | - - - | - - - | 24523 | 22908 | 21634 | 69065 | Over-range | 13192 | 11024 | 11943 | 36243 | 5944 | 5804 | 5564 | 17545 | 20680 | 20120 | 18105 | 58905 | 20680 | 20120 | 18105 | 58905 | - - - | - - - | - - - | - - -
5/6/2026 | 2:00:00 PM | 279.48 | 276.9 | 275.59 | 482.99 | 476.84 | 481.16 | 84.7304 | 79.4078 | 76.081 | 0.8276 | 1.438 | 1.442 | 1.439 | 1.967 | 1.969 | 2.028 | Over-range | 60 | 19858 | 19114 | 17290 | 56262 | - - - | - - - | - - - | - - - | 19858 | 19114 | 17290 | 56262 | 11434 | 9187 | 10440 | 31061 | - - - | - - - | - - - | - - - | 11434 | 9187 | 10440 | 31061 | 23577 | 21877 | 20866 | 66321 | # # # | # # # | # # # | # # # | 0.842 | 0.874 | 0.829 | 0.848 | # # # | # # # | # # # | - - - | 0.866 | 0.901 | 0.855 | 0.874 | - - - | 0.552 | 2.07 | 2.02 | 2.02 | 1.88 | 1.94 | 2.03 | 22.3 | 23.65 | 24.56 | 0 | - - - | - - - | - - - | - - - | 23577 | 21877 | 20866 | 66321 | Over-range | 12703 | 10629 | 11669 | 35083 | 5462 | 5278 | 5144 | 16108 | 19887 | 19187 | 17320 | 56393 | 19887 | 19187 | 17320 | 56393 | - - - | - - - | - - - | - - -
5/6/2026 | 2:15:00 PM | 279.42 | 276.89 | 275.56 | 482.92 | 476.88 | 481.04 | 86.2562 | 81.0141 | 77.7389 | 0.8268 | 1.438 | 1.442 | 1.439 | 1.938 | 1.95 | 2.001 | Over-range | 60.01 | 20234 | 19505 | 17708 | 57447 | - - - | - - - | - - - | - - - | 20234 | 19505 | 17708 | 57447 | 11718 | 9523 | 10743 | 31984 | - - - | - - - | - - - | - - - | 11718 | 9523 | 10743 | 31984 | 23989 | 22315 | 21316 | 67620 | # # # | # # # | # # # | # # # | 0.844 | 0.874 | 0.831 | 0.85 | # # # | # # # | # # # | - - - | 0.865 | 0.898 | 0.854 | 0.873 | - - - | 0.557 | 2.12 | 2.04 | 2.05 | 1.91 | 1.97 | 2.06 | 21.04 | 22.29 | 23.11 | 0 | - - - | - - - | - - - | - - - | 23989 | 22315 | 21316 | 67620 | Over-range | 12879 | 10828 | 11858 | 35644 | 5271 | 5088 | 4951 | 15531 | 20253 | 19585 | 17734 | 57572 | 20253 | 19585 | 17734 | 57572 | - - - | - - - | - - - | - - -
5/6/2026 | 2:30:00 PM | 279.7 | 277.22 | 275.86 | 483.44 | 477.4 | 481.57 | 84.2343 | 78.8536 | 75.5233 | 0.8184 | 1.439 | 1.443 | 1.44 | 1.943 | 1.964 | 2.01 | Over-range | 60.01 | 19748 | 19006 | 17162 | 55915 | - - - | - - - | - - - | - - - | 19748 | 19006 | 17162 | 55915 | 11459 | 9185 | 10482 | 31127 | - - - | - - - | - - - | - - - | 11459 | 9185 | 10482 | 31127 | 23457 | 21747 | 20732 | 65936 | # # # | # # # | # # # | # # # | 0.842 | 0.874 | 0.828 | 0.848 | # # # | # # # | # # # | - - - | 0.864 | 0.9 | 0.853 | 0.872 | - - - | 0.557 | 2.16 | 2.09 | 2.13 | 1.97 | 2.04 | 2.12 | 21.45 | 22.9 | 23.63 | 0 | - - - | - - - | - - - | - - - | 23457 | 21747 | 20732 | 65936 | Over-range | 12650 | 10555 | 11620 | 34912 | 5281 | 5132 | 4938 | 15592 | 19746 | 19075 | 17223 | 56044 | 19746 | 19075 | 17223 | 56044 | - - - | - - - | - - - | - - -
5/6/2026 | 2:45:00 PM | 279.55 | 277.08 | 275.73 | 483.22 | 477.17 | 481.29 | 86.7506 | 81.6214 | 78.4997 | 0.8204 | 1.439 | 1.444 | 1.44 | 1.97 | 1.974 | 2.001 | Over-range | 60.01 | 20357 | 19607 | 17878 | 57842 | - - - | - - - | - - - | - - - | 20357 | 19607 | 17878 | 57842 | 11663 | 9517 | 10743 | 31923 | - - - | - - - | - - - | - - - | 11663 | 9517 | 10743 | 31923 | 24151 | 22508 | 21546 | 68204 | # # # | # # # | # # # | # # # | 0.843 | 0.871 | 0.83 | 0.848 | # # # | # # # | # # # | - - - | 0.867 | 0.899 | 0.857 | 0.874 | - - - | 0.552 | 2.2 | 2.14 | 2.18 | 2.01 | 2.09 | 2.18 | 22.41 | 23.91 | 24.45 | 0 | - - - | - - - | - - - | - - - | 24151 | 22508 | 21546 | 68204 | Over-range | 12981 | 11035 | 12009 | 36095 | 5634 | 5526 | 5303 | 16663 | 20380 | 19647 | 17954 | 57981 | 20380 | 19647 | 17954 | 57981 | - - - | - - - | - - - | - - -
5/6/2026 | 3:00:00 PM | 279.64 | 277.29 | 275.89 | 483.44 | 477.6 | 481.42 | 86.3779 | 81.4735 | 77.4408 | 0.8182 | 1.439 | 1.444 | 1.441 | 1.963 | 1.974 | 2.006 | Over-range | 60.01 | 20235 | 19660 | 17671 | 57565 | - - - | - - - | - - - | - - - | 20235 | 19660 | 17671 | 57565 | 11671 | 9344 | 10541 | 31556 | - - - | - - - | - - - | - - - | 11671 | 9344 | 10541 | 31556 | 24023 | 22454 | 21240 | 67717 | # # # | # # # | # # # | # # # | 0.842 | 0.876 | 0.832 | 0.85 | # # # | # # # | # # # | - - - | 0.865 | 0.903 | 0.859 | 0.875 | - - - | 0.548 | 2.21 | 2.16 | 2.19 | 2.02 | 2.09 | 2.18 | 22.11 | 23.57 | 24.34 | 0 | - - - | - - - | - - - | - - - | 24023 | 22454 | 21240 | 67717 | Over-range | 12941 | 10834 | 11772 | 35630 | 5520 | 5414 | 5168 | 16338 | 20240 | 19723 | 17741 | 57705 | 20240 | 19723 | 17741 | 57705 | - - - | - - - | - - - | - - -
5/6/2026 | 3:15:00 PM | 279.57 | 277.27 | 275.88 | 483.35 | 477.54 | 481.4 | 84.4721 | 79.4541 | 76.1699 | 0.8167 | 1.439 | 1.444 | 1.441 | 1.936 | 1.965 | 1.997 | Over-range | 60.01 | 19778 | 19112 | 17328 | 56217 | - - - | - - - | - - - | - - - | 19778 | 19112 | 17328 | 56217 | 11570 | 9404 | 10597 | 31571 | - - - | - - - | - - - | - - - | 11570 | 9404 | 10597 | 31571 | 23515 | 21921 | 20916 | 66353 | # # # | # # # | # # # | # # # | 0.841 | 0.872 | 0.828 | 0.847 | # # # | # # # | # # # | - - - | 0.862 | 0.896 | 0.853 | 0.871 | - - - | 0.562 | 2.24 | 2.18 | 2.21 | 2.04 | 2.11 | 2.2 | 21.16 | 22.52 | 23.21 | 0 | - - - | - - - | - - - | - - - | 23515 | 21921 | 20916 | 66353 | Over-range | 12712 | 10724 | 11704 | 35216 | 5198 | 5093 | 4899 | 15411 | 19802 | 19156 | 17394 | 56352 | 19802 | 19156 | 17394 | 56352 | - - - | - - - | - - - | - - -
5/6/2026 | 3:30:00 PM | 279.3 | 277.08 | 275.65 | 482.97 | 477.2 | 480.92 | 83.7966 | 79.067 | 75.6604 | 0.8135 | 1.439 | 1.444 | 1.441 | 1.922 | 1.949 | 1.992 | Over-range | 60.01 | 19589 | 19003 | 17222 | 55814 | - - - | - - - | - - - | - - - | 19589 | 19003 | 17222 | 55814 | 11493 | 9394 | 10500 | 31388 | - - - | - - - | - - - | - - - | 11493 | 9394 | 10500 | 31388 | 23287 | 21781 | 20739 | 65807 | # # # | # # # | # # # | # # # | 0.841 | 0.873 | 0.83 | 0.848 | # # # | # # # | # # # | - - - | 0.861 | 0.896 | 0.853 | 0.87 | - - - | 0.562 | 2.27 | 2.22 | 2.24 | 2.08 | 2.14 | 2.24 | 20.6 | 21.74 | 22.52 | 0 | - - - | - - - | - - - | - - - | 23287 | 21781 | 20739 | 65807 | Over-range | 12584 | 10632 | 11545 | 34835 | 5052 | 4913 | 4728 | 14902 | 19596 | 19059 | 17287 | 55942 | 19596 | 19059 | 17287 | 55942 | - - - | - - - | - - - | - - -
5/6/2026 | 3:45:00 PM | 279.07 | 276.89 | 275.52 | 482.56 | 476.98 | 480.58 | 86.042 | 81.2504 | 77.2055 | 0.8181 | 1.439 | 1.444 | 1.441 | 1.904 | 1.933 | 1.975 | Over-range | 60 | 20087 | 19576 | 17591 | 57254 | - - - | - - - | - - - | - - - | 20087 | 19576 | 17591 | 57254 | 11813 | 9546 | 10649 | 32008 | - - - | - - - | - - - | - - - | 11813 | 9546 | 10649 | 32008 | 23873 | 22348 | 21135 | 67356 | # # # | # # # | # # # | # # # | 0.841 | 0.876 | 0.832 | 0.85 | # # # | # # # | # # # | - - - | 0.861 | 0.898 | 0.854 | 0.871 | - - - | 0.559 | 2.27 | 2.24 | 2.24 | 2.08 | 2.15 | 2.24 | 20.01 | 21.11 | 22.07 | 0 | - - - | - - - | - - - | - - - | 23873 | 22348 | 21135 | 67356 | Over-range | 12885 | 10758 | 11698 | 35427 | 5062 | 4886 | 4763 | 14956 | 20128 | 19670 | 17583 | 57381 | 20128 | 19670 | 17583 | 57381 | - - - | - - - | - - - | - - -
5/6/2026 | 4:00:00 PM | 279.34 | 277.12 | 275.69 | 482.96 | 477.36 | 480.98 | 82.1671 | 77.391 | 74.6198 | 0.8154 | 1.44 | 1.444 | 1.441 | 1.908 | 1.94 | 1.978 | Over-range | 60 | 19189 | 18521 | 16922 | 54633 | - - - | - - - | - - - | - - - | 19189 | 18521 | 16922 | 54633 | 11302 | 9364 | 10477 | 31142 | - - - | - - - | - - - | - - - | 11302 | 9364 | 10477 | 31142 | 22819 | 21304 | 20443 | 64566 | # # # | # # # | # # # | # # # | 0.841 | 0.869 | 0.828 | 0.846 | # # # | # # # | # # # | - - - | 0.86 | 0.892 | 0.849 | 0.867 | - - - | 0.57 | 2.27 | 2.19 | 2.22 | 2.06 | 2.13 | 2.23 | 20.17 | 21.29 | 21.96 | 0 | - - - | - - - | - - - | - - - | 22819 | 21304 | 20443 | 64566 | Over-range | 12340 | 10515 | 11456 | 34377 | 4871 | 4707 | 4550 | 14319 | 19189 | 18593 | 16977 | 54759 | 19189 | 18593 | 16977 | 54759 | - - - | - - - | - - - | - - -
5/6/2026 | 4:15:00 PM | 279.54 | 277.42 | 275.91 | 483.46 | 477.77 | 481.31 | 85.8344 | 80.8687 | 77.5072 | 0.8166 | 1.44 | 1.444 | 1.441 | 1.884 | 1.914 | 1.952 | Over-range | 60.01 | 20130 | 19508 | 17695 | 57333 | - - - | - - - | - - - | - - - | 20130 | 19508 | 17695 | 57333 | 11959 | 9785 | 10931 | 32675 | - - - | - - - | - - - | - - - | 11959 | 9785 | 10931 | 32675 | 23893 | 22326 | 21288 | 67508 | # # # | # # # | # # # | # # # | 0.843 | 0.874 | 0.831 | 0.849 | # # # | # # # | # # # | - - - | 0.86 | 0.893 | 0.851 | 0.868 | - - - | 0.57 | 2.27 | 2.2 | 2.23 | 2.07 | 2.13 | 2.23 | 18.66 | 19.81 | 20.37 | 0 | - - - | - - - | - - - | - - - | 23893 | 22326 | 21288 | 67508 | Over-range | 12866 | 10849 | 11827 | 35619 | 4685 | 4629 | 4458 | 14010 | 20212 | 19496 | 17744 | 57451 | 20212 | 19496 | 17744 | 57451 | - - - | - - - | - - - | - - -
5/6/2026 | 4:30:00 PM | 279.65 | 277.47 | 275.98 | 483.6 | 477.86 | 481.48 | 83.3713 | 78.4516 | 75.0842 | 0.8128 | 1.439 | 1.444 | 1.441 | 1.918 | 1.945 | 1.989 | Over-range | 60 | 19479 | 18858 | 17053 | 55391 | - - - | - - - | - - - | - - - | 19479 | 18858 | 17053 | 55391 | 11509 | 9340 | 10511 | 31360 | - - - | - - - | - - - | - - - | 11509 | 9340 | 10511 | 31360 | 23183 | 21626 | 20594 | 65403 | # # # | # # # | # # # | # # # | 0.84 | 0.872 | 0.828 | 0.847 | # # # | # # # | # # # | - - - | 0.86 | 0.895 | 0.851 | 0.869 | - - - | 0.566 | 2.25 | 2.17 | 2.21 | 2.04 | 2.1 | 2.21 | 20.33 | 21.69 | 22.32 | 0 | - - - | - - - | - - - | - - - | 23183 | 21626 | 20594 | 65403 | Over-range | 12562 | 10571 | 11534 | 34744 | 4949 | 4875 | 4664 | 14720 | 19515 | 18870 | 17130 | 55516 | 19515 | 18870 | 17130 | 55516 | - - - | - - - | - - - | - - -
5/6/2026 | 4:45:00 PM | 280.06 | 277.81 | 276.29 | 484.26 | 478.4 | 482.13 | 84.0975 | 79.4317 | 76.2725 | 0.8158 | 1.44 | 1.444 | 1.441 | 1.915 | 1.943 | 1.982 | Over-range | 60 | 19679 | 19072 | 17365 | 56116 | - - - | - - - | - - - | - - - | 19679 | 19072 | 17365 | 56116 | 11647 | 9609 | 10682 | 31938 | - - - | - - - | - - - | - - - | 11647 | 9609 | 10682 | 31938 | 23442 | 21946 | 20964 | 66351 | # # # | # # # | # # # | # # # | 0.839 | 0.869 | 0.828 | 0.846 | # # # | # # # | # # # | - - - | 0.86 | 0.892 | 0.851 | 0.868 | - - - | 0.569 | 2.24 | 2.16 | 2.19 | 2.03 | 2.08 | 2.21 | 20.48 | 21.63 | 22.34 | 0 | - - - | - - - | - - - | - - - | 23442 | 21946 | 20964 | 66351 | Over-range | 12726 | 10838 | 11730 | 35361 | 5047 | 4939 | 4768 | 14951 | 19726 | 19095 | 17427 | 56249 | 19726 | 19095 | 17427 | 56249 | - - - | - - - | - - - | - - -
5/6/2026 | 5:00:00 PM | 280.14 | 277.88 | 276.29 | 484.42 | 478.45 | 482.17 | 84.1007 | 79.3954 | 75.2939 | 0.8141 | 1.44 | 1.444 | 1.441 | 1.9 | 1.931 | 1.977 | Over-range | 60 | 19645 | 19173 | 17159 | 55976 | - - - | - - - | - - - | - - - | 19645 | 19173 | 17159 | 55976 | 11812 | 9495 | 10577 | 31885 | - - - | - - - | - - - | - - - | 11812 | 9495 | 10577 | 31885 | 23439 | 21932 | 20685 | 66056 | # # # | # # # | # # # | # # # | 0.838 | 0.874 | 0.83 | 0.847 | # # # | # # # | # # # | - - - | 0.857 | 0.895 | 0.85 | 0.867 | - - - | 0.57 | 2.24 | 2.18 | 2.18 | 2.03 | 2.09 | 2.21 | 19.44 | 20.6 | 21.45 | 0 | - - - | - - - | - - - | - - - | 23439 | 21932 | 20685 | 66056 | Over-range | 12778 | 10637 | 11541 | 35043 | 4794 | 4726 | 4540 | 14321 | 19715 | 19165 | 17215 | 56095 | 19715 | 19165 | 17215 | 56095 | - - - | - - - | - - - | - - -
5/6/2026 | 5:15:00 PM | 280.54 | 278.23 | 276.7 | 485.11 | 479.07 | 482.88 | 82.6126 | 77.7739 | 74.5143 | 0.8132 | 1.44 | 1.444 | 1.442 | 1.903 | 1.944 | 1.99 | Over-range | 60.02 | 19323 | 18713 | 16931 | 54967 | - - - | - - - | - - - | - - - | 19323 | 18713 | 16931 | 54967 | 11635 | 9523 | 10616 | 31774 | - - - | - - - | - - - | - - - | 11635 | 9523 | 10616 | 31774 | 23072 | 21528 | 20513 | 65112 | # # # | # # # | # # # | # # # | 0.838 | 0.869 | 0.825 | 0.844 | # # # | # # # | # # # | - - - | 0.856 | 0.89 | 0.846 | 0.864 | - - - | 0.578 | 2.19 | 2.12 | 2.15 | 1.99 | 2.05 | 2.17 | 19.54 | 20.73 | 21.46 | 0 | - - - | - - - | - - - | - - - | 23072 | 21528 | 20513 | 65112 | Over-range | 12599 | 10631 | 11570 | 34874 | 4756 | 4658 | 4523 | 14160 | 19376 | 18741 | 16974 | 55091 | 19376 | 18741 | 16974 | 55091 | - - - | - - - | - - - | - - -
5/6/2026 | 5:30:00 PM | 280.38 | 278.12 | 276.6 | 484.83 | 478.96 | 482.64 | 85.5474 | 80.9798 | 77.1384 | 0.8161 | 1.44 | 1.444 | 1.442 | 1.893 | 1.939 | 1.987 | Over-range | 60.01 | 20064 | 19569 | 17656 | 57290 | - - - | - - - | - - - | - - - | 20064 | 19569 | 17656 | 57290 | 11955 | 9788 | 10788 | 32531 | - - - | - - - | - - - | - - - | 11955 | 9788 | 10788 | 32531 | 23883 | 22413 | 21238 | 67534 | # # # | # # # | # # # | # # # | 0.84 | 0.873 | 0.831 | 0.848 | # # # | # # # | # # # | - - - | 0.859 | 0.894 | 0.852 | 0.868 | - - - | 0.568 | 2.22 | 2.13 | 2.2 | 2.02 | 2.09 | 2.2 | 19.47 | 20.6 | 21.44 | 0 | - - - | - - - | - - - | - - - | 23883 | 22413 | 21238 | 67534 | Over-range | 12948 | 10916 | 11793 | 35734 | 4897 | 4766 | 4697 | 14584 | 20147 | 19629 | 17637 | 57413 | 20147 | 19629 | 17637 | 57413 | - - - | - - - | - - - | - - -
5/6/2026 | 5:45:00 PM | 280.45 | 278.25 | 276.66 | 485.01 | 479.17 | 482.7 | 82.6543 | 78.1061 | 74.3305 | 0.8107 | 1.441 | 1.444 | 1.443 | 1.905 | 1.948 | 2.006 | Over-range | 60.01 | 19293 | 18802 | 16900 | 54995 | - - - | - - - | - - - | - - - | 19293 | 18802 | 16900 | 54995 | 11570 | 9417 | 10424 | 31410 | - - - | - - - | - - - | - - - | 11570 | 9417 | 10424 | 31410 | 23046 | 21589 | 20431 | 65067 | # # # | # # # | # # # | # # # | 0.837 | 0.871 | 0.827 | 0.845 | # # # | # # # | # # # | - - - | 0.857 | 0.893 | 0.849 | 0.866 | - - - | 0.571 | 2.24 | 2.16 | 2.22 | 2.05 | 2.1 | 2.23 | 19.96 | 21.14 | 22.02 | 0 | - - - | - - - | - - - | - - - | 23046 | 21589 | 20431 | 65067 | Over-range | 12591 | 10588 | 11463 | 34721 | 4866 | 4750 | 4676 | 14520 | 19384 | 18856 | 16883 | 55123 | 19384 | 18856 | 16883 | 55123 | - - - | - - - | - - - | - - -
5/6/2026 | 6:00:00 PM | 280.57 | 278.32 | 276.8 | 485.17 | 479.3 | 482.97 | 83.9544 | 78.9021 | 76.0754 | 0.8135 | 1.441 | 1.444 | 1.443 | 1.882 | 1.946 | 1.998 | Over-range | 60.01 | 19663 | 18962 | 17268 | 55893 | - - - | - - - | - - - | - - - | 19663 | 18962 | 17268 | 55893 | 11908 | 9852 | 10971 | 32731 | - - - | - - - | - - - | - - - | 11908 | 9852 | 10971 | 32731 | 23466 | 21862 | 20970 | 66298 | # # # | # # # | # # # | # # # | 0.838 | 0.867 | 0.824 | 0.843 | # # # | # # # | # # # | - - - | 0.856 | 0.887 | 0.843 | 0.862 | - - - | 0.586 | 2.2 | 2.12 | 2.2 | 2.02 | 2.07 | 2.19 | 18.81 | 20.01 | 20.75 | 0 | - - - | - - - | - - - | - - - | 23466 | 21862 | 20970 | 66298 | Over-range | 12801 | 10873 | 11888 | 35635 | 4632 | 4543 | 4518 | 13911 | 19765 | 18986 | 17261 | 56012 | 19765 | 18986 | 17261 | 56012 | - - - | - - - | - - - | - - -
5/6/2026 | 6:15:00 PM | 281.62 | 279.59 | 277.99 | 487.17 | 481.55 | 484.8 | 83.1448 | 78.2464 | 74.7399 | 0.812 | 1.44 | 1.441 | 1.442 | 1.892 | 1.96 | 2.016 | Over-range | 60.01 | 19454 | 18900 | 16994 | 55348 | - - - | - - - | - - - | - - - | 19454 | 18900 | 16994 | 55348 | 11956 | 9768 | 10860 | 32585 | - - - | - - - | - - - | - - - | 11956 | 9768 | 10860 | 32585 | 23301 | 21756 | 20664 | 65720 | # # # | # # # | # # # | # # # | 0.835 | 0.869 | 0.822 | 0.842 | # # # | # # # | # # # | - - - | 0.852 | 0.887 | 0.841 | 0.86 | - - - | 0.589 | 2.12 | 1.98 | 2.04 | 1.93 | 1.93 | 2.06 | 18.38 | 19.74 | 20.45 | 0 | - - - | - - - | - - - | - - - | 23301 | 21756 | 20664 | 65720 | Over-range | 12818 | 10764 | 11747 | 35412 | 4532 | 4442 | 4392 | 13619 | 19535 | 18951 | 16970 | 55456 | 19535 | 18951 | 16970 | 55456 | - - - | - - - | - - - | - - -
5/6/2026 | 6:30:00 PM | 281.59 | 279.58 | 277.95 | 487.14 | 481.55 | 484.7 | 82.4727 | 77.7504 | 74.8919 | 0.8107 | 1.44 | 1.441 | 1.442 | 1.897 | 1.97 | 2.023 | Over-range | 60 | 19240 | 18630 | 16945 | 54815 | - - - | - - - | - - - | - - - | 19240 | 18630 | 16945 | 54815 | 11880 | 9927 | 10961 | 32768 | - - - | - - - | - - - | - - - | 11880 | 9927 | 10961 | 32768 | 23089 | 21593 | 20684 | 65367 | # # # | # # # | # # # | # # # | 0.833 | 0.863 | 0.819 | 0.839 | # # # | # # # | # # # | - - - | 0.851 | 0.882 | 0.838 | 0.857 | - - - | 0.598 | 2.06 | 1.96 | 1.99 | 1.89 | 1.89 | 2.02 | 18.79 | 19.97 | 20.69 | 0 | - - - | - - - | - - - | - - - | 23089 | 21593 | 20684 | 65367 | Over-range | 12758 | 10907 | 11851 | 35584 | 4566 | 4445 | 4426 | 13643 | 19307 | 18695 | 16920 | 54923 | 19307 | 18695 | 16920 | 54923 | - - - | - - - | - - - | - - -
5/6/2026 | 6:45:00 PM | 281.71 | 279.8 | 278.12 | 487.42 | 481.96 | 484.89 | 82.4435 | 78.0802 | 74.5498 | 0.8109 | 1.44 | 1.44 | 1.441 | 1.888 | 1.952 | 2.006 | Over-range | 59.99 | 19206 | 18757 | 16918 | 54881 | - - - | - - - | - - - | - - - | 19206 | 18757 | 16918 | 54881 | 11932 | 9888 | 10840 | 32660 | - - - | - - - | - - - | - - - | 11932 | 9888 | 10840 | 32660 | 23065 | 21672 | 20575 | 65312 | # # # | # # # | # # # | # # # | 0.833 | 0.866 | 0.822 | 0.84 | # # # | # # # | # # # | - - - | 0.849 | 0.884 | 0.84 | 0.858 | - - - | 0.595 | 2.04 | 1.91 | 1.94 | 1.86 | 1.85 | 1.98 | 18.11 | 19.3 | 20.04 | 0 | - - - | - - - | - - - | - - - | 23065 | 21672 | 20575 | 65312 | Over-range | 12757 | 10835 | 11693 | 35358 | 4416 | 4342 | 4295 | 13282 | 19291 | 18796 | 16900 | 54986 | 19291 | 18796 | 16900 | 54986 | - - - | - - - | - - - | - - -
5/6/2026 | 7:00:00 PM | 281.81 | 279.98 | 278.26 | 487.71 | 482.24 | 485.06 | 80.8656 | 76.3675 | 72.841 | 0.8077 | 1.439 | 1.44 | 1.44 | 1.891 | 1.933 | 2.008 | Over-range | 60 | 18796 | 18365 | 16492 | 53653 | - - - | - - - | - - - | - - - | 18796 | 18365 | 16492 | 53653 | 11967 | 9911 | 10867 | 32744 | - - - | - - - | - - - | - - - | 11967 | 9911 | 10867 | 32744 | 22696 | 21280 | 20176 | 64152 | # # # | # # # | # # # | # # # | 0.828 | 0.863 | 0.817 | 0.836 | # # # | # # # | # # # | - - - | 0.843 | 0.879 | 0.833 | 0.852 | - - - | 0.61 | 1.97 | 1.82 | 1.83 | 1.77 | 1.75 | 1.88 | 17.38 | 18.28 | 19.01 | 0 | - - - | - - - | - - - | - - - | 22696 | 21280 | 20176 | 64152 | Over-range | 12714 | 10736 | 11613 | 35140 | 4201 | 4047 | 4006 | 12500 | 18849 | 18421 | 16469 | 53739 | 18849 | 18421 | 16469 | 53739 | - - - | - - - | - - - | - - -
5/6/2026 | 7:15:00 PM | 282.21 | 280.4 | 278.71 | 488.37 | 482.98 | 485.84 | 80.7489 | 75.6875 | 73.095 | 0.8084 | 1.44 | 1.439 | 1.44 | 1.901 | 1.942 | 2.015 | Over-range | 60 | 18817 | 18156 | 16479 | 53452 | - - - | - - - | - - - | - - - | 18817 | 18156 | 16479 | 53452 | 11913 | 9916 | 11036 | 32865 | - - - | - - - | - - - | - - - | 11913 | 9916 | 11036 | 32865 | 22670 | 21091 | 20252 | 64013 | # # # | # # # | # # # | # # # | 0.83 | 0.861 | 0.814 | 0.835 | # # # | # # # | # # # | - - - | 0.845 | 0.877 | 0.83 | 0.851 | - - - | 0.615 | 1.99 | 1.84 | 1.87 | 1.8 | 1.77 | 1.9 | 17.36 | 18.27 | 18.91 | 0 | - - - | - - - | - - - | - - - | 22670 | 21091 | 20252 | 64013 | Over-range | 12636 | 10723 | 11764 | 35197 | 4125 | 4002 | 3992 | 12359 | 18895 | 18172 | 16470 | 53537 | 18895 | 18172 | 16470 | 53537 | - - - | - - - | - - - | - - -
5/6/2026 | 7:30:00 PM | 282.42 | 280.68 | 278.94 | 488.79 | 483.49 | 486.17 | 82.2311 | 77.8556 | 73.8563 | 0.8092 | 1.44 | 1.439 | 1.441 | 1.903 | 1.946 | 2.017 | Over-range | 60 | 19103 | 18771 | 16757 | 54632 | - - - | - - - | - - - | - - - | 19103 | 18771 | 16757 | 54632 | 12252 | 10065 | 11002 | 33318 | - - - | - - - | - - - | - - - | 12252 | 10065 | 11002 | 33318 | 23093 | 21712 | 20474 | 65278 | # # # | # # # | # # # | # # # | 0.827 | 0.865 | 0.819 | 0.837 | # # # | # # # | # # # | - - - | 0.842 | 0.88 | 0.835 | 0.852 | - - - | 0.61 | 2.02 | 1.89 | 1.92 | 1.85 | 1.82 | 1.95 | 17.23 | 18.23 | 19 | 0 | - - - | - - - | - - - | - - - | 23093 | 21712 | 20474 | 65278 | Over-range | 12968 | 10901 | 11752 | 35703 | 4161 | 4108 | 4049 | 12590 | 19186 | 18781 | 16747 | 54713 | 19186 | 18781 | 16747 | 54713 | - - - | - - - | - - - | - - -
5/6/2026 | 7:45:00 PM | 282.37 | 280.59 | 278.88 | 488.68 | 483.29 | 486.11 | 80.9725 | 76.5815 | 73.5837 | 0.8088 | 1.439 | 1.439 | 1.44 | 1.929 | 1.976 | 2.041 | Over-range | 59.99 | 18789 | 18292 | 16597 | 53679 | - - - | - - - | - - - | - - - | 18789 | 18292 | 16597 | 53679 | 11933 | 9985 | 10955 | 32873 | - - - | - - - | - - - | - - - | 11933 | 9985 | 10955 | 32873 | 22718 | 21327 | 20376 | 64420 | # # # | # # # | # # # | # # # | 0.827 | 0.858 | 0.815 | 0.833 | # # # | # # # | # # # | - - - | 0.843 | 0.875 | 0.833 | 0.851 | - - - | 0.612 | 2.01 | 1.86 | 1.88 | 1.82 | 1.8 | 1.93 | 18.35 | 19.44 | 20.13 | 0 | - - - | - - - | - - - | - - - | 22718 | 21327 | 20376 | 64420 | Over-range | 12753 | 10941 | 11801 | 35562 | 4368 | 4359 | 4266 | 13207 | 18864 | 18267 | 16638 | 53769 | 18864 | 18267 | 16638 | 53769 | - - - | - - - | - - - | - - -
5/6/2026 | 8:00:00 PM | 282.46 | 280.55 | 278.93 | 488.74 | 483.28 | 486.25 | 83.3156 | 78.8423 | 75.696 | 0.8145 | 1.439 | 1.439 | 1.44 | 1.905 | 1.966 | 2.029 | Over-range | 60 | 19489 | 18985 | 17238 | 55713 | - - - | - - - | - - - | - - - | 19489 | 18985 | 17238 | 55713 | 12204 | 10257 | 11232 | 33693 | - - - | - - - | - - - | - - - | 12204 | 10257 | 11232 | 33693 | 23451 | 22030 | 21033 | 66515 | # # # | # # # | # # # | # # # | 0.831 | 0.862 | 0.82 | 0.838 | # # # | # # # | # # # | - - - | 0.847 | 0.879 | 0.837 | 0.854 | - - - | 0.605 | 1.98 | 1.85 | 1.86 | 1.79 | 1.78 | 1.9 | 18.17 | 19.1 | 19.87 | 0 | - - - | - - - | - - - | - - - | 23451 | 22030 | 21033 | 66515 | Over-range | 13037 | 11165 | 12044 | 36314 | 4511 | 4340 | 4278 | 13337 | 19496 | 19070 | 17239 | 55805 | 19496 | 19070 | 17239 | 55805 | - - - | - - - | - - - | - - -
5/6/2026 | 8:15:00 PM | 282.55 | 280.67 | 278.89 | 488.99 | 483.33 | 486.26 | 82.1788 | 77.572 | 74.087 | 0.8099 | 1.439 | 1.439 | 1.44 | 1.917 | 1.978 | 2.047 | Over-range | 59.99 | 19146 | 18680 | 16787 | 54614 | - - - | - - - | - - - | - - - | 19146 | 18680 | 16787 | 54614 | 12115 | 10035 | 11026 | 33175 | - - - | - - - | - - - | - - - | 12115 | 10035 | 11026 | 33175 | 23122 | 21667 | 20562 | 65350 | # # # | # # # | # # # | # # # | 0.828 | 0.862 | 0.816 | 0.836 | # # # | # # # | # # # | - - - | 0.844 | 0.88 | 0.834 | 0.853 | - - - | 0.608 | 1.98 | 1.85 | 1.86 | 1.79 | 1.77 | 1.9 | 18.44 | 19.46 | 20.31 | 0 | - - - | - - - | - - - | - - - | 23122 | 21667 | 20562 | 65350 | Over-range | 12956 | 10965 | 11863 | 35862 | 4510 | 4344 | 4295 | 13383 | 19176 | 18761 | 16767 | 54705 | 19176 | 18761 | 16767 | 54705 | - - - | - - - | - - - | - - -
5/6/2026 | 8:30:00 PM | 282.58 | 280.67 | 278.92 | 488.99 | 483.37 | 486.32 | 82.2903 | 77.5261 | 74.6579 | 0.8131 | 1.439 | 1.439 | 1.44 | 1.939 | 2.003 | 2.061 | Over-range | 59.99 | 19243 | 18639 | 16923 | 54805 | - - - | - - - | - - - | - - - | 19243 | 18639 | 16923 | 54805 | 11972 | 9976 | 11024 | 32972 | - - - | - - - | - - - | - - - | 11972 | 9976 | 11024 | 32972 | 23140 | 21635 | 20710 | 65485 | # # # | # # # | # # # | # # # | 0.832 | 0.862 | 0.817 | 0.837 | # # # | # # # | # # # | - - - | 0.849 | 0.881 | 0.837 | 0.856 | - - - | 0.602 | 1.96 | 1.86 | 1.87 | 1.79 | 1.77 | 1.9 | 19.07 | 20.24 | 21.02 | 0 | - - - | - - - | - - - | - - - | 23140 | 21635 | 20710 | 65485 | Over-range | 12845 | 10974 | 11927 | 35816 | 4571 | 4501 | 4478 | 13763 | 19332 | 18647 | 16913 | 54891 | 19332 | 18647 | 16913 | 54891 | - - - | - - - | - - - | - - -
5/6/2026 | 8:45:00 PM | 283.01 | 281.13 | 279.39 | 489.79 | 484.19 | 487.06 | 85.0332 | 80.396 | 76.5002 | 0.8133 | 1.439 | 1.439 | 1.44 | 1.95 | 2.01 | 2.073 | Over-range | 59.99 | 19907 | 19454 | 17433 | 56794 | - - - | - - - | - - - | - - - | 19907 | 19454 | 17433 | 56794 | 12280 | 10038 | 11114 | 33432 | - - - | - - - | - - - | - - - | 12280 | 10038 | 11114 | 33432 | 23932 | 22457 | 21239 | 67627 | # # # | # # # | # # # | # # # | 0.832 | 0.866 | 0.821 | 0.84 | # # # | # # # | # # # | - - - | 0.85 | 0.887 | 0.842 | 0.86 | - - - | 0.589 | 1.97 | 1.84 | 1.87 | 1.79 | 1.78 | 1.9 | 19.74 | 21.08 | 21.93 | 0 | - - - | - - - | - - - | - - - | 23932 | 22457 | 21239 | 67627 | Over-range | 13268 | 11199 | 12116 | 36665 | 4930 | 4879 | 4737 | 14797 | 19939 | 19483 | 17472 | 56895 | 19939 | 19483 | 17472 | 56895 | - - - | - - - | - - - | - - -
5/6/2026 | 9:00:00 PM | 281.92 | 280.04 | 278.2 | 487.93 | 482.19 | 485.07 | 83.8798 | 79.5606 | 76.3283 | 0.8124 | 1.437 | 1.438 | 1.439 | 1.981 | 2.046 | 2.088 | Over-range | 60 | 19664 | 19139 | 17402 | 56205 | - - - | - - - | - - - | - - - | 19664 | 19139 | 17402 | 56205 | 11787 | 9871 | 10843 | 32502 | - - - | - - - | - - - | - - - | 11787 | 9871 | 10843 | 32502 | 23529 | 22152 | 21119 | 66800 | # # # | # # # | # # # | # # # | 0.836 | 0.864 | 0.824 | 0.841 | # # # | # # # | # # # | - - - | 0.857 | 0.888 | 0.847 | 0.864 | - - - | 0.578 | 1.91 | 1.82 | 1.82 | 1.74 | 1.74 | 1.86 | 21.31 | 22.67 | 23.35 | 0 | - - - | - - - | - - - | - - - | 23529 | 22152 | 21119 | 66800 | Over-range | 12912 | 11142 | 11953 | 36069 | 5196 | 5099 | 4958 | 15428 | 19681 | 19226 | 17410 | 56316 | 19681 | 19226 | 17410 | 56316 | - - - | - - - | - - - | - - -
5/6/2026 | 9:15:00 PM | 282 | 280.16 | 278.33 | 488.05 | 482.52 | 485.21 | 84.208 | 80.0555 | 76.3775 | 0.8125 | 1.437 | 1.437 | 1.438 | 1.978 | 2.038 | 2.081 | Over-range | 59.98 | 19746 | 19321 | 17459 | 56526 | - - - | - - - | - - - | - - - | 19746 | 19321 | 17459 | 56526 | 11907 | 9890 | 10819 | 32616 | - - - | - - - | - - - | - - - | 11907 | 9890 | 10819 | 32616 | 23644 | 22315 | 21154 | 67113 | # # # | # # # | # # # | # # # | 0.835 | 0.866 | 0.825 | 0.842 | # # # | # # # | # # # | - - - | 0.856 | 0.889 | 0.848 | 0.865 | - - - | 0.577 | 1.9 | 1.8 | 1.82 | 1.74 | 1.73 | 1.84 | 21.02 | 22.45 | 23.17 | 0 | - - - | - - - | - - - | - - - | 23644 | 22315 | 21154 | 67113 | Over-range | 12997 | 11155 | 11934 | 36152 | 5137 | 5094 | 4970 | 15392 | 19811 | 19373 | 17442 | 56625 | 19811 | 19373 | 17442 | 56625 | - - - | - - - | - - - | - - -
5/6/2026 | 9:30:00 PM | 281.97 | 280.26 | 278.35 | 488.14 | 482.59 | 485.18 | 83.0634 | 78.9477 | 75.4748 | 0.8099 | 1.437 | 1.437 | 1.438 | 1.979 | 2.03 | 2.071 | Over-range | 60.01 | 19467 | 19031 | 17239 | 55736 | - - - | - - - | - - - | - - - | 19467 | 19031 | 17239 | 55736 | 11808 | 9852 | 10761 | 32420 | - - - | - - - | - - - | - - - | 11808 | 9852 | 10761 | 32420 | 23319 | 22015 | 20907 | 66241 | # # # | # # # | # # # | # # # | 0.835 | 0.864 | 0.825 | 0.841 | # # # | # # # | # # # | - - - | 0.855 | 0.887 | 0.847 | 0.863 | - - - | 0.582 | 1.93 | 1.77 | 1.83 | 1.74 | 1.73 | 1.85 | 20.64 | 22.08 | 22.64 | 0 | - - - | - - - | - - - | - - - | 23319 | 22015 | 20907 | 66241 | Over-range | 12833 | 11057 | 11819 | 35772 | 4959 | 4957 | 4823 | 14928 | 19553 | 19046 | 17236 | 55834 | 19553 | 19046 | 17236 | 55834 | - - - | - - - | - - - | - - -
5/6/2026 | 9:45:00 PM | 282.02 | 280.24 | 278.33 | 488.2 | 482.52 | 485.21 | 83.8327 | 79.4425 | 76.2506 | 0.8119 | 1.436 | 1.437 | 1.438 | 1.946 | 2.004 | 2.052 | Over-range | 60.01 | 19626 | 19103 | 17357 | 56086 | - - - | - - - | - - - | - - - | 19626 | 19103 | 17357 | 56086 | 11974 | 10051 | 11003 | 33029 | - - - | - - - | - - - | - - - | 11974 | 10051 | 11003 | 33029 | 23523 | 22130 | 21103 | 66756 | # # # | # # # | # # # | # # # | 0.834 | 0.863 | 0.823 | 0.84 | # # # | # # # | # # # | - - - | 0.853 | 0.884 | 0.843 | 0.86 | - - - | 0.589 | 1.9 | 1.76 | 1.84 | 1.74 | 1.72 | 1.84 | 19.71 | 20.89 | 21.46 | 0 | - - - | - - - | - - - | - - - | 23523 | 22130 | 21103 | 66756 | Over-range | 12954 | 11153 | 11988 | 36159 | 4849 | 4746 | 4672 | 14456 | 19694 | 19165 | 17322 | 56181 | 19694 | 19165 | 17322 | 56181 | - - - | - - - | - - - | - - -
5/6/2026 | 10:00:00 PM | 282.43 | 280.67 | 278.71 | 488.94 | 483.27 | 485.83 | 83.6549 | 79.1594 | 75.3698 | 0.81 | 1.436 | 1.437 | 1.438 | 1.949 | 2.006 | 2.055 | Over-range | 60.01 | 19561 | 19119 | 17156 | 55836 | - - - | - - - | - - - | - - - | 19561 | 19119 | 17156 | 55836 | 12125 | 9991 | 10980 | 33096 | - - - | - - - | - - - | - - - | 12125 | 9991 | 10980 | 33096 | 23511 | 22092 | 20895 | 66498 | # # # | # # # | # # # | # # # | 0.832 | 0.865 | 0.821 | 0.84 | # # # | # # # | # # # | - - - | 0.85 | 0.885 | 0.841 | 0.859 | - - - | 0.593 | 1.95 | 1.79 | 1.85 | 1.76 | 1.74 | 1.87 | 19.22 | 20.56 | 21.17 | 0 | - - - | - - - | - - - | - - - | 23511 | 22092 | 20895 | 66498 | Over-range | 13035 | 11055 | 11916 | 36084 | 4696 | 4653 | 4546 | 14131 | 19641 | 19153 | 17132 | 55926 | 19641 | 19153 | 17132 | 55926 | - - - | - - - | - - - | - - -
5/6/2026 | 10:15:00 PM | 281.75 | 279.97 | 277.99 | 487.76 | 481.97 | 484.67 | 82.8181 | 78.5667 | 75.1382 | 0.8123 | 1.436 | 1.437 | 1.437 | 1.963 | 2.026 | 2.07 | Over-range | 60 | 19349 | 18896 | 17089 | 55334 | - - - | - - - | - - - | - - - | 19349 | 18896 | 17089 | 55334 | 11927 | 9950 | 10866 | 32744 | - - - | - - - | - - - | - - - | 11927 | 9950 | 10866 | 32744 | 23224 | 21875 | 20779 | 65878 | # # # | # # # | # # # | # # # | 0.833 | 0.864 | 0.822 | 0.84 | # # # | # # # | # # # | - - - | 0.851 | 0.884 | 0.843 | 0.859 | - - - | 0.592 | 2.01 | 1.83 | 1.9 | 1.81 | 1.8 | 1.93 | 19.57 | 20.83 | 21.56 | 0 | - - - | - - - | - - - | - - - | 23224 | 21875 | 20779 | 65878 | Over-range | 12838 | 11010 | 11811 | 35725 | 4682 | 4651 | 4567 | 14101 | 19433 | 18902 | 17090 | 55424 | 19433 | 18902 | 17090 | 55424 | - - - | - - - | - - - | - - -
5/6/2026 | 10:30:00 PM | 281.68 | 279.72 | 277.79 | 487.58 | 481.44 | 484.49 | 83.641 | 78.845 | 74.6898 | 0.8147 | 1.436 | 1.436 | 1.437 | 1.95 | 2 | 2.066 | Over-range | 60 | 19517 | 19065 | 16954 | 55535 | - - - | - - - | - - - | - - - | 19517 | 19065 | 16954 | 55535 | 12013 | 9690 | 10801 | 32503 | - - - | - - - | - - - | - - - | 12013 | 9690 | 10801 | 32503 | 23436 | 21922 | 20625 | 65982 | # # # | # # # | # # # | # # # | 0.833 | 0.87 | 0.822 | 0.842 | # # # | # # # | # # # | - - - | 0.85 | 0.89 | 0.843 | 0.861 | - - - | 0.585 | 1.86 | 1.73 | 1.74 | 1.68 | 1.66 | 1.78 | 19.67 | 20.88 | 21.74 | 0 | - - - | - - - | - - - | - - - | 23436 | 21922 | 20625 | 65982 | Over-range | 12967 | 10810 | 11734 | 35602 | 4801 | 4718 | 4509 | 14303 | 19511 | 19083 | 17029 | 55624 | 19511 | 19083 | 17029 | 55624 | - - - | - - - | - - - | - - -
5/6/2026 | 10:45:00 PM | 282.54 | 280.51 | 278.6 | 489.04 | 482.77 | 485.95 | 82.1164 | 77.2931 | 73.8008 | 0.8209 | 1.434 | 1.435 | 1.434 | 1.898 | 1.974 | 2.061 | Over-range | 60.01 | 19170 | 18634 | 16715 | 54519 | - - - | - - - | - - - | - - - | 19170 | 18634 | 16715 | 54519 | 11888 | 9758 | 10831 | 32477 | - - - | - - - | - - - | - - - | 11888 | 9758 | 10831 | 32477 | 23061 | 21527 | 20422 | 65010 | # # # | # # # | # # # | # # # | 0.831 | 0.866 | 0.819 | 0.839 | # # # | # # # | # # # | - - - | 0.848 | 0.885 | 0.838 | 0.857 | - - - | 0.596 | 1.7 | 1.55 | 1.54 | 1.52 | 1.47 | 1.57 | 19.19 | 19.97 | 21.21 | 0 | - - - | - - - | - - - | - - - | 23061 | 21527 | 20422 | 65010 | Over-range | 12805 | 10758 | 11717 | 35364 | 4663 | 4440 | 4378 | 13727 | 19150 | 18699 | 16753 | 54602 | 19150 | 18699 | 16753 | 54602 | - - - | - - - | - - - | - - -
5/6/2026 | 11:00:00 PM | 282.88 | 280.72 | 278.84 | 489.5 | 483.16 | 486.48 | 82.7022 | 77.795 | 73.985 | 0.8098 | 1.433 | 1.433 | 1.431 | 1.884 | 1.964 | 2.042 | Over-range | 60.01 | 19284 | 18794 | 16747 | 54824 | - - - | - - - | - - - | - - - | 19284 | 18794 | 16747 | 54824 | 12147 | 9878 | 10973 | 32997 | - - - | - - - | - - - | - - - | 12147 | 9878 | 10973 | 32997 | 23250 | 21682 | 20488 | 65420 | # # # | # # # | # # # | # # # | 0.829 | 0.867 | 0.817 | 0.838 | # # # | # # # | # # # | - - - | 0.845 | 0.884 | 0.836 | 0.855 | - - - | 0.602 | 1.68 | 1.54 | 1.49 | 1.5 | 1.44 | 1.53 | 18.37 | 19.15 | 20.48 | 0 | - - - | - - - | - - - | - - - | 23250 | 21682 | 20488 | 65420 | Over-range | 12979 | 10800 | 11791 | 35663 | 4477 | 4272 | 4218 | 13249 | 19263 | 18838 | 16793 | 54894 | 19263 | 18838 | 16793 | 54894 | - - - | - - - | - - - | - - -
5/6/2026 | 11:15:00 PM | 282.97 | 280.57 | 278.7 | 489.54 | 482.74 | 486.51 | 83.5161 | 78.369 | 74.4314 | 0.7965 | 1.432 | 1.434 | 1.43 | 1.905 | 2.003 | 2.067 | Over-range | 59.98 | 19549 | 18995 | 16885 | 55429 | - - - | - - - | - - - | - - - | 19549 | 18995 | 16885 | 55429 | 12082 | 9728 | 10870 | 32680 | - - - | - - - | - - - | - - - | 12082 | 9728 | 10870 | 32680 | 23505 | 21852 | 20622 | 65979 | # # # | # # # | # # # | # # # | 0.832 | 0.869 | 0.819 | 0.84 | # # # | # # # | # # # | - - - | 0.849 | 0.89 | 0.839 | 0.86 | - - - | 0.59 | 1.69 | 1.57 | 1.52 | 1.5 | 1.47 | 1.55 | 19.75 | 20.7 | 22.16 | 0 | - - - | - - - | - - - | - - - | 23505 | 21852 | 20622 | 65979 | Over-range | 13044 | 10787 | 11826 | 35757 | 4827 | 4582 | 4572 | 14264 | 19540 | 19078 | 16890 | 55508 | 19540 | 19078 | 16890 | 55508 | - - - | - - - | - - - | - - -
5/6/2026 | 11:30:00 PM | 283.52 | 281.16 | 279.24 | 490.51 | 483.75 | 487.45 | 83.6716 | 78.3619 | 75.1347 | 0.7983 | 1.433 | 1.434 | 1.43 | 1.901 | 1.998 | 2.062 | Over-range | 60 | 19627 | 18951 | 17025 | 55603 | - - - | - - - | - - - | - - - | 19627 | 18951 | 17025 | 55603 | 12170 | 9951 | 11138 | 33259 | - - - | - - - | - - - | - - - | 12170 | 9951 | 11138 | 33259 | 23610 | 21910 | 20873 | 66393 | # # # | # # # | # # # | # # # | 0.831 | 0.865 | 0.816 | 0.838 | # # # | # # # | # # # | - - - | 0.849 | 0.885 | 0.836 | 0.857 | - - - | 0.598 | 1.69 | 1.58 | 1.55 | 1.52 | 1.49 | 1.57 | 19.58 | 20.48 | 21.82 | 0 | - - - | - - - | - - - | - - - | 23610 | 21910 | 20873 | 66393 | Over-range | 13118 | 10985 | 12067 | 36258 | 4814 | 4572 | 4563 | 14204 | 19608 | 19024 | 17046 | 55679 | 19608 | 19024 | 17046 | 55679 | - - - | - - - | - - - | - - -
5/6/2026 | 11:45:00 PM | 283.58 | 281.26 | 279.33 | 490.62 | 483.99 | 487.51 | 84.339 | 79.4664 | 75.4671 | 0.7987 | 1.432 | 1.432 | 1.43 | 1.942 | 2.021 | 2.079 | Over-range | 60 | 19736 | 19227 | 17131 | 56094 | - - - | - - - | - - - | - - - | 19736 | 19227 | 17131 | 56094 | 12175 | 9820 | 10939 | 32934 | - - - | - - - | - - - | - - - | 12175 | 9820 | 10939 | 32934 | 23752 | 22173 | 20920 | 66846 | # # # | # # # | # # # | # # # | 0.831 | 0.867 | 0.819 | 0.839 | # # # | # # # | # # # | - - - | 0.85 | 0.889 | 0.842 | 0.86 | - - - | 0.587 | 1.65 | 1.58 | 1.53 | 1.51 | 1.47 | 1.55 | 20.57 | 21.74 | 23.07 | 0 | - - - | - - - | - - - | - - - | 23752 | 22173 | 20920 | 66846 | Over-range | 13200 | 11024 | 11990 | 36306 | 5000 | 4912 | 4817 | 14999 | 19764 | 19217 | 17193 | 56174 | 19764 | 19217 | 17193 | 56174 | - - - | - - - | - - - | - - -
5/7/2026 | 12:00:00 AM | 284.03 | 281.74 | 279.73 | 491.51 | 484.69 | 488.24 | 84.189 | 79.5393 | 75.5593 | 0.798 | 1.432 | 1.433 | 1.429 | 1.935 | 2.023 | 2.079 | Over-range | 60.01 | 19771 | 19301 | 17248 | 56320 | - - - | - - - | - - - | - - - | 19771 | 19301 | 17248 | 56320 | 12194 | 9954 | 10983 | 33131 | - - - | - - - | - - - | - - - | 12194 | 9954 | 10983 | 33131 | 23798 | 22288 | 21032 | 67119 | # # # | # # # | # # # | # # # | 0.831 | 0.866 | 0.82 | 0.839 | # # # | # # # | # # # | - - - | 0.85 | 0.888 | 0.843 | 0.86 | - - - | 0.588 | 1.7 | 1.57 | 1.53 | 1.52 | 1.48 | 1.56 | 20.65 | 21.68 | 22.99 | 0 | - - - | - - - | - - - | - - - | 23798 | 22288 | 21032 | 67119 | Over-range | 13239 | 11135 | 12025 | 36483 | 5077 | 4920 | 4823 | 15059 | 19761 | 19347 | 17300 | 56408 | 19761 | 19347 | 17300 | 56408 | - - - | - - - | - - - | - - -
5/7/2026 | 12:15:00 AM | 284.34 | 281.94 | 280.07 | 491.93 | 485.15 | 488.84 | 82.6918 | 77.5815 | 74.1631 | 0.8001 | 1.431 | 1.432 | 1.429 | 1.916 | 2.005 | 2.083 | Over-range | 59.99 | 19387 | 18784 | 16819 | 54991 | - - - | - - - | - - - | - - - | 19387 | 18784 | 16819 | 54991 | 12136 | 9907 | 11021 | 33064 | - - - | - - - | - - - | - - - | 12136 | 9907 | 11021 | 33064 | 23403 | 21753 | 20662 | 65819 | # # # | # # # | # # # | # # # | 0.828 | 0.864 | 0.814 | 0.836 | # # # | # # # | # # # | - - - | 0.847 | 0.884 | 0.835 | 0.856 | - - - | 0.601 | 1.65 | 1.55 | 1.52 | 1.5 | 1.46 | 1.54 | 20.13 | 20.93 | 22.43 | 0 | - - - | - - - | - - - | - - - | 23403 | 21753 | 20662 | 65819 | Over-range | 13103 | 10960 | 11992 | 36143 | 4867 | 4619 | 4658 | 14395 | 19401 | 18839 | 16824 | 55064 | 19401 | 18839 | 16824 | 55064 | - - - | - - - | - - - | - - -
5/7/2026 | 12:30:00 AM | 284.7 | 282.42 | 280.49 | 492.62 | 486.05 | 489.42 | 84.063 | 79.086 | 74.9722 | 0.7996 | 1.431 | 1.431 | 1.429 | 1.907 | 1.99 | 2.065 | Over-range | 60.01 | 19715 | 19240 | 17066 | 56021 | - - - | - - - | - - - | - - - | 19715 | 19240 | 17066 | 56021 | 12426 | 10048 | 11119 | 33593 | - - - | - - - | - - - | - - - | 12426 | 10048 | 11119 | 33593 | 23816 | 22210 | 20915 | 66940 | # # # | # # # | # # # | # # # | 0.828 | 0.866 | 0.816 | 0.837 | # # # | # # # | # # # | - - - | 0.846 | 0.886 | 0.836 | 0.856 | - - - | 0.6 | 1.66 | 1.54 | 1.5 | 1.5 | 1.46 | 1.53 | 19.58 | 20.52 | 22.01 | 0 | - - - | - - - | - - - | - - - | 23816 | 22210 | 20915 | 66940 | Over-range | 13355 | 11085 | 12083 | 36621 | 4815 | 4609 | 4656 | 14365 | 19775 | 19293 | 17031 | 56099 | 19775 | 19293 | 17031 | 56099 | - - - | - - - | - - - | - - -
5/7/2026 | 12:45:00 AM | 284.89 | 282.44 | 280.59 | 492.83 | 486.05 | 489.75 | 82.6742 | 77.7413 | 74.5297 | 0.8015 | 1.431 | 1.431 | 1.429 | 1.929 | 2.023 | 2.094 | Over-range | 60 | 19396 | 18774 | 16910 | 55081 | - - - | - - - | - - - | - - - | 19396 | 18774 | 16910 | 55081 | 12023 | 9895 | 10946 | 32864 | - - - | - - - | - - - | - - - | 12023 | 9895 | 10946 | 32864 | 23402 | 21795 | 20768 | 65964 | # # # | # # # | # # # | # # # | 0.829 | 0.861 | 0.814 | 0.835 | # # # | # # # | # # # | - - - | 0.849 | 0.883 | 0.837 | 0.857 | - - - | 0.597 | 1.67 | 1.53 | 1.51 | 1.49 | 1.45 | 1.53 | 20.9 | 21.84 | 23.34 | 0 | - - - | - - - | - - - | - - - | 23402 | 21795 | 20768 | 65964 | Over-range | 13077 | 11048 | 12038 | 36242 | 5040 | 4814 | 4911 | 14987 | 19463 | 18819 | 16874 | 55157 | 19463 | 18819 | 16874 | 55157 | - - - | - - - | - - - | - - -
5/7/2026 | 1:00:00 AM | 285.1 | 282.64 | 280.78 | 493.19 | 486.37 | 490.1 | 84.1154 | 79.2504 | 75.6676 | 0.8017 | 1.431 | 1.431 | 1.428 | 1.937 | 2.017 | 2.084 | Over-range | 60.01 | 19813 | 19257 | 17281 | 56350 | - - - | - - - | - - - | - - - | 19813 | 19257 | 17281 | 56350 | 12320 | 10062 | 11121 | 33503 | - - - | - - - | - - - | - - - | 12320 | 10062 | 11121 | 33503 | 23875 | 22284 | 21142 | 67301 | # # # | # # # | # # # | # # # | 0.83 | 0.864 | 0.817 | 0.837 | # # # | # # # | # # # | - - - | 0.849 | 0.885 | 0.84 | 0.858 | - - - | 0.595 | 1.67 | 1.53 | 1.5 | 1.49 | 1.46 | 1.54 | 20.56 | 21.51 | 22.98 | 0 | - - - | - - - | - - - | - - - | 23875 | 22284 | 21142 | 67301 | Over-range | 13317 | 11205 | 12171 | 36776 | 4986 | 4866 | 4882 | 14974 | 19894 | 19226 | 17308 | 56428 | 19894 | 19226 | 17308 | 56428 | - - - | - - - | - - - | - - -
5/7/2026 | 1:15:00 AM | 285 | 282.51 | 280.77 | 492.92 | 486.28 | 490.04 | 84.5384 | 79.4082 | 75.8814 | 0.804 | 1.431 | 1.431 | 1.428 | 1.932 | 2.011 | 2.082 | Over-range | 60 | 19905 | 19291 | 17296 | 56492 | - - - | - - - | - - - | - - - | 19905 | 19291 | 17296 | 56492 | 12320 | 10010 | 11187 | 33517 | - - - | - - - | - - - | - - - | 12320 | 10010 | 11187 | 33517 | 23967 | 22297 | 21181 | 67445 | # # # | # # # | # # # | # # # | 0.831 | 0.865 | 0.817 | 0.838 | # # # | # # # | # # # | - - - | 0.849 | 0.886 | 0.839 | 0.858 | - - - | 0.593 | 1.68 | 1.55 | 1.53 | 1.5 | 1.48 | 1.55 | 20.52 | 21.54 | 22.88 | 0 | - - - | - - - | - - - | - - - | 23967 | 22297 | 21181 | 67445 | Over-range | 13342 | 11171 | 12216 | 36817 | 5042 | 4885 | 4833 | 15016 | 19912 | 19296 | 17358 | 56566 | 19912 | 19296 | 17358 | 56566 | - - - | - - - | - - - | - - -
5/7/2026 | 1:30:00 AM | 285.14 | 282.65 | 280.92 | 493.18 | 486.53 | 490.29 | 83.0113 | 77.8135 | 74.8777 | 0.7861 | 1.431 | 1.431 | 1.429 | 1.927 | 2.009 | 2.078 | Over-range | 60.01 | 19585 | 18876 | 17054 | 55516 | - - - | - - - | - - - | - - - | 19585 | 18876 | 17054 | 55516 | 12050 | 9863 | 11069 | 32982 | - - - | - - - | - - - | - - - | 12050 | 9863 | 11069 | 32982 | 23557 | 21872 | 20926 | 66354 | # # # | # # # | # # # | # # # | 0.831 | 0.863 | 0.815 | 0.837 | # # # | # # # | # # # | - - - | 0.851 | 0.885 | 0.838 | 0.858 | - - - | 0.594 | 1.7 | 1.6 | 1.57 | 1.53 | 1.51 | 1.59 | 20.78 | 21.82 | 23.17 | 0 | - - - | - - - | - - - | - - - | 23557 | 21872 | 20926 | 66354 | Over-range | 13082 | 11037 | 12117 | 36318 | 5011 | 4880 | 4851 | 14979 | 19610 | 18860 | 17122 | 55592 | 19610 | 18860 | 17122 | 55592 | - - - | - - - | - - - | - - -
5/7/2026 | 1:45:00 AM | 285.54 | 282.82 | 281.1 | 493.8 | 486.66 | 490.86 | 84.988 | 78.9094 | 76.566 | 0.2525 | 1.432 | 1.431 | 1.43 | 1.825 | 1.842 | 1.938 | Over-range | 60.01 | 20053 | 19199 | 17337 | 56589 | - - - | - - - | - - - | - - - | 20053 | 19199 | 17337 | 56589 | 12631 | 10231 | 11753 | 34615 | - - - | - - - | - - - | - - - | 12631 | 10231 | 11753 | 34615 | 24168 | 22205 | 21426 | 67799 | # # # | # # # | # # # | # # # | 0.83 | 0.865 | 0.809 | 0.835 | # # # | # # # | # # # | - - - | 0.845 | 0.881 | 0.827 | 0.851 | - - - | 0.612 | 1.8 | 1.68 | 1.68 | 1.64 | 1.64 | 1.68 | 18.36 | 18.71 | 20.07 | 0 | - - - | - - - | - - - | - - - | 24168 | 22205 | 21426 | 67799 | Over-range | 13477 | 11139 | 12576 | 37300 | 4603 | 4315 | 4383 | 13631 | 20068 | 19186 | 17400 | 56654 | 20068 | 19186 | 17400 | 56654 | - - - | - - - | - - - | - - -
5/7/2026 | 2:00:00 AM | 285.64 | 282.95 | 281.23 | 493.98 | 486.9 | 491.05 | 83.3424 | 77.2674 | 74.682 | 0.2485 | 1.433 | 1.431 | 1.431 | 1.824 | 1.831 | 1.945 | Over-range | 60.02 | 19637 | 18829 | 16893 | 55359 | - - - | - - - | - - - | - - - | 19637 | 18829 | 16893 | 55359 | 12436 | 9959 | 11459 | 33854 | - - - | - - - | - - - | - - - | 12436 | 9959 | 11459 | 33854 | 23678 | 21720 | 20879 | 66278 | # # # | # # # | # # # | # # # | 0.829 | 0.867 | 0.809 | 0.835 | # # # | # # # | # # # | - - - | 0.845 | 0.883 | 0.827 | 0.852 | - - - | 0.612 | 1.85 | 1.76 | 1.72 | 1.69 | 1.71 | 1.75 | 18.18 | 18.54 | 20.02 | 0 | - - - | - - - | - - - | - - - | 23678 | 21720 | 20879 | 66278 | Over-range | 13224 | 10816 | 12260 | 36417 | 4404 | 4133 | 4277 | 13170 | 19717 | 18795 | 16918 | 55430 | 19717 | 18795 | 16918 | 55430 | - - - | - - - | - - - | - - -
5/7/2026 | 2:15:00 AM | 285.57 | 282.9 | 281.14 | 493.84 | 486.84 | 490.87 | 82.8455 | 76.7189 | 74.5125 | 0.2482 | 1.433 | 1.431 | 1.432 | 1.835 | 1.844 | 1.951 | Over-range | 60 | 19495 | 18626 | 16794 | 54916 | - - - | - - - | - - - | - - - | 19495 | 18626 | 16794 | 54916 | 12329 | 9963 | 11511 | 33802 | - - - | - - - | - - - | - - - | 12329 | 9963 | 11511 | 33802 | 23534 | 21568 | 20830 | 65931 | # # # | # # # | # # # | # # # | 0.828 | 0.864 | 0.806 | 0.833 | # # # | # # # | # # # | - - - | 0.844 | 0.881 | 0.824 | 0.85 | - - - | 0.616 | 1.88 | 1.78 | 1.76 | 1.71 | 1.74 | 1.78 | 18.61 | 19.08 | 20.29 | 0 | - - - | - - - | - - - | - - - | 23534 | 21568 | 20830 | 65931 | Over-range | 13175 | 10860 | 12312 | 36457 | 4546 | 4233 | 4272 | 13383 | 19491 | 18640 | 16852 | 54983 | 19491 | 18640 | 16852 | 54983 | - - - | - - - | - - - | - - -
5/7/2026 | 2:30:00 AM | 285.58 | 282.94 | 281.29 | 493.87 | 487.01 | 491.02 | 82.4931 | 76.2922 | 74.3207 | 0.246 | 1.434 | 1.432 | 1.432 | 1.824 | 1.834 | 1.945 | Over-range | 60.01 | 19418 | 18516 | 16741 | 54676 | - - - | - - - | - - - | - - - | 19418 | 18516 | 16741 | 54676 | 12321 | 10004 | 11572 | 33898 | - - - | - - - | - - - | - - - | 12321 | 10004 | 11572 | 33898 | 23444 | 21460 | 20794 | 65698 | # # # | # # # | # # # | # # # | 0.828 | 0.863 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.843 | 0.879 | 0.822 | 0.848 | - - - | 0.62 | 1.93 | 1.81 | 1.8 | 1.75 | 1.78 | 1.82 | 18.23 | 18.58 | 19.9 | 0 | - - - | - - - | - - - | - - - | 23444 | 21460 | 20794 | 65698 | Over-range | 13130 | 10839 | 12325 | 36403 | 4459 | 4092 | 4161 | 13042 | 19393 | 18557 | 16796 | 54746 | 19393 | 18557 | 16796 | 54746 | - - - | - - - | - - - | - - -
5/7/2026 | 2:45:00 AM | 285.77 | 283.18 | 281.46 | 494.27 | 487.39 | 491.29 | 83.837 | 77.7974 | 74.7891 | 0.2466 | 1.434 | 1.432 | 1.432 | 1.822 | 1.818 | 1.939 | Over-range | 60 | 19681 | 18953 | 16879 | 55513 | - - - | - - - | - - - | - - - | 19681 | 18953 | 16879 | 55513 | 12591 | 10035 | 11568 | 34194 | - - - | - - - | - - - | - - - | 12591 | 10035 | 11568 | 34194 | 23815 | 21872 | 20908 | 66595 | # # # | # # # | # # # | # # # | 0.826 | 0.867 | 0.807 | 0.834 | # # # | # # # | # # # | - - - | 0.841 | 0.882 | 0.824 | 0.849 | - - - | 0.616 | 1.95 | 1.82 | 1.79 | 1.76 | 1.78 | 1.83 | 17.81 | 18.24 | 19.5 | 0 | - - - | - - - | - - - | - - - | 23815 | 21872 | 20908 | 66595 | Over-range | 13395 | 10895 | 12324 | 36739 | 4459 | 4140 | 4140 | 13130 | 19664 | 18971 | 16943 | 55578 | 19664 | 18971 | 16943 | 55578 | - - - | - - - | - - - | - - -
5/7/2026 | 3:00:00 AM | 285.86 | 283.27 | 281.57 | 494.38 | 487.61 | 491.45 | 81.192 | 75.303 | 73.3914 | 0.2439 | 1.434 | 1.432 | 1.432 | 1.834 | 1.84 | 1.948 | Over-range | 60.01 | 19128 | 18271 | 16566 | 53965 | - - - | - - - | - - - | - - - | 19128 | 18271 | 16566 | 53965 | 12130 | 9906 | 11403 | 33439 | - - - | - - - | - - - | - - - | 12130 | 9906 | 11403 | 33439 | 23099 | 21212 | 20559 | 64870 | # # # | # # # | # # # | # # # | 0.828 | 0.861 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.843 | 0.878 | 0.824 | 0.849 | - - - | 0.62 | 1.93 | 1.83 | 1.81 | 1.77 | 1.79 | 1.83 | 18.51 | 18.91 | 20.08 | 0 | - - - | - - - | - - - | - - - | 23099 | 21212 | 20559 | 64870 | Over-range | 12944 | 10765 | 12166 | 35975 | 4439 | 4139 | 4164 | 13046 | 19113 | 18286 | 16637 | 54036 | 19113 | 18286 | 16637 | 54036 | - - - | - - - | - - - | - - -
5/7/2026 | 3:15:00 AM | 285.83 | 283.31 | 281.55 | 494.42 | 487.61 | 491.39 | 83.9213 | 77.939 | 75.6494 | 0.3085 | 1.434 | 1.432 | 1.432 | 1.832 | 1.824 | 1.932 | Over-range | 60.01 | 19769 | 18941 | 17108 | 55818 | - - - | - - - | - - - | - - - | 19769 | 18941 | 17108 | 55818 | 12589 | 10252 | 11744 | 34585 | - - - | - - - | - - - | - - - | 12589 | 10252 | 11744 | 34585 | 23879 | 21961 | 21193 | 67033 | # # # | # # # | # # # | # # # | 0.828 | 0.863 | 0.807 | 0.833 | # # # | # # # | # # # | - - - | 0.843 | 0.878 | 0.824 | 0.848 | - - - | 0.62 | 1.92 | 1.79 | 1.8 | 1.74 | 1.77 | 1.82 | 17.92 | 18.36 | 19.36 | 0 | - - - | - - - | - - - | - - - | 23879 | 21961 | 21193 | 67033 | Over-range | 13386 | 11103 | 12498 | 37090 | 4460 | 4181 | 4184 | 13150 | 19779 | 18938 | 17165 | 55883 | 19779 | 18938 | 17165 | 55883 | - - - | - - - | - - - | - - -
5/7/2026 | 3:30:00 AM | 285.03 | 282.64 | 280.82 | 493.09 | 486.48 | 490.04 | 83.0363 | 77.2942 | 74.4067 | 0.2651 | 1.436 | 1.434 | 1.431 | 1.884 | 1.853 | 1.979 | Over-range | 60.01 | 19466 | 18775 | 16803 | 55045 | - - - | - - - | - - - | - - - | 19466 | 18775 | 16803 | 55045 | 12375 | 9942 | 11373 | 33690 | - - - | - - - | - - - | - - - | 12375 | 9942 | 11373 | 33690 | 23533 | 21703 | 20768 | 66004 | # # # | # # # | # # # | # # # | 0.827 | 0.865 | 0.809 | 0.834 | # # # | # # # | # # # | - - - | 0.844 | 0.882 | 0.828 | 0.851 | - - - | 0.612 | 1.89 | 1.81 | 1.82 | 1.74 | 1.78 | 1.82 | 19 | 19.51 | 20.42 | 0 | - - - | - - - | - - - | - - - | 23533 | 21703 | 20768 | 66004 | Over-range | 13217 | 10873 | 12192 | 36392 | 4550 | 4320 | 4308 | 13512 | 19530 | 18742 | 16842 | 55114 | 19530 | 18742 | 16842 | 55114 | - - - | - - - | - - - | - - -
5/7/2026 | 3:45:00 AM | 285.24 | 282.91 | 281.24 | 493.42 | 487.19 | 490.57 | 81.934 | 76.5669 | 74.416 | 0.2792 | 1.434 | 1.433 | 1.431 | 1.899 | 1.882 | 1.979 | Over-range | 60 | 19248 | 18497 | 16826 | 54570 | - - - | - - - | - - - | - - - | 19248 | 18497 | 16826 | 54570 | 12092 | 9974 | 11357 | 33423 | - - - | - - - | - - - | - - - | 12092 | 9974 | 11357 | 33423 | 23253 | 21529 | 20812 | 65594 | # # # | # # # | # # # | # # # | 0.828 | 0.859 | 0.809 | 0.832 | # # # | # # # | # # # | - - - | 0.845 | 0.878 | 0.828 | 0.851 | - - - | 0.613 | 1.97 | 1.92 | 1.94 | 1.82 | 1.9 | 1.92 | 19.68 | 20.37 | 21.03 | 0 | - - - | - - - | - - - | - - - | 23253 | 21529 | 20812 | 65594 | Over-range | 13032 | 10996 | 12233 | 36347 | 4745 | 4522 | 4434 | 13960 | 19246 | 18503 | 16893 | 54643 | 19246 | 18503 | 16893 | 54643 | - - - | - - - | - - - | - - -
5/7/2026 | 4:00:00 AM | 285.49 | 283.15 | 281.47 | 493.93 | 487.51 | 490.97 | 84.3101 | 78.9365 | 76.1954 | 0.2791 | 1.434 | 1.432 | 1.431 | 1.883 | 1.863 | 1.969 | Over-range | 60.02 | 19862 | 19200 | 17340 | 56401 | - - - | - - - | - - - | - - - | 19862 | 19200 | 17340 | 56401 | 12524 | 10256 | 11620 | 34400 | - - - | - - - | - - - | - - - | 12524 | 10256 | 11620 | 34400 | 23972 | 22244 | 21351 | 67566 | # # # | # # # | # # # | # # # | 0.829 | 0.863 | 0.812 | 0.835 | # # # | # # # | # # # | - - - | 0.845 | 0.881 | 0.831 | 0.852 | - - - | 0.61 | 1.88 | 1.84 | 1.83 | 1.73 | 1.79 | 1.83 | 19.05 | 19.54 | 20.38 | 0 | - - - | - - - | - - - | - - - | 23972 | 22244 | 21351 | 67566 | Over-range | 13416 | 11223 | 12449 | 37181 | 4727 | 4479 | 4383 | 13873 | 19856 | 19202 | 17418 | 56476 | 19856 | 19202 | 17418 | 56476 | - - - | - - - | - - - | - - -
5/7/2026 | 4:15:00 AM | 285.47 | 283.03 | 281.46 | 493.78 | 487.38 | 491 | 83.8801 | 78.428 | 75.7328 | 0.2775 | 1.434 | 1.432 | 1.431 | 1.88 | 1.871 | 1.977 | Over-range | 60 | 19756 | 19067 | 17212 | 56034 | - - - | - - - | - - - | - - - | 19756 | 19067 | 17212 | 56034 | 12424 | 10116 | 11503 | 34043 | - - - | - - - | - - - | - - - | 12424 | 10116 | 11503 | 34043 | 23827 | 22068 | 21201 | 67095 | # # # | # # # | # # # | # # # | 0.829 | 0.864 | 0.812 | 0.835 | # # # | # # # | # # # | - - - | 0.846 | 0.882 | 0.831 | 0.853 | - - - | 0.608 | 1.88 | 1.76 | 1.79 | 1.7 | 1.73 | 1.78 | 19.25 | 19.84 | 20.82 | 0 | - - - | - - - | - - - | - - - | 23827 | 22068 | 21201 | 67095 | Over-range | 13313 | 11096 | 12367 | 36873 | 4704 | 4485 | 4461 | 13942 | 19784 | 19049 | 17278 | 56111 | 19784 | 19049 | 17278 | 56111 | - - - | - - - | - - - | - - -
5/7/2026 | 4:30:00 AM | 285.29 | 282.92 | 281.3 | 493.51 | 487.22 | 490.65 | 81.8798 | 76.5355 | 74.5531 | 0.2763 | 1.434 | 1.432 | 1.431 | 1.896 | 1.892 | 1.99 | Over-range | 60 | 19251 | 18478 | 16861 | 54590 | - - - | - - - | - - - | - - - | 19251 | 18478 | 16861 | 54590 | 12038 | 9983 | 11302 | 33324 | - - - | - - - | - - - | - - - | 12038 | 9983 | 11302 | 33324 | 23221 | 21501 | 20839 | 65561 | # # # | # # # | # # # | # # # | 0.829 | 0.859 | 0.809 | 0.833 | # # # | # # # | # # # | - - - | 0.848 | 0.879 | 0.829 | 0.852 | - - - | 0.61 | 1.86 | 1.76 | 1.77 | 1.69 | 1.72 | 1.78 | 19.97 | 20.67 | 21.63 | 0 | - - - | - - - | - - - | - - - | 23221 | 21501 | 20839 | 65561 | Over-range | 12977 | 10983 | 12234 | 36277 | 4752 | 4490 | 4593 | 14073 | 19320 | 18498 | 16850 | 54668 | 19320 | 18498 | 16850 | 54668 | - - - | - - - | - - - | - - -
5/7/2026 | 4:45:00 AM | 285.17 | 282.78 | 281.19 | 493.31 | 486.94 | 490.49 | 84.6651 | 79.6799 | 76.8443 | 0.2806 | 1.434 | 1.432 | 1.431 | 1.913 | 1.911 | 2.009 | Over-range | 60 | 19991 | 19370 | 17559 | 56920 | - - - | - - - | - - - | - - - | 19991 | 19370 | 17559 | 56920 | 12221 | 10061 | 11296 | 33578 | - - - | - - - | - - - | - - - | 12221 | 10061 | 11296 | 33578 | 24034 | 22409 | 21498 | 67941 | # # # | # # # | # # # | # # # | 0.832 | 0.864 | 0.817 | 0.838 | # # # | # # # | # # # | - - - | 0.852 | 0.886 | 0.839 | 0.859 | - - - | 0.59 | 1.87 | 1.76 | 1.79 | 1.7 | 1.73 | 1.78 | 21.05 | 21.76 | 22.91 | 0 | - - - | - - - | - - - | - - - | 24034 | 22409 | 21498 | 67941 | Over-range | 13327 | 11248 | 12388 | 37048 | 5232 | 4948 | 5008 | 15421 | 20040 | 19435 | 17537 | 57012 | 20040 | 19435 | 17537 | 57012 | - - - | - - - | - - - | - - -
5/7/2026 | 5:00:00 AM | 285.41 | 283.08 | 281.44 | 493.78 | 487.43 | 490.89 | 84.9226 | 79.7672 | 77.3765 | 0.2815 | 1.434 | 1.432 | 1.431 | 1.92 | 1.918 | 2.005 | Over-range | 60.02 | 20083 | 19369 | 17668 | 57120 | - - - | - - - | - - - | - - - | 20083 | 19369 | 17668 | 57120 | 12265 | 10176 | 11496 | 33937 | - - - | - - - | - - - | - - - | 12265 | 10176 | 11496 | 33937 | 24128 | 22462 | 21671 | 68261 | # # # | # # # | # # # | # # # | 0.832 | 0.862 | 0.815 | 0.837 | # # # | # # # | # # # | - - - | 0.852 | 0.885 | 0.838 | 0.858 | - - - | 0.594 | 1.86 | 1.77 | 1.82 | 1.71 | 1.75 | 1.8 | 21.17 | 22.01 | 22.86 | 0 | - - - | - - - | - - - | - - - | 24128 | 22462 | 21671 | 68261 | Over-range | 13367 | 11365 | 12539 | 37351 | 5249 | 5000 | 4943 | 15415 | 20071 | 19430 | 17719 | 57219 | 20071 | 19430 | 17719 | 57219 | - - - | - - - | - - - | - - -
5/7/2026 | 5:15:00 AM | 284.99 | 282.73 | 281.01 | 493.1 | 486.82 | 490.12 | 84.2166 | 79.2783 | 77.0493 | 0.2808 | 1.435 | 1.434 | 1.432 | 1.91 | 1.912 | 1.99 | Over-range | 60 | 19885 | 19190 | 17570 | 56646 | - - - | - - - | - - - | - - - | 19885 | 19190 | 17570 | 56646 | 12198 | 10196 | 11446 | 33840 | - - - | - - - | - - - | - - - | 12198 | 10196 | 11446 | 33840 | 23894 | 22299 | 21548 | 67741 | # # # | # # # | # # # | # # # | 0.832 | 0.861 | 0.815 | 0.836 | # # # | # # # | # # # | - - - | 0.852 | 0.882 | 0.837 | 0.857 | - - - | 0.597 | 1.91 | 1.82 | 1.84 | 1.74 | 1.78 | 1.84 | 20.57 | 21.53 | 22.24 | 0 | - - - | - - - | - - - | - - - | 23894 | 22299 | 21548 | 67741 | Over-range | 13240 | 11345 | 12464 | 37121 | 5064 | 4896 | 4852 | 15020 | 19921 | 19206 | 17609 | 56735 | 19921 | 19206 | 17609 | 56735 | - - - | - - - | - - - | - - -
5/7/2026 | 5:30:00 AM | 284.77 | 282.53 | 280.86 | 492.73 | 486.49 | 489.82 | 84.5109 | 79.6619 | 77.0535 | 0.2814 | 1.435 | 1.434 | 1.432 | 1.906 | 1.9 | 1.985 | Over-range | 60.01 | 19934 | 19309 | 17602 | 56845 | - - - | - - - | - - - | - - - | 19934 | 19309 | 17602 | 56845 | 12203 | 10153 | 11386 | 33742 | - - - | - - - | - - - | - - - | 12203 | 10153 | 11386 | 33742 | 23936 | 22368 | 21521 | 67824 | # # # | # # # | # # # | # # # | 0.833 | 0.863 | 0.818 | 0.838 | # # # | # # # | # # # | - - - | 0.852 | 0.884 | 0.839 | 0.858 | - - - | 0.594 | 1.92 | 1.83 | 1.83 | 1.74 | 1.78 | 1.84 | 20.31 | 21.14 | 21.88 | 0 | - - - | - - - | - - - | - - - | 23936 | 22368 | 21521 | 67824 | Over-range | 13242 | 11277 | 12371 | 36967 | 5048 | 4824 | 4747 | 14840 | 19929 | 19356 | 17654 | 56939 | 19929 | 19356 | 17654 | 56939 | - - - | - - - | - - - | - - -
5/7/2026 | 5:45:00 AM | 284.05 | 281.78 | 280.08 | 491.51 | 485.09 | 488.54 | 83.1784 | 78.1903 | 75.5895 | 0.2777 | 1.435 | 1.433 | 1.432 | 1.908 | 1.899 | 1.992 | Over-range | 60 | 19539 | 18898 | 17168 | 55605 | - - - | - - - | - - - | - - - | 19539 | 18898 | 17168 | 55605 | 12050 | 9957 | 11184 | 33190 | - - - | - - - | - - - | - - - | 12050 | 9957 | 11184 | 33190 | 23509 | 21902 | 21054 | 66465 | # # # | # # # | # # # | # # # | 0.831 | 0.863 | 0.815 | 0.837 | # # # | # # # | # # # | - - - | 0.85 | 0.883 | 0.836 | 0.857 | - - - | 0.597 | 1.88 | 1.83 | 1.82 | 1.73 | 1.77 | 1.83 | 20.29 | 21.03 | 21.93 | 0 | - - - | - - - | - - - | - - - | 23509 | 21902 | 21054 | 66465 | Over-range | 13060 | 11053 | 12173 | 36366 | 4943 | 4710 | 4716 | 14600 | 19598 | 18926 | 17171 | 55695 | 19598 | 18926 | 17171 | 55695 | - - - | - - - | - - - | - - -
5/7/2026 | 6:00:00 AM | 283.64 | 281.42 | 279.83 | 490.76 | 484.66 | 487.96 | 84.0031 | 78.8888 | 75.7688 | 0.2794 | 1.435 | 1.434 | 1.432 | 1.893 | 1.891 | 1.985 | Over-range | 60.02 | 19720 | 19139 | 17226 | 56085 | - - - | - - - | - - - | - - - | 19720 | 19139 | 17226 | 56085 | 12165 | 9904 | 11205 | 33273 | - - - | - - - | - - - | - - - | 12165 | 9904 | 11205 | 33273 | 23696 | 22060 | 21075 | 66831 | # # # | # # # | # # # | # # # | 0.832 | 0.868 | 0.817 | 0.839 | # # # | # # # | # # # | - - - | 0.85 | 0.887 | 0.837 | 0.858 | - - - | 0.593 | 1.93 | 1.85 | 1.89 | 1.77 | 1.81 | 1.87 | 19.74 | 20.58 | 21.53 | 0 | - - - | - - - | - - - | - - - | 23696 | 22060 | 21075 | 66831 | Over-range | 13131 | 10958 | 12131 | 36315 | 4859 | 4610 | 4567 | 14310 | 19730 | 19206 | 17243 | 56178 | 19730 | 19206 | 17243 | 56178 | - - - | - - - | - - - | - - -
5/7/2026 | 6:15:00 AM | 282.77 | 280.6 | 278.85 | 489.34 | 483.06 | 486.34 | 82.8798 | 78.0816 | 75.6233 | 0.2778 | 1.436 | 1.436 | 1.433 | 1.929 | 1.923 | 2.012 | Over-range | 59.98 | 19478 | 18836 | 17204 | 55518 | - - - | - - - | - - - | - - - | 19478 | 18836 | 17204 | 55518 | 11691 | 9721 | 10916 | 32329 | - - - | - - - | - - - | - - - | 11691 | 9721 | 10916 | 32329 | 23312 | 21776 | 20969 | 66058 | # # # | # # # | # # # | # # # | 0.836 | 0.865 | 0.82 | 0.84 | # # # | # # # | # # # | - - - | 0.857 | 0.888 | 0.843 | 0.863 | - - - | 0.582 | 2.05 | 1.97 | 2.01 | 1.87 | 1.93 | 2 | 21.43 | 22.23 | 23.06 | 0 | - - - | - - - | - - - | - - - | 23312 | 21776 | 20969 | 66058 | Over-range | 12803 | 10916 | 11978 | 35771 | 5148 | 4900 | 4863 | 15109 | 19515 | 18895 | 17214 | 55624 | 19515 | 18895 | 17214 | 55624 | - - - | - - - | - - - | - - -
5/7/2026 | 6:30:00 AM | 281.92 | 279.72 | 278.09 | 487.82 | 481.63 | 484.98 | 84.0997 | 79.1303 | 76.7858 | 0.2789 | 1.436 | 1.437 | 1.434 | 1.911 | 1.914 | 2.004 | Over-range | 59.99 | 19792 | 19108 | 17490 | 56390 | - - - | - - - | - - - | - - - | 19792 | 19108 | 17490 | 56390 | 11769 | 9790 | 11040 | 32599 | - - - | - - - | - - - | - - - | 11769 | 9790 | 11040 | 32599 | 23616 | 22034 | 21262 | 66911 | # # # | # # # | # # # | # # # | 0.838 | 0.867 | 0.823 | 0.843 | # # # | # # # | # # # | - - - | 0.859 | 0.89 | 0.845 | 0.864 | - - - | 0.578 | 2.07 | 2.01 | 2.03 | 1.88 | 1.95 | 2.02 | 20.93 | 21.62 | 22.59 | 0 | - - - | - - - | - - - | - - - | 23616 | 22034 | 21262 | 66911 | Over-range | 12876 | 10961 | 12080 | 35992 | 5151 | 4858 | 4831 | 15044 | 19792 | 19189 | 17517 | 56499 | 19792 | 19189 | 17517 | 56499 | - - - | - - - | - - - | - - -
5/7/2026 | 6:45:00 AM | 281.56 | 279.33 | 277.67 | 487.18 | 480.91 | 484.32 | 85.3057 | 80.1323 | 76.9079 | 0.2796 | 1.436 | 1.437 | 1.433 | 1.913 | 1.916 | 2.014 | Over-range | 60 | 19969 | 19363 | 17446 | 56778 | - - - | - - - | - - - | - - - | 19969 | 19363 | 17446 | 56778 | 11954 | 9666 | 10966 | 32586 | - - - | - - - | - - - | - - - | 11954 | 9666 | 10966 | 32586 | 23885 | 22237 | 21227 | 67349 | # # # | # # # | # # # | # # # | 0.836 | 0.871 | 0.822 | 0.843 | # # # | # # # | # # # | - - - | 0.857 | 0.894 | 0.845 | 0.866 | - - - | 0.574 | 2.03 | 1.98 | 1.99 | 1.84 | 1.9 | 1.98 | 21.08 | 21.93 | 23.09 | 0 | - - - | - - - | - - - | - - - | 23885 | 22237 | 21227 | 67349 | Over-range | 13088 | 10911 | 12073 | 36166 | 5221 | 4961 | 4953 | 15395 | 20036 | 19416 | 17431 | 56883 | 20036 | 19416 | 17431 | 56883 | - - - | - - - | - - - | - - -
5/7/2026 | 7:00:00 AM | 281.5 | 279.41 | 277.78 | 487.12 | 481.16 | 484.34 | 83.4703 | 78.6478 | 76.2732 | 0.2788 | 1.436 | 1.437 | 1.433 | 1.91 | 1.913 | 2.007 | Over-range | 60.01 | 19595 | 18958 | 17352 | 55905 | - - - | - - - | - - - | - - - | 19595 | 18958 | 17352 | 55905 | 11713 | 9760 | 10938 | 32411 | - - - | - - - | - - - | - - - | 11713 | 9760 | 10938 | 32411 | 23403 | 21873 | 21094 | 66370 | # # # | # # # | # # # | # # # | 0.837 | 0.867 | 0.823 | 0.842 | # # # | # # # | # # # | - - - | 0.858 | 0.888 | 0.844 | 0.864 | - - - | 0.58 | 2.01 | 1.93 | 1.94 | 1.81 | 1.86 | 1.94 | 20.86 | 21.5 | 22.61 | 0 | - - - | - - - | - - - | - - - | 23403 | 21873 | 21094 | 66370 | Over-range | 12789 | 10899 | 11985 | 35746 | 5067 | 4786 | 4833 | 14881 | 19666 | 19020 | 17320 | 56007 | 19666 | 19020 | 17320 | 56007 | - - - | - - - | - - - | - - -
5/7/2026 | 7:15:00 AM | 282.25 | 280.2 | 278.55 | 488.46 | 482.49 | 485.69 | 84.7172 | 79.9868 | 76.7708 | 0.2785 | 1.436 | 1.438 | 1.433 | 1.917 | 1.923 | 2.018 | Over-range | 60 | 19906 | 19397 | 17542 | 56845 | - - - | - - - | - - - | - - - | 19906 | 19397 | 17542 | 56845 | 11891 | 9726 | 10940 | 32558 | - - - | - - - | - - - | - - - | 11891 | 9726 | 10940 | 32558 | 23806 | 22296 | 21281 | 67383 | # # # | # # # | # # # | # # # | 0.836 | 0.87 | 0.824 | 0.844 | # # # | # # # | # # # | - - - | 0.857 | 0.893 | 0.848 | 0.866 | - - - | 0.573 | 2.04 | 1.98 | 1.99 | 1.85 | 1.9 | 1.98 | 21.43 | 22.15 | 23.31 | 0 | - - - | - - - | - - - | - - - | 23806 | 22296 | 21281 | 67383 | Over-range | 13049 | 10983 | 12037 | 36154 | 5302 | 5034 | 4951 | 15515 | 19900 | 19476 | 17578 | 56954 | 19900 | 19476 | 17578 | 56954 | - - - | - - - | - - - | - - -
5/7/2026 | 7:30:00 AM | 282.56 | 280.55 | 278.82 | 489.07 | 483.01 | 486.17 | 81.9838 | 77.9702 | 74.9607 | 0.2772 | 1.436 | 1.437 | 1.432 | 1.934 | 1.932 | 2.031 | Over-range | 60.01 | 19203 | 18802 | 17128 | 55133 | - - - | - - - | - - - | - - - | 19203 | 18802 | 17128 | 55133 | 11597 | 9707 | 10693 | 31997 | - - - | - - - | - - - | - - - | 11597 | 9707 | 10693 | 31997 | 23058 | 21759 | 20798 | 65615 | # # # | # # # | # # # | # # # | 0.833 | 0.864 | 0.824 | 0.84 | # # # | # # # | # # # | - - - | 0.855 | 0.888 | 0.848 | 0.864 | - - - | 0.58 | 2.07 | 1.99 | 2 | 1.87 | 1.92 | 2 | 22.03 | 22.54 | 23.66 | 0 | - - - | - - - | - - - | - - - | 23058 | 21759 | 20798 | 65615 | Over-range | 12757 | 10942 | 11790 | 35554 | 5257 | 4993 | 4909 | 15332 | 19200 | 18882 | 17162 | 55245 | 19200 | 18882 | 17162 | 55245 | - - - | - - - | - - - | - - -
5/7/2026 | 7:45:00 AM | 282.32 | 280.21 | 278.53 | 488.51 | 482.47 | 485.76 | 85.2959 | 81.1521 | 78.236 | 0.2842 | 1.436 | 1.437 | 1.432 | 1.952 | 1.955 | 2.042 | Over-range | 60.01 | 20012 | 19547 | 17885 | 57444 | - - - | - - - | - - - | - - - | 20012 | 19547 | 17885 | 57444 | 11865 | 9953 | 10987 | 32805 | - - - | - - - | - - - | - - - | 11865 | 9953 | 10987 | 32805 | 23972 | 22620 | 21685 | 68276 | # # # | # # # | # # # | # # # | 0.835 | 0.864 | 0.825 | 0.841 | # # # | # # # | # # # | - - - | 0.859 | 0.89 | 0.851 | 0.867 | - - - | 0.571 | 2 | 1.94 | 1.93 | 1.82 | 1.85 | 1.93 | 22.92 | 23.54 | 24.67 | 0 | - - - | - - - | - - - | - - - | 23972 | 22620 | 21685 | 68276 | Over-range | 13184 | 11364 | 12245 | 36856 | 5678 | 5415 | 5340 | 16599 | 20016 | 19639 | 17910 | 57565 | 20016 | 19639 | 17910 | 57565 | - - - | - - - | - - - | - - -
5/7/2026 | 8:00:00 AM | 282.14 | 280.04 | 278.35 | 488.25 | 482.11 | 485.46 | 85.0169 | 80.8959 | 77.1747 | 0.2821 | 1.436 | 1.437 | 1.432 | 1.957 | 1.956 | 2.054 | Over-range | 60.01 | 19953 | 19604 | 17702 | 57259 | - - - | - - - | - - - | - - - | 19953 | 19604 | 17702 | 57259 | 11812 | 9696 | 10708 | 32216 | - - - | - - - | - - - | - - - | 11812 | 9696 | 10708 | 32216 | 23891 | 22551 | 21389 | 67832 | # # # | # # # | # # # | # # # | 0.835 | 0.869 | 0.828 | 0.844 | # # # | # # # | # # # | - - - | 0.86 | 0.896 | 0.854 | 0.87 | - - - | 0.563 | 1.99 | 1.93 | 1.86 | 1.78 | 1.81 | 1.89 | 23.12 | 23.79 | 25.13 | 0 | - - - | - - - | - - - | - - - | 23891 | 22551 | 21389 | 67832 | Over-range | 13134 | 11136 | 11997 | 36343 | 5680 | 5422 | 5356 | 16654 | 19993 | 19689 | 17694 | 57377 | 19993 | 19689 | 17694 | 57377 | - - - | - - - | - - - | - - -
5/7/2026 | 8:15:00 AM | 281.83 | 279.58 | 277.99 | 487.55 | 481.35 | 484.96 | 84.1531 | 79.4256 | 77.2228 | 0.2791 | 1.436 | 1.437 | 1.432 | 1.954 | 1.961 | 2.059 | Over-range | 60 | 19755 | 19086 | 17575 | 56416 | - - - | - - - | - - - | - - - | 19755 | 19086 | 17575 | 56416 | 11587 | 9711 | 10855 | 32152 | - - - | - - - | - - - | - - - | 11587 | 9711 | 10855 | 32152 | 23593 | 22077 | 21350 | 67021 | # # # | # # # | # # # | # # # | 0.837 | 0.865 | 0.823 | 0.842 | # # # | # # # | # # # | - - - | 0.862 | 0.891 | 0.849 | 0.868 | - - - | 0.57 | 1.97 | 1.93 | 1.91 | 1.79 | 1.84 | 1.91 | 23.12 | 23.8 | 24.92 | 0 | - - - | - - - | - - - | - - - | 23593 | 22077 | 21350 | 67021 | Over-range | 12889 | 11084 | 12112 | 36149 | 5578 | 5283 | 5311 | 16340 | 19817 | 19164 | 17555 | 56536 | 19817 | 19164 | 17555 | 56536 | - - - | - - - | - - - | - - -
5/7/2026 | 8:30:00 AM | 281.56 | 279.4 | 277.69 | 487.2 | 480.95 | 484.42 | 86.2062 | 81.7632 | 78.9746 | 0.2839 | 1.436 | 1.437 | 1.432 | 1.943 | 1.943 | 2.027 | Over-range | 60.01 | 20257 | 19710 | 18056 | 58023 | - - - | - - - | - - - | - - - | 20257 | 19710 | 18056 | 58023 | 11956 | 10003 | 11076 | 33035 | - - - | - - - | - - - | - - - | 11956 | 10003 | 11076 | 33035 | 24186 | 22750 | 21846 | 68782 | # # # | # # # | # # # | # # # | 0.838 | 0.866 | 0.827 | 0.844 | # # # | # # # | # # # | - - - | 0.861 | 0.891 | 0.851 | 0.868 | - - - | 0.569 | 2 | 1.94 | 1.89 | 1.8 | 1.83 | 1.92 | 22.27 | 23.01 | 23.98 | 0 | - - - | - - - | - - - | - - - | 24186 | 22750 | 21846 | 68782 | Over-range | 13208 | 11353 | 12288 | 36913 | 5551 | 5312 | 5265 | 16300 | 20320 | 19773 | 18047 | 58141 | 20320 | 19773 | 18047 | 58141 | - - - | - - - | - - - | - - -
5/7/2026 | 8:45:00 AM | 282.35 | 280.07 | 278.39 | 488.52 | 482.02 | 485.76 | 85.6154 | 81.2235 | 77.6213 | 0.2816 | 1.436 | 1.437 | 1.432 | 1.955 | 1.954 | 2.052 | Over-range | 60.02 | 20077 | 19641 | 17749 | 57468 | - - - | - - - | - - - | - - - | 20077 | 19641 | 17749 | 57468 | 11888 | 9700 | 10781 | 32369 | - - - | - - - | - - - | - - - | 11888 | 9700 | 10781 | 32369 | 24046 | 22612 | 21488 | 68147 | # # # | # # # | # # # | # # # | 0.835 | 0.869 | 0.826 | 0.843 | # # # | # # # | # # # | - - - | 0.86 | 0.895 | 0.853 | 0.87 | - - - | 0.563 | 1.98 | 1.94 | 1.91 | 1.8 | 1.84 | 1.91 | 23.15 | 23.91 | 25.11 | 0 | - - - | - - - | - - - | - - - | 24046 | 22612 | 21488 | 68147 | Over-range | 13220 | 11182 | 12097 | 36576 | 5695 | 5485 | 5409 | 16798 | 20155 | 19674 | 17767 | 57596 | 20155 | 19674 | 17767 | 57596 | - - - | - - - | - - - | - - -
5/7/2026 | 9:00:00 AM | 282.12 | 279.8 | 278.09 | 488.09 | 481.53 | 485.3 | 84.743 | 80.3844 | 77.4013 | 0.28 | 1.436 | 1.438 | 1.432 | 1.954 | 1.956 | 2.052 | Over-range | 60.02 | 19899 | 19386 | 17691 | 56976 | - - - | - - - | - - - | - - - | 19899 | 19386 | 17691 | 56976 | 11757 | 9732 | 10784 | 32273 | - - - | - - - | - - - | - - - | 11757 | 9732 | 10784 | 32273 | 23794 | 22369 | 21415 | 67578 | # # # | # # # | # # # | # # # | 0.836 | 0.867 | 0.826 | 0.843 | # # # | # # # | # # # | - - - | 0.861 | 0.893 | 0.853 | 0.869 | - - - | 0.566 | 1.98 | 1.95 | 1.89 | 1.82 | 1.84 | 1.92 | 23.11 | 23.81 | 24.97 | 0 | - - - | - - - | - - - | - - - | 23794 | 22369 | 21415 | 67578 | Over-range | 13038 | 11150 | 12058 | 36313 | 5576 | 5386 | 5341 | 16479 | 20007 | 19381 | 17716 | 57103 | 20007 | 19381 | 17716 | 57103 | - - - | - - - | - - - | - - -
5/7/2026 | 9:15:00 AM | 281.73 | 279.38 | 277.71 | 487.34 | 480.9 | 484.62 | 85.4905 | 81.3344 | 78.099 | 0.283 | 1.436 | 1.437 | 1.433 | 1.954 | 1.956 | 2.049 | Over-range | 59.99 | 20088 | 19642 | 17901 | 57632 | - - - | - - - | - - - | - - - | 20088 | 19642 | 17901 | 57632 | 11819 | 9823 | 10804 | 32446 | - - - | - - - | - - - | - - - | 11819 | 9823 | 10804 | 32446 | 24003 | 22633 | 21610 | 68245 | # # # | # # # | # # # | # # # | 0.837 | 0.868 | 0.828 | 0.845 | # # # | # # # | # # # | - - - | 0.862 | 0.894 | 0.855 | 0.87 | - - - | 0.563 | 1.96 | 1.91 | 1.89 | 1.8 | 1.83 | 1.9 | 23.04 | 23.64 | 24.85 | 0 | - - - | - - - | - - - | - - - | 24003 | 22633 | 21610 | 68245 | Over-range | 13132 | 11237 | 12097 | 36531 | 5670 | 5405 | 5389 | 16633 | 20167 | 19718 | 17871 | 57755 | 20167 | 19718 | 17871 | 57755 | - - - | - - - | - - - | - - -
5/7/2026 | 9:30:00 AM | 281.43 | 278.87 | 277.36 | 486.63 | 480.03 | 484.18 | 86.0772 | 81.4475 | 77.9055 | 0.2814 | 1.436 | 1.438 | 1.433 | 1.977 | 1.986 | 2.085 | Over-range | 60 | 20192 | 19684 | 17788 | 57664 | - - - | - - - | - - - | - - - | 20192 | 19684 | 17788 | 57664 | 11724 | 9497 | 10655 | 31877 | - - - | - - - | - - - | - - - | 11724 | 9497 | 10655 | 31877 | 24122 | 22603 | 21507 | 68232 | # # # | # # # | # # # | # # # | 0.837 | 0.871 | 0.827 | 0.845 | # # # | # # # | # # # | - - - | 0.864 | 0.901 | 0.857 | 0.874 | - - - | 0.553 | 1.97 | 1.93 | 1.9 | 1.79 | 1.84 | 1.9 | 24.3 | 25.06 | 26.5 | 0 | - - - | - - - | - - - | - - - | 24122 | 22603 | 21507 | 68232 | Over-range | 13189 | 11098 | 12077 | 36446 | 5979 | 5681 | 5629 | 17492 | 20221 | 19777 | 17800 | 57798 | 20221 | 19777 | 17800 | 57798 | - - - | - - - | - - - | - - -
5/7/2026 | 9:45:00 AM | 281.38 | 278.88 | 277.25 | 486.63 | 479.94 | 484.01 | 85.144 | 80.5255 | 77.5269 | 0.2779 | 1.436 | 1.437 | 1.432 | 1.975 | 1.978 | 2.071 | Over-range | 60 | 19956 | 19373 | 17651 | 56980 | - - - | - - - | - - - | - - - | 19956 | 19373 | 17651 | 56980 | 11621 | 9515 | 10675 | 31810 | - - - | - - - | - - - | - - - | 11621 | 9515 | 10675 | 31810 | 23848 | 22337 | 21388 | 67573 | # # # | # # # | # # # | # # # | 0.837 | 0.867 | 0.825 | 0.843 | # # # | # # # | # # # | - - - | 0.864 | 0.896 | 0.855 | 0.872 | - - - | 0.558 | 1.96 | 1.92 | 1.87 | 1.78 | 1.83 | 1.89 | 24.04 | 24.9 | 26.02 | 0 | - - - | - - - | - - - | - - - | 23848 | 22337 | 21388 | 67573 | Over-range | 13043 | 11099 | 12064 | 36276 | 5851 | 5648 | 5553 | 17239 | 20021 | 19377 | 17711 | 57110 | 20021 | 19377 | 17711 | 57110 | - - - | - - - | - - - | - - -
5/7/2026 | 10:00:00 AM | 281.21 | 278.66 | 277.09 | 486.24 | 479.65 | 483.72 | 87.3306 | 82.5196 | 79.5184 | 0.284 | 1.435 | 1.437 | 1.432 | 1.974 | 1.983 | 2.069 | Over-range | 60 | 20539 | 19913 | 18157 | 58609 | - - - | - - - | - - - | - - - | 20539 | 19913 | 18157 | 58609 | 11863 | 9693 | 10926 | 32482 | - - - | - - - | - - - | - - - | 11863 | 9693 | 10926 | 32482 | 24474 | 22905 | 21952 | 69331 | # # # | # # # | # # # | # # # | 0.839 | 0.869 | 0.827 | 0.845 | # # # | # # # | # # # | - - - | 0.866 | 0.898 | 0.857 | 0.874 | - - - | 0.554 | 1.93 | 1.94 | 1.87 | 1.77 | 1.82 | 1.88 | 24.01 | 24.94 | 26.03 | 0 | - - - | - - - | - - - | - - - | 24474 | 22905 | 21952 | 69331 | Over-range | 13303 | 11310 | 12328 | 37015 | 5972 | 5783 | 5664 | 17613 | 20590 | 19919 | 18232 | 58741 | 20590 | 19919 | 18232 | 58741 | - - - | - - - | - - - | - - -
5/7/2026 | 10:15:00 AM | 281.06 | 278.56 | 276.94 | 486.1 | 479.4 | 483.43 | 86.7311 | 81.8434 | 78.5708 | 0.2839 | 1.435 | 1.437 | 1.432 | 1.971 | 1.976 | 2.07 | Over-range | 60.01 | 20394 | 19784 | 17941 | 58119 | - - - | - - - | - - - | - - - | 20394 | 19784 | 17941 | 58119 | 11736 | 9528 | 10775 | 32039 | - - - | - - - | - - - | - - - | 11736 | 9528 | 10775 | 32039 | 24286 | 22699 | 21673 | 68658 | # # # | # # # | # # # | # # # | 0.84 | 0.872 | 0.828 | 0.847 | # # # | # # # | # # # | - - - | 0.866 | 0.901 | 0.857 | 0.875 | - - - | 0.551 | 1.94 | 1.92 | 1.87 | 1.77 | 1.82 | 1.87 | 23.89 | 24.79 | 25.92 | 0 | - - - | - - - | - - - | - - - | 24286 | 22699 | 21673 | 68658 | Over-range | 13180 | 11118 | 12149 | 36527 | 5944 | 5681 | 5563 | 17395 | 20401 | 19863 | 17984 | 58248 | 20401 | 19863 | 17984 | 58248 | - - - | - - - | - - - | - - -
5/7/2026 | 10:30:00 AM | 281.05 | 278.48 | 276.95 | 485.98 | 479.31 | 483.52 | 84.9065 | 79.9075 | 77.0461 | 0.2814 | 1.435 | 1.436 | 1.431 | 1.975 | 1.982 | 2.08 | Over-range | 60 | 19866 | 19193 | 17472 | 56531 | - - - | - - - | - - - | - - - | 19866 | 19193 | 17472 | 56531 | 11529 | 9405 | 10657 | 31591 | - - - | - - - | - - - | - - - | 11529 | 9405 | 10657 | 31591 | 23712 | 22093 | 21204 | 67009 | # # # | # # # | # # # | # # # | 0.838 | 0.869 | 0.824 | 0.844 | # # # | # # # | # # # | - - - | 0.864 | 0.898 | 0.853 | 0.872 | - - - | 0.559 | 1.93 | 1.92 | 1.85 | 1.75 | 1.83 | 1.86 | 24.04 | 24.89 | 26.09 | 0 | - - - | - - - | - - - | - - - | 23712 | 22093 | 21204 | 67009 | Over-range | 12939 | 10928 | 12001 | 35947 | 5800 | 5498 | 5450 | 16947 | 19881 | 19280 | 17495 | 56655 | 19881 | 19280 | 17495 | 56655 | - - - | - - - | - - - | - - -
5/7/2026 | 10:45:00 AM | 280.82 | 278.31 | 276.77 | 485.59 | 479.09 | 483.1 | 86.3099 | 81.3444 | 78.5106 | 0.2834 | 1.435 | 1.436 | 1.432 | 1.939 | 1.943 | 2.032 | Over-range | 60 | 20235 | 19578 | 17851 | 57664 | - - - | - - - | - - - | - - - | 20235 | 19578 | 17851 | 57664 | 11909 | 9742 | 10984 | 32634 | - - - | - - - | - - - | - - - | 11909 | 9742 | 10984 | 32634 | 24133 | 22523 | 21627 | 68283 | # # # | # # # | # # # | # # # | 0.839 | 0.869 | 0.825 | 0.845 | # # # | # # # | # # # | - - - | 0.862 | 0.894 | 0.851 | 0.869 | - - - | 0.566 | 1.93 | 1.91 | 1.87 | 1.76 | 1.82 | 1.87 | 22.12 | 22.96 | 23.96 | 0 | - - - | - - - | - - - | - - - | 24133 | 22523 | 21627 | 68283 | Over-range | 13136 | 11117 | 12193 | 36523 | 5473 | 5289 | 5228 | 16204 | 20327 | 19562 | 17887 | 57776 | 20327 | 19562 | 17887 | 57776 | - - - | - - - | - - - | - - -
5/7/2026 | 11:00:00 AM | 280.84 | 278.38 | 276.84 | 485.69 | 479.22 | 483.16 | 85.5033 | 80.5832 | 76.9438 | 0.28 | 1.435 | 1.437 | 1.432 | 1.932 | 1.934 | 2.028 | Over-range | 60 | 19987 | 19459 | 17488 | 56934 | - - - | - - - | - - - | - - - | 19987 | 19459 | 17488 | 56934 | 11897 | 9532 | 10764 | 32193 | - - - | - - - | - - - | - - - | 11897 | 9532 | 10764 | 32193 | 23884 | 22294 | 21179 | 67357 | # # # | # # # | # # # | # # # | 0.837 | 0.873 | 0.826 | 0.845 | # # # | # # # | # # # | - - - | 0.859 | 0.897 | 0.851 | 0.869 | - - - | 0.565 | 1.97 | 1.95 | 1.92 | 1.79 | 1.86 | 1.91 | 21.77 | 22.67 | 23.77 | 0 | - - - | - - - | - - - | - - - | 23884 | 22294 | 21179 | 67357 | Over-range | 13068 | 10868 | 11933 | 35961 | 5322 | 5144 | 5070 | 15792 | 20089 | 19455 | 17511 | 57055 | 20089 | 19455 | 17511 | 57055 | - - - | - - - | - - - | - - -
5/7/2026 | 11:15:00 AM | 281.14 | 278.66 | 277.25 | 486.13 | 479.84 | 483.82 | 85.2427 | 79.8445 | 78.1836 | 0.2821 | 1.435 | 1.437 | 1.432 | 1.942 | 1.96 | 2.047 | Over-range | 60.01 | 20130 | 19222 | 17803 | 57156 | - - - | - - - | - - - | - - - | 20130 | 19222 | 17803 | 57156 | 11487 | 9557 | 10910 | 31955 | - - - | - - - | - - - | - - - | 11487 | 9557 | 10910 | 31955 | 23867 | 22140 | 21580 | 67587 | # # # | # # # | # # # | # # # | 0.843 | 0.868 | 0.825 | 0.846 | # # # | # # # | # # # | - - - | 0.868 | 0.895 | 0.851 | 0.872 | - - - | 0.559 | 2 | 1.99 | 1.93 | 1.82 | 1.89 | 1.94 | 22.87 | 23.87 | 24.81 | 0 | - - - | - - - | - - - | - - - | 23867 | 22140 | 21580 | 67587 | Over-range | 12810 | 10975 | 12185 | 36044 | 5611 | 5340 | 5370 | 16510 | 20199 | 19294 | 17787 | 57279 | 20199 | 19294 | 17787 | 57279 | - - - | - - - | - - - | - - -
5/7/2026 | 11:30:00 AM | 281.56 | 279.03 | 277.63 | 486.79 | 480.51 | 484.52 | 85.4588 | 80.4004 | 77.5051 | 0.283 | 1.435 | 1.437 | 1.432 | 1.921 | 1.925 | 2.025 | Over-range | 60 | 20037 | 19400 | 17628 | 57066 | - - - | - - - | - - - | - - - | 20037 | 19400 | 17628 | 57066 | 11949 | 9748 | 11040 | 32736 | - - - | - - - | - - - | - - - | 11949 | 9748 | 11040 | 32736 | 23951 | 22315 | 21409 | 67675 | # # # | # # # | # # # | # # # | 0.837 | 0.869 | 0.823 | 0.843 | # # # | # # # | # # # | - - - | 0.858 | 0.893 | 0.847 | 0.866 | - - - | 0.574 | 1.99 | 1.98 | 1.95 | 1.82 | 1.9 | 1.95 | 21.55 | 22.21 | 23.33 | 0 | - - - | - - - | - - - | - - - | 23951 | 22315 | 21409 | 67675 | Over-range | 13114 | 11016 | 12139 | 36353 | 5342 | 5075 | 4988 | 15633 | 20040 | 19444 | 17695 | 57180 | 20040 | 19444 | 17695 | 57180 | - - - | - - - | - - - | - - -
5/7/2026 | 11:45:00 AM | 282.02 | 279.56 | 278.21 | 487.62 | 481.5 | 485.42 | 84.3619 | 79.4516 | 76.3314 | 0.2793 | 1.435 | 1.437 | 1.432 | 1.922 | 1.933 | 2.036 | Over-range | 60 | 19746 | 19172 | 17352 | 56269 | - - - | - - - | - - - | - - - | 19746 | 19172 | 17352 | 56269 | 11806 | 9569 | 10838 | 32213 | - - - | - - - | - - - | - - - | 11806 | 9569 | 10838 | 32213 | 23651 | 22063 | 21102 | 66816 | # # # | # # # | # # # | # # # | 0.835 | 0.869 | 0.822 | 0.842 | # # # | # # # | # # # | - - - | 0.857 | 0.893 | 0.847 | 0.866 | - - - | 0.573 | 2.02 | 1.99 | 1.98 | 1.84 | 1.92 | 1.97 | 21.98 | 22.74 | 23.96 | 0 | - - - | - - - | - - - | - - - | 23651 | 22063 | 21102 | 66816 | Over-range | 13004 | 10895 | 11992 | 35978 | 5374 | 5137 | 5059 | 15807 | 19761 | 19207 | 17419 | 56387 | 19761 | 19207 | 17419 | 56387 | - - - | - - - | - - - | - - -
5/7/2026 | 12:00:00 PM | 281.94 | 279.53 | 278.15 | 487.56 | 481.4 | 485.28 | 82.0077 | 76.9306 | 74.7131 | 0.2762 | 1.435 | 1.437 | 1.433 | 1.903 | 1.911 | 2.016 | Over-range | 60 | 19213 | 18505 | 16931 | 54649 | - - - | - - - | - - - | - - - | 19213 | 18505 | 16931 | 54649 | 11591 | 9590 | 10837 | 32017 | - - - | - - - | - - - | - - - | 11591 | 9590 | 10837 | 32017 | 23009 | 21382 | 20673 | 65064 | # # # | # # # | # # # | # # # | 0.835 | 0.865 | 0.819 | 0.84 | # # # | # # # | # # # | - - - | 0.856 | 0.888 | 0.841 | 0.862 | - - - | 0.586 | 2.02 | 1.98 | 1.96 | 1.84 | 1.92 | 1.96 | 21.05 | 21.61 | 22.8 | 0 | - - - | - - - | - - - | - - - | 23009 | 21382 | 20673 | 65064 | Over-range | 12655 | 10703 | 11851 | 35287 | 5016 | 4694 | 4737 | 14655 | 19251 | 18581 | 16928 | 54760 | 19251 | 18581 | 16928 | 54760 | - - - | - - - | - - - | - - -
5/7/2026 | 12:15:00 PM | 281.6 | 279.09 | 277.75 | 486.9 | 480.68 | 484.63 | 85.1248 | 80.1786 | 77.3819 | 0.2822 | 1.435 | 1.438 | 1.433 | 1.925 | 1.936 | 2.039 | Over-range | 60.02 | 19994 | 19362 | 17638 | 56995 | - - - | - - - | - - - | - - - | 19994 | 19362 | 17638 | 56995 | 11824 | 9670 | 10913 | 32407 | - - - | - - - | - - - | - - - | 11824 | 9670 | 10913 | 32407 | 23879 | 22278 | 21402 | 67560 | # # # | # # # | # # # | # # # | 0.837 | 0.869 | 0.824 | 0.844 | # # # | # # # | # # # | - - - | 0.86 | 0.893 | 0.849 | 0.868 | - - - | 0.569 | 2.01 | 2.04 | 1.98 | 1.85 | 1.94 | 1.98 | 22.07 | 22.7 | 24.02 | 0 | - - - | - - - | - - - | - - - | 23879 | 22278 | 21402 | 67560 | Over-range | 13047 | 11007 | 12111 | 36245 | 5438 | 5186 | 5179 | 16015 | 20055 | 19380 | 17675 | 57110 | 20055 | 19380 | 17675 | 57110 | - - - | - - - | - - - | - - -
5/7/2026 | 12:30:00 PM | 281.56 | 279.05 | 277.68 | 486.84 | 480.59 | 484.52 | 84.7276 | 79.7718 | 76.9104 | 0.2808 | 1.436 | 1.437 | 1.433 | 1.916 | 1.931 | 2.034 | Over-range | 60.01 | 19886 | 19263 | 17515 | 56664 | - - - | - - - | - - - | - - - | 19886 | 19263 | 17515 | 56664 | 11810 | 9626 | 10890 | 32326 | - - - | - - - | - - - | - - - | 11810 | 9626 | 10890 | 32326 | 23753 | 22153 | 21258 | 67164 | # # # | # # # | # # # | # # # | 0.837 | 0.87 | 0.824 | 0.844 | # # # | # # # | # # # | - - - | 0.859 | 0.893 | 0.849 | 0.867 | - - - | 0.571 | 2.04 | 2.01 | 1.96 | 1.84 | 1.92 | 1.97 | 21.88 | 22.61 | 23.87 | 0 | - - - | - - - | - - - | - - - | 23753 | 22153 | 21258 | 67164 | Over-range | 12985 | 10929 | 12038 | 36034 | 5337 | 5116 | 5069 | 15745 | 19932 | 19270 | 17582 | 56783 | 19932 | 19270 | 17582 | 56783 | - - - | - - - | - - - | - - -
5/7/2026 | 12:45:00 PM | 281.53 | 279 | 277.68 | 486.77 | 480.48 | 484.55 | 85.4287 | 80.236 | 78.0818 | 0.2821 | 1.436 | 1.438 | 1.433 | 1.924 | 1.937 | 2.033 | Over-range | 60 | 20070 | 19291 | 17742 | 57103 | - - - | - - - | - - - | - - - | 20070 | 19291 | 17742 | 57103 | 11780 | 9732 | 11019 | 32531 | - - - | - - - | - - - | - - - | 11780 | 9732 | 11019 | 32531 | 23931 | 22255 | 21566 | 67751 | # # # | # # # | # # # | # # # | 0.839 | 0.867 | 0.823 | 0.843 | # # # | # # # | # # # | - - - | 0.862 | 0.891 | 0.848 | 0.867 | - - - | 0.57 | 2 | 2 | 1.97 | 1.83 | 1.91 | 1.96 | 22.22 | 22.94 | 24.1 | 0 | - - - | - - - | - - - | - - - | 23931 | 22255 | 21566 | 67751 | Over-range | 13018 | 11078 | 12244 | 36414 | 5463 | 5216 | 5264 | 16140 | 20178 | 19302 | 17752 | 57232 | 20178 | 19302 | 17752 | 57232 | - - - | - - - | - - - | - - -
5/7/2026 | 1:00:00 PM | 281.31 | 278.75 | 277.5 | 486.33 | 480.12 | 484.24 | 85.5024 | 80.2579 | 77.6256 | 0.2817 | 1.435 | 1.437 | 1.432 | 1.914 | 1.928 | 2.034 | Over-range | 60 | 20053 | 19345 | 17635 | 57033 | - - - | - - - | - - - | - - - | 20053 | 19345 | 17635 | 57033 | 11841 | 9650 | 10946 | 32438 | - - - | - - - | - - - | - - - | 11841 | 9650 | 10946 | 32438 | 23912 | 22223 | 21403 | 67539 | # # # | # # # | # # # | # # # | 0.839 | 0.871 | 0.824 | 0.844 | # # # | # # # | # # # | - - - | 0.861 | 0.894 | 0.848 | 0.868 | - - - | 0.569 | 1.98 | 1.95 | 1.94 | 1.8 | 1.89 | 1.93 | 21.74 | 22.39 | 23.73 | 0 | - - - | - - - | - - - | - - - | 23912 | 22223 | 21403 | 67539 | Over-range | 13017 | 10925 | 12116 | 36143 | 5330 | 5049 | 5122 | 15726 | 20154 | 19370 | 17623 | 57148 | 20154 | 19370 | 17623 | 57148 | - - - | - - - | - - - | - - -
5/7/2026 | 1:15:00 PM | 281.29 | 278.74 | 277.4 | 486.3 | 480.07 | 484.08 | 82.9751 | 78.1173 | 75.5176 | 0.2801 | 1.435 | 1.437 | 1.433 | 1.915 | 1.92 | 2.028 | Over-range | 60.01 | 19474 | 18837 | 17199 | 55511 | - - - | - - - | - - - | - - - | 19474 | 18837 | 17199 | 55511 | 11557 | 9519 | 10694 | 31769 | - - - | - - - | - - - | - - - | 11557 | 9519 | 10694 | 31769 | 23240 | 21669 | 20855 | 65763 | # # # | # # # | # # # | # # # | 0.838 | 0.869 | 0.825 | 0.844 | # # # | # # # | # # # | - - - | 0.86 | 0.892 | 0.848 | 0.867 | - - - | 0.572 | 1.98 | 1.93 | 1.97 | 1.8 | 1.89 | 1.93 | 21.5 | 21.98 | 23.21 | 0 | - - - | - - - | - - - | - - - | 23240 | 21669 | 20855 | 65763 | Over-range | 12676 | 10698 | 11786 | 35237 | 5144 | 4825 | 4895 | 15067 | 19547 | 18900 | 17176 | 55623 | 19547 | 18900 | 17176 | 55623 | - - - | - - - | - - - | - - -
5/7/2026 | 1:30:00 PM | 280.98 | 278.21 | 276.95 | 485.65 | 479.06 | 483.52 | 84.4591 | 79.0812 | 76.5666 | 0.2802 | 1.435 | 1.437 | 1.432 | 1.917 | 1.925 | 2.04 | Over-range | 60.01 | 19803 | 19050 | 17365 | 56217 | - - - | - - - | - - - | - - - | 19803 | 19050 | 17365 | 56217 | 11681 | 9497 | 10800 | 31978 | - - - | - - - | - - - | - - - | 11681 | 9497 | 10800 | 31978 | 23609 | 21871 | 21085 | 66565 | # # # | # # # | # # # | # # # | 0.839 | 0.871 | 0.824 | 0.845 | # # # | # # # | # # # | - - - | 0.861 | 0.894 | 0.848 | 0.868 | - - - | 0.569 | 1.95 | 1.93 | 1.92 | 1.77 | 1.87 | 1.9 | 21.81 | 22.24 | 23.7 | 0 | - - - | - - - | - - - | - - - | 23609 | 21871 | 21085 | 66565 | Over-range | 12847 | 10735 | 11950 | 35619 | 5281 | 4942 | 5050 | 15498 | 19902 | 19077 | 17350 | 56330 | 19902 | 19077 | 17350 | 56330 | - - - | - - - | - - - | - - -
5/7/2026 | 1:45:00 PM | 281.14 | 278.41 | 277.11 | 485.97 | 479.34 | 483.8 | 85.1762 | 79.8823 | 76.4468 | 0.2799 | 1.435 | 1.437 | 1.432 | 1.922 | 1.934 | 2.046 | Over-range | 60 | 19921 | 19304 | 17344 | 56569 | - - - | - - - | - - - | - - - | 19921 | 19304 | 17344 | 56569 | 11842 | 9411 | 10719 | 31972 | - - - | - - - | - - - | - - - | 11842 | 9411 | 10719 | 31972 | 23829 | 22112 | 21069 | 67011 | # # # | # # # | # # # | # # # | 0.836 | 0.873 | 0.823 | 0.844 | # # # | # # # | # # # | - - - | 0.859 | 0.897 | 0.849 | 0.868 | - - - | 0.565 | 1.93 | 1.95 | 1.89 | 1.76 | 1.86 | 1.89 | 22.06 | 22.69 | 24.26 | 0 | - - - | - - - | - - - | - - - | 23829 | 22112 | 21069 | 67011 | Over-range | 13059 | 10760 | 11942 | 35863 | 5416 | 5136 | 5185 | 16007 | 20030 | 19308 | 17344 | 56682 | 20030 | 19308 | 17344 | 56682 | - - - | - - - | - - - | - - -
5/7/2026 | 2:00:00 PM | 281.16 | 278.45 | 277.14 | 485.98 | 479.48 | 483.81 | 83.9483 | 78.698 | 76.2068 | 0.2803 | 1.435 | 1.436 | 1.432 | 1.937 | 1.955 | 2.061 | Over-range | 60 | 19667 | 18920 | 17266 | 55853 | - - - | - - - | - - - | - - - | 19667 | 18920 | 17266 | 55853 | 11507 | 9395 | 10686 | 31588 | - - - | - - - | - - - | - - - | 11507 | 9395 | 10686 | 31588 | 23460 | 21761 | 20989 | 66210 | # # # | # # # | # # # | # # # | 0.838 | 0.869 | 0.823 | 0.844 | # # # | # # # | # # # | - - - | 0.863 | 0.895 | 0.849 | 0.869 | - - - | 0.566 | 1.91 | 1.89 | 1.85 | 1.73 | 1.81 | 1.85 | 22.92 | 23.51 | 25 | 0 | - - - | - - - | - - - | - - - | 23460 | 21761 | 20989 | 66210 | Over-range | 12782 | 10736 | 11922 | 35523 | 5486 | 5124 | 5214 | 16035 | 19720 | 19005 | 17248 | 55974 | 19720 | 19005 | 17248 | 55974 | - - - | - - - | - - - | - - -
5/7/2026 | 2:15:00 PM | 281.67 | 279 | 277.64 | 486.95 | 480.36 | 484.67 | 84.4283 | 79.0582 | 76.6265 | 0.2799 | 1.436 | 1.437 | 1.432 | 1.93 | 1.938 | 2.055 | Over-range | 60.01 | 19821 | 19058 | 17383 | 56263 | - - - | - - - | - - - | - - - | 19821 | 19058 | 17383 | 56263 | 11671 | 9530 | 10853 | 32055 | - - - | - - - | - - - | - - - | 11671 | 9530 | 10853 | 32055 | 23667 | 21931 | 21162 | 66760 | # # # | # # # | # # # | # # # | 0.838 | 0.869 | 0.822 | 0.843 | # # # | # # # | # # # | - - - | 0.861 | 0.894 | 0.847 | 0.868 | - - - | 0.57 | 1.93 | 1.87 | 1.82 | 1.73 | 1.79 | 1.84 | 22.5 | 22.97 | 24.51 | 0 | - - - | - - - | - - - | - - - | 23667 | 21931 | 21162 | 66760 | Over-range | 12925 | 10841 | 12056 | 35906 | 5485 | 5102 | 5183 | 15984 | 19861 | 19138 | 17381 | 56380 | 19861 | 19138 | 17381 | 56380 | - - - | - - - | - - - | - - -
5/7/2026 | 2:30:00 PM | 281.68 | 279.04 | 277.67 | 486.99 | 480.43 | 484.7 | 84.7395 | 79.1596 | 76.2577 | 0.2798 | 1.436 | 1.437 | 1.432 | 1.914 | 1.928 | 2.042 | Over-range | 59.99 | 19880 | 19151 | 17293 | 56324 | - - - | - - - | - - - | - - - | 19880 | 19151 | 17293 | 56324 | 11828 | 9488 | 10860 | 32177 | - - - | - - - | - - - | - - - | 11828 | 9488 | 10860 | 32177 | 23769 | 21980 | 21078 | 66827 | # # # | # # # | # # # | # # # | 0.836 | 0.871 | 0.82 | 0.843 | # # # | # # # | # # # | - - - | 0.859 | 0.895 | 0.845 | 0.867 | - - - | 0.571 | 1.93 | 1.86 | 1.83 | 1.73 | 1.79 | 1.84 | 21.91 | 22.58 | 24.1 | 0 | - - - | - - - | - - - | - - - | 23769 | 21980 | 21078 | 66827 | Over-range | 13022 | 10776 | 12041 | 35939 | 5383 | 5051 | 5141 | 15833 | 19968 | 19215 | 17266 | 56449 | 19968 | 19215 | 17266 | 56449 | - - - | - - - | - - - | - - -
5/7/2026 | 2:45:00 PM | 281.6 | 278.9 | 277.62 | 486.73 | 480.32 | 484.59 | 84.8347 | 79.2004 | 77.3025 | 0.2825 | 1.436 | 1.437 | 1.432 | 1.917 | 1.928 | 2.041 | Over-range | 59.99 | 19921 | 19046 | 17493 | 56460 | - - - | - - - | - - - | - - - | 19921 | 19046 | 17493 | 56460 | 11737 | 9649 | 11062 | 32448 | - - - | - - - | - - - | - - - | 11737 | 9649 | 11062 | 32448 | 23778 | 21971 | 21352 | 67102 | # # # | # # # | # # # | # # # | 0.838 | 0.867 | 0.819 | 0.841 | # # # | # # # | # # # | - - - | 0.86 | 0.891 | 0.844 | 0.865 | - - - | 0.575 | 1.92 | 1.86 | 1.81 | 1.72 | 1.77 | 1.83 | 21.99 | 22.48 | 23.85 | 0 | - - - | - - - | - - - | - - - | 23778 | 21971 | 21352 | 67102 | Over-range | 12966 | 10933 | 12227 | 36210 | 5426 | 5062 | 5125 | 15831 | 19942 | 19109 | 17524 | 56574 | 19942 | 19109 | 17524 | 56574 | - - - | - - - | - - - | - - -
5/7/2026 | 3:00:00 PM | 281.73 | 278.99 | 277.67 | 487 | 480.37 | 484.75 | 83.9416 | 78.4343 | 75.752 | 0.2794 | 1.435 | 1.436 | 1.432 | 1.884 | 1.886 | 2.017 | Over-range | 60 | 19663 | 18940 | 17158 | 55762 | - - - | - - - | - - - | - - - | 19663 | 18940 | 17158 | 55762 | 11881 | 9640 | 10992 | 32512 | - - - | - - - | - - - | - - - | 11881 | 9640 | 10992 | 32512 | 23530 | 21756 | 20920 | 66206 | # # # | # # # | # # # | # # # | 0.836 | 0.871 | 0.82 | 0.842 | # # # | # # # | # # # | - - - | 0.855 | 0.891 | 0.841 | 0.862 | - - - | 0.583 | 1.84 | 1.83 | 1.74 | 1.67 | 1.7 | 1.76 | 20.35 | 20.43 | 22.12 | 0 | - - - | - - - | - - - | - - - | 23530 | 21756 | 20920 | 66206 | Over-range | 12916 | 10692 | 11957 | 35661 | 4987 | 4550 | 4630 | 14428 | 19659 | 19028 | 17180 | 55867 | 19659 | 19028 | 17180 | 55867 | - - - | - - - | - - - | - - -
5/7/2026 | 3:15:00 PM | 281.63 | 278.93 | 277.58 | 486.89 | 480.2 | 484.59 | 82.6458 | 77.2784 | 74.2919 | 0.2762 | 1.436 | 1.437 | 1.432 | 1.896 | 1.9 | 2.032 | Over-range | 60.01 | 19294 | 18637 | 16788 | 54719 | - - - | - - - | - - - | - - - | 19294 | 18637 | 16788 | 54719 | 11694 | 9412 | 10721 | 31828 | - - - | - - - | - - - | - - - | 11694 | 9412 | 10721 | 31828 | 23135 | 21404 | 20489 | 65028 | # # # | # # # | # # # | # # # | 0.834 | 0.871 | 0.819 | 0.842 | # # # | # # # | # # # | - - - | 0.854 | 0.892 | 0.842 | 0.863 | - - - | 0.582 | 1.86 | 1.82 | 1.75 | 1.68 | 1.71 | 1.77 | 20.92 | 21.14 | 22.86 | 0 | - - - | - - - | - - - | - - - | 23135 | 21404 | 20489 | 65028 | Over-range | 12758 | 10511 | 11734 | 35103 | 5017 | 4601 | 4690 | 14575 | 19308 | 18720 | 16791 | 54819 | 19308 | 18720 | 16791 | 54819 | - - - | - - - | - - - | - - -
5/7/2026 | 3:30:00 PM | 281.6 | 278.96 | 277.49 | 486.88 | 480.19 | 484.46 | 81.7296 | 76.3809 | 73.9319 | 0.275 | 1.436 | 1.437 | 1.433 | 1.896 | 1.898 | 2.02 | Over-range | 60 | 19118 | 18396 | 16704 | 54218 | - - - | - - - | - - - | - - - | 19118 | 18396 | 16704 | 54218 | 11551 | 9389 | 10704 | 31644 | - - - | - - - | - - - | - - - | 11551 | 9389 | 10704 | 31644 | 22904 | 21189 | 20405 | 64498 | # # # | # # # | # # # | # # # | 0.835 | 0.868 | 0.819 | 0.841 | # # # | # # # | # # # | - - - | 0.855 | 0.889 | 0.841 | 0.862 | - - - | 0.584 | 1.93 | 1.86 | 1.81 | 1.73 | 1.77 | 1.84 | 20.86 | 21.18 | 22.63 | 0 | - - - | - - - | - - - | - - - | 22904 | 21189 | 20405 | 64498 | Over-range | 12605 | 10502 | 11710 | 34906 | 4963 | 4628 | 4665 | 14495 | 19153 | 18428 | 16747 | 54329 | 19153 | 18428 | 16747 | 54329 | - - - | - - - | - - - | - - -
5/7/2026 | 3:45:00 PM | 281.83 | 279.22 | 277.78 | 487.3 | 480.66 | 484.91 | 85.0312 | 79.9131 | 76.6111 | 0.2808 | 1.436 | 1.437 | 1.433 | 1.894 | 1.899 | 2.019 | Over-range | 60.02 | 19896 | 19319 | 17407 | 56622 | - - - | - - - | - - - | - - - | 19896 | 19319 | 17407 | 56622 | 12040 | 9697 | 10947 | 32684 | - - - | - - - | - - - | - - - | 12040 | 9697 | 10947 | 32684 | 23845 | 22185 | 21167 | 67198 | # # # | # # # | # # # | # # # | 0.834 | 0.871 | 0.822 | 0.843 | # # # | # # # | # # # | - - - | 0.855 | 0.892 | 0.845 | 0.864 | - - - | 0.577 | 1.91 | 1.87 | 1.82 | 1.73 | 1.77 | 1.83 | 20.78 | 21.12 | 22.69 | 0 | - - - | - - - | - - - | - - - | 23845 | 22185 | 21167 | 67198 | Over-range | 13128 | 10886 | 12028 | 36138 | 5135 | 4857 | 4891 | 15148 | 19982 | 19310 | 17440 | 56733 | 19982 | 19310 | 17440 | 56733 | - - - | - - - | - - - | - - -
5/7/2026 | 4:00:00 PM | 281.73 | 279.08 | 277.73 | 487.1 | 480.47 | 484.81 | 83.5444 | 78.4063 | 75.6239 | 0.279 | 1.436 | 1.437 | 1.433 | 1.931 | 1.943 | 2.066 | Over-range | 60.02 | 19569 | 18904 | 17161 | 55634 | - - - | - - - | - - - | - - - | 19569 | 18904 | 17161 | 55634 | 11590 | 9408 | 10662 | 31659 | - - - | - - - | - - - | - - - | 11590 | 9408 | 10662 | 31659 | 23405 | 21741 | 20879 | 66025 | # # # | # # # | # # # | # # # | 0.836 | 0.87 | 0.822 | 0.843 | # # # | # # # | # # # | - - - | 0.86 | 0.895 | 0.848 | 0.868 | - - - | 0.569 | 1.87 | 1.83 | 1.76 | 1.69 | 1.73 | 1.79 | 22.7 | 23.12 | 24.83 | 0 | - - - | - - - | - - - | - - - | 23405 | 21741 | 20879 | 66025 | Over-range | 12834 | 10726 | 11881 | 35528 | 5438 | 5082 | 5175 | 15916 | 19631 | 18956 | 17167 | 55755 | 19631 | 18956 | 17167 | 55755 | - - - | - - - | - - - | - - -
5/7/2026 | 4:15:00 PM | 282.07 | 279.51 | 278.07 | 487.76 | 481.19 | 485.34 | 85.3367 | 80.1923 | 77.8469 | 0.2819 | 1.437 | 1.437 | 1.433 | 1.933 | 1.948 | 2.052 | Over-range | 60.02 | 20103 | 19362 | 17744 | 57209 | - - - | - - - | - - - | - - - | 20103 | 19362 | 17744 | 57209 | 11787 | 9695 | 10975 | 32458 | - - - | - - - | - - - | - - - | 11787 | 9695 | 10975 | 32458 | 23984 | 22319 | 21563 | 67865 | # # # | # # # | # # # | # # # | 0.838 | 0.868 | 0.823 | 0.843 | # # # | # # # | # # # | - - - | 0.863 | 0.893 | 0.85 | 0.869 | - - - | 0.567 | 1.89 | 1.82 | 1.79 | 1.7 | 1.73 | 1.8 | 22.8 | 23.45 | 24.79 | 0 | - - - | - - - | - - - | - - - | 23984 | 22319 | 21563 | 67865 | Over-range | 13074 | 11093 | 12241 | 36485 | 5600 | 5337 | 5369 | 16503 | 20182 | 19367 | 17788 | 57337 | 20182 | 19367 | 17788 | 57337 | - - - | - - - | - - - | - - -
5/7/2026 | 4:30:00 PM | 281.93 | 279.38 | 277.99 | 487.48 | 481.04 | 485.18 | 84.9113 | 79.5159 | 76.7782 | 0.2809 | 1.437 | 1.437 | 1.432 | 1.916 | 1.929 | 2.043 | Over-range | 60 | 19912 | 19208 | 17418 | 56538 | - - - | - - - | - - - | - - - | 19912 | 19208 | 17418 | 56538 | 11900 | 9622 | 10951 | 32473 | - - - | - - - | - - - | - - - | 11900 | 9622 | 10951 | 32473 | 23826 | 22093 | 21232 | 67151 | # # # | # # # | # # # | # # # | 0.836 | 0.869 | 0.82 | 0.842 | # # # | # # # | # # # | - - - | 0.858 | 0.893 | 0.845 | 0.866 | - - - | 0.574 | 1.86 | 1.83 | 1.73 | 1.68 | 1.7 | 1.77 | 21.88 | 22.52 | 24.06 | 0 | - - - | - - - | - - - | - - - | 23826 | 22093 | 21232 | 67151 | Over-range | 13076 | 10908 | 12132 | 36208 | 5349 | 5074 | 5155 | 15821 | 20021 | 19213 | 17420 | 56654 | 20021 | 19213 | 17420 | 56654 | - - - | - - - | - - - | - - -
5/7/2026 | 4:45:00 PM | 282.14 | 279.63 | 278.22 | 487.92 | 481.43 | 485.55 | 83.5443 | 78.5887 | 76.2154 | 0.2794 | 1.437 | 1.438 | 1.433 | 1.925 | 1.937 | 2.056 | Over-range | 60.01 | 19577 | 18894 | 17303 | 55774 | - - - | - - - | - - - | - - - | 19577 | 18894 | 17303 | 55774 | 11617 | 9582 | 10819 | 32018 | - - - | - - - | - - - | - - - | 11617 | 9582 | 10819 | 32018 | 23427 | 21822 | 21071 | 66320 | # # # | # # # | # # # | # # # | 0.836 | 0.866 | 0.821 | 0.841 | # # # | # # # | # # # | - - - | 0.859 | 0.89 | 0.847 | 0.866 | - - - | 0.574 | 1.9 | 1.85 | 1.78 | 1.71 | 1.73 | 1.81 | 22.5 | 22.9 | 24.38 | 0 | - - - | - - - | - - - | - - - | 23427 | 21822 | 21071 | 66320 | Over-range | 12852 | 10896 | 12008 | 35831 | 5413 | 5111 | 5127 | 15850 | 19610 | 18908 | 17379 | 55897 | 19610 | 18908 | 17379 | 55897 | - - - | - - - | - - - | - - -
5/7/2026 | 5:00:00 PM | 282.21 | 279.58 | 278.22 | 487.9 | 481.35 | 485.66 | 84.005 | 78.8538 | 76.4477 | 0.2808 | 1.437 | 1.437 | 1.432 | 1.919 | 1.931 | 2.052 | Over-range | 60 | 19739 | 19031 | 17390 | 56160 | - - - | - - - | - - - | - - - | 19739 | 19031 | 17390 | 56160 | 11732 | 9605 | 10882 | 32219 | - - - | - - - | - - - | - - - | 11732 | 9605 | 10882 | 32219 | 23602 | 21931 | 21167 | 66700 | # # # | # # # | # # # | # # # | 0.836 | 0.868 | 0.822 | 0.842 | # # # | # # # | # # # | - - - | 0.859 | 0.891 | 0.847 | 0.866 | - - - | 0.574 | 1.88 | 1.82 | 1.76 | 1.68 | 1.7 | 1.78 | 22.19 | 22.55 | 24.14 | 0 | - - - | - - - | - - - | - - - | 23602 | 21931 | 21167 | 66700 | Over-range | 12931 | 10889 | 12057 | 35958 | 5367 | 5061 | 5120 | 15758 | 19802 | 19023 | 17450 | 56276 | 19802 | 19023 | 17450 | 56276 | - - - | - - - | - - - | - - -
5/7/2026 | 5:15:00 PM | 282.71 | 280.2 | 278.77 | 488.83 | 482.52 | 486.47 | 83.9232 | 79.0247 | 76.2213 | 0.2803 | 1.437 | 1.437 | 1.433 | 1.91 | 1.921 | 2.037 | Over-range | 60.01 | 19748 | 19143 | 17403 | 56293 | - - - | - - - | - - - | - - - | 19748 | 19143 | 17403 | 56293 | 11802 | 9640 | 10883 | 32325 | - - - | - - - | - - - | - - - | 11802 | 9640 | 10883 | 32325 | 23622 | 22032 | 21149 | 66804 | # # # | # # # | # # # | # # # | 0.836 | 0.869 | 0.823 | 0.843 | # # # | # # # | # # # | - - - | 0.858 | 0.892 | 0.848 | 0.866 | - - - | 0.574 | 1.81 | 1.79 | 1.7 | 1.65 | 1.65 | 1.73 | 21.8 | 22.3 | 23.75 | 0 | - - - | - - - | - - - | - - - | 23622 | 22032 | 21149 | 66804 | Over-range | 12957 | 10899 | 12011 | 35949 | 5280 | 5022 | 5015 | 15539 | 19785 | 19145 | 17481 | 56411 | 19785 | 19145 | 17481 | 56411 | - - - | - - - | - - - | - - -
5/7/2026 | 5:30:00 PM | 282.78 | 280.37 | 278.96 | 489.04 | 482.86 | 486.67 | 82.7005 | 77.9791 | 75.6356 | 0.2785 | 1.437 | 1.437 | 1.433 | 1.901 | 1.91 | 2.024 | Over-range | 60 | 19427 | 18796 | 17231 | 55454 | - - - | - - - | - - - | - - - | 19427 | 18796 | 17231 | 55454 | 11636 | 9666 | 10862 | 32165 | - - - | - - - | - - - | - - - | 11636 | 9666 | 10862 | 32165 | 23260 | 21727 | 20982 | 65969 | # # # | # # # | # # # | # # # | 0.835 | 0.865 | 0.821 | 0.841 | # # # | # # # | # # # | - - - | 0.857 | 0.888 | 0.846 | 0.864 | - - - | 0.58 | 1.81 | 1.76 | 1.71 | 1.65 | 1.64 | 1.73 | 21.66 | 21.97 | 23.34 | 0 | - - - | - - - | - - - | - - - | 23260 | 21727 | 20982 | 65969 | Over-range | 12782 | 10882 | 11960 | 35696 | 5206 | 4920 | 4922 | 15242 | 19434 | 18819 | 17313 | 55566 | 19434 | 18819 | 17313 | 55566 | - - - | - - - | - - - | - - -
5/7/2026 | 5:45:00 PM | 283 | 280.6 | 279.25 | 489.43 | 483.3 | 487.12 | 83.1087 | 78.0543 | 75.894 | 0.2796 | 1.437 | 1.437 | 1.434 | 1.875 | 1.886 | 1.996 | Over-range | 60 | 19502 | 18802 | 17225 | 55530 | - - - | - - - | - - - | - - - | 19502 | 18802 | 17225 | 55530 | 11867 | 9860 | 11136 | 32863 | - - - | - - - | - - - | - - - | 11867 | 9860 | 11136 | 32863 | 23399 | 21770 | 21074 | 66243 | # # # | # # # | # # # | # # # | 0.834 | 0.864 | 0.817 | 0.838 | # # # | # # # | # # # | - - - | 0.853 | 0.884 | 0.839 | 0.859 | - - - | 0.592 | 1.84 | 1.74 | 1.7 | 1.66 | 1.66 | 1.73 | 20.39 | 20.76 | 22.1 | 0 | - - - | - - - | - - - | - - - | 23399 | 21770 | 21074 | 66243 | Over-range | 12915 | 10951 | 12124 | 36067 | 5003 | 4675 | 4704 | 14597 | 19492 | 18856 | 17292 | 55639 | 19492 | 18856 | 17292 | 55639 | - - - | - - - | - - - | - - -
5/7/2026 | 6:00:00 PM | 283.11 | 280.73 | 279.29 | 489.61 | 483.5 | 487.21 | 82.4148 | 77.2369 | 74.951 | 0.2798 | 1.438 | 1.437 | 1.434 | 1.851 | 1.854 | 1.97 | Over-range | 60 | 19367 | 18678 | 17030 | 55075 | - - - | - - - | - - - | - - - | 19367 | 18678 | 17030 | 55075 | 11919 | 9858 | 11150 | 32927 | - - - | - - - | - - - | - - - | 11919 | 9858 | 11150 | 32927 | 23229 | 21571 | 20831 | 65631 | # # # | # # # | # # # | # # # | 0.834 | 0.866 | 0.818 | 0.839 | # # # | # # # | # # # | - - - | 0.851 | 0.884 | 0.836 | 0.857 | - - - | 0.598 | 1.81 | 1.75 | 1.69 | 1.64 | 1.63 | 1.71 | 19.01 | 19.28 | 20.59 | 0 | - - - | - - - | - - - | - - - | 23229 | 21571 | 20831 | 65631 | Over-range | 12820 | 10782 | 11987 | 35673 | 4648 | 4297 | 4331 | 13518 | 19357 | 18751 | 17068 | 55176 | 19357 | 18751 | 17068 | 55176 | - - - | - - - | - - - | - - -
5/7/2026 | 6:15:00 PM | 283.73 | 281.35 | 279.98 | 490.7 | 484.63 | 488.34 | 81.7007 | 76.2636 | 74.7049 | 0.2798 | 1.436 | 1.435 | 1.433 | 1.873 | 1.876 | 1.99 | Over-range | 60 | 19191 | 18353 | 16888 | 54432 | - - - | - - - | - - - | - - - | 19191 | 18353 | 16888 | 54432 | 11828 | 9883 | 11245 | 32956 | - - - | - - - | - - - | - - - | 11828 | 9883 | 11245 | 32956 | 23061 | 21328 | 20802 | 65191 | # # # | # # # | # # # | # # # | 0.832 | 0.861 | 0.812 | 0.835 | # # # | # # # | # # # | - - - | 0.85 | 0.88 | 0.831 | 0.854 | - - - | 0.606 | 1.72 | 1.64 | 1.56 | 1.55 | 1.53 | 1.6 | 19.69 | 20.08 | 21.25 | 0 | - - - | - - - | - - - | - - - | 23061 | 21328 | 20802 | 65191 | Over-range | 12779 | 10852 | 12133 | 35843 | 4739 | 4389 | 4459 | 13811 | 19180 | 18420 | 16917 | 54517 | 19180 | 18420 | 16917 | 54517 | - - - | - - - | - - - | - - -
5/7/2026 | 6:30:00 PM | 283.95 | 281.73 | 280.21 | 491.27 | 485.21 | 488.63 | 81.5248 | 76.4796 | 74.5037 | 0.2792 | 1.436 | 1.434 | 1.433 | 1.875 | 1.871 | 1.989 | Over-range | 59.99 | 19118 | 18421 | 16873 | 54411 | - - - | - - - | - - - | - - - | 19118 | 18421 | 16873 | 54411 | 11909 | 9983 | 11215 | 33107 | - - - | - - - | - - - | - - - | 11909 | 9983 | 11215 | 33107 | 23030 | 21417 | 20759 | 65205 | # # # | # # # | # # # | # # # | 0.83 | 0.86 | 0.813 | 0.835 | # # # | # # # | # # # | - - - | 0.848 | 0.879 | 0.832 | 0.853 | - - - | 0.609 | 1.7 | 1.64 | 1.54 | 1.54 | 1.52 | 1.58 | 19.6 | 19.86 | 21.1 | 0 | - - - | - - - | - - - | - - - | 23030 | 21417 | 20759 | 65205 | Over-range | 12833 | 10915 | 12083 | 35906 | 4703 | 4337 | 4419 | 13674 | 19120 | 18500 | 16880 | 54500 | 19120 | 18500 | 16880 | 54500 | - - - | - - - | - - - | - - -
5/7/2026 | 6:45:00 PM | 284.11 | 281.82 | 280.36 | 491.41 | 485.49 | 488.88 | 81.9264 | 77.1508 | 74.6354 | 0.2807 | 1.436 | 1.434 | 1.432 | 1.888 | 1.888 | 2.001 | Over-range | 60 | 19185 | 18599 | 16925 | 54709 | - - - | - - - | - - - | - - - | 19185 | 18599 | 16925 | 54709 | 11948 | 9895 | 11073 | 32916 | - - - | - - - | - - - | - - - | 11948 | 9895 | 11073 | 32916 | 23134 | 21587 | 20782 | 65503 | # # # | # # # | # # # | # # # | 0.829 | 0.862 | 0.814 | 0.835 | # # # | # # # | # # # | - - - | 0.848 | 0.881 | 0.835 | 0.855 | - - - | 0.602 | 1.7 | 1.6 | 1.53 | 1.53 | 1.5 | 1.56 | 20.13 | 20.69 | 21.9 | 0 | - - - | - - - | - - - | - - - | 23134 | 21587 | 20782 | 65503 | Over-range | 12913 | 10938 | 12043 | 35973 | 4799 | 4566 | 4645 | 14236 | 19261 | 18605 | 16929 | 54795 | 19261 | 18605 | 16929 | 54795 | - - - | - - - | - - - | - - -
5/7/2026 | 7:00:00 PM | 284.35 | 282.08 | 280.58 | 491.9 | 485.83 | 489.32 | 80.7111 | 75.7314 | 73.4773 | 0.2759 | 1.435 | 1.433 | 1.431 | 1.868 | 1.856 | 1.98 | Over-range | 60 | 18856 | 18216 | 16601 | 53673 | - - - | - - - | - - - | - - - | 18856 | 18216 | 16601 | 53673 | 11975 | 9934 | 11164 | 33073 | - - - | - - - | - - - | - - - | 11975 | 9934 | 11164 | 33073 | 22793 | 21191 | 20473 | 64457 | # # # | # # # | # # # | # # # | 0.827 | 0.86 | 0.811 | 0.833 | # # # | # # # | # # # | - - - | 0.844 | 0.876 | 0.829 | 0.85 | - - - | 0.616 | 1.63 | 1.54 | 1.46 | 1.48 | 1.44 | 1.49 | 18.88 | 19.1 | 20.28 | 0 | - - - | - - - | - - - | - - - | 22793 | 21191 | 20473 | 64457 | Over-range | 12796 | 10812 | 11968 | 35656 | 4407 | 4171 | 4211 | 13034 | 18902 | 18181 | 16655 | 53739 | 18902 | 18181 | 16655 | 53739 | - - - | - - - | - - - | - - -
5/7/2026 | 7:15:00 PM | 284.85 | 282.59 | 281.03 | 492.83 | 486.62 | 490.13 | 79.5631 | 74.4198 | 72.3253 | 0.2599 | 1.435 | 1.433 | 1.43 | 1.871 | 1.852 | 1.982 | Over-range | 59.99 | 18599 | 17926 | 16307 | 52832 | - - - | - - - | - - - | - - - | 18599 | 17926 | 16307 | 52832 | 11920 | 9867 | 11114 | 32900 | - - - | - - - | - - - | - - - | 11920 | 9867 | 11114 | 32900 | 22533 | 20887 | 20195 | 63616 | # # # | # # # | # # # | # # # | 0.825 | 0.858 | 0.808 | 0.831 | # # # | # # # | # # # | - - - | 0.842 | 0.875 | 0.825 | 0.847 | - - - | 0.623 | 1.64 | 1.57 | 1.45 | 1.49 | 1.45 | 1.49 | 18.81 | 19.06 | 20.23 | 0 | - - - | - - - | - - - | - - - | 22533 | 20887 | 20195 | 63616 | Over-range | 12713 | 10711 | 11902 | 35409 | 4333 | 4083 | 4175 | 12840 | 18668 | 17907 | 16329 | 52904 | 18668 | 17907 | 16329 | 52904 | - - - | - - - | - - - | - - -
5/7/2026 | 7:30:00 PM | 284.91 | 282.74 | 281.04 | 493.01 | 486.83 | 490.11 | 75.5456 | 70.6079 | 67.8497 | 0.2419 | 1.433 | 1.431 | 1.428 | 1.921 | 1.899 | 2.033 | Over-range | 60 | 17539 | 16999 | 15204 | 49742 | - - - | - - - | - - - | - - - | 17539 | 16999 | 15204 | 49742 | 11256 | 9068 | 10305 | 30630 | - - - | - - - | - - - | - - - | 11256 | 9068 | 10305 | 30630 | 21350 | 19774 | 18899 | 60024 | # # # | # # # | # # # | # # # | 0.822 | 0.86 | 0.805 | 0.829 | # # # | # # # | # # # | - - - | 0.841 | 0.88 | 0.827 | 0.85 | - - - | 0.616 | 1.63 | 1.55 | 1.44 | 1.49 | 1.44 | 1.48 | 20.92 | 21.59 | 22.71 | 0 | - - - | - - - | - - - | - - - | 21350 | 19774 | 18899 | 60024 | Over-range | 12166 | 10088 | 11213 | 33561 | 4517 | 4333 | 4327 | 13451 | 17600 | 16965 | 15245 | 49810 | 17600 | 16965 | 15245 | 49810 | - - - | - - - | - - - | - - -
5/7/2026 | 7:45:00 PM | 285.24 | 283.16 | 281.37 | 493.7 | 487.49 | 490.64 | 76.1077 | 71.2523 | 69.4188 | 0.2416 | 1.433 | 1.432 | 1.428 | 1.955 | 1.933 | 2.054 | Over-range | 59.99 | 17772 | 17095 | 15604 | 50471 | - - - | - - - | - - - | - - - | 17772 | 17095 | 15604 | 50471 | 11172 | 9273 | 10506 | 30952 | - - - | - - - | - - - | - - - | 11172 | 9273 | 10506 | 30952 | 21576 | 20030 | 19398 | 61004 | # # # | # # # | # # # | # # # | 0.824 | 0.854 | 0.804 | 0.827 | # # # | # # # | # # # | - - - | 0.846 | 0.877 | 0.829 | 0.851 | - - - | 0.613 | 1.64 | 1.58 | 1.46 | 1.5 | 1.46 | 1.5 | 22.3 | 23.02 | 23.82 | 0 | - - - | - - - | - - - | - - - | 21576 | 20030 | 19398 | 61004 | Over-range | 12221 | 10421 | 11510 | 34222 | 4876 | 4682 | 4626 | 14383 | 17803 | 17079 | 15669 | 50550 | 17803 | 17079 | 15669 | 50550 | - - - | - - - | - - - | - - -
5/7/2026 | 8:00:00 PM | 284.18 | 282.03 | 280.26 | 491.83 | 485.49 | 488.79 | 76.857 | 72.0831 | 70.0086 | 0.2428 | 1.431 | 1.43 | 1.426 | 1.957 | 1.934 | 2.048 | Over-range | 60 | 17979 | 17335 | 15801 | 51115 | - - - | - - - | - - - | - - - | 17979 | 17335 | 15801 | 51115 | 11120 | 9242 | 10433 | 30795 | - - - | - - - | - - - | - - - | 11120 | 9242 | 10433 | 30795 | 21732 | 20208 | 19510 | 61451 | # # # | # # # | # # # | # # # | 0.827 | 0.858 | 0.81 | 0.832 | # # # | # # # | # # # | - - - | 0.849 | 0.882 | 0.833 | 0.855 | - - - | 0.603 | 1.58 | 1.52 | 1.41 | 1.44 | 1.41 | 1.44 | 22.27 | 22.88 | 23.74 | 0 | - - - | - - - | - - - | - - - | 21732 | 20208 | 19510 | 61451 | Over-range | 12202 | 10376 | 11436 | 34085 | 4959 | 4655 | 4617 | 14424 | 17969 | 17398 | 15823 | 51190 | 17969 | 17398 | 15823 | 51190 | - - - | - - - | - - - | - - -
5/7/2026 | 8:15:00 PM | 283.83 | 281.85 | 279.88 | 491.43 | 485.08 | 488.03 | 77.6802 | 73.2951 | 70.1843 | 0.242 | 1.43 | 1.43 | 1.425 | 1.966 | 1.939 | 2.049 | Over-range | 59.99 | 18072 | 17633 | 15843 | 51548 | - - - | - - - | - - - | - - - | 18072 | 17633 | 15843 | 51548 | 11243 | 9177 | 10284 | 30703 | - - - | - - - | - - - | - - - | 11243 | 9177 | 10284 | 30703 | 21879 | 20476 | 19482 | 61838 | # # # | # # # | # # # | # # # | 0.826 | 0.861 | 0.813 | 0.834 | # # # | # # # | # # # | - - - | 0.848 | 0.885 | 0.838 | 0.857 | - - - | 0.596 | 1.56 | 1.51 | 1.39 | 1.42 | 1.38 | 1.41 | 22.5 | 23.35 | 24.11 | 0 | - - - | - - - | - - - | - - - | 21879 | 20476 | 19482 | 61838 | Over-range | 12325 | 10396 | 11327 | 34128 | 4964 | 4806 | 4666 | 14658 | 18105 | 17624 | 15899 | 51628 | 18105 | 17624 | 15899 | 51628 | - - - | - - - | - - - | - - -
5/7/2026 | 8:30:00 PM | 283.95 | 281.99 | 280.03 | 491.62 | 485.37 | 488.27 | 75.4579 | 71.1997 | 68.7704 | 0.24 | 1.43 | 1.43 | 1.425 | 1.987 | 1.961 | 2.068 | Over-range | 60 | 17571 | 17058 | 15500 | 50128 | - - - | - - - | - - - | - - - | 17571 | 17058 | 15500 | 50128 | 10875 | 9019 | 10103 | 29997 | - - - | - - - | - - - | - - - | 10875 | 9019 | 10103 | 29997 | 21271 | 19904 | 19105 | 60280 | # # # | # # # | # # # | # # # | 0.826 | 0.857 | 0.811 | 0.832 | # # # | # # # | # # # | - - - | 0.85 | 0.883 | 0.838 | 0.857 | - - - | 0.598 | 1.56 | 1.52 | 1.39 | 1.43 | 1.39 | 1.42 | 23.35 | 24.17 | 24.82 | 0 | - - - | - - - | - - - | - - - | 21271 | 19904 | 19105 | 60280 | Over-range | 11981 | 10247 | 11158 | 33452 | 4960 | 4797 | 4672 | 14610 | 17597 | 17047 | 15562 | 50206 | 17597 | 17047 | 15562 | 50206 | - - - | - - - | - - - | - - -
5/7/2026 | 8:45:00 PM | 283.97 | 282 | 279.96 | 491.7 | 485.29 | 488.2 | 77.8622 | 73.3767 | 70.7457 | 0.2435 | 1.43 | 1.43 | 1.425 | 1.99 | 1.967 | 2.065 | Over-range | 60 | 18216 | 17662 | 16010 | 51888 | - - - | - - - | - - - | - - - | 18216 | 17662 | 16010 | 51888 | 11029 | 9088 | 10198 | 30315 | - - - | - - - | - - - | - - - | 11029 | 9088 | 10198 | 30315 | 21964 | 20530 | 19662 | 62156 | # # # | # # # | # # # | # # # | 0.829 | 0.86 | 0.814 | 0.835 | # # # | # # # | # # # | - - - | 0.855 | 0.887 | 0.841 | 0.861 | - - - | 0.584 | 1.56 | 1.54 | 1.44 | 1.44 | 1.42 | 1.43 | 23.64 | 24.64 | 25.31 | 0 | - - - | - - - | - - - | - - - | 21964 | 20530 | 19662 | 62156 | Over-range | 12256 | 10445 | 11397 | 34169 | 5245 | 5058 | 4998 | 15492 | 18304 | 17673 | 15997 | 51973 | 18304 | 17673 | 15997 | 51973 | - - - | - - - | - - - | - - -
5/7/2026 | 9:00:00 PM | 284.18 | 282.19 | 280.19 | 492.01 | 485.65 | 488.6 | 78.6156 | 73.9698 | 70.5334 | 0.2436 | 1.431 | 1.43 | 1.425 | 1.999 | 1.984 | 2.078 | Over-range | 60.01 | 18439 | 17966 | 16023 | 52428 | - - - | - - - | - - - | - - - | 18439 | 17966 | 16023 | 52428 | 11165 | 8920 | 10113 | 30198 | - - - | - - - | - - - | - - - | 11165 | 8920 | 10113 | 30198 | 22232 | 20751 | 19652 | 62636 | # # # | # # # | # # # | # # # | 0.829 | 0.866 | 0.815 | 0.837 | # # # | # # # | # # # | - - - | 0.855 | 0.894 | 0.844 | 0.865 | - - - | 0.576 | 1.58 | 1.55 | 1.42 | 1.45 | 1.42 | 1.44 | 23.98 | 25.36 | 26.16 | 0 | - - - | - - - | - - - | - - - | 22232 | 20751 | 19652 | 62636 | Over-range | 12412 | 10375 | 11368 | 34244 | 5359 | 5239 | 5133 | 15970 | 18535 | 17956 | 16024 | 52515 | 18535 | 17956 | 16024 | 52515 | - - - | - - - | - - - | - - -
5/7/2026 | 9:15:00 PM | 284.58 | 282.54 | 280.66 | 492.61 | 486.39 | 489.39 | 76.0734 | 71.4356 | 69.2075 | 0.2417 | 1.431 | 1.431 | 1.426 | 2.007 | 1.99 | 2.08 | Over-range | 60.01 | 17795 | 17156 | 15610 | 50560 | - - - | - - - | - - - | - - - | 17795 | 17156 | 15610 | 50560 | 10778 | 8895 | 10061 | 29734 | - - - | - - - | - - - | - - - | 10778 | 8895 | 10061 | 29734 | 21476 | 19995 | 19258 | 60730 | # # # | # # # | # # # | # # # | 0.829 | 0.858 | 0.811 | 0.833 | # # # | # # # | # # # | - - - | 0.855 | 0.887 | 0.839 | 0.86 | - - - | 0.588 | 1.62 | 1.56 | 1.47 | 1.48 | 1.46 | 1.48 | 24.33 | 25.58 | 26.14 | 0 | - - - | - - - | - - - | - - - | 21476 | 19995 | 19258 | 60730 | Over-range | 12018 | 10260 | 11266 | 33613 | 5232 | 5035 | 4995 | 15444 | 17874 | 17189 | 15584 | 50647 | 17874 | 17189 | 15584 | 50647 | - - - | - - - | - - - | - - -
5/7/2026 | 9:30:00 PM | 285.07 | 283.08 | 281.1 | 493.54 | 487.21 | 490.18 | 77.1851 | 72.4195 | 70.1076 | 0.2426 | 1.431 | 1.431 | 1.426 | 1.978 | 1.964 | 2.05 | Over-range | 60.02 | 18147 | 17514 | 15898 | 51559 | - - - | - - - | - - - | - - - | 18147 | 17514 | 15898 | 51559 | 11103 | 9145 | 10330 | 30578 | - - - | - - - | - - - | - - - | 11103 | 9145 | 10330 | 30578 | 21903 | 20389 | 19606 | 61898 | # # # | # # # | # # # | # # # | 0.829 | 0.859 | 0.811 | 0.833 | # # # | # # # | # # # | - - - | 0.853 | 0.885 | 0.837 | 0.859 | - - - | 0.593 | 1.63 | 1.61 | 1.49 | 1.5 | 1.47 | 1.51 | 23.15 | 24.33 | 24.94 | 0 | - - - | - - - | - - - | - - - | 21903 | 20389 | 19606 | 61898 | Over-range | 12257 | 10430 | 11465 | 34225 | 5131 | 4960 | 4917 | 15205 | 18242 | 17528 | 15876 | 51645 | 18242 | 17528 | 15876 | 51645 | - - - | - - - | - - - | - - -
5/7/2026 | 9:45:00 PM | 285.41 | 283.38 | 281.45 | 494.07 | 487.75 | 490.82 | 78.7494 | 73.5138 | 70.6462 | 0.245 | 1.432 | 1.431 | 1.426 | 1.969 | 1.955 | 2.049 | Over-range | 60.01 | 18426 | 17787 | 15919 | 52131 | - - - | - - - | - - - | - - - | 18426 | 17787 | 15919 | 52131 | 11380 | 9140 | 10509 | 31029 | - - - | - - - | - - - | - - - | 11380 | 9140 | 10509 | 31029 | 22301 | 20643 | 19716 | 62660 | # # # | # # # | # # # | # # # | 0.826 | 0.862 | 0.807 | 0.832 | # # # | # # # | # # # | - - - | 0.85 | 0.888 | 0.833 | 0.857 | - - - | 0.595 | 1.68 | 1.58 | 1.48 | 1.52 | 1.48 | 1.53 | 22.86 | 24.24 | 24.84 | 0 | - - - | - - - | - - - | - - - | 22301 | 20643 | 19716 | 62660 | Over-range | 12548 | 10455 | 11614 | 34712 | 5190 | 4986 | 4855 | 15295 | 18438 | 17849 | 15931 | 52218 | 18438 | 17849 | 15931 | 52218 | - - - | - - - | - - - | - - -
5/7/2026 | 10:00:00 PM | 285.4 | 283.34 | 281.36 | 494.04 | 487.64 | 490.71 | 76.7312 | 71.5269 | 69.6214 | 0.2422 | 1.432 | 1.431 | 1.426 | 1.96 | 1.943 | 2.04 | Over-range | 60.02 | 18013 | 17265 | 15686 | 50965 | - - - | - - - | - - - | - - - | 18013 | 17265 | 15686 | 50965 | 11167 | 9197 | 10528 | 30892 | - - - | - - - | - - - | - - - | 11167 | 9197 | 10528 | 30892 | 21790 | 20145 | 19475 | 61409 | # # # | # # # | # # # | # # # | 0.827 | 0.857 | 0.806 | 0.83 | # # # | # # # | # # # | - - - | 0.848 | 0.882 | 0.829 | 0.853 | - - - | 0.606 | 1.68 | 1.62 | 1.49 | 1.54 | 1.5 | 1.55 | 22.16 | 23.18 | 23.76 | 0 | - - - | - - - | - - - | - - - | 21790 | 20145 | 19475 | 61409 | Over-range | 12252 | 10367 | 11531 | 34230 | 4965 | 4712 | 4625 | 14522 | 18009 | 17325 | 15706 | 51040 | 18009 | 17325 | 15706 | 51040 | - - - | - - - | - - - | - - -
5/7/2026 | 10:15:00 PM | 284.66 | 282.46 | 280.59 | 492.65 | 486.14 | 489.48 | 76.1126 | 70.6856 | 68.6057 | 0.2417 | 1.431 | 1.43 | 1.425 | 1.946 | 1.92 | 2.041 | Over-range | 60 | 17791 | 17035 | 15386 | 50212 | - - - | - - - | - - - | - - - | 17791 | 17035 | 15386 | 50212 | 11067 | 9009 | 10368 | 30444 | - - - | - - - | - - - | - - - | 11067 | 9009 | 10368 | 30444 | 21509 | 19794 | 19097 | 60401 | # # # | # # # | # # # | # # # | 0.827 | 0.861 | 0.806 | 0.831 | # # # | # # # | # # # | - - - | 0.848 | 0.883 | 0.828 | 0.853 | - - - | 0.606 | 1.65 | 1.58 | 1.5 | 1.51 | 1.48 | 1.52 | 21.58 | 22.28 | 23.1 | 0 | - - - | - - - | - - - | - - - | 21509 | 19794 | 19097 | 60401 | Over-range | 12080 | 10068 | 11300 | 33539 | 4756 | 4412 | 4411 | 13826 | 17798 | 17104 | 15376 | 50278 | 17798 | 17104 | 15376 | 50278 | - - - | - - - | - - - | - - -
5/7/2026 | 10:30:00 PM | 284.65 | 282.5 | 280.6 | 492.67 | 486.19 | 489.46 | 76.1823 | 70.6615 | 67.7543 | 0.2403 | 1.43 | 1.429 | 1.424 | 1.94 | 1.91 | 2.04 | Over-range | 60.01 | 17816 | 17167 | 15235 | 50218 | - - - | - - - | - - - | - - - | 17816 | 17167 | 15235 | 50218 | 11156 | 8808 | 10252 | 30216 | - - - | - - - | - - - | - - - | 11156 | 8808 | 10252 | 30216 | 21552 | 19813 | 18878 | 60242 | # # # | # # # | # # # | # # # | 0.827 | 0.866 | 0.807 | 0.834 | # # # | # # # | # # # | - - - | 0.846 | 0.889 | 0.83 | 0.855 | - - - | 0.602 | 1.67 | 1.56 | 1.48 | 1.51 | 1.49 | 1.52 | 21.28 | 22.19 | 22.97 | 0 | - - - | - - - | - - - | - - - | 21552 | 19813 | 18878 | 60242 | Over-range | 12121 | 9882 | 11138 | 33253 | 4673 | 4413 | 4286 | 13688 | 17797 | 17201 | 15289 | 50287 | 17797 | 17201 | 15289 | 50287 | - - - | - - - | - - - | - - -
5/7/2026 | 10:45:00 PM | 285.07 | 282.85 | 281.02 | 493.28 | 486.89 | 490.24 | 74.8711 | 69.3912 | 67.6103 | 0.2406 | 1.43 | 1.429 | 1.424 | 1.927 | 1.899 | 2.025 | Over-range | 60.01 | 17505 | 16717 | 15138 | 49360 | - - - | - - - | - - - | - - - | 17505 | 16717 | 15138 | 49360 | 11043 | 8982 | 10351 | 30376 | - - - | - - - | - - - | - - - | 11043 | 8982 | 10351 | 30376 | 21211 | 19477 | 18866 | 59554 | # # # | # # # | # # # | # # # | 0.825 | 0.858 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.845 | 0.878 | 0.823 | 0.849 | - - - | 0.615 | 1.68 | 1.59 | 1.51 | 1.52 | 1.5 | 1.54 | 20.75 | 21.33 | 22.2 | 0 | - - - | - - - | - - - | - - - | 21211 | 19477 | 18866 | 59554 | Over-range | 11964 | 9975 | 11243 | 33272 | 4503 | 4248 | 4292 | 13302 | 17577 | 16692 | 15153 | 49421 | 17577 | 16692 | 15153 | 49421 | - - - | - - - | - - - | - - -
5/7/2026 | 11:00:00 PM | 285.65 | 283.46 | 281.6 | 494.36 | 487.89 | 491.23 | 75.6588 | 70.2199 | 68.0146 | 0.2407 | 1.431 | 1.429 | 1.424 | 1.917 | 1.873 | 2.012 | Over-range | 60.01 | 17685 | 16975 | 15266 | 49926 | - - - | - - - | - - - | - - - | 17685 | 16975 | 15266 | 49926 | 11294 | 9154 | 10487 | 30935 | - - - | - - - | - - - | - - - | 11294 | 9154 | 10487 | 30935 | 21461 | 19736 | 19003 | 60200 | # # # | # # # | # # # | # # # | 0.824 | 0.86 | 0.803 | 0.829 | # # # | # # # | # # # | - - - | 0.842 | 0.879 | 0.823 | 0.848 | - - - | 0.62 | 1.68 | 1.58 | 1.51 | 1.52 | 1.5 | 1.54 | 20.03 | 20.48 | 21.33 | 0 | - - - | - - - | - - - | - - - | 21461 | 19736 | 19003 | 60200 | Over-range | 12149 | 10057 | 11305 | 33608 | 4381 | 4076 | 4133 | 12868 | 17754 | 16974 | 15254 | 49982 | 17754 | 16974 | 15254 | 49982 | - - - | - - - | - - - | - - -
5/7/2026 | 11:15:00 PM | 285.52 | 283.18 | 281.37 | 494.04 | 487.37 | 490.94 | 75.9899 | 70.1687 | 67.9226 | 0.2415 | 1.43 | 1.428 | 1.424 | 1.933 | 1.899 | 2.043 | Over-range | 59.98 | 17779 | 16991 | 15217 | 49988 | - - - | - - - | - - - | - - - | 17779 | 16991 | 15217 | 49988 | 11197 | 8962 | 10401 | 30560 | - - - | - - - | - - - | - - - | 11197 | 8962 | 10401 | 30560 | 21538 | 19698 | 18960 | 60196 | # # # | # # # | # # # | # # # | 0.826 | 0.863 | 0.803 | 0.83 | # # # | # # # | # # # | - - - | 0.846 | 0.884 | 0.824 | 0.851 | - - - | 0.611 | 1.7 | 1.58 | 1.51 | 1.53 | 1.51 | 1.54 | 21.14 | 21.71 | 22.73 | 0 | - - - | - - - | - - - | - - - | 21538 | 19698 | 18960 | 60196 | Over-range | 12150 | 9953 | 11299 | 33510 | 4631 | 4248 | 4331 | 13508 | 17824 | 17036 | 15190 | 50049 | 17824 | 17036 | 15190 | 50049 | - - - | - - - | - - - | - - -
5/7/2026 | 11:30:00 PM | 285.87 | 283.55 | 281.68 | 494.65 | 488.02 | 491.47 | 75.1204 | 69.3147 | 67.5562 | 0.2407 | 1.43 | 1.429 | 1.424 | 1.93 | 1.898 | 2.035 | Over-range | 60.01 | 17558 | 16712 | 15078 | 49348 | - - - | - - - | - - - | - - - | 17558 | 16712 | 15078 | 49348 | 11178 | 9049 | 10479 | 30705 | - - - | - - - | - - - | - - - | 11178 | 9049 | 10479 | 30705 | 21317 | 19481 | 18878 | 59676 | # # # | # # # | # # # | # # # | 0.824 | 0.858 | 0.799 | 0.827 | # # # | # # # | # # # | - - - | 0.843 | 0.878 | 0.819 | 0.847 | - - - | 0.622 | 1.71 | 1.59 | 1.53 | 1.54 | 1.53 | 1.56 | 20.86 | 21.44 | 22.34 | 0 | - - - | - - - | - - - | - - - | 21317 | 19481 | 18878 | 59676 | Over-range | 12082 | 10000 | 11347 | 33528 | 4494 | 4170 | 4268 | 13210 | 17633 | 16711 | 15059 | 49403 | 17633 | 16711 | 15059 | 49403 | - - - | - - - | - - - | - - -
5/7/2026 | 11:45:00 PM | 286.24 | 283.9 | 281.97 | 495.34 | 488.46 | 492.06 | 77.9105 | 72.1428 | 69.5901 | 0.2438 | 1.429 | 1.428 | 1.423 | 1.925 | 1.892 | 2.035 | Over-range | 60.01 | 18232 | 17491 | 15614 | 51338 | - - - | - - - | - - - | - - - | 18232 | 17491 | 15614 | 51338 | 11572 | 9264 | 10680 | 31517 | - - - | - - - | - - - | - - - | 11572 | 9264 | 10680 | 31517 | 22140 | 20303 | 19465 | 61908 | # # # | # # # | # # # | # # # | 0.824 | 0.862 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.843 | 0.882 | 0.823 | 0.85 | - - - | 0.614 | 1.72 | 1.6 | 1.49 | 1.53 | 1.52 | 1.55 | 20.83 | 21.41 | 22.51 | 0 | - - - | - - - | - - - | - - - | 22140 | 20303 | 19465 | 61908 | Over-range | 12545 | 10286 | 11605 | 34545 | 4733 | 4360 | 4435 | 13834 | 18281 | 17534 | 15580 | 51395 | 18281 | 17534 | 15580 | 51395 | - - - | - - - | - - - | - - -
5/8/2026 | 12:00:00 AM | 286.06 | 283.83 | 281.94 | 495.09 | 488.45 | 491.88 | 75.3536 | 69.7486 | 67.4949 | 0.2409 | 1.43 | 1.428 | 1.423 | 1.923 | 1.893 | 2.038 | Over-range | 60 | 17573 | 16853 | 15086 | 49512 | - - - | - - - | - - - | - - - | 17573 | 16853 | 15086 | 49512 | 11287 | 9106 | 10505 | 30897 | - - - | - - - | - - - | - - - | 11287 | 9106 | 10505 | 30897 | 21404 | 19631 | 18881 | 59916 | # # # | # # # | # # # | # # # | 0.821 | 0.859 | 0.799 | 0.826 | # # # | # # # | # # # | - - - | 0.84 | 0.879 | 0.819 | 0.846 | - - - | 0.624 | 1.71 | 1.58 | 1.5 | 1.53 | 1.5 | 1.54 | 20.86 | 21.31 | 22.43 | 0 | - - - | - - - | - - - | - - - | 21404 | 19631 | 18881 | 59916 | Over-range | 12211 | 10054 | 11344 | 33713 | 4577 | 4184 | 4198 | 13250 | 17552 | 16918 | 15098 | 49567 | 17552 | 16918 | 15098 | 49567 | - - - | - - - | - - - | - - -
5/8/2026 | 12:15:00 AM | 284.48 | 282.25 | 280.37 | 492.31 | 485.81 | 489.1 | 75.5596 | 70.1325 | 68.2796 | 0.2425 | 1.43 | 1.427 | 1.423 | 1.919 | 1.883 | 2.026 | Over-range | 59.99 | 17649 | 16887 | 15290 | 49826 | - - - | - - - | - - - | - - - | 17649 | 16887 | 15290 | 49826 | 11120 | 9115 | 10448 | 30683 | - - - | - - - | - - - | - - - | 11120 | 9115 | 10448 | 30683 | 21363 | 19647 | 19010 | 60021 | # # # | # # # | # # # | # # # | 0.826 | 0.86 | 0.804 | 0.83 | # # # | # # # | # # # | - - - | 0.845 | 0.879 | 0.824 | 0.85 | - - - | 0.616 | 1.72 | 1.57 | 1.5 | 1.53 | 1.51 | 1.55 | 20.5 | 20.76 | 21.79 | 0 | - - - | - - - | - - - | - - - | 21363 | 19647 | 19010 | 60021 | Over-range | 12029 | 10030 | 11285 | 33434 | 4495 | 4095 | 4176 | 13018 | 17661 | 16938 | 15276 | 49875 | 17661 | 16938 | 15276 | 49875 | - - - | - - - | - - - | - - -
5/8/2026 | 12:30:00 AM | 284.34 | 281.89 | 280.17 | 491.89 | 485.23 | 488.89 | 75.8371 | 70.0462 | 67.7704 | 0.238 | 1.428 | 1.426 | 1.421 | 1.921 | 1.89 | 2.048 | Over-range | 60 | 17772 | 16997 | 15224 | 49993 | - - - | - - - | - - - | - - - | 17772 | 16997 | 15224 | 49993 | 11062 | 8836 | 10266 | 30164 | - - - | - - - | - - - | - - - | 11062 | 8836 | 10266 | 30164 | 21450 | 19619 | 18875 | 59944 | # # # | # # # | # # # | # # # | 0.829 | 0.866 | 0.807 | 0.834 | # # # | # # # | # # # | - - - | 0.848 | 0.887 | 0.827 | 0.854 | - - - | 0.603 | 1.66 | 1.54 | 1.5 | 1.51 | 1.48 | 1.52 | 20.93 | 21.1 | 22.54 | 0 | - - - | - - - | - - - | - - - | 21450 | 19619 | 18875 | 59944 | Over-range | 12004 | 9786 | 11149 | 33050 | 4587 | 4135 | 4277 | 13298 | 17797 | 17050 | 15195 | 50041 | 17797 | 17050 | 15195 | 50041 | - - - | - - - | - - - | - - -
5/8/2026 | 12:45:00 AM | 284.71 | 282.26 | 280.45 | 492.58 | 485.79 | 489.4 | 77.403 | 71.9748 | 69.4185 | 0.2261 | 1.428 | 1.426 | 1.422 | 1.937 | 1.908 | 2.051 | Over-range | 60 | 18046 | 17353 | 15553 | 50952 | - - - | - - - | - - - | - - - | 18046 | 17353 | 15553 | 50952 | 11282 | 9085 | 10454 | 30821 | - - - | - - - | - - - | - - - | 11282 | 9085 | 10454 | 30821 | 21852 | 20109 | 19292 | 61253 | # # # | # # # | # # # | # # # | 0.826 | 0.863 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.846 | 0.885 | 0.828 | 0.853 | - - - | 0.605 | 1.7 | 1.57 | 1.52 | 1.53 | 1.51 | 1.54 | 21.54 | 21.83 | 23.16 | 0 | - - - | - - - | - - - | - - - | 21852 | 20109 | 19292 | 61253 | Over-range | 12309 | 10139 | 11397 | 33948 | 4817 | 4403 | 4438 | 13941 | 18025 | 17420 | 15567 | 51011 | 18025 | 17420 | 15567 | 51011 | - - - | - - - | - - - | - - -
5/8/2026 | 1:00:00 AM | 284.83 | 282.31 | 280.53 | 492.7 | 485.91 | 489.6 | 76.2086 | 70.6927 | 68.6774 | 0.2432 | 1.429 | 1.426 | 1.422 | 1.942 | 1.916 | 2.063 | Over-range | 60.01 | 17838 | 17059 | 15407 | 50305 | - - - | - - - | - - - | - - - | 17838 | 17059 | 15407 | 50305 | 11089 | 9008 | 10369 | 30466 | - - - | - - - | - - - | - - - | 11089 | 9008 | 10369 | 30466 | 21562 | 19795 | 19125 | 60482 | # # # | # # # | # # # | # # # | 0.827 | 0.862 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.848 | 0.883 | 0.828 | 0.853 | - - - | 0.606 | 1.71 | 1.57 | 1.52 | 1.54 | 1.51 | 1.55 | 21.74 | 21.88 | 23.32 | 0 | - - - | - - - | - - - | - - - | 21562 | 19795 | 19125 | 60482 | Over-range | 12106 | 10029 | 11318 | 33549 | 4772 | 4328 | 4456 | 13809 | 17847 | 17111 | 15394 | 50352 | 17847 | 17111 | 15394 | 50352 | - - - | - - - | - - - | - - -
5/8/2026 | 1:15:00 AM | 284.75 | 282.14 | 280.44 | 492.52 | 485.59 | 489.5 | 78.0582 | 72.0575 | 69.661 | 0.2441 | 1.428 | 1.425 | 1.421 | 1.928 | 1.902 | 2.062 | Over-range | 60 | 18268 | 17450 | 15612 | 51330 | - - - | - - - | - - - | - - - | 18268 | 17450 | 15612 | 51330 | 11361 | 9008 | 10484 | 30852 | - - - | - - - | - - - | - - - | 11361 | 9008 | 10484 | 30852 | 22044 | 20132 | 19363 | 61539 | # # # | # # # | # # # | # # # | 0.829 | 0.867 | 0.806 | 0.834 | # # # | # # # | # # # | - - - | 0.849 | 0.887 | 0.828 | 0.855 | - - - | 0.601 | 1.67 | 1.56 | 1.5 | 1.51 | 1.49 | 1.52 | 21.34 | 21.61 | 23.2 | 0 | - - - | - - - | - - - | - - - | 22044 | 20132 | 19363 | 61539 | Over-range | 12332 | 10028 | 11443 | 33919 | 4702 | 4321 | 4501 | 13841 | 18348 | 17434 | 15597 | 51379 | 18348 | 17434 | 15597 | 51379 | - - - | - - - | - - - | - - -
5/8/2026 | 1:30:00 AM | 284.8 | 282.04 | 280.41 | 492.5 | 485.4 | 489.59 | 74.4557 | 68.2714 | 66.7308 | 0.2154 | 1.428 | 1.425 | 1.422 | 1.946 | 1.922 | 2.089 | Over-range | 60 | 17418 | 16461 | 14857 | 48736 | - - - | - - - | - - - | - - - | 17418 | 16461 | 14857 | 48736 | 10765 | 8617 | 10155 | 29537 | - - - | - - - | - - - | - - - | 10765 | 8617 | 10155 | 29537 | 21050 | 19084 | 18564 | 58698 | # # # | # # # | # # # | # # # | 0.828 | 0.863 | 0.8 | 0.83 | # # # | # # # | # # # | - - - | 0.849 | 0.885 | 0.824 | 0.853 | - - - | 0.606 | 1.68 | 1.58 | 1.5 | 1.52 | 1.5 | 1.54 | 22.43 | 22.47 | 24.23 | 0 | - - - | - - - | - - - | - - - | 21050 | 19084 | 18564 | 58698 | Over-range | 11812 | 9644 | 11119 | 32686 | 4780 | 4252 | 4451 | 13767 | 17419 | 16523 | 14841 | 48783 | 17419 | 16523 | 14841 | 48783 | - - - | - - - | - - - | - - -
5/8/2026 | 1:45:00 AM | 284.77 | 282.17 | 280.51 | 492.53 | 485.73 | 489.58 | 74.4051 | 68.5688 | 66.7797 | 0.2413 | 1.428 | 1.425 | 1.421 | 1.938 | 1.917 | 2.07 | Over-range | 60.02 | 17406 | 16548 | 14914 | 48867 | - - - | - - - | - - - | - - - | 17406 | 16548 | 14914 | 48867 | 10845 | 8704 | 10147 | 29696 | - - - | - - - | - - - | - - - | 10845 | 8704 | 10147 | 29696 | 21062 | 19205 | 18605 | 58872 | # # # | # # # | # # # | # # # | 0.826 | 0.862 | 0.802 | 0.83 | # # # | # # # | # # # | - - - | 0.848 | 0.883 | 0.825 | 0.852 | - - - | 0.608 | 1.66 | 1.55 | 1.5 | 1.51 | 1.48 | 1.52 | 21.82 | 22.06 | 23.66 | 0 | - - - | - - - | - - - | - - - | 21062 | 19205 | 18605 | 58872 | Over-range | 11845 | 9727 | 11109 | 32785 | 4672 | 4252 | 4438 | 13640 | 17449 | 16567 | 14897 | 48914 | 17449 | 16567 | 14897 | 48914 | - - - | - - - | - - - | - - -
5/8/2026 | 2:00:00 AM | 285.11 | 282.33 | 280.72 | 493.03 | 485.89 | 490.13 | 76.4227 | 69.8899 | 67.4952 | 0.2239 | 1.428 | 1.425 | 1.421 | 1.907 | 1.878 | 2.057 | Over-range | 60.01 | 17866 | 16990 | 15035 | 49891 | - - - | - - - | - - - | - - - | 17866 | 16990 | 15035 | 49891 | 11353 | 8795 | 10468 | 30616 | - - - | - - - | - - - | - - - | 11353 | 8795 | 10468 | 30616 | 21665 | 19592 | 18822 | 60079 | # # # | # # # | # # # | # # # | 0.825 | 0.867 | 0.799 | 0.83 | # # # | # # # | # # # | - - - | 0.843 | 0.886 | 0.82 | 0.85 | - - - | 0.614 | 1.66 | 1.56 | 1.5 | 1.51 | 1.49 | 1.52 | 20.5 | 20.58 | 22.39 | 0 | - - - | - - - | - - - | - - - | 21665 | 19592 | 18822 | 60079 | Over-range | 12247 | 9741 | 11312 | 33441 | 4506 | 4104 | 4199 | 13204 | 17863 | 16973 | 15098 | 49934 | 17863 | 16973 | 15098 | 49934 | - - - | - - - | - - - | - - -
5/8/2026 | 2:15:00 AM | 285.11 | 282.3 | 280.71 | 492.99 | 485.83 | 490.16 | 75.2835 | 68.7354 | 67.28 | 0.2403 | 1.427 | 1.424 | 1.42 | 1.914 | 1.889 | 2.062 | Over-range | 60.01 | 17633 | 16618 | 14965 | 49216 | - - - | - - - | - - - | - - - | 17633 | 16618 | 14965 | 49216 | 11088 | 8814 | 10463 | 30365 | - - - | - - - | - - - | - - - | 11088 | 8814 | 10463 | 30365 | 21339 | 19263 | 18763 | 59365 | # # # | # # # | # # # | # # # | 0.826 | 0.863 | 0.798 | 0.829 | # # # | # # # | # # # | - - - | 0.845 | 0.882 | 0.819 | 0.849 | - - - | 0.617 | 1.66 | 1.53 | 1.47 | 1.49 | 1.48 | 1.5 | 20.95 | 20.82 | 22.59 | 0 | - - - | - - - | - - - | - - - | 21339 | 19263 | 18763 | 59365 | Over-range | 12011 | 9731 | 11308 | 33170 | 4543 | 4048 | 4213 | 13133 | 17613 | 16637 | 15007 | 49257 | 17613 | 16637 | 15007 | 49257 | - - - | - - - | - - - | - - -
5/8/2026 | 2:30:00 AM | 285.2 | 282.45 | 280.8 | 493.19 | 486.11 | 490.26 | 76.8178 | 70.5235 | 68.4477 | 0.2249 | 1.427 | 1.424 | 1.42 | 1.919 | 1.891 | 2.06 | Over-range | 60 | 17992 | 17097 | 15294 | 50383 | - - - | - - - | - - - | - - - | 17992 | 17097 | 15294 | 50383 | 11293 | 8913 | 10511 | 30717 | - - - | - - - | - - - | - - - | 11293 | 8913 | 10511 | 30717 | 21759 | 19755 | 19076 | 60590 | # # # | # # # | # # # | # # # | 0.827 | 0.865 | 0.802 | 0.832 | # # # | # # # | # # # | - - - | 0.846 | 0.885 | 0.824 | 0.852 | - - - | 0.61 | 1.65 | 1.53 | 1.48 | 1.5 | 1.48 | 1.5 | 21.08 | 21.15 | 22.81 | 0 | - - - | - - - | - - - | - - - | 21759 | 19755 | 19076 | 60590 | Over-range | 12230 | 9886 | 11391 | 33631 | 4615 | 4199 | 4313 | 13465 | 17998 | 17088 | 15343 | 50428 | 17998 | 17088 | 15343 | 50428 | - - - | - - - | - - - | - - -
5/8/2026 | 2:45:00 AM | 285.27 | 282.38 | 280.83 | 493.19 | 485.99 | 490.41 | 77.6117 | 71.1963 | 68.7606 | 0.2351 | 1.426 | 1.423 | 1.419 | 1.914 | 1.89 | 2.068 | Over-range | 60.01 | 18116 | 17241 | 15317 | 50674 | - - - | - - - | - - - | - - - | 18116 | 17241 | 15317 | 50674 | 11400 | 8920 | 10495 | 30814 | - - - | - - - | - - - | - - - | 11400 | 8920 | 10495 | 30814 | 21954 | 19896 | 19133 | 60983 | # # # | # # # | # # # | # # # | 0.825 | 0.867 | 0.801 | 0.831 | # # # | # # # | # # # | - - - | 0.845 | 0.886 | 0.822 | 0.851 | - - - | 0.608 | 1.64 | 1.54 | 1.46 | 1.49 | 1.48 | 1.5 | 21.14 | 21.11 | 23.19 | 0 | - - - | - - - | - - - | - - - | 21954 | 19896 | 19133 | 60983 | Over-range | 12383 | 9904 | 11447 | 33869 | 4724 | 4194 | 4468 | 13747 | 18162 | 17278 | 15277 | 50717 | 18162 | 17278 | 15277 | 50717 | - - - | - - - | - - - | - - -
5/8/2026 | 3:00:00 AM | 285.48 | 282.6 | 281 | 493.6 | 486.31 | 490.72 | 76.163 | 69.4227 | 68.063 | 0.2322 | 1.426 | 1.424 | 1.419 | 1.911 | 1.88 | 2.062 | Over-range | 60.01 | 17875 | 16813 | 15152 | 49840 | - - - | - - - | - - - | - - - | 17875 | 16813 | 15152 | 49840 | 11230 | 8949 | 10588 | 30767 | - - - | - - - | - - - | - - - | 11230 | 8949 | 10588 | 30767 | 21622 | 19485 | 19007 | 60114 | # # # | # # # | # # # | # # # | 0.827 | 0.863 | 0.797 | 0.829 | # # # | # # # | # # # | - - - | 0.846 | 0.882 | 0.818 | 0.849 | - - - | 0.617 | 1.67 | 1.53 | 1.46 | 1.49 | 1.48 | 1.49 | 20.88 | 20.68 | 22.56 | 0 | - - - | - - - | - - - | - - - | 21622 | 19485 | 19007 | 60114 | Over-range | 12159 | 9838 | 11465 | 33585 | 4585 | 4011 | 4323 | 13250 | 17916 | 16850 | 15113 | 49878 | 17916 | 16850 | 15113 | 49878 | - - - | - - - | - - - | - - -
5/8/2026 | 3:15:00 AM | 285.77 | 282.96 | 281.41 | 494.08 | 487.09 | 491.31 | 75.7482 | 69.1626 | 67.4601 | 0.2407 | 1.427 | 1.424 | 1.419 | 1.903 | 1.875 | 2.051 | Over-range | 60 | 17784 | 16799 | 15055 | 49638 | - - - | - - - | - - - | - - - | 17784 | 16799 | 15055 | 49638 | 11222 | 8887 | 10507 | 30617 | - - - | - - - | - - - | - - - | 11222 | 8887 | 10507 | 30617 | 21519 | 19430 | 18860 | 59810 | # # # | # # # | # # # | # # # | 0.826 | 0.865 | 0.798 | 0.83 | # # # | # # # | # # # | - - - | 0.845 | 0.883 | 0.818 | 0.849 | - - - | 0.617 | 1.66 | 1.53 | 1.45 | 1.5 | 1.47 | 1.49 | 20.36 | 20.33 | 22.17 | 0 | - - - | - - - | - - - | - - - | 21519 | 19430 | 18860 | 59810 | Over-range | 12111 | 9753 | 11352 | 33344 | 4471 | 3940 | 4216 | 12976 | 17818 | 16840 | 15014 | 49671 | 17818 | 16840 | 15014 | 49671 | - - - | - - - | - - - | - - -
5/8/2026 | 3:30:00 AM | 285.93 | 283.18 | 281.58 | 494.48 | 487.38 | 491.56 | 74.6875 | 68.1992 | 66.1954 | 0.2206 | 1.427 | 1.424 | 1.419 | 1.909 | 1.879 | 2.063 | Over-range | 60 | 17461 | 16556 | 14719 | 48736 | - - - | - - - | - - - | - - - | 17461 | 16556 | 14719 | 48736 | 11174 | 8775 | 10361 | 30310 | - - - | - - - | - - - | - - - | 11174 | 8775 | 10361 | 30310 | 21227 | 19171 | 18513 | 58910 | # # # | # # # | # # # | # # # | 0.823 | 0.864 | 0.795 | 0.827 | # # # | # # # | # # # | - - - | 0.842 | 0.883 | 0.816 | 0.847 | - - - | 0.622 | 1.64 | 1.54 | 1.48 | 1.5 | 1.47 | 1.5 | 20.77 | 20.69 | 22.66 | 0 | - - - | - - - | - - - | - - - | 21227 | 19171 | 18513 | 58910 | Over-range | 12064 | 9655 | 11219 | 33070 | 4466 | 3950 | 4226 | 13002 | 17509 | 16585 | 14683 | 48778 | 17509 | 16585 | 14683 | 48778 | - - - | - - - | - - - | - - -
5/8/2026 | 3:45:00 AM | 285.87 | 283.05 | 281.53 | 494.29 | 487.22 | 491.51 | 74.9031 | 68.4844 | 67.0149 | 0.2399 | 1.427 | 1.424 | 1.421 | 1.926 | 1.904 | 2.074 | Over-range | 60.01 | 17557 | 16563 | 14923 | 49043 | - - - | - - - | - - - | - - - | 17557 | 16563 | 14923 | 49043 | 11027 | 8812 | 10397 | 30236 | - - - | - - - | - - - | - - - | 11027 | 8812 | 10397 | 30236 | 21293 | 19248 | 18747 | 59288 | # # # | # # # | # # # | # # # | 0.825 | 0.861 | 0.796 | 0.827 | # # # | # # # | # # # | - - - | 0.845 | 0.882 | 0.818 | 0.849 | - - - | 0.617 | 1.67 | 1.57 | 1.44 | 1.5 | 1.48 | 1.5 | 21.58 | 21.53 | 23.42 | 0 | - - - | - - - | - - - | - - - | 21293 | 19248 | 18747 | 59288 | Over-range | 12031 | 9785 | 11331 | 33264 | 4721 | 4164 | 4420 | 13613 | 17565 | 16626 | 14893 | 49083 | 17565 | 16626 | 14893 | 49083 | - - - | - - - | - - - | - - -
5/8/2026 | 4:00:00 AM | 285.99 | 283.28 | 281.68 | 494.58 | 487.62 | 491.68 | 77.8918 | 71.6623 | 69.404 | 0.2345 | 1.426 | 1.424 | 1.42 | 1.917 | 1.892 | 2.051 | Over-range | 60.02 | 18260 | 17398 | 15541 | 51199 | - - - | - - - | - - - | - - - | 18260 | 17398 | 15541 | 51199 | 11529 | 9132 | 10714 | 31375 | - - - | - - - | - - - | - - - | 11529 | 9132 | 10714 | 31375 | 22119 | 20127 | 19398 | 61644 | # # # | # # # | # # # | # # # | 0.826 | 0.864 | 0.801 | 0.831 | # # # | # # # | # # # | - - - | 0.844 | 0.884 | 0.822 | 0.851 | - - - | 0.613 | 1.64 | 1.53 | 1.45 | 1.49 | 1.46 | 1.48 | 20.87 | 21.1 | 22.68 | 0 | - - - | - - - | - - - | - - - | 22119 | 20127 | 19398 | 61644 | Over-range | 12476 | 10106 | 11596 | 34301 | 4682 | 4247 | 4355 | 13624 | 18251 | 17429 | 15564 | 51244 | 18251 | 17429 | 15564 | 51244 | - - - | - - - | - - - | - - -
5/8/2026 | 4:15:00 AM | 285.76 | 283 | 281.4 | 494.15 | 487.05 | 491.29 | 75.6576 | 69.5251 | 67.4443 | 0.2265 | 1.427 | 1.424 | 1.421 | 1.928 | 1.91 | 2.074 | Over-range | 60 | 17659 | 16793 | 15016 | 49468 | - - - | - - - | - - - | - - - | 17659 | 16793 | 15016 | 49468 | 11142 | 8839 | 10372 | 30353 | - - - | - - - | - - - | - - - | 11142 | 8839 | 10372 | 30353 | 21432 | 19469 | 18802 | 59702 | # # # | # # # | # # # | # # # | 0.824 | 0.863 | 0.799 | 0.829 | # # # | # # # | # # # | - - - | 0.844 | 0.884 | 0.821 | 0.85 | - - - | 0.614 | 1.66 | 1.56 | 1.48 | 1.5 | 1.49 | 1.5 | 21.7 | 21.83 | 23.69 | 0 | - - - | - - - | - - - | - - - | 21432 | 19469 | 18802 | 59702 | Over-range | 12137 | 9834 | 11301 | 33391 | 4718 | 4220 | 4397 | 13654 | 17647 | 16847 | 15015 | 49509 | 17647 | 16847 | 15015 | 49509 | - - - | - - - | - - - | - - -
5/8/2026 | 4:30:00 AM | 285.86 | 283.16 | 281.56 | 494.38 | 487.37 | 491.48 | 77.5283 | 71.4085 | 69.5587 | 0.2413 | 1.426 | 1.424 | 1.42 | 1.922 | 1.904 | 2.051 | Over-range | 60.01 | 18196 | 17297 | 15585 | 51077 | - - - | - - - | - - - | - - - | 18196 | 17297 | 15585 | 51077 | 11452 | 9206 | 10748 | 31406 | - - - | - - - | - - - | - - - | 11452 | 9206 | 10748 | 31406 | 22040 | 20084 | 19463 | 61587 | # # # | # # # | # # # | # # # | 0.826 | 0.861 | 0.801 | 0.829 | # # # | # # # | # # # | - - - | 0.845 | 0.882 | 0.822 | 0.85 | - - - | 0.615 | 1.66 | 1.54 | 1.47 | 1.49 | 1.48 | 1.5 | 21.13 | 21.35 | 22.89 | 0 | - - - | - - - | - - - | - - - | 22040 | 20084 | 19463 | 61587 | Over-range | 12431 | 10197 | 11649 | 34387 | 4757 | 4308 | 4416 | 13777 | 18167 | 17341 | 15613 | 51121 | 18167 | 17341 | 15613 | 51121 | - - - | - - - | - - - | - - -
5/8/2026 | 4:45:00 AM | 285.53 | 282.79 | 281.24 | 493.72 | 486.82 | 490.92 | 77.3545 | 71.3198 | 68.9839 | 0.2331 | 1.426 | 1.424 | 1.42 | 1.942 | 1.932 | 2.068 | Over-range | 59.99 | 18099 | 17252 | 15423 | 50774 | - - - | - - - | - - - | - - - | 18099 | 17252 | 15423 | 50774 | 11237 | 8896 | 10427 | 30561 | - - - | - - - | - - - | - - - | 11237 | 8896 | 10427 | 30561 | 21904 | 19965 | 19225 | 61095 | # # # | # # # | # # # | # # # | 0.826 | 0.864 | 0.802 | 0.831 | # # # | # # # | # # # | - - - | 0.848 | 0.887 | 0.826 | 0.854 | - - - | 0.602 | 1.65 | 1.58 | 1.45 | 1.5 | 1.48 | 1.5 | 22.17 | 22.78 | 24.37 | 0 | - - - | - - - | - - - | - - - | 21904 | 19965 | 19225 | 61095 | Over-range | 12322 | 10027 | 11461 | 33928 | 4958 | 4534 | 4668 | 14471 | 18109 | 17314 | 15399 | 50821 | 18109 | 17314 | 15399 | 50821 | - - - | - - - | - - - | - - -
5/8/2026 | 5:00:00 AM | 285.62 | 282.9 | 281.29 | 493.97 | 486.85 | 491.08 | 75.3393 | 69.4393 | 67.5699 | 0.2305 | 1.426 | 1.424 | 1.42 | 1.973 | 1.962 | 2.102 | Over-range | 60.03 | 17672 | 16781 | 15132 | 49585 | - - - | - - - | - - - | - - - | 17672 | 16781 | 15132 | 49585 | 10819 | 8661 | 10148 | 29629 | - - - | - - - | - - - | - - - | 10819 | 8661 | 10148 | 29629 | 21357 | 19469 | 18855 | 59681 | # # # | # # # | # # # | # # # | 0.828 | 0.862 | 0.803 | 0.831 | # # # | # # # | # # # | - - - | 0.852 | 0.888 | 0.829 | 0.856 | - - - | 0.598 | 1.67 | 1.57 | 1.47 | 1.5 | 1.49 | 1.5 | 23.63 | 24.19 | 25.75 | 0 | - - - | - - - | - - - | - - - | 21357 | 19469 | 18855 | 59681 | Over-range | 11986 | 9860 | 11239 | 33188 | 5083 | 4642 | 4761 | 14748 | 17663 | 16850 | 15126 | 49639 | 17663 | 16850 | 15126 | 49639 | - - - | - - - | - - - | - - -
5/8/2026 | 5:15:00 AM | 285.16 | 282.47 | 280.85 | 493.19 | 486.12 | 490.28 | 76.7358 | 71.0126 | 69.0021 | 0.2369 | 1.427 | 1.425 | 1.422 | 1.953 | 1.948 | 2.071 | Over-range | 60.01 | 18032 | 17188 | 15523 | 50743 | - - - | - - - | - - - | - - - | 18032 | 17188 | 15523 | 50743 | 11045 | 8868 | 10333 | 30247 | - - - | - - - | - - - | - - - | 11045 | 8868 | 10333 | 30247 | 21748 | 19913 | 19251 | 60912 | # # # | # # # | # # # | # # # | 0.829 | 0.863 | 0.806 | 0.833 | # # # | # # # | # # # | - - - | 0.851 | 0.887 | 0.832 | 0.857 | - - - | 0.596 | 1.69 | 1.59 | 1.54 | 1.53 | 1.53 | 1.56 | 22.68 | 23.31 | 24.72 | 0 | - - - | - - - | - - - | - - - | 21748 | 19913 | 19251 | 60912 | Over-range | 12151 | 10045 | 11376 | 33670 | 4993 | 4652 | 4690 | 14595 | 18017 | 17210 | 15578 | 50805 | 18017 | 17210 | 15578 | 50805 | - - - | - - - | - - - | - - -
5/8/2026 | 5:30:00 AM | 285.09 | 282.49 | 280.88 | 493.11 | 486.25 | 490.19 | 76.7289 | 70.9773 | 68.1303 | 0.2303 | 1.427 | 1.425 | 1.422 | 1.934 | 1.924 | 2.057 | Over-range | 60 | 17981 | 17274 | 15322 | 50577 | - - - | - - - | - - - | - - - | 17981 | 17274 | 15322 | 50577 | 11249 | 8802 | 10299 | 30350 | - - - | - - - | - - - | - - - | 11249 | 8802 | 10299 | 30350 | 21753 | 19917 | 19016 | 60687 | # # # | # # # | # # # | # # # | 0.827 | 0.867 | 0.806 | 0.833 | # # # | # # # | # # # | - - - | 0.847 | 0.89 | 0.83 | 0.856 | - - - | 0.6 | 1.7 | 1.64 | 1.55 | 1.54 | 1.54 | 1.57 | 21.61 | 22.35 | 23.83 | 0 | - - - | - - - | - - - | - - - | 21753 | 19917 | 19016 | 60687 | Over-range | 12237 | 9905 | 11254 | 33515 | 4751 | 4482 | 4475 | 14037 | 17980 | 17268 | 15383 | 50632 | 17980 | 17268 | 15383 | 50632 | - - - | - - - | - - - | - - -
5/8/2026 | 5:45:00 AM | 284.94 | 282.35 | 280.69 | 492.9 | 485.89 | 489.93 | 75.2502 | 69.6111 | 67.5817 | 0.2346 | 1.427 | 1.425 | 1.421 | 1.951 | 1.932 | 2.066 | Over-range | 60 | 17586 | 16775 | 15116 | 49477 | - - - | - - - | - - - | - - - | 17586 | 16775 | 15116 | 49477 | 10961 | 8793 | 10182 | 29936 | - - - | - - - | - - - | - - - | 10961 | 8793 | 10182 | 29936 | 21293 | 19488 | 18825 | 59605 | # # # | # # # | # # # | # # # | 0.826 | 0.861 | 0.803 | 0.83 | # # # | # # # | # # # | - - - | 0.848 | 0.883 | 0.828 | 0.853 | - - - | 0.605 | 1.7 | 1.63 | 1.57 | 1.54 | 1.55 | 1.58 | 22.15 | 22.76 | 24.14 | 0 | - - - | - - - | - - - | - - - | 21293 | 19488 | 18825 | 59605 | Over-range | 11989 | 9896 | 11202 | 33185 | 4759 | 4451 | 4584 | 14060 | 17670 | 16751 | 15116 | 49536 | 17670 | 16751 | 15116 | 49536 | - - - | - - - | - - - | - - -
5/8/2026 | 6:00:00 AM | 284.52 | 281.88 | 280.29 | 492.1 | 485.13 | 489.28 | 77.1014 | 71.197 | 68.8852 | 0.2394 | 1.427 | 1.426 | 1.422 | 1.925 | 1.913 | 2.046 | Over-range | 60 | 18055 | 17237 | 15451 | 50744 | - - - | - - - | - - - | - - - | 18055 | 17237 | 15451 | 50744 | 11233 | 8918 | 10377 | 30528 | - - - | - - - | - - - | - - - | 11233 | 8918 | 10377 | 30528 | 21792 | 19909 | 19171 | 60872 | # # # | # # # | # # # | # # # | 0.829 | 0.866 | 0.806 | 0.834 | # # # | # # # | # # # | - - - | 0.849 | 0.887 | 0.829 | 0.855 | - - - | 0.602 | 1.73 | 1.64 | 1.58 | 1.55 | 1.57 | 1.61 | 21.18 | 21.79 | 23.27 | 0 | - - - | - - - | - - - | - - - | 21792 | 19909 | 19171 | 60872 | Over-range | 12195 | 9951 | 11336 | 33594 | 4668 | 4343 | 4491 | 13805 | 18134 | 17229 | 15443 | 50806 | 18134 | 17229 | 15443 | 50806 | - - - | - - - | - - - | - - -
5/8/2026 | 6:15:00 AM | 283.83 | 281.25 | 279.49 | 490.98 | 483.91 | 487.93 | 76.2688 | 70.6465 | 67.6723 | 0.2238 | 1.426 | 1.426 | 1.422 | 1.925 | 1.908 | 2.055 | Over-range | 59.98 | 17850 | 17183 | 15225 | 50258 | - - - | - - - | - - - | - - - | 17850 | 17183 | 15225 | 50258 | 11067 | 8652 | 10037 | 29755 | - - - | - - - | - - - | - - - | 11067 | 8652 | 10037 | 29755 | 21533 | 19743 | 18797 | 60073 | # # # | # # # | # # # | # # # | 0.829 | 0.87 | 0.81 | 0.837 | # # # | # # # | # # # | - - - | 0.85 | 0.892 | 0.834 | 0.859 | - - - | 0.592 | 1.75 | 1.7 | 1.64 | 1.58 | 1.61 | 1.65 | 21.38 | 21.92 | 23.58 | 0 | - - - | - - - | - - - | - - - | 21533 | 19743 | 18797 | 60073 | Over-range | 12037 | 9712 | 11015 | 32884 | 4667 | 4350 | 4474 | 13811 | 17937 | 17171 | 15214 | 50321 | 17937 | 17171 | 15214 | 50321 | - - - | - - - | - - - | - - -
5/8/2026 | 6:30:00 AM | 283.95 | 281.5 | 279.7 | 491.33 | 484.29 | 488.22 | 77.2166 | 71.6954 | 69.5743 | 0.2384 | 1.426 | 1.426 | 1.422 | 1.973 | 1.969 | 2.102 | Over-range | 60 | 18103 | 17304 | 15648 | 51055 | - - - | - - - | - - - | - - - | 18103 | 17304 | 15648 | 51055 | 10889 | 8752 | 10114 | 29756 | - - - | - - - | - - - | - - - | 10889 | 8752 | 10114 | 29756 | 21769 | 20010 | 19309 | 61088 | # # # | # # # | # # # | # # # | 0.832 | 0.865 | 0.81 | 0.836 | # # # | # # # | # # # | - - - | 0.857 | 0.891 | 0.839 | 0.862 | - - - | 0.583 | 1.72 | 1.7 | 1.62 | 1.56 | 1.58 | 1.62 | 23.72 | 24.39 | 26 | 0 | - - - | - - - | - - - | - - - | 21769 | 20010 | 19309 | 61088 | Over-range | 12083 | 10038 | 11301 | 33516 | 5164 | 4850 | 4977 | 15228 | 18190 | 17293 | 15642 | 51125 | 18190 | 17293 | 15642 | 51125 | - - - | - - - | - - - | - - -
5/8/2026 | 6:45:00 AM | 283.91 | 281.52 | 279.72 | 491.28 | 484.36 | 488.19 | 77.6694 | 72.6828 | 69.7769 | 0.2362 | 1.426 | 1.426 | 1.421 | 1.968 | 1.962 | 2.095 | Over-range | 59.99 | 18183 | 17598 | 15783 | 51564 | - - - | - - - | - - - | - - - | 18183 | 17598 | 15783 | 51564 | 11053 | 8841 | 10084 | 29977 | - - - | - - - | - - - | - - - | 11053 | 8841 | 10084 | 29977 | 21925 | 20324 | 19397 | 61647 | # # # | # # # | # # # | # # # | 0.829 | 0.866 | 0.814 | 0.836 | # # # | # # # | # # # | - - - | 0.854 | 0.892 | 0.842 | 0.863 | - - - | 0.581 | 1.74 | 1.67 | 1.58 | 1.55 | 1.56 | 1.61 | 23.38 | 24.03 | 25.66 | 0 | - - - | - - - | - - - | - - - | 21925 | 20324 | 19397 | 61647 | Over-range | 12237 | 10148 | 11263 | 33742 | 5178 | 4917 | 4950 | 15290 | 18246 | 17575 | 15815 | 51635 | 18246 | 17575 | 15815 | 51635 | - - - | - - - | - - - | - - -
5/8/2026 | 7:00:00 AM | 283.62 | 281.19 | 279.42 | 490.71 | 483.81 | 487.72 | 75.2401 | 70.5461 | 67.8444 | 0.2297 | 1.426 | 1.425 | 1.42 | 1.987 | 1.986 | 2.125 | Over-range | 60 | 17592 | 17049 | 15334 | 49975 | - - - | - - - | - - - | - - - | 17592 | 17049 | 15334 | 49975 | 10670 | 8581 | 9736 | 28987 | - - - | - - - | - - - | - - - | 10670 | 8581 | 9736 | 28987 | 21257 | 19746 | 18872 | 59875 | # # # | # # # | # # # | # # # | 0.828 | 0.864 | 0.813 | 0.835 | # # # | # # # | # # # | - - - | 0.854 | 0.891 | 0.843 | 0.863 | - - - | 0.58 | 1.74 | 1.67 | 1.56 | 1.54 | 1.55 | 1.6 | 24.53 | 25.12 | 26.97 | 0 | - - - | - - - | - - - | - - - | 21257 | 19746 | 18872 | 59875 | Over-range | 11924 | 9948 | 10991 | 32949 | 5262 | 4977 | 5044 | 15495 | 17651 | 17032 | 15362 | 50045 | 17651 | 17032 | 15362 | 50045 | - - - | - - - | - - - | - - -
5/8/2026 | 7:15:00 AM | 283.45 | 281.14 | 279.28 | 490.55 | 483.59 | 487.45 | 76.9012 | 72.1596 | 69.2891 | 0.2403 | 1.425 | 1.425 | 1.419 | 1.968 | 1.964 | 2.096 | Over-range | 60 | 17928 | 17405 | 15633 | 50965 | - - - | - - - | - - - | - - - | 17928 | 17405 | 15633 | 50965 | 11032 | 8894 | 10056 | 29983 | - - - | - - - | - - - | - - - | 11032 | 8894 | 10056 | 29983 | 21681 | 20157 | 19235 | 61072 | # # # | # # # | # # # | # # # | 0.827 | 0.864 | 0.813 | 0.835 | # # # | # # # | # # # | - - - | 0.851 | 0.889 | 0.841 | 0.86 | - - - | 0.588 | 1.73 | 1.69 | 1.59 | 1.54 | 1.56 | 1.61 | 23.48 | 23.93 | 25.67 | 0 | - - - | - - - | - - - | - - - | 21681 | 20157 | 19235 | 61072 | Over-range | 12185 | 10157 | 11196 | 33625 | 5111 | 4846 | 4863 | 15043 | 17970 | 17380 | 15688 | 51038 | 17970 | 17380 | 15688 | 51038 | - - - | - - - | - - - | - - -
5/8/2026 | 7:30:00 AM | 283.6 | 281.29 | 279.64 | 490.69 | 484.12 | 487.95 | 75.8598 | 71.0227 | 67.8221 | 0.2201 | 1.425 | 1.425 | 1.42 | 1.953 | 1.956 | 2.091 | Over-range | 60.02 | 17661 | 17179 | 15296 | 50136 | - - - | - - - | - - - | - - - | 17661 | 17179 | 15296 | 50136 | 10926 | 8658 | 9872 | 29456 | - - - | - - - | - - - | - - - | 10926 | 8658 | 9872 | 29456 | 21371 | 19823 | 18831 | 60024 | # # # | # # # | # # # | # # # | 0.826 | 0.867 | 0.812 | 0.835 | # # # | # # # | # # # | - - - | 0.85 | 0.891 | 0.839 | 0.86 | - - - | 0.588 | 1.77 | 1.73 | 1.6 | 1.57 | 1.59 | 1.64 | 22.97 | 23.56 | 25.4 | 0 | - - - | - - - | - - - | - - - | 21371 | 19823 | 18831 | 60024 | Over-range | 12025 | 9877 | 10972 | 32974 | 4941 | 4679 | 4713 | 14595 | 17705 | 17167 | 15336 | 50208 | 17705 | 17167 | 15336 | 50208 | - - - | - - - | - - - | - - -
5/8/2026 | 7:45:00 AM | 283.39 | 281.11 | 279.42 | 490.32 | 483.81 | 487.56 | 75.1164 | 70.5128 | 68.0145 | 0.2417 | 1.425 | 1.425 | 1.42 | 1.966 | 1.97 | 2.09 | Over-range | 60.01 | 17453 | 16903 | 15277 | 49634 | - - - | - - - | - - - | - - - | 17453 | 16903 | 15277 | 49634 | 10720 | 8761 | 9891 | 29373 | - - - | - - - | - - - | - - - | 10720 | 8761 | 9891 | 29373 | 21129 | 19648 | 18848 | 59624 | # # # | # # # | # # # | # # # | 0.826 | 0.86 | 0.811 | 0.832 | # # # | # # # | # # # | - - - | 0.851 | 0.887 | 0.838 | 0.859 | - - - | 0.592 | 1.74 | 1.72 | 1.6 | 1.56 | 1.58 | 1.63 | 23.47 | 23.98 | 25.67 | 0 | - - - | - - - | - - - | - - - | 21129 | 19648 | 18848 | 59624 | Over-range | 11895 | 9993 | 11022 | 32989 | 5067 | 4725 | 4781 | 14775 | 17463 | 16972 | 15271 | 49705 | 17463 | 16972 | 15271 | 49705 | - - - | - - - | - - - | - - -
5/8/2026 | 8:00:00 AM | 283.11 | 280.73 | 279.18 | 489.78 | 483.19 | 487.16 | 76.5198 | 71.7193 | 69.2197 | 0.2402 | 1.426 | 1.426 | 1.42 | 1.979 | 1.982 | 2.102 | Over-range | 60.02 | 17864 | 17269 | 15624 | 50756 | - - - | - - - | - - - | - - - | 17864 | 17269 | 15624 | 50756 | 10791 | 8773 | 9969 | 29533 | - - - | - - - | - - - | - - - | 10791 | 8773 | 9969 | 29533 | 21548 | 20007 | 19208 | 60762 | # # # | # # # | # # # | # # # | 0.829 | 0.863 | 0.813 | 0.835 | # # # | # # # | # # # | - - - | 0.855 | 0.891 | 0.842 | 0.863 | - - - | 0.582 | 1.76 | 1.71 | 1.63 | 1.57 | 1.6 | 1.65 | 24.13 | 24.68 | 26.35 | 0 | - - - | - - - | - - - | - - - | 21548 | 20007 | 19208 | 60762 | Over-range | 12042 | 10092 | 11163 | 33377 | 5282 | 4930 | 4964 | 15376 | 17857 | 17338 | 15641 | 50835 | 17857 | 17338 | 15641 | 50835 | - - - | - - - | - - - | - - -
5/8/2026 | 8:15:00 AM | 282.58 | 280.19 | 278.54 | 488.88 | 482.16 | 486.14 | 77.9865 | 73.1289 | 70.0275 | 0.233 | 1.427 | 1.427 | 1.421 | 1.989 | 1.997 | 2.111 | Over-range | 60.01 | 18214 | 17660 | 15831 | 51706 | - - - | - - - | - - - | - - - | 18214 | 17660 | 15831 | 51706 | 10828 | 8622 | 9848 | 29299 | - - - | - - - | - - - | - - - | 10828 | 8622 | 9848 | 29299 | 21905 | 20349 | 19378 | 61631 | # # # | # # # | # # # | # # # | 0.832 | 0.868 | 0.817 | 0.839 | # # # | # # # | # # # | - - - | 0.859 | 0.898 | 0.848 | 0.868 | - - - | 0.567 | 1.74 | 1.75 | 1.63 | 1.58 | 1.61 | 1.65 | 24.69 | 25.59 | 27.27 | 0 | - - - | - - - | - - - | - - - | 21905 | 20349 | 19378 | 61631 | Over-range | 12159 | 10094 | 11164 | 33510 | 5465 | 5189 | 5197 | 16080 | 18253 | 17703 | 15835 | 51790 | 18253 | 17703 | 15835 | 51790 | - - - | - - - | - - - | - - -
5/8/2026 | 8:30:00 AM | 282.7 | 280.21 | 278.65 | 488.98 | 482.25 | 486.38 | 77.2079 | 72.1085 | 69.9774 | 0.2453 | 1.428 | 1.428 | 1.421 | 1.988 | 1.997 | 2.096 | Over-range | 60.01 | 18027 | 17295 | 15738 | 51059 | - - - | - - - | - - - | - - - | 18027 | 17295 | 15738 | 51059 | 10777 | 8735 | 10039 | 29551 | - - - | - - - | - - - | - - - | 10777 | 8735 | 10039 | 29551 | 21686 | 20055 | 19364 | 61105 | # # # | # # # | # # # | # # # | 0.831 | 0.862 | 0.813 | 0.836 | # # # | # # # | # # # | - - - | 0.858 | 0.891 | 0.843 | 0.864 | - - - | 0.579 | 1.78 | 1.74 | 1.63 | 1.6 | 1.62 | 1.66 | 24.37 | 25.38 | 26.65 | 0 | - - - | - - - | - - - | - - - | 21686 | 20055 | 19364 | 61105 | Over-range | 12048 | 10143 | 11273 | 33542 | 5320 | 5093 | 5064 | 15680 | 18052 | 17294 | 15801 | 51147 | 18052 | 17294 | 15801 | 51147 | - - - | - - - | - - - | - - -
5/8/2026 | 8:45:00 AM | 282.57 | 280.19 | 278.6 | 488.88 | 482.18 | 486.19 | 79.3479 | 74.6472 | 71.8417 | 0.2442 | 1.427 | 1.428 | 1.421 | 1.997 | 2.004 | 2.104 | Over-range | 60.01 | 18545 | 17962 | 16261 | 52768 | - - - | - - - | - - - | - - - | 18545 | 17962 | 16261 | 52768 | 10966 | 8868 | 10074 | 29908 | - - - | - - - | - - - | - - - | 10966 | 8868 | 10074 | 29908 | 22310 | 20794 | 19906 | 63010 | # # # | # # # | # # # | # # # | 0.831 | 0.864 | 0.817 | 0.838 | # # # | # # # | # # # | - - - | 0.859 | 0.895 | 0.849 | 0.868 | - - - | 0.567 | 1.77 | 1.76 | 1.63 | 1.59 | 1.62 | 1.66 | 24.92 | 25.89 | 27.29 | 0 | - - - | - - - | - - - | - - - | 22310 | 20794 | 19906 | 63010 | Over-range | 12384 | 10450 | 11463 | 34374 | 5660 | 5437 | 5376 | 16674 | 18568 | 17971 | 16320 | 52858 | 18568 | 17971 | 16320 | 52858 | - - - | - - - | - - - | - - -
5/8/2026 | 9:00:00 AM | 282.28 | 279.75 | 278.12 | 488.25 | 481.36 | 485.56 | 79.6652 | 75.0282 | 71.9023 | 0.2455 | 1.428 | 1.428 | 1.421 | 2.019 | 2.031 | 2.127 | Over-range | 60.01 | 18628 | 18072 | 16294 | 52994 | - - - | - - - | - - - | - - - | 18628 | 18072 | 16294 | 52994 | 10822 | 8638 | 9833 | 29293 | - - - | - - - | - - - | - - - | 10822 | 8638 | 9833 | 29293 | 22348 | 20840 | 19865 | 63053 | # # # | # # # | # # # | # # # | 0.834 | 0.867 | 0.82 | 0.841 | # # # | # # # | # # # | - - - | 0.864 | 0.901 | 0.855 | 0.873 | - - - | 0.553 | 1.77 | 1.75 | 1.63 | 1.6 | 1.61 | 1.67 | 26.25 | 27.38 | 28.89 | 0 | - - - | - - - | - - - | - - - | 22348 | 20840 | 19865 | 63053 | Over-range | 12338 | 10364 | 11352 | 34135 | 5860 | 5668 | 5611 | 17342 | 18689 | 18056 | 16353 | 53098 | 18689 | 18056 | 16353 | 53098 | - - - | - - - | - - - | - - -
5/8/2026 | 9:15:00 AM | 281.82 | 279.2 | 277.67 | 487.35 | 480.46 | 484.83 | 79.8062 | 74.8987 | 72.4287 | 0.2489 | 1.429 | 1.429 | 1.421 | 2.034 | 2.043 | 2.131 | Over-range | 60 | 18664 | 17957 | 16359 | 52980 | - - - | - - - | - - - | - - - | 18664 | 17957 | 16359 | 52980 | 10704 | 8639 | 9912 | 29255 | - - - | - - - | - - - | - - - | 10704 | 8639 | 9912 | 29255 | 22345 | 20757 | 19972 | 63073 | # # # | # # # | # # # | # # # | 0.835 | 0.865 | 0.819 | 0.84 | # # # | # # # | # # # | - - - | 0.867 | 0.9 | 0.855 | 0.874 | - - - | 0.552 | 1.76 | 1.76 | 1.63 | 1.59 | 1.62 | 1.67 | 26.73 | 27.9 | 29.2 | 0 | - - - | - - - | - - - | - - - | 22345 | 20757 | 19972 | 63073 | Over-range | 12278 | 10399 | 11446 | 34197 | 5944 | 5723 | 5657 | 17507 | 18698 | 17959 | 16431 | 53087 | 18698 | 17959 | 16431 | 53087 | - - - | - - - | - - - | - - -
5/8/2026 | 9:30:00 AM | 281.94 | 279.25 | 277.79 | 487.48 | 480.57 | 485.07 | 79.5981 | 74.7396 | 71.3469 | 0.2384 | 1.429 | 1.429 | 1.422 | 2.048 | 2.056 | 2.155 | Over-range | 60 | 18578 | 17999 | 16122 | 52699 | - - - | - - - | - - - | - - - | 18578 | 17999 | 16122 | 52699 | 10663 | 8331 | 9623 | 28616 | - - - | - - - | - - - | - - - | 10663 | 8331 | 9623 | 28616 | 22292 | 20713 | 19677 | 62682 | # # # | # # # | # # # | # # # | 0.833 | 0.869 | 0.819 | 0.841 | # # # | # # # | # # # | - - - | 0.866 | 0.906 | 0.858 | 0.877 | - - - | 0.543 | 1.8 | 1.8 | 1.66 | 1.62 | 1.65 | 1.68 | 27.48 | 28.82 | 30.42 | 0 | - - - | - - - | - - - | - - - | 22292 | 20713 | 19677 | 62682 | Over-range | 12312 | 10234 | 11267 | 33902 | 6083 | 5880 | 5796 | 17982 | 18628 | 17986 | 16191 | 52805 | 18628 | 17986 | 16191 | 52805 | - - - | - - - | - - - | - - -
5/8/2026 | 9:45:00 AM | 282.73 | 279.95 | 278.56 | 488.75 | 481.85 | 486.45 | 79.246 | 74.0747 | 71.5033 | 0.2485 | 1.43 | 1.43 | 1.423 | 2.024 | 2.037 | 2.132 | Over-range | 60.01 | 18481 | 17749 | 16067 | 52297 | - - - | - - - | - - - | - - - | 18481 | 17749 | 16067 | 52297 | 10822 | 8628 | 9947 | 29397 | - - - | - - - | - - - | - - - | 10822 | 8628 | 9947 | 29397 | 22240 | 20560 | 19759 | 62559 | # # # | # # # | # # # | # # # | 0.831 | 0.863 | 0.813 | 0.836 | # # # | # # # | # # # | - - - | 0.862 | 0.898 | 0.849 | 0.87 | - - - | 0.562 | 1.78 | 1.8 | 1.66 | 1.62 | 1.66 | 1.69 | 26.46 | 27.78 | 29.31 | 0 | - - - | - - - | - - - | - - - | 22240 | 20560 | 19759 | 62559 | Over-range | 12358 | 10355 | 11485 | 34282 | 5886 | 5652 | 5668 | 17418 | 18566 | 17753 | 16086 | 52406 | 18566 | 17753 | 16086 | 52406 | - - - | - - - | - - - | - - -
5/8/2026 | 10:00:00 AM | 282.56 | 279.83 | 278.38 | 488.52 | 481.62 | 486.1 | 79.256 | 74.1674 | 71.2392 | 0.2527 | 1.429 | 1.429 | 1.423 | 2.023 | 2.036 | 2.133 | Over-range | 60.01 | 18567 | 17892 | 16110 | 52569 | - - - | - - - | - - - | - - - | 18567 | 17892 | 16110 | 52569 | 10748 | 8510 | 9828 | 29086 | - - - | - - - | - - - | - - - | 10748 | 8510 | 9828 | 29086 | 22275 | 20624 | 19716 | 62614 | # # # | # # # | # # # | # # # | 0.834 | 0.868 | 0.817 | 0.84 | # # # | # # # | # # # | - - - | 0.865 | 0.902 | 0.853 | 0.873 | - - - | 0.553 | 1.77 | 1.77 | 1.65 | 1.61 | 1.64 | 1.67 | 26.51 | 27.74 | 29.34 | 0 | - - - | - - - | - - - | - - - | 22275 | 20624 | 19716 | 62614 | Over-range | 12299 | 10246 | 11354 | 33987 | 5923 | 5656 | 5638 | 17434 | 18605 | 17942 | 16129 | 52676 | 18605 | 17942 | 16129 | 52676 | - - - | - - - | - - - | - - -
5/8/2026 | 10:15:00 AM | 282.2 | 279.29 | 277.94 | 487.74 | 480.69 | 485.48 | 78.0035 | 72.5646 | 69.5829 | 0.2495 | 1.43 | 1.43 | 1.423 | 1.993 | 2.005 | 2.114 | Over-range | 60.01 | 18204 | 17494 | 15639 | 51336 | - - - | - - - | - - - | - - - | 18204 | 17494 | 15639 | 51336 | 10753 | 8371 | 9796 | 28920 | - - - | - - - | - - - | - - - | 10753 | 8371 | 9796 | 28920 | 21884 | 20128 | 19216 | 61227 | # # # | # # # | # # # | # # # | 0.832 | 0.869 | 0.814 | 0.839 | # # # | # # # | # # # | - - - | 0.86 | 0.901 | 0.847 | 0.869 | - - - | 0.563 | 1.79 | 1.76 | 1.65 | 1.6 | 1.65 | 1.68 | 25.19 | 26.39 | 28.03 | 0 | - - - | - - - | - - - | - - - | 21884 | 20128 | 19216 | 61227 | Over-range | 12136 | 9941 | 11153 | 33333 | 5562 | 5301 | 5270 | 16394 | 18216 | 17512 | 15705 | 51433 | 18216 | 17512 | 15705 | 51433 | - - - | - - - | - - - | - - -
5/8/2026 | 10:30:00 AM | 282.21 | 279.36 | 277.94 | 487.84 | 480.81 | 485.41 | 78.2774 | 72.8159 | 70.5049 | 0.2508 | 1.43 | 1.43 | 1.424 | 1.986 | 1.997 | 2.094 | Over-range | 60.01 | 18291 | 17475 | 15830 | 51596 | - - - | - - - | - - - | - - - | 18291 | 17475 | 15830 | 51596 | 10756 | 8567 | 9992 | 29315 | - - - | - - - | - - - | - - - | 10756 | 8567 | 9992 | 29315 | 21932 | 20169 | 19446 | 61547 | # # # | # # # | # # # | # # # | 0.834 | 0.866 | 0.814 | 0.838 | # # # | # # # | # # # | - - - | 0.861 | 0.897 | 0.845 | 0.868 | - - - | 0.568 | 1.79 | 1.79 | 1.66 | 1.62 | 1.66 | 1.69 | 24.62 | 25.77 | 27.09 | 0 | - - - | - - - | - - - | - - - | 21932 | 20169 | 19446 | 61547 | Over-range | 12094 | 10059 | 11280 | 33522 | 5453 | 5201 | 5165 | 16049 | 18305 | 17485 | 15903 | 51694 | 18305 | 17485 | 15903 | 51694 | - - - | - - - | - - - | - - -
5/8/2026 | 10:45:00 AM | 281.78 | 278.82 | 277.52 | 486.95 | 479.96 | 484.74 | 79.4401 | 73.8656 | 70.9621 | 0.2512 | 1.43 | 1.431 | 1.424 | 1.964 | 1.974 | 2.08 | Over-range | 60 | 18533 | 17779 | 15939 | 52250 | - - - | - - - | - - - | - - - | 18533 | 17779 | 15939 | 52250 | 10950 | 8570 | 10016 | 29536 | - - - | - - - | - - - | - - - | 10950 | 8570 | 10016 | 29536 | 22220 | 20417 | 19535 | 62172 | # # # | # # # | # # # | # # # | 0.834 | 0.871 | 0.816 | 0.84 | # # # | # # # | # # # | - - - | 0.859 | 0.899 | 0.845 | 0.868 | - - - | 0.565 | 1.79 | 1.81 | 1.68 | 1.64 | 1.68 | 1.71 | 23.75 | 24.78 | 26.34 | 0 | - - - | - - - | - - - | - - - | 22220 | 20417 | 19535 | 62172 | Over-range | 12240 | 10011 | 11274 | 33631 | 5382 | 5097 | 5094 | 15847 | 18558 | 17808 | 15983 | 52348 | 18558 | 17808 | 15983 | 52348 | - - - | - - - | - - - | - - -
5/8/2026 | 11:00:00 AM | 281.74 | 278.83 | 277.54 | 486.92 | 479.97 | 484.74 | 78.1149 | 72.6356 | 70.143 | 0.2484 | 1.431 | 1.431 | 1.425 | 1.979 | 1.994 | 2.095 | Over-range | 60 | 18269 | 17485 | 15783 | 51537 | - - - | - - - | - - - | - - - | 18269 | 17485 | 15783 | 51537 | 10708 | 8500 | 9888 | 29096 | - - - | - - - | - - - | - - - | 10708 | 8500 | 9888 | 29096 | 21897 | 20133 | 19359 | 61389 | # # # | # # # | # # # | # # # | 0.834 | 0.869 | 0.815 | 0.84 | # # # | # # # | # # # | - - - | 0.862 | 0.899 | 0.846 | 0.869 | - - - | 0.565 | 1.8 | 1.81 | 1.7 | 1.63 | 1.68 | 1.71 | 24.61 | 25.63 | 27.25 | 0 | - - - | - - - | - - - | - - - | 21897 | 20133 | 19359 | 61389 | Over-range | 12064 | 9968 | 11200 | 33327 | 5488 | 5146 | 5194 | 16063 | 18290 | 17574 | 15779 | 51643 | 18290 | 17574 | 15779 | 51643 | - - - | - - - | - - - | - - -
5/8/2026 | 11:15:00 AM | 281.66 | 278.72 | 277.42 | 486.77 | 479.76 | 484.56 | 82.3804 | 76.6779 | 74.4018 | 0.2541 | 1.431 | 1.431 | 1.424 | 1.992 | 2.012 | 2.107 | Over-range | 60 | 19376 | 18480 | 16822 | 54678 | - - - | - - - | - - - | - - - | 19376 | 18480 | 16822 | 54678 | 11016 | 8779 | 10227 | 30022 | - - - | - - - | - - - | - - - | 11016 | 8779 | 10227 | 30022 | 23075 | 21232 | 20512 | 64819 | # # # | # # # | # # # | # # # | 0.84 | 0.87 | 0.82 | 0.844 | # # # | # # # | # # # | - - - | 0.869 | 0.902 | 0.853 | 0.875 | - - - | 0.549 | 1.79 | 1.82 | 1.68 | 1.63 | 1.67 | 1.71 | 25.36 | 26.57 | 28.1 | 0 | - - - | - - - | - - - | - - - | 23075 | 21232 | 20512 | 64819 | Over-range | 12520 | 10444 | 11724 | 34781 | 5891 | 5606 | 5679 | 17402 | 19470 | 18506 | 16812 | 54789 | 19470 | 18506 | 16812 | 54789 | - - - | - - - | - - - | - - -
5/8/2026 | 11:30:00 AM | 281.49 | 278.63 | 277.29 | 486.52 | 479.64 | 484.27 | 80.8041 | 75.3878 | 72.1734 | 0.251 | 1.431 | 1.431 | 1.425 | 2.006 | 2.023 | 2.121 | Over-range | 60 | 18911 | 18189 | 16297 | 53397 | - - - | - - - | - - - | - - - | 18911 | 18189 | 16297 | 53397 | 10849 | 8430 | 9841 | 29120 | - - - | - - - | - - - | - - - | 10849 | 8430 | 9841 | 29120 | 22605 | 20851 | 19885 | 63341 | # # # | # # # | # # # | # # # | 0.837 | 0.872 | 0.82 | 0.843 | # # # | # # # | # # # | - - - | 0.867 | 0.906 | 0.855 | 0.876 | - - - | 0.545 | 1.79 | 1.83 | 1.68 | 1.64 | 1.68 | 1.71 | 25.97 | 27.44 | 29.06 | 0 | - - - | - - - | - - - | - - - | 22605 | 20851 | 19885 | 63341 | Over-range | 12373 | 10182 | 11382 | 34041 | 5878 | 5652 | 5663 | 17451 | 19015 | 18198 | 16302 | 53515 | 19015 | 18198 | 16302 | 53515 | - - - | - - - | - - - | - - -
5/8/2026 | 11:45:00 AM | 281.35 | 278.43 | 277.19 | 486.2 | 479.34 | 484.13 | 79.4891 | 74.0693 | 71.6808 | 0.2493 | 1.431 | 1.431 | 1.425 | 1.998 | 2.012 | 2.111 | Over-range | 60 | 18524 | 17716 | 16075 | 52315 | - - - | - - - | - - - | - - - | 18524 | 17716 | 16075 | 52315 | 10722 | 8510 | 9924 | 29156 | - - - | - - - | - - - | - - - | 10722 | 8510 | 9924 | 29156 | 22193 | 20442 | 19707 | 62342 | # # # | # # # | # # # | # # # | 0.835 | 0.867 | 0.816 | 0.839 | # # # | # # # | # # # | - - - | 0.864 | 0.899 | 0.85 | 0.871 | - - - | 0.557 | 1.79 | 1.82 | 1.7 | 1.63 | 1.68 | 1.72 | 25.73 | 26.93 | 28.4 | 0 | - - - | - - - | - - - | - - - | 22193 | 20442 | 19707 | 62342 | Over-range | 12207 | 10177 | 11383 | 33855 | 5748 | 5500 | 5494 | 16965 | 18567 | 17718 | 16144 | 52429 | 18567 | 17718 | 16144 | 52429 | - - - | - - - | - - - | - - -
5/8/2026 | 12:00:00 PM | 281.01 | 278.06 | 276.89 | 485.51 | 478.78 | 483.61 | 79.2195 | 73.7441 | 71.4298 | 0.248 | 1.431 | 1.431 | 1.425 | 1.985 | 2.001 | 2.098 | Over-range | 60 | 18569 | 17742 | 16121 | 52432 | - - - | - - - | - - - | - - - | 18569 | 17742 | 16121 | 52432 | 10596 | 8402 | 9844 | 28843 | - - - | - - - | - - - | - - - | 10596 | 8402 | 9844 | 28843 | 22142 | 20379 | 19664 | 62185 | # # # | # # # | # # # | # # # | 0.839 | 0.871 | 0.82 | 0.843 | # # # | # # # | # # # | - - - | 0.867 | 0.903 | 0.853 | 0.875 | - - - | 0.55 | 1.78 | 1.79 | 1.7 | 1.63 | 1.68 | 1.71 | 25.33 | 26.39 | 27.88 | 0 | - - - | - - - | - - - | - - - | 22142 | 20379 | 19664 | 62185 | Over-range | 12052 | 10014 | 11249 | 33405 | 5678 | 5390 | 5386 | 16676 | 18576 | 17772 | 16194 | 52542 | 18576 | 17772 | 16194 | 52542 | - - - | - - - | - - - | - - -
5/8/2026 | 12:15:00 PM | 280.94 | 278.04 | 276.81 | 485.45 | 478.73 | 483.45 | 81.0512 | 75.572 | 72.7406 | 0.2508 | 1.431 | 1.431 | 1.425 | 1.986 | 2.001 | 2.095 | Over-range | 59.99 | 18961 | 18191 | 16410 | 53562 | - - - | - - - | - - - | - - - | 18961 | 18191 | 16410 | 53562 | 10902 | 8543 | 9989 | 29434 | - - - | - - - | - - - | - - - | 10902 | 8543 | 9989 | 29434 | 22620 | 20853 | 19995 | 63468 | # # # | # # # | # # # | # # # | 0.838 | 0.872 | 0.821 | 0.844 | # # # | # # # | # # # | - - - | 0.867 | 0.904 | 0.854 | 0.875 | - - - | 0.55 | 1.79 | 1.79 | 1.71 | 1.63 | 1.68 | 1.71 | 25.08 | 26.39 | 27.82 | 0 | - - - | - - - | - - - | - - - | 22620 | 20853 | 19995 | 63468 | Over-range | 12327 | 10181 | 11413 | 34018 | 5686 | 5477 | 5458 | 16869 | 19031 | 18173 | 16478 | 53682 | 19031 | 18173 | 16478 | 53682 | - - - | - - - | - - - | - - -
5/8/2026 | 12:30:00 PM | 281.08 | 278.12 | 276.91 | 485.67 | 478.82 | 483.67 | 80.7423 | 75.0352 | 73.1223 | 0.2504 | 1.431 | 1.431 | 1.425 | 2.006 | 2.025 | 2.116 | Over-range | 59.98 | 18922 | 17977 | 16449 | 53348 | - - - | - - - | - - - | - - - | 18922 | 17977 | 16449 | 53348 | 10688 | 8533 | 10040 | 29261 | - - - | - - - | - - - | - - - | 10688 | 8533 | 10040 | 29261 | 22547 | 20712 | 20108 | 63367 | # # # | # # # | # # # | # # # | 0.839 | 0.868 | 0.818 | 0.842 | # # # | # # # | # # # | - - - | 0.87 | 0.902 | 0.854 | 0.875 | - - - | 0.549 | 1.8 | 1.8 | 1.7 | 1.63 | 1.68 | 1.71 | 26.26 | 27.58 | 28.88 | 0 | - - - | - - - | - - - | - - - | 22547 | 20712 | 20108 | 63367 | Over-range | 12253 | 10276 | 11555 | 34168 | 5927 | 5666 | 5660 | 17462 | 18950 | 17991 | 16530 | 53471 | 18950 | 17991 | 16530 | 53471 | - - - | - - - | - - - | - - -
5/8/2026 | 12:45:00 PM | 281.2 | 278.35 | 277.06 | 486 | 479.19 | 483.84 | 81.7817 | 76.6664 | 73.9181 | 0.2528 | 1.431 | 1.431 | 1.426 | 1.997 | 2.016 | 2.105 | Over-range | 59.99 | 19146 | 18419 | 16719 | 54284 | - - - | - - - | - - - | - - - | 19146 | 18419 | 16719 | 54284 | 10892 | 8716 | 10043 | 29651 | - - - | - - - | - - - | - - - | 10892 | 8716 | 10043 | 29651 | 22855 | 21187 | 20344 | 64386 | # # # | # # # | # # # | # # # | 0.838 | 0.869 | 0.822 | 0.843 | # # # | # # # | # # # | - - - | 0.868 | 0.903 | 0.856 | 0.876 | - - - | 0.546 | 1.8 | 1.82 | 1.69 | 1.63 | 1.69 | 1.71 | 25.81 | 26.93 | 28.47 | 0 | - - - | - - - | - - - | - - - | 22855 | 21187 | 20344 | 64386 | Over-range | 12462 | 10448 | 11574 | 34568 | 5982 | 5692 | 5687 | 17568 | 19166 | 18492 | 16745 | 54402 | 19166 | 18492 | 16745 | 54402 | - - - | - - - | - - - | - - -
5/8/2026 | 1:00:00 PM | 281.1 | 278.32 | 277.07 | 485.81 | 479.28 | 483.75 | 79.3507 | 74.3151 | 72.0514 | 0.2492 | 1.432 | 1.432 | 1.426 | 2.008 | 2.036 | 2.125 | Over-range | 59.98 | 18607 | 17846 | 16293 | 52746 | - - - | - - - | - - - | - - - | 18607 | 17846 | 16293 | 52746 | 10510 | 8443 | 9740 | 28693 | - - - | - - - | - - - | - - - | 10510 | 8443 | 9740 | 28693 | 22196 | 20566 | 19857 | 62619 | # # # | # # # | # # # | # # # | 0.838 | 0.868 | 0.821 | 0.842 | # # # | # # # | # # # | - - - | 0.871 | 0.903 | 0.857 | 0.877 | - - - | 0.544 | 1.8 | 1.83 | 1.69 | 1.64 | 1.69 | 1.72 | 26.57 | 27.84 | 29.46 | 0 | - - - | - - - | - - - | - - - | 22196 | 20566 | 19857 | 62619 | Over-range | 12092 | 10207 | 11338 | 33715 | 5925 | 5686 | 5753 | 17550 | 18703 | 17864 | 16305 | 52871 | 18703 | 17864 | 16305 | 52871 | - - - | - - - | - - - | - - -
5/8/2026 | 1:15:00 PM | 281.01 | 278.28 | 276.95 | 485.77 | 479.08 | 483.55 | 81.34 | 76.2156 | 73.8357 | 0.2512 | 1.431 | 1.431 | 1.426 | 1.995 | 2.013 | 2.103 | Over-range | 59.97 | 19066 | 18310 | 16707 | 54083 | - - - | - - - | - - - | - - - | 19066 | 18310 | 16707 | 54083 | 10854 | 8765 | 10088 | 29708 | - - - | - - - | - - - | - - - | 10854 | 8765 | 10088 | 29708 | 22737 | 21082 | 20332 | 64151 | # # # | # # # | # # # | # # # | 0.839 | 0.869 | 0.822 | 0.843 | # # # | # # # | # # # | - - - | 0.868 | 0.901 | 0.855 | 0.875 | - - - | 0.549 | 1.8 | 1.79 | 1.7 | 1.63 | 1.67 | 1.71 | 25.68 | 26.73 | 28.16 | 0 | - - - | - - - | - - - | - - - | 22737 | 21082 | 20332 | 64151 | Over-range | 12381 | 10441 | 11577 | 34477 | 5901 | 5620 | 5627 | 17339 | 19090 | 18362 | 16752 | 54204 | 19090 | 18362 | 16752 | 54204 | - - - | - - - | - - - | - - -
5/8/2026 | 1:30:00 PM | 280.71 | 277.89 | 276.53 | 485.2 | 478.33 | 482.94 | 79.1997 | 73.9911 | 70.9128 | 0.2465 | 1.431 | 1.432 | 1.426 | 1.973 | 1.988 | 2.09 | Over-range | 59.98 | 18482 | 17819 | 15988 | 52289 | - - - | - - - | - - - | - - - | 18482 | 17819 | 15988 | 52289 | 10755 | 8438 | 9750 | 28943 | - - - | - - - | - - - | - - - | 10755 | 8438 | 9750 | 28943 | 22102 | 20425 | 19486 | 62014 | # # # | # # # | # # # | # # # | 0.836 | 0.872 | 0.821 | 0.843 | # # # | # # # | # # # | - - - | 0.864 | 0.902 | 0.852 | 0.873 | - - - | 0.554 | 1.79 | 1.81 | 1.68 | 1.62 | 1.67 | 1.7 | 24.62 | 25.71 | 27.4 | 0 | - - - | - - - | - - - | - - - | 22102 | 20425 | 19486 | 62014 | Over-range | 12113 | 9971 | 11130 | 33312 | 5502 | 5248 | 5303 | 16296 | 18585 | 17826 | 15990 | 52400 | 18585 | 17826 | 15990 | 52400 | - - - | - - - | - - - | - - -
5/8/2026 | 1:45:00 PM | 280.45 | 277.56 | 276.22 | 484.65 | 477.8 | 482.47 | 77.8609 | 72.5909 | 70.0871 | 0.2444 | 1.432 | 1.432 | 1.426 | 1.985 | 2.002 | 2.105 | Over-range | 59.98 | 18097 | 17337 | 15688 | 51122 | - - - | - - - | - - - | - - - | 18097 | 17337 | 15688 | 51122 | 10454 | 8270 | 9643 | 28367 | - - - | - - - | - - - | - - - | 10454 | 8270 | 9643 | 28367 | 21659 | 19959 | 19195 | 60813 | # # # | # # # | # # # | # # # | 0.836 | 0.869 | 0.817 | 0.841 | # # # | # # # | # # # | - - - | 0.865 | 0.901 | 0.851 | 0.872 | - - - | 0.555 | 1.77 | 1.79 | 1.7 | 1.62 | 1.67 | 1.71 | 25.46 | 26.51 | 28.08 | 0 | - - - | - - - | - - - | - - - | 21659 | 19959 | 19195 | 60813 | Over-range | 11883 | 9862 | 11042 | 32877 | 5571 | 5305 | 5309 | 16411 | 18137 | 17348 | 15753 | 51238 | 18137 | 17348 | 15753 | 51238 | - - - | - - - | - - - | - - -
5/8/2026 | 2:00:00 PM | 280.29 | 277.42 | 276.05 | 484.47 | 477.47 | 482.16 | 78.3205 | 72.6818 | 70.4924 | 0.2442 | 1.431 | 1.432 | 1.426 | 1.989 | 2 | 2.108 | Over-range | 59.99 | 18319 | 17454 | 15836 | 51608 | - - - | - - - | - - - | - - - | 18319 | 17454 | 15836 | 51608 | 10509 | 8328 | 9775 | 28612 | - - - | - - - | - - - | - - - | 10509 | 8328 | 9775 | 28612 | 21857 | 20058 | 19365 | 61280 | # # # | # # # | # # # | # # # | 0.838 | 0.87 | 0.818 | 0.842 | # # # | # # # | # # # | - - - | 0.867 | 0.902 | 0.851 | 0.873 | - - - | 0.554 | 1.78 | 1.79 | 1.68 | 1.62 | 1.67 | 1.7 | 25.2 | 26.25 | 27.75 | 0 | - - - | - - - | - - - | - - - | 21857 | 20058 | 19365 | 61280 | Over-range | 11917 | 9876 | 11138 | 33022 | 5571 | 5263 | 5294 | 16352 | 18362 | 17485 | 15874 | 51720 | 18362 | 17485 | 15874 | 51720 | - - - | - - - | - - - | - - -
5/8/2026 | 2:15:00 PM | 280.42 | 277.63 | 276.3 | 484.72 | 477.92 | 482.48 | 78.6061 | 72.9802 | 70.4239 | 0.2438 | 1.431 | 1.432 | 1.427 | 1.972 | 1.983 | 2.104 | Over-range | 59.97 | 18303 | 17508 | 15779 | 51590 | - - - | - - - | - - - | - - - | 18303 | 17508 | 15779 | 51590 | 10630 | 8373 | 9779 | 28782 | - - - | - - - | - - - | - - - | 10630 | 8373 | 9779 | 28782 | 21877 | 20089 | 19305 | 61272 | # # # | # # # | # # # | # # # | 0.837 | 0.872 | 0.817 | 0.842 | # # # | # # # | # # # | - - - | 0.865 | 0.901 | 0.848 | 0.871 | - - - | 0.558 | 1.77 | 1.8 | 1.69 | 1.63 | 1.67 | 1.71 | 24.52 | 25.39 | 27.16 | 0 | - - - | - - - | - - - | - - - | 21877 | 20089 | 19305 | 61272 | Over-range | 11974 | 9832 | 11109 | 33016 | 5435 | 5085 | 5202 | 15968 | 18384 | 17557 | 15754 | 51695 | 18384 | 17557 | 15754 | 51695 | - - - | - - - | - - - | - - -
5/8/2026 | 2:30:00 PM | 280.32 | 277.58 | 276.23 | 484.55 | 477.86 | 482.31 | 79.6862 | 74.1304 | 72.0897 | 0.2469 | 1.432 | 1.432 | 1.427 | 1.977 | 1.991 | 2.096 | Over-range | 59.98 | 18601 | 17744 | 16180 | 52525 | - - - | - - - | - - - | - - - | 18601 | 17744 | 16180 | 52525 | 10744 | 8627 | 10017 | 29388 | - - - | - - - | - - - | - - - | 10744 | 8627 | 10017 | 29388 | 22201 | 20431 | 19783 | 62415 | # # # | # # # | # # # | # # # | 0.838 | 0.869 | 0.818 | 0.842 | # # # | # # # | # # # | - - - | 0.866 | 0.899 | 0.849 | 0.871 | - - - | 0.56 | 1.79 | 1.79 | 1.72 | 1.64 | 1.68 | 1.73 | 24.69 | 25.68 | 27.16 | 0 | - - - | - - - | - - - | - - - | 22201 | 20431 | 19783 | 62415 | Over-range | 12112 | 10118 | 11373 | 33690 | 5528 | 5228 | 5328 | 16295 | 18703 | 17765 | 16176 | 52643 | 18703 | 17765 | 16176 | 52643 | - - - | - - - | - - - | - - -
5/8/2026 | 2:45:00 PM | 280 | 277.16 | 275.83 | 483.95 | 477.09 | 481.74 | 81.0319 | 75.7856 | 73.1634 | 0.2479 | 1.431 | 1.432 | 1.427 | 2 | 2.022 | 2.126 | Over-range | 59.97 | 18896 | 18146 | 16462 | 53504 | - - - | - - - | - - - | - - - | 18896 | 18146 | 16462 | 53504 | 10739 | 8578 | 9899 | 29216 | - - - | - - - | - - - | - - - | 10739 | 8578 | 9899 | 29216 | 22559 | 20864 | 20056 | 63479 | # # # | # # # | # # # | # # # | 0.838 | 0.87 | 0.821 | 0.843 | # # # | # # # | # # # | - - - | 0.869 | 0.903 | 0.855 | 0.876 | - - - | 0.546 | 1.8 | 1.81 | 1.68 | 1.63 | 1.68 | 1.71 | 25.99 | 26.97 | 28.78 | 0 | - - - | - - - | - - - | - - - | 22559 | 20864 | 20056 | 63479 | Over-range | 12306 | 10276 | 11440 | 34108 | 5941 | 5592 | 5671 | 17409 | 18949 | 18234 | 16444 | 53627 | 18949 | 18234 | 16444 | 53627 | - - - | - - - | - - - | - - -
5/8/2026 | 3:00:00 PM | 280.1 | 277.34 | 275.99 | 484.18 | 477.38 | 481.96 | 79.4587 | 74.1414 | 71.2198 | 0.2436 | 1.431 | 1.433 | 1.427 | 1.998 | 2.013 | 2.127 | Over-range | 59.98 | 18517 | 17803 | 16019 | 52340 | - - - | - - - | - - - | - - - | 18517 | 17803 | 16019 | 52340 | 10541 | 8291 | 9647 | 28479 | - - - | - - - | - - - | - - - | 10541 | 8291 | 9647 | 28479 | 22103 | 20402 | 19514 | 62019 | # # # | # # # | # # # | # # # | 0.838 | 0.873 | 0.821 | 0.844 | # # # | # # # | # # # | - - - | 0.868 | 0.906 | 0.855 | 0.876 | - - - | 0.544 | 1.82 | 1.83 | 1.7 | 1.65 | 1.7 | 1.73 | 25.86 | 26.82 | 28.69 | 0 | - - - | - - - | - - - | - - - | 22103 | 20402 | 19514 | 62019 | Over-range | 12061 | 9949 | 11132 | 33238 | 5792 | 5437 | 5492 | 16948 | 18555 | 17898 | 16010 | 52462 | 18555 | 17898 | 16010 | 52462 | - - - | - - - | - - - | - - -
5/8/2026 | 3:15:00 PM | 280.34 | 277.67 | 276.25 | 484.65 | 477.97 | 482.34 | 77.9477 | 72.6178 | 70.4052 | 0.2432 | 1.432 | 1.433 | 1.428 | 1.989 | 1.998 | 2.116 | Over-range | 59.99 | 18154 | 17377 | 15783 | 51314 | - - - | - - - | - - - | - - - | 18154 | 17377 | 15783 | 51314 | 10528 | 8446 | 9774 | 28747 | - - - | - - - | - - - | - - - | 10528 | 8446 | 9774 | 28747 | 21734 | 20035 | 19332 | 61101 | # # # | # # # | # # # | # # # | 0.835 | 0.867 | 0.816 | 0.84 | # # # | # # # | # # # | - - - | 0.865 | 0.899 | 0.849 | 0.871 | - - - | 0.56 | 1.83 | 1.82 | 1.72 | 1.66 | 1.7 | 1.75 | 25.26 | 26.13 | 27.77 | 0 | - - - | - - - | - - - | - - - | 21734 | 20035 | 19332 | 61101 | Over-range | 11942 | 9960 | 11153 | 33141 | 5575 | 5223 | 5315 | 16318 | 18218 | 17437 | 15770 | 51425 | 18218 | 17437 | 15770 | 51425 | - - - | - - - | - - - | - - -
5/8/2026 | 3:30:00 PM | 280.16 | 277.35 | 275.94 | 484.22 | 477.39 | 481.95 | 79.0229 | 73.7739 | 71.2718 | 0.2445 | 1.432 | 1.433 | 1.427 | 1.978 | 1.991 | 2.106 | Over-range | 59.99 | 18439 | 17702 | 16039 | 52180 | - - - | - - - | - - - | - - - | 18439 | 17702 | 16039 | 52180 | 10674 | 8510 | 9809 | 28992 | - - - | - - - | - - - | - - - | 10674 | 8510 | 9809 | 28992 | 22015 | 20329 | 19546 | 61890 | # # # | # # # | # # # | # # # | 0.838 | 0.871 | 0.821 | 0.843 | # # # | # # # | # # # | - - - | 0.866 | 0.9 | 0.852 | 0.873 | - - - | 0.556 | 1.82 | 1.81 | 1.73 | 1.66 | 1.7 | 1.75 | 24.65 | 25.52 | 27.24 | 0 | - - - | - - - | - - - | - - - | 22015 | 20329 | 19546 | 61890 | Over-range | 12022 | 9986 | 11163 | 33259 | 5475 | 5172 | 5275 | 16137 | 18546 | 17713 | 16034 | 52293 | 18546 | 17713 | 16034 | 52293 | - - - | - - - | - - - | - - -
5/8/2026 | 3:45:00 PM | 280.28 | 277.54 | 276.07 | 484.52 | 477.65 | 482.14 | 81.2333 | 75.9839 | 72.9587 | 0.2476 | 1.432 | 1.433 | 1.428 | 1.977 | 1.991 | 2.098 | Over-range | 59.98 | 18896 | 18220 | 16393 | 53510 | - - - | - - - | - - - | - - - | 18896 | 18220 | 16393 | 53510 | 11015 | 8728 | 10031 | 29773 | - - - | - - - | - - - | - - - | 11015 | 8728 | 10031 | 29773 | 22629 | 20935 | 20005 | 63569 | # # # | # # # | # # # | # # # | 0.835 | 0.87 | 0.82 | 0.842 | # # # | # # # | # # # | - - - | 0.863 | 0.9 | 0.851 | 0.872 | - - - | 0.556 | 1.81 | 1.81 | 1.75 | 1.67 | 1.71 | 1.75 | 24.72 | 25.62 | 27.33 | 0 | - - - | - - - | - - - | - - - | 22629 | 20935 | 20005 | 63569 | Over-range | 12435 | 10290 | 11450 | 34269 | 5691 | 5376 | 5451 | 16756 | 18995 | 18269 | 16371 | 53635 | 18995 | 18269 | 16371 | 53635 | - - - | - - - | - - - | - - -
5/8/2026 | 4:00:00 PM | 280.42 | 277.74 | 276.3 | 484.82 | 478.04 | 482.44 | 78.4326 | 73.1944 | 71.1919 | 0.2433 | 1.432 | 1.432 | 1.427 | 2.017 | 2.04 | 2.142 | Over-range | 59.99 | 18306 | 17488 | 15985 | 51779 | - - - | - - - | - - - | - - - | 18306 | 17488 | 15985 | 51779 | 10369 | 8368 | 9674 | 28411 | - - - | - - - | - - - | - - - | 10369 | 8368 | 9674 | 28411 | 21863 | 20191 | 19546 | 61601 | # # # | # # # | # # # | # # # | 0.837 | 0.866 | 0.818 | 0.841 | # # # | # # # | # # # | - - - | 0.87 | 0.901 | 0.854 | 0.875 | - - - | 0.549 | 1.81 | 1.82 | 1.73 | 1.66 | 1.69 | 1.74 | 26.73 | 27.85 | 29.47 | 0 | - - - | - - - | - - - | - - - | 21863 | 20191 | 19546 | 61601 | Over-range | 11946 | 10080 | 11238 | 33341 | 5868 | 5562 | 5660 | 17270 | 18399 | 17535 | 15963 | 51897 | 18399 | 17535 | 15963 | 51897 | - - - | - - - | - - - | - - -
5/8/2026 | 4:15:00 PM | 280.56 | 277.99 | 276.46 | 485.12 | 478.5 | 482.65 | 80.0466 | 75.101 | 72.6432 | 0.2474 | 1.432 | 1.433 | 1.428 | 1.987 | 2.002 | 2.107 | Over-range | 59.99 | 18669 | 17980 | 16370 | 53020 | - - - | - - - | - - - | - - - | 18669 | 17980 | 16370 | 53020 | 10798 | 8755 | 9974 | 29527 | - - - | - - - | - - - | - - - | 10798 | 8755 | 9974 | 29527 | 22307 | 20716 | 19938 | 62961 | # # # | # # # | # # # | # # # | 0.837 | 0.868 | 0.821 | 0.842 | # # # | # # # | # # # | - - - | 0.866 | 0.898 | 0.853 | 0.872 | - - - | 0.557 | 1.83 | 1.82 | 1.75 | 1.67 | 1.71 | 1.76 | 25.02 | 25.93 | 27.46 | 0 | - - - | - - - | - - - | - - - | 22307 | 20716 | 19938 | 62961 | Over-range | 12202 | 10279 | 11372 | 33931 | 5621 | 5330 | 5407 | 16547 | 18770 | 18017 | 16349 | 53136 | 18770 | 18017 | 16349 | 53136 | - - - | - - - | - - - | - - -
5/8/2026 | 4:30:00 PM | 280.52 | 278.04 | 276.5 | 485.15 | 478.58 | 482.62 | 77.7901 | 72.7518 | 70.0683 | 0.2415 | 1.433 | 1.433 | 1.428 | 1.96 | 1.97 | 2.088 | Over-range | 59.98 | 18132 | 17490 | 15783 | 51405 | - - - | - - - | - - - | - - - | 18132 | 17490 | 15783 | 51405 | 10668 | 8544 | 9788 | 29000 | - - - | - - - | - - - | - - - | 10668 | 8544 | 9788 | 29000 | 21710 | 20109 | 19264 | 61084 | # # # | # # # | # # # | # # # | 0.835 | 0.87 | 0.819 | 0.842 | # # # | # # # | # # # | - - - | 0.862 | 0.898 | 0.848 | 0.869 | - - - | 0.564 | 1.85 | 1.81 | 1.73 | 1.67 | 1.69 | 1.76 | 23.87 | 24.64 | 26.25 | 0 | - - - | - - - | - - - | - - - | 21710 | 20109 | 19264 | 61084 | Over-range | 11933 | 9914 | 11038 | 32973 | 5292 | 4978 | 5051 | 15538 | 18211 | 17542 | 15766 | 51519 | 18211 | 17542 | 15766 | 51519 | - - - | - - - | - - - | - - -
5/8/2026 | 4:45:00 PM | 280.39 | 277.88 | 276.41 | 484.88 | 478.36 | 482.44 | 78.8491 | 73.8701 | 71.6449 | 0.2449 | 1.433 | 1.433 | 1.428 | 1.969 | 1.985 | 2.09 | Over-range | 59.98 | 18321 | 17607 | 16061 | 51989 | - - - | - - - | - - - | - - - | 18321 | 17607 | 16061 | 51989 | 10712 | 8715 | 9943 | 29370 | - - - | - - - | - - - | - - - | 10712 | 8715 | 9943 | 29370 | 21943 | 20345 | 19640 | 61928 | # # # | # # # | # # # | # # # | 0.835 | 0.865 | 0.818 | 0.84 | # # # | # # # | # # # | - - - | 0.862 | 0.894 | 0.848 | 0.868 | - - - | 0.565 | 1.84 | 1.8 | 1.73 | 1.67 | 1.69 | 1.75 | 24.37 | 25.25 | 26.75 | 0 | - - - | - - - | - - - | - - - | 21943 | 20345 | 19640 | 61928 | Over-range | 12061 | 10173 | 11287 | 33597 | 5454 | 5163 | 5255 | 16065 | 18418 | 17638 | 16047 | 52103 | 18418 | 17638 | 16047 | 52103 | - - - | - - - | - - - | - - -
5/8/2026 | 5:00:00 PM | 280.41 | 277.96 | 276.33 | 484.99 | 478.41 | 482.32 | 81.1085 | 76.7412 | 73.7349 | 0.2484 | 1.432 | 1.432 | 1.427 | 2.003 | 2.022 | 2.116 | Over-range | 60 | 18967 | 18439 | 16742 | 54149 | - - - | - - - | - - - | - - - | 18967 | 18439 | 16742 | 54149 | 10798 | 8785 | 9874 | 29456 | - - - | - - - | - - - | - - - | 10798 | 8785 | 9874 | 29456 | 22638 | 21217 | 20271 | 64126 | # # # | # # # | # # # | # # # | 0.838 | 0.869 | 0.826 | 0.844 | # # # | # # # | # # # | - - - | 0.869 | 0.903 | 0.86 | 0.877 | - - - | 0.544 | 1.78 | 1.78 | 1.71 | 1.63 | 1.66 | 1.72 | 26.03 | 26.94 | 28.53 | 0 | - - - | - - - | - - - | - - - | 22638 | 21217 | 20271 | 64126 | Over-range | 12352 | 10486 | 11418 | 34327 | 5947 | 5678 | 5690 | 17486 | 19035 | 18513 | 16727 | 54275 | 19035 | 18513 | 16727 | 54275 | - - - | - - - | - - - | - - -
5/8/2026 | 5:15:00 PM | 281 | 278.58 | 277.02 | 486.06 | 479.59 | 483.39 | 79.2943 | 75.0265 | 72.0973 | 0.2445 | 1.432 | 1.432 | 1.427 | 2.022 | 2.033 | 2.123 | Over-range | 59.99 | 18515 | 17980 | 16336 | 52830 | - - - | - - - | - - - | - - - | 18515 | 17980 | 16336 | 52830 | 10518 | 8565 | 9672 | 28756 | - - - | - - - | - - - | - - - | 10518 | 8565 | 9672 | 28756 | 22137 | 20744 | 19838 | 62718 | # # # | # # # | # # # | # # # | 0.836 | 0.867 | 0.824 | 0.842 | # # # | # # # | # # # | - - - | 0.868 | 0.902 | 0.859 | 0.876 | - - - | 0.544 | 1.77 | 1.79 | 1.68 | 1.63 | 1.65 | 1.7 | 26.72 | 27.75 | 29.2 | 0 | - - - | - - - | - - - | - - - | 22137 | 20744 | 19838 | 62718 | Over-range | 12126 | 10330 | 11242 | 33767 | 5968 | 5715 | 5672 | 17522 | 18536 | 18075 | 16347 | 52958 | 18536 | 18075 | 16347 | 52958 | - - - | - - - | - - - | - - -
5/8/2026 | 5:30:00 PM | 281.1 | 278.72 | 277.07 | 486.32 | 479.75 | 483.45 | 78.8681 | 74.4903 | 71.8431 | 0.2442 | 1.432 | 1.432 | 1.428 | 2.02 | 2.028 | 2.114 | Over-range | 59.98 | 18429 | 17842 | 16253 | 52525 | - - - | - - - | - - - | - - - | 18429 | 17842 | 16253 | 52525 | 10550 | 8649 | 9760 | 28959 | - - - | - - - | - - - | - - - | 10550 | 8649 | 9760 | 28959 | 22050 | 20631 | 19788 | 62469 | # # # | # # # | # # # | # # # | 0.836 | 0.865 | 0.821 | 0.841 | # # # | # # # | # # # | - - - | 0.867 | 0.9 | 0.856 | 0.875 | - - - | 0.551 | 1.79 | 1.76 | 1.72 | 1.65 | 1.67 | 1.72 | 26.48 | 27.61 | 28.84 | 0 | - - - | - - - | - - - | - - - | 22050 | 20631 | 19788 | 62469 | Over-range | 12101 | 10348 | 11278 | 33792 | 5880 | 5636 | 5607 | 17281 | 18472 | 17936 | 16248 | 52655 | 18472 | 17936 | 16248 | 52655 | - - - | - - - | - - - | - - -
5/8/2026 | 5:45:00 PM | 281.15 | 278.83 | 277.2 | 486.37 | 480.03 | 483.63 | 81.648 | 77.19 | 74.2663 | 0.2496 | 1.432 | 1.432 | 1.428 | 1.991 | 2.001 | 2.084 | Over-range | 59.99 | 19094 | 18531 | 16842 | 54467 | - - - | - - - | - - - | - - - | 19094 | 18531 | 16842 | 54467 | 10991 | 8968 | 10104 | 30063 | - - - | - - - | - - - | - - - | 10991 | 8968 | 10104 | 30063 | 22806 | 21362 | 20442 | 64610 | # # # | # # # | # # # | # # # | 0.837 | 0.868 | 0.824 | 0.843 | # # # | # # # | # # # | - - - | 0.866 | 0.899 | 0.856 | 0.874 | - - - | 0.552 | 1.76 | 1.77 | 1.65 | 1.63 | 1.64 | 1.68 | 25.06 | 26.26 | 27.45 | 0 | - - - | - - - | - - - | - - - | 22806 | 21362 | 20442 | 64610 | Over-range | 12457 | 10606 | 11569 | 34704 | 5780 | 5590 | 5565 | 17121 | 19175 | 18582 | 16832 | 54589 | 19175 | 18582 | 16832 | 54589 | - - - | - - - | - - - | - - -
5/8/2026 | 6:00:00 PM | 281.43 | 279.18 | 277.56 | 486.9 | 480.64 | 484.18 | 78.8159 | 73.9172 | 71.7968 | 0.2445 | 1.432 | 1.431 | 1.427 | 1.965 | 1.975 | 2.067 | Over-range | 59.99 | 18402 | 17697 | 16168 | 52267 | - - - | - - - | - - - | - - - | 18402 | 17697 | 16168 | 52267 | 10893 | 8919 | 10197 | 30008 | - - - | - - - | - - - | - - - | 10893 | 8919 | 10197 | 30008 | 22053 | 20498 | 19803 | 62355 | # # # | # # # | # # # | # # # | 0.834 | 0.863 | 0.816 | 0.838 | # # # | # # # | # # # | - - - | 0.86 | 0.892 | 0.846 | 0.866 | - - - | 0.574 | 1.74 | 1.73 | 1.63 | 1.6 | 1.61 | 1.65 | 23.67 | 24.79 | 25.77 | 0 | - - - | - - - | - - - | - - - | 22053 | 20498 | 19803 | 62355 | Over-range | 12144 | 10328 | 11423 | 33968 | 5299 | 5142 | 5081 | 15718 | 18439 | 17691 | 16244 | 52374 | 18439 | 17691 | 16244 | 52374 | - - - | - - - | - - - | - - -
5/8/2026 | 6:15:00 PM | 281.38 | 279.18 | 277.53 | 486.84 | 480.65 | 484.1 | 79.0874 | 74.4648 | 72.0465 | 0.2456 | 1.43 | 1.429 | 1.425 | 1.974 | 1.966 | 2.068 | Over-range | 59.99 | 18475 | 17866 | 16290 | 52632 | - - - | - - - | - - - | - - - | 18475 | 17866 | 16290 | 52632 | 10921 | 8995 | 10183 | 30099 | - - - | - - - | - - - | - - - | 10921 | 8995 | 10183 | 30099 | 22127 | 20649 | 19868 | 62644 | # # # | # # # | # # # | # # # | 0.835 | 0.865 | 0.82 | 0.84 | # # # | # # # | # # # | - - - | 0.86 | 0.892 | 0.847 | 0.867 | - - - | 0.572 | 1.65 | 1.6 | 1.5 | 1.51 | 1.5 | 1.53 | 23.58 | 24.35 | 25.37 | 0 | - - - | - - - | - - - | - - - | 22127 | 20649 | 19868 | 62644 | Over-range | 12170 | 10342 | 11363 | 33946 | 5303 | 5043 | 4979 | 15510 | 18464 | 17926 | 16337 | 52727 | 18464 | 17926 | 16337 | 52727 | - - - | - - - | - - - | - - -
5/8/2026 | 6:30:00 PM | 281.2 | 278.86 | 277.28 | 486.4 | 480.15 | 483.75 | 79.1088 | 74.1384 | 71.3044 | 0.2453 | 1.43 | 1.429 | 1.425 | 1.964 | 1.957 | 2.066 | Over-range | 59.97 | 18460 | 17845 | 16088 | 52393 | - - - | - - - | - - - | - - - | 18460 | 17845 | 16088 | 52393 | 10970 | 8841 | 10093 | 29904 | - - - | - - - | - - - | - - - | 10970 | 8841 | 10093 | 29904 | 22120 | 20537 | 19648 | 62305 | # # # | # # # | # # # | # # # | 0.835 | 0.869 | 0.819 | 0.841 | # # # | # # # | # # # | - - - | 0.859 | 0.895 | 0.845 | 0.867 | - - - | 0.571 | 1.63 | 1.57 | 1.52 | 1.5 | 1.5 | 1.52 | 23.16 | 24.01 | 25.2 | 0 | - - - | - - - | - - - | - - - | 22120 | 20537 | 19648 | 62305 | Over-range | 12179 | 10153 | 11269 | 33689 | 5222 | 4925 | 4949 | 15323 | 18503 | 17915 | 16063 | 52482 | 18503 | 17915 | 16063 | 52482 | - - - | - - - | - - - | - - -
5/8/2026 | 6:45:00 PM | 281.25 | 278.98 | 277.3 | 486.58 | 480.31 | 483.75 | 77.2804 | 72.6279 | 70.2981 | 0.244 | 1.43 | 1.429 | 1.425 | 1.961 | 1.946 | 2.054 | Over-range | 59.97 | 17933 | 17314 | 15763 | 51010 | - - - | - - - | - - - | - - - | 17933 | 17314 | 15763 | 51010 | 10766 | 8869 | 10050 | 29685 | - - - | - - - | - - - | - - - | 10766 | 8869 | 10050 | 29685 | 21562 | 20074 | 19326 | 60962 | # # # | # # # | # # # | # # # | 0.832 | 0.863 | 0.816 | 0.837 | # # # | # # # | # # # | - - - | 0.855 | 0.889 | 0.842 | 0.862 | - - - | 0.582 | 1.65 | 1.58 | 1.49 | 1.5 | 1.5 | 1.52 | 23.05 | 23.78 | 24.73 | 0 | - - - | - - - | - - - | - - - | 21562 | 20074 | 19326 | 60962 | Over-range | 11954 | 10134 | 11162 | 33322 | 5088 | 4801 | 4754 | 14837 | 17927 | 17382 | 15798 | 51106 | 17927 | 17382 | 15798 | 51106 | - - - | - - - | - - - | - - -
5/8/2026 | 7:00:00 PM | 281.47 | 279.1 | 277.52 | 486.86 | 480.54 | 484.21 | 75.8003 | 70.7645 | 68.5364 | 0.2396 | 1.431 | 1.429 | 1.425 | 1.954 | 1.93 | 2.051 | Over-range | 59.98 | 17634 | 16960 | 15373 | 49967 | - - - | - - - | - - - | - - - | 17634 | 16960 | 15373 | 49967 | 10741 | 8746 | 9969 | 29456 | - - - | - - - | - - - | - - - | 10741 | 8746 | 9969 | 29456 | 21213 | 19616 | 18897 | 59726 | # # # | # # # | # # # | # # # | 0.831 | 0.865 | 0.814 | 0.837 | # # # | # # # | # # # | - - - | 0.854 | 0.888 | 0.837 | 0.86 | - - - | 0.59 | 1.62 | 1.54 | 1.46 | 1.47 | 1.47 | 1.48 | 22.18 | 22.76 | 23.87 | 0 | - - - | - - - | - - - | - - - | 21213 | 19616 | 18897 | 59726 | Over-range | 11784 | 9846 | 10980 | 32692 | 4783 | 4464 | 4542 | 14006 | 17702 | 16995 | 15344 | 50041 | 17702 | 16995 | 15344 | 50041 | - - - | - - - | - - - | - - -
5/8/2026 | 7:15:00 PM | 281.19 | 278.77 | 277.14 | 486.39 | 479.85 | 483.67 | 75.3944 | 70.1938 | 67.4805 | 0.2353 | 1.43 | 1.429 | 1.425 | 1.962 | 1.935 | 2.065 | Over-range | 59.99 | 17492 | 16851 | 15091 | 49434 | - - - | - - - | - - - | - - - | 17492 | 16851 | 15091 | 49434 | 10695 | 8497 | 9799 | 28990 | - - - | - - - | - - - | - - - | 10695 | 8497 | 9799 | 28990 | 21072 | 19426 | 18573 | 59071 | # # # | # # # | # # # | # # # | 0.83 | 0.867 | 0.813 | 0.837 | # # # | # # # | # # # | - - - | 0.853 | 0.891 | 0.838 | 0.861 | - - - | 0.586 | 1.6 | 1.54 | 1.45 | 1.46 | 1.46 | 1.46 | 22.4 | 23.16 | 24.25 | 0 | - - - | - - - | - - - | - - - | 21072 | 19426 | 18573 | 59071 | Over-range | 11741 | 9654 | 10814 | 32306 | 4774 | 4517 | 4507 | 14057 | 17548 | 16847 | 15115 | 49510 | 17548 | 16847 | 15115 | 49510 | - - - | - - - | - - - | - - -
5/8/2026 | 7:30:00 PM | 281.26 | 278.92 | 277.2 | 486.56 | 480.08 | 483.73 | 74.6755 | 69.4382 | 67.4692 | 0.2358 | 1.43 | 1.429 | 1.424 | 1.951 | 1.915 | 2.041 | Over-range | 59.99 | 17354 | 16612 | 15071 | 49037 | - - - | - - - | - - - | - - - | 17354 | 16612 | 15071 | 49037 | 10652 | 8633 | 9952 | 29236 | - - - | - - - | - - - | - - - | 10652 | 8633 | 9952 | 29236 | 20891 | 19243 | 18590 | 58723 | # # # | # # # | # # # | # # # | 0.831 | 0.863 | 0.811 | 0.835 | # # # | # # # | # # # | - - - | 0.852 | 0.886 | 0.834 | 0.857 | - - - | 0.596 | 1.58 | 1.54 | 1.46 | 1.46 | 1.46 | 1.46 | 21.61 | 22.23 | 22.98 | 0 | - - - | - - - | - - - | - - - | 20891 | 19243 | 18590 | 58723 | Over-range | 11623 | 9701 | 10873 | 32281 | 4580 | 4360 | 4307 | 13482 | 17392 | 16583 | 15130 | 49104 | 17392 | 16583 | 15130 | 49104 | - - - | - - - | - - - | - - -
5/8/2026 | 7:45:00 PM | 281.39 | 278.98 | 277.34 | 486.75 | 480.2 | 484 | 77.6094 | 72.3618 | 70.0913 | 0.2416 | 1.43 | 1.429 | 1.424 | 1.942 | 1.907 | 2.037 | Over-range | 59.98 | 17996 | 17286 | 15652 | 50934 | - - - | - - - | - - - | - - - | 17996 | 17286 | 15652 | 50934 | 11071 | 9025 | 10312 | 30408 | - - - | - - - | - - - | - - - | 11071 | 9025 | 10312 | 30408 | 21683 | 20015 | 19281 | 60980 | # # # | # # # | # # # | # # # | 0.83 | 0.864 | 0.812 | 0.835 | # # # | # # # | # # # | - - - | 0.85 | 0.885 | 0.833 | 0.857 | - - - | 0.597 | 1.59 | 1.55 | 1.45 | 1.45 | 1.47 | 1.46 | 21.32 | 21.71 | 22.7 | 0 | - - - | - - - | - - - | - - - | 21683 | 20015 | 19281 | 60980 | Over-range | 12080 | 10070 | 11243 | 33480 | 4751 | 4385 | 4396 | 13770 | 18007 | 17350 | 15650 | 51006 | 18007 | 17350 | 15650 | 51006 | - - - | - - - | - - - | - - -
5/8/2026 | 8:00:00 PM | 281.71 | 279.32 | 277.63 | 487.34 | 480.77 | 484.48 | 77.962 | 73.0591 | 69.7716 | 0.2416 | 1.43 | 1.429 | 1.425 | 1.949 | 1.906 | 2.041 | Over-range | 59.98 | 18123 | 17602 | 15721 | 51446 | - - - | - - - | - - - | - - - | 18123 | 17602 | 15721 | 51446 | 11095 | 8894 | 10093 | 30082 | - - - | - - - | - - - | - - - | 11095 | 8894 | 10093 | 30082 | 21814 | 20243 | 19228 | 61284 | # # # | # # # | # # # | # # # | 0.831 | 0.87 | 0.818 | 0.84 | # # # | # # # | # # # | - - - | 0.852 | 0.892 | 0.84 | 0.861 | - - - | 0.585 | 1.6 | 1.55 | 1.45 | 1.46 | 1.47 | 1.47 | 21.58 | 21.96 | 23 | 0 | - - - | - - - | - - - | - - - | 21814 | 20243 | 19228 | 61284 | Over-range | 12133 | 9982 | 11058 | 33271 | 4825 | 4454 | 4438 | 13978 | 18140 | 17676 | 15700 | 51516 | 18140 | 17676 | 15700 | 51516 | - - - | - - - | - - - | - - -
5/8/2026 | 8:15:00 PM | 281.76 | 279.36 | 277.68 | 487.4 | 480.86 | 484.58 | 74.6246 | 69.3985 | 67.3409 | 0.2381 | 1.43 | 1.429 | 1.424 | 1.956 | 1.915 | 2.047 | Over-range | 59.98 | 17280 | 16558 | 14988 | 48827 | - - - | - - - | - - - | - - - | 17280 | 16558 | 14988 | 48827 | 10695 | 8713 | 10005 | 29412 | - - - | - - - | - - - | - - - | 10695 | 8713 | 10005 | 29412 | 20874 | 19221 | 18549 | 58644 | # # # | # # # | # # # | # # # | 0.828 | 0.861 | 0.808 | 0.833 | # # # | # # # | # # # | - - - | 0.849 | 0.884 | 0.83 | 0.855 | - - - | 0.602 | 1.58 | 1.53 | 1.44 | 1.44 | 1.45 | 1.45 | 21.82 | 22.24 | 23.12 | 0 | - - - | - - - | - - - | - - - | 20874 | 19221 | 18549 | 58644 | Over-range | 11701 | 9749 | 10914 | 32449 | 4653 | 4284 | 4271 | 13440 | 17273 | 16625 | 14993 | 48891 | 17273 | 16625 | 14993 | 48891 | - - - | - - - | - - - | - - -
5/8/2026 | 8:30:00 PM | 281.73 | 279.28 | 277.55 | 487.37 | 480.63 | 484.42 | 75.8434 | 70.7806 | 68.1538 | 0.2389 | 1.43 | 1.429 | 1.424 | 1.946 | 1.902 | 2.037 | Over-range | 59.97 | 17628 | 17000 | 15291 | 49918 | - - - | - - - | - - - | - - - | 17628 | 17000 | 15291 | 49918 | 10872 | 8802 | 10022 | 29696 | - - - | - - - | - - - | - - - | 10872 | 8802 | 10022 | 29696 | 21246 | 19633 | 18798 | 59677 | # # # | # # # | # # # | # # # | 0.83 | 0.866 | 0.813 | 0.837 | # # # | # # # | # # # | - - - | 0.85 | 0.888 | 0.835 | 0.858 | - - - | 0.595 | 1.58 | 1.53 | 1.44 | 1.44 | 1.45 | 1.45 | 21.43 | 21.72 | 22.73 | 0 | - - - | - - - | - - - | - - - | 21246 | 19633 | 18798 | 59677 | Over-range | 11853 | 9812 | 10925 | 32679 | 4655 | 4273 | 4283 | 13453 | 17648 | 17064 | 15272 | 49983 | 17648 | 17064 | 15272 | 49983 | - - - | - - - | - - - | - - -
5/8/2026 | 8:45:00 PM | 281.72 | 279.26 | 277.51 | 487.36 | 480.56 | 484.38 | 76.9628 | 71.8083 | 68.768 | 0.2381 | 1.43 | 1.429 | 1.424 | 1.964 | 1.931 | 2.06 | Over-range | 59.98 | 17892 | 17276 | 15428 | 50595 | - - - | - - - | - - - | - - - | 17892 | 17276 | 15428 | 50595 | 10861 | 8613 | 9890 | 29364 | - - - | - - - | - - - | - - - | 10861 | 8613 | 9890 | 29364 | 21536 | 19891 | 18940 | 60367 | # # # | # # # | # # # | # # # | 0.831 | 0.869 | 0.815 | 0.838 | # # # | # # # | # # # | - - - | 0.854 | 0.893 | 0.84 | 0.862 | - - - | 0.58 | 1.6 | 1.55 | 1.45 | 1.45 | 1.47 | 1.47 | 22.41 | 23.17 | 24.17 | 0 | - - - | - - - | - - - | - - - | 21536 | 19891 | 18940 | 60367 | Over-range | 11969 | 9832 | 10967 | 32868 | 4926 | 4644 | 4643 | 14481 | 17965 | 17279 | 15420 | 50664 | 17965 | 17279 | 15420 | 50664 | - - - | - - - | - - - | - - -
5/8/2026 | 9:00:00 PM | 281.68 | 279.23 | 277.43 | 487.28 | 480.49 | 484.27 | 76.9826 | 71.5379 | 69.3384 | 0.2396 | 1.43 | 1.43 | 1.424 | 1.957 | 1.928 | 2.043 | Over-range | 59.98 | 17964 | 17179 | 15542 | 50685 | - - - | - - - | - - - | - - - | 17964 | 17179 | 15542 | 50685 | 10834 | 8737 | 10075 | 29646 | - - - | - - - | - - - | - - - | 10834 | 8737 | 10075 | 29646 | 21542 | 19819 | 19098 | 60459 | # # # | # # # | # # # | # # # | 0.834 | 0.867 | 0.814 | 0.838 | # # # | # # # | # # # | - - - | 0.856 | 0.89 | 0.837 | 0.861 | - - - | 0.585 | 1.61 | 1.56 | 1.47 | 1.47 | 1.48 | 1.49 | 21.96 | 22.71 | 23.55 | 0 | - - - | - - - | - - - | - - - | 21542 | 19819 | 19098 | 60459 | Over-range | 11882 | 9870 | 11087 | 32928 | 4794 | 4513 | 4547 | 14096 | 18049 | 17186 | 15523 | 50759 | 18049 | 17186 | 15523 | 50759 | - - - | - - - | - - - | - - -
5/8/2026 | 9:15:00 PM | 281.96 | 279.66 | 277.86 | 487.89 | 481.26 | 484.86 | 78.2838 | 72.8424 | 70.7396 | 0.2412 | 1.431 | 1.43 | 1.425 | 1.944 | 1.914 | 2.028 | Over-range | 59.97 | 18325 | 17528 | 15922 | 51775 | - - - | - - - | - - - | - - - | 18325 | 17528 | 15922 | 51775 | 11018 | 8938 | 10325 | 30281 | - - - | - - - | - - - | - - - | 11018 | 8938 | 10325 | 30281 | 21921 | 20203 | 19508 | 61631 | # # # | # # # | # # # | # # # | 0.836 | 0.868 | 0.816 | 0.84 | # # # | # # # | # # # | - - - | 0.856 | 0.89 | 0.839 | 0.862 | - - - | 0.585 | 1.63 | 1.56 | 1.49 | 1.49 | 1.49 | 1.51 | 21.34 | 22.12 | 22.72 | 0 | - - - | - - - | - - - | - - - | 21921 | 20203 | 19508 | 61631 | Over-range | 12022 | 10037 | 11260 | 33408 | 4730 | 4493 | 4416 | 13887 | 18357 | 17520 | 15975 | 51851 | 18357 | 17520 | 15975 | 51851 | - - - | - - - | - - - | - - -
5/8/2026 | 9:30:00 PM | 282.36 | 280.02 | 278.27 | 488.5 | 481.97 | 485.57 | 77.2522 | 72.0943 | 69.4446 | 0.2392 | 1.431 | 1.43 | 1.425 | 1.951 | 1.927 | 2.045 | Over-range | 59.98 | 18047 | 17384 | 15648 | 51079 | - - - | - - - | - - - | - - - | 18047 | 17384 | 15648 | 51079 | 10913 | 8741 | 10077 | 29732 | - - - | - - - | - - - | - - - | 10913 | 8741 | 10077 | 29732 | 21653 | 20014 | 19174 | 60841 | # # # | # # # | # # # | # # # | 0.834 | 0.869 | 0.816 | 0.84 | # # # | # # # | # # # | - - - | 0.855 | 0.892 | 0.84 | 0.862 | - - - | 0.582 | 1.65 | 1.57 | 1.48 | 1.49 | 1.48 | 1.51 | 21.89 | 22.64 | 23.56 | 0 | - - - | - - - | - - - | - - - | 21653 | 20014 | 19174 | 60841 | Over-range | 11957 | 9903 | 11067 | 33020 | 4797 | 4574 | 4490 | 14120 | 18063 | 17370 | 15719 | 51152 | 18063 | 17370 | 15719 | 51152 | - - - | - - - | - - - | - - -
5/8/2026 | 9:45:00 PM | 282.44 | 280.22 | 278.35 | 488.75 | 482.27 | 485.64 | 77.551 | 72.1557 | 70.115 | 0.2416 | 1.431 | 1.43 | 1.425 | 1.946 | 1.919 | 2.029 | Over-range | 59.99 | 18093 | 17317 | 15707 | 51116 | - - - | - - - | - - - | - - - | 18093 | 17317 | 15707 | 51116 | 11056 | 8975 | 10366 | 30397 | - - - | - - - | - - - | - - - | 11056 | 8975 | 10366 | 30397 | 21764 | 20065 | 19376 | 61206 | # # # | # # # | # # # | # # # | 0.831 | 0.863 | 0.811 | 0.835 | # # # | # # # | # # # | - - - | 0.852 | 0.886 | 0.834 | 0.857 | - - - | 0.595 | 1.63 | 1.57 | 1.47 | 1.49 | 1.47 | 1.5 | 21.43 | 22.27 | 22.92 | 0 | - - - | - - - | - - - | - - - | 21764 | 20065 | 19376 | 61206 | Over-range | 12080 | 10112 | 11328 | 33608 | 4770 | 4568 | 4473 | 14061 | 18114 | 17299 | 15771 | 51184 | 18114 | 17299 | 15771 | 51184 | - - - | - - - | - - - | - - -
5/8/2026 | 10:00:00 PM | 282.39 | 280.11 | 278.33 | 488.61 | 482.11 | 485.62 | 77.2466 | 71.4533 | 69.0826 | 0.2398 | 1.431 | 1.43 | 1.425 | 1.931 | 1.9 | 2.028 | Over-range | 59.99 | 18032 | 17241 | 15468 | 50741 | - - - | - - - | - - - | - - - | 18032 | 17241 | 15468 | 50741 | 11074 | 8817 | 10266 | 30158 | - - - | - - - | - - - | - - - | 11074 | 8817 | 10266 | 30158 | 21669 | 19855 | 19085 | 60609 | # # # | # # # | # # # | # # # | 0.832 | 0.868 | 0.811 | 0.837 | # # # | # # # | # # # | - - - | 0.852 | 0.889 | 0.832 | 0.858 | - - - | 0.594 | 1.62 | 1.56 | 1.46 | 1.48 | 1.46 | 1.49 | 20.79 | 21.61 | 22.51 | 0 | - - - | - - - | - - - | - - - | 21669 | 19855 | 19085 | 60609 | Over-range | 12010 | 9835 | 11170 | 33123 | 4572 | 4288 | 4330 | 13489 | 18105 | 17254 | 15446 | 50806 | 18105 | 17254 | 15446 | 50806 | - - - | - - - | - - - | - - -
5/8/2026 | 10:15:00 PM | 282.5 | 280.14 | 278.31 | 488.78 | 482.05 | 485.71 | 77.2633 | 71.441 | 69.1587 | 0.2402 | 1.43 | 1.429 | 1.424 | 1.933 | 1.9 | 2.03 | Over-range | 59.97 | 18013 | 17205 | 15453 | 50672 | - - - | - - - | - - - | - - - | 18013 | 17205 | 15453 | 50672 | 11123 | 8872 | 10322 | 30316 | - - - | - - - | - - - | - - - | 11123 | 8872 | 10322 | 30316 | 21686 | 19857 | 19111 | 60654 | # # # | # # # | # # # | # # # | 0.831 | 0.866 | 0.809 | 0.835 | # # # | # # # | # # # | - - - | 0.851 | 0.887 | 0.83 | 0.856 | - - - | 0.598 | 1.63 | 1.56 | 1.49 | 1.49 | 1.48 | 1.5 | 20.96 | 21.67 | 22.56 | 0 | - - - | - - - | - - - | - - - | 21686 | 19857 | 19111 | 60654 | Over-range | 12068 | 9903 | 11233 | 33310 | 4603 | 4328 | 4355 | 13581 | 18080 | 17200 | 15454 | 50735 | 18080 | 17200 | 15454 | 50735 | - - - | - - - | - - - | - - -
5/8/2026 | 10:30:00 PM | 282.78 | 280.43 | 278.63 | 489.24 | 482.63 | 486.23 | 75.9701 | 70.3367 | 68.2969 | 0.2387 | 1.43 | 1.429 | 1.424 | 1.94 | 1.916 | 2.041 | Over-range | 59.98 | 17743 | 16945 | 15287 | 49976 | - - - | - - - | - - - | - - - | 17743 | 16945 | 15287 | 49976 | 10949 | 8786 | 10195 | 29931 | - - - | - - - | - - - | - - - | 10949 | 8786 | 10195 | 29931 | 21372 | 19602 | 18918 | 59892 | # # # | # # # | # # # | # # # | 0.83 | 0.865 | 0.808 | 0.834 | # # # | # # # | # # # | - - - | 0.851 | 0.886 | 0.831 | 0.856 | - - - | 0.599 | 1.66 | 1.57 | 1.48 | 1.51 | 1.49 | 1.53 | 21.35 | 22.11 | 23.07 | 0 | - - - | - - - | - - - | - - - | 21372 | 19602 | 18918 | 59892 | Over-range | 11907 | 9844 | 11136 | 32985 | 4608 | 4373 | 4412 | 13661 | 17820 | 16911 | 15310 | 50041 | 17820 | 16911 | 15310 | 50041 | - - - | - - - | - - - | - - -
5/8/2026 | 10:45:00 PM | 282.94 | 280.66 | 278.86 | 489.57 | 483.06 | 486.54 | 76.6647 | 71.1076 | 68.3724 | 0.2402 | 1.431 | 1.429 | 1.425 | 1.935 | 1.902 | 2.035 | Over-range | 59.98 | 17838 | 17152 | 15289 | 50279 | - - - | - - - | - - - | - - - | 17838 | 17152 | 15289 | 50279 | 11085 | 8759 | 10162 | 30006 | - - - | - - - | - - - | - - - | 11085 | 8759 | 10162 | 30006 | 21540 | 19790 | 18912 | 60242 | # # # | # # # | # # # | # # # | 0.828 | 0.867 | 0.808 | 0.835 | # # # | # # # | # # # | - - - | 0.848 | 0.888 | 0.831 | 0.856 | - - - | 0.597 | 1.67 | 1.57 | 1.5 | 1.52 | 1.5 | 1.54 | 21.09 | 21.89 | 22.84 | 0 | - - - | - - - | - - - | - - - | 21540 | 19790 | 18912 | 60242 | Over-range | 12056 | 9849 | 11115 | 33129 | 4634 | 4408 | 4401 | 13752 | 17909 | 17124 | 15306 | 50338 | 17909 | 17124 | 15306 | 50338 | - - - | - - - | - - - | - - -
5/8/2026 | 11:00:00 PM | 283.22 | 281.03 | 279.26 | 490.13 | 483.75 | 487.11 | 74.7264 | 69.4113 | 66.9636 | 0.2378 | 1.431 | 1.429 | 1.425 | 1.919 | 1.878 | 2.016 | Over-range | 59.99 | 17419 | 16761 | 15024 | 49204 | - - - | - - - | - - - | - - - | 17419 | 16761 | 15024 | 49204 | 10947 | 8806 | 10100 | 29853 | - - - | - - - | - - - | - - - | 10947 | 8806 | 10100 | 29853 | 21046 | 19376 | 18582 | 59004 | # # # | # # # | # # # | # # # | 0.828 | 0.865 | 0.809 | 0.834 | # # # | # # # | # # # | - - - | 0.846 | 0.884 | 0.828 | 0.853 | - - - | 0.607 | 1.71 | 1.59 | 1.52 | 1.54 | 1.52 | 1.56 | 20.19 | 20.63 | 21.66 | 0 | - - - | - - - | - - - | - - - | 21046 | 19376 | 18582 | 59004 | Over-range | 11804 | 9710 | 10927 | 32541 | 4342 | 4022 | 4100 | 12744 | 17486 | 16777 | 15003 | 49266 | 17486 | 16777 | 15003 | 49266 | - - - | - - - | - - - | - - -
5/8/2026 | 11:15:00 PM | 283.33 | 280.91 | 279.16 | 490.16 | 483.44 | 487.2 | 75.334 | 69.5989 | 67.3877 | 0.2384 | 1.431 | 1.429 | 1.425 | 1.921 | 1.881 | 2.022 | Over-range | 59.97 | 17563 | 16789 | 15057 | 49409 | - - - | - - - | - - - | - - - | 17563 | 16789 | 15057 | 49409 | 11055 | 8818 | 10246 | 30119 | - - - | - - - | - - - | - - - | 11055 | 8818 | 10246 | 30119 | 21231 | 19423 | 18698 | 59352 | # # # | # # # | # # # | # # # | 0.827 | 0.864 | 0.805 | 0.833 | # # # | # # # | # # # | - - - | 0.846 | 0.884 | 0.826 | 0.852 | - - - | 0.61 | 1.72 | 1.61 | 1.53 | 1.55 | 1.54 | 1.58 | 20.3 | 20.74 | 21.77 | 0 | - - - | - - - | - - - | - - - | 21231 | 19423 | 18698 | 59352 | Over-range | 11922 | 9755 | 11076 | 32858 | 4381 | 4092 | 4127 | 12901 | 17610 | 16767 | 15085 | 49462 | 17610 | 16767 | 15085 | 49462 | - - - | - - - | - - - | - - -
5/8/2026 | 11:30:00 PM | 283.38 | 280.98 | 279.15 | 490.3 | 483.49 | 487.2 | 76.0691 | 70.4412 | 67.5253 | 0.2399 | 1.432 | 1.43 | 1.426 | 1.921 | 1.877 | 2.023 | Over-range | 59.98 | 17702 | 17030 | 15108 | 49841 | - - - | - - - | - - - | - - - | 17702 | 17030 | 15108 | 49841 | 11091 | 8728 | 10162 | 29981 | - - - | - - - | - - - | - - - | 11091 | 8728 | 10162 | 29981 | 21382 | 19603 | 18683 | 59668 | # # # | # # # | # # # | # # # | 0.828 | 0.869 | 0.809 | 0.835 | # # # | # # # | # # # | - - - | 0.846 | 0.889 | 0.829 | 0.855 | - - - | 0.602 | 1.72 | 1.62 | 1.54 | 1.56 | 1.55 | 1.59 | 20.46 | 20.94 | 21.97 | 0 | - - - | - - - | - - - | - - - | 21382 | 19603 | 18683 | 59668 | Over-range | 11985 | 9696 | 10979 | 32777 | 4455 | 4141 | 4074 | 13005 | 17697 | 17053 | 15158 | 49907 | 17697 | 17053 | 15158 | 49907 | - - - | - - - | - - - | - - -
5/8/2026 | 11:45:00 PM | 283.81 | 281.4 | 279.69 | 490.98 | 484.35 | 488.07 | 77.4429 | 71.685 | 69.94 | 0.2443 | 1.431 | 1.429 | 1.425 | 1.939 | 1.912 | 2.034 | Over-range | 59.99 | 18079 | 17210 | 15620 | 50908 | - - - | - - - | - - - | - - - | 18079 | 17210 | 15620 | 50908 | 11206 | 9112 | 10546 | 30864 | - - - | - - - | - - - | - - - | 11206 | 9112 | 10546 | 30864 | 21833 | 20011 | 19415 | 61259 | # # # | # # # | # # # | # # # | 0.828 | 0.86 | 0.805 | 0.831 | # # # | # # # | # # # | - - - | 0.849 | 0.882 | 0.827 | 0.853 | - - - | 0.606 | 1.72 | 1.64 | 1.56 | 1.57 | 1.55 | 1.59 | 21.38 | 22.05 | 23 | 0 | - - - | - - - | - - - | - - - | 21833 | 20011 | 19415 | 61259 | Over-range | 12226 | 10190 | 11516 | 34025 | 4786 | 4460 | 4521 | 14025 | 18121 | 17238 | 15612 | 50971 | 18121 | 17238 | 15612 | 50971 | - - - | - - - | - - - | - - -
5/9/2026 | 12:00:00 AM | 283.91 | 281.55 | 279.75 | 491.22 | 484.55 | 488.17 | 78.1296 | 72.6498 | 70.5644 | 0.2459 | 1.431 | 1.43 | 1.424 | 1.949 | 1.925 | 2.041 | Over-range | 59.99 | 18287 | 17504 | 15853 | 51643 | - - - | - - - | - - - | - - - | 18287 | 17504 | 15853 | 51643 | 11288 | 9173 | 10539 | 31000 | - - - | - - - | - - - | - - - | 11288 | 9173 | 10539 | 31000 | 22050 | 20309 | 19610 | 61968 | # # # | # # # | # # # | # # # | 0.829 | 0.862 | 0.808 | 0.833 | # # # | # # # | # # # | - - - | 0.85 | 0.884 | 0.831 | 0.856 | - - - | 0.6 | 1.74 | 1.63 | 1.57 | 1.58 | 1.57 | 1.61 | 21.66 | 22.49 | 23.33 | 0 | - - - | - - - | - - - | - - - | 22050 | 20309 | 19610 | 61968 | Over-range | 12313 | 10288 | 11532 | 34222 | 4833 | 4578 | 4600 | 14258 | 18342 | 17506 | 15861 | 51709 | 18342 | 17506 | 15861 | 51709 | - - - | - - - | - - - | - - -
5/9/2026 | 12:15:00 AM | 283.93 | 281.41 | 279.71 | 491.11 | 484.37 | 488.18 | 79.3 | 73.5434 | 71.053 | 0.2457 | 1.431 | 1.428 | 1.424 | 1.941 | 1.917 | 2.042 | Over-range | 59.98 | 18580 | 17802 | 15982 | 52364 | - - - | - - - | - - - | - - - | 18580 | 17802 | 15982 | 52364 | 11452 | 9115 | 10593 | 31160 | - - - | - - - | - - - | - - - | 11452 | 9115 | 10593 | 31160 | 22385 | 20555 | 19747 | 62687 | # # # | # # # | # # # | # # # | 0.83 | 0.866 | 0.809 | 0.835 | # # # | # # # | # # # | - - - | 0.85 | 0.888 | 0.833 | 0.857 | - - - | 0.595 | 1.76 | 1.63 | 1.58 | 1.59 | 1.57 | 1.6 | 21.47 | 22.27 | 23.27 | 0 | - - - | - - - | - - - | - - - | 22385 | 20555 | 19747 | 62687 | Over-range | 12477 | 10261 | 11587 | 34430 | 4860 | 4629 | 4607 | 14393 | 18620 | 17766 | 16045 | 52431 | 18620 | 17766 | 16045 | 52431 | - - - | - - - | - - - | - - -
5/9/2026 | 12:30:00 AM | 284.41 | 281.88 | 280.19 | 491.98 | 485.2 | 488.96 | 76.8483 | 71.1809 | 69.1714 | 0.242 | 1.43 | 1.428 | 1.423 | 1.959 | 1.932 | 2.059 | Over-range | 59.99 | 18010 | 17189 | 15528 | 50727 | - - - | - - - | - - - | - - - | 18010 | 17189 | 15528 | 50727 | 11103 | 8945 | 10407 | 30455 | - - - | - - - | - - - | - - - | 11103 | 8945 | 10407 | 30455 | 21745 | 19942 | 19269 | 60955 | # # # | # # # | # # # | # # # | 0.828 | 0.862 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.85 | 0.886 | 0.83 | 0.855 | - - - | 0.6 | 1.73 | 1.63 | 1.57 | 1.58 | 1.56 | 1.6 | 22.3 | 22.92 | 23.92 | 0 | - - - | - - - | - - - | - - - | 21745 | 19942 | 19269 | 60955 | Over-range | 12177 | 10099 | 11399 | 33770 | 4926 | 4616 | 4575 | 14376 | 17991 | 17200 | 15595 | 50786 | 17991 | 17200 | 15595 | 50786 | - - - | - - - | - - - | - - -
5/9/2026 | 12:45:00 AM | 284.79 | 282.25 | 280.62 | 492.56 | 485.93 | 489.68 | 79.0578 | 73.6117 | 71.1247 | 0.2287 | 1.431 | 1.428 | 1.423 | 1.956 | 1.94 | 2.067 | Over-range | 59.98 | 18536 | 17803 | 16032 | 52370 | - - - | - - - | - - - | - - - | 18536 | 17803 | 16032 | 52370 | 11336 | 9121 | 10542 | 30999 | - - - | - - - | - - - | - - - | 11336 | 9121 | 10542 | 30999 | 22356 | 20601 | 19806 | 62762 | # # # | # # # | # # # | # # # | 0.829 | 0.864 | 0.81 | 0.834 | # # # | # # # | # # # | - - - | 0.851 | 0.889 | 0.835 | 0.858 | - - - | 0.592 | 1.75 | 1.64 | 1.56 | 1.59 | 1.56 | 1.61 | 22.63 | 23.25 | 24.53 | 0 | - - - | - - - | - - - | - - - | 22356 | 20601 | 19806 | 62762 | Over-range | 12486 | 10347 | 11615 | 34547 | 5138 | 4792 | 4787 | 14981 | 18509 | 17850 | 16079 | 52438 | 18509 | 17850 | 16079 | 52438 | - - - | - - - | - - - | - - -
5/9/2026 | 1:00:00 AM | 285.06 | 282.54 | 280.79 | 493.12 | 486.3 | 490.03 | 78.8762 | 73.6123 | 70.833 | 0.2471 | 1.43 | 1.428 | 1.424 | 1.977 | 1.961 | 2.087 | Over-range | 59.99 | 18471 | 17811 | 15968 | 52250 | - - - | - - - | - - - | - - - | 18471 | 17811 | 15968 | 52250 | 11322 | 9095 | 10433 | 30850 | - - - | - - - | - - - | - - - | 11322 | 9095 | 10433 | 30850 | 22335 | 20636 | 19743 | 62715 | # # # | # # # | # # # | # # # | 0.827 | 0.863 | 0.809 | 0.833 | # # # | # # # | # # # | - - - | 0.851 | 0.89 | 0.836 | 0.859 | - - - | 0.59 | 1.77 | 1.64 | 1.58 | 1.6 | 1.57 | 1.62 | 23.58 | 24.31 | 25.64 | 0 | - - - | - - - | - - - | - - - | 22335 | 20636 | 19743 | 62715 | Over-range | 12549 | 10409 | 11599 | 34654 | 5328 | 4983 | 4988 | 15548 | 18464 | 17870 | 15985 | 52319 | 18464 | 17870 | 15985 | 52319 | - - - | - - - | - - - | - - -
5/9/2026 | 1:15:00 AM | 285.02 | 282.46 | 280.88 | 492.95 | 486.3 | 490.14 | 77.9988 | 72.2921 | 70.5667 | 0.247 | 1.431 | 1.428 | 1.424 | 1.978 | 1.97 | 2.092 | Over-range | 59.97 | 18302 | 17429 | 15844 | 51575 | - - - | - - - | - - - | - - - | 18302 | 17429 | 15844 | 51575 | 11171 | 9097 | 10528 | 30795 | - - - | - - - | - - - | - - - | 11171 | 9097 | 10528 | 30795 | 22108 | 20286 | 19699 | 62094 | # # # | # # # | # # # | # # # | 0.828 | 0.859 | 0.804 | 0.831 | # # # | # # # | # # # | - - - | 0.853 | 0.886 | 0.831 | 0.857 | - - - | 0.597 | 1.77 | 1.66 | 1.57 | 1.61 | 1.57 | 1.62 | 23.65 | 24.37 | 25.69 | 0 | - - - | - - - | - - - | - - - | 22108 | 20286 | 19699 | 62094 | Over-range | 12395 | 10370 | 11696 | 34551 | 5300 | 4910 | 5027 | 15464 | 18326 | 17489 | 15828 | 51644 | 18326 | 17489 | 15828 | 51644 | - - - | - - - | - - - | - - -
5/9/2026 | 1:30:00 AM | 285.07 | 282.51 | 280.91 | 493.04 | 486.39 | 490.2 | 79.7375 | 74.167 | 71.8036 | 0.2494 | 1.431 | 1.429 | 1.424 | 1.968 | 1.955 | 2.076 | Over-range | 59.99 | 18781 | 18004 | 16249 | 53034 | - - - | - - - | - - - | - - - | 18781 | 18004 | 16249 | 53034 | 11422 | 9178 | 10577 | 31177 | - - - | - - - | - - - | - - - | 11422 | 9178 | 10577 | 31177 | 22619 | 20832 | 20059 | 63510 | # # # | # # # | # # # | # # # | 0.83 | 0.864 | 0.81 | 0.835 | # # # | # # # | # # # | - - - | 0.854 | 0.889 | 0.837 | 0.86 | - - - | 0.588 | 1.78 | 1.66 | 1.58 | 1.61 | 1.59 | 1.62 | 23.05 | 23.99 | 25.18 | 0 | - - - | - - - | - - - | - - - | 22619 | 20832 | 20059 | 63510 | Over-range | 12598 | 10469 | 11752 | 34915 | 5240 | 4969 | 5053 | 15514 | 18874 | 17989 | 16243 | 53106 | 18874 | 17989 | 16243 | 53106 | - - - | - - - | - - - | - - -
5/9/2026 | 1:45:00 AM | 285.27 | 282.75 | 281.09 | 493.42 | 486.79 | 490.49 | 79.1304 | 73.3484 | 71.229 | 0.2484 | 1.43 | 1.428 | 1.424 | 1.956 | 1.943 | 2.071 | Over-range | 59.99 | 18530 | 17698 | 15966 | 52194 | - - - | - - - | - - - | - - - | 18530 | 17698 | 15966 | 52194 | 11482 | 9220 | 10726 | 31428 | - - - | - - - | - - - | - - - | 11482 | 9220 | 10726 | 31428 | 22415 | 20564 | 19864 | 62843 | # # # | # # # | # # # | # # # | 0.827 | 0.861 | 0.804 | 0.831 | # # # | # # # | # # # | - - - | 0.849 | 0.885 | 0.829 | 0.854 | - - - | 0.602 | 1.78 | 1.66 | 1.57 | 1.6 | 1.58 | 1.61 | 22.51 | 23.34 | 24.52 | 0 | - - - | - - - | - - - | - - - | 22415 | 20564 | 19864 | 62843 | Over-range | 12598 | 10451 | 11803 | 34953 | 5095 | 4837 | 4841 | 15049 | 18553 | 17679 | 16029 | 52261 | 18553 | 17679 | 16029 | 52261 | - - - | - - - | - - - | - - -
5/9/2026 | 2:00:00 AM | 285.4 | 282.86 | 281.21 | 493.64 | 486.93 | 490.73 | 78.2863 | 72.2417 | 70.6449 | 0.2469 | 1.431 | 1.429 | 1.424 | 1.949 | 1.934 | 2.071 | Over-range | 59.99 | 18371 | 17433 | 15822 | 51625 | - - - | - - - | - - - | - - - | 18371 | 17433 | 15822 | 51625 | 11363 | 9209 | 10757 | 31328 | - - - | - - - | - - - | - - - | 11363 | 9209 | 10757 | 31328 | 22199 | 20275 | 19727 | 62201 | # # # | # # # | # # # | # # # | 0.828 | 0.86 | 0.802 | 0.83 | # # # | # # # | # # # | - - - | 0.849 | 0.883 | 0.826 | 0.853 | - - - | 0.607 | 1.76 | 1.66 | 1.58 | 1.61 | 1.58 | 1.62 | 22.27 | 22.74 | 24.06 | 0 | - - - | - - - | - - - | - - - | 22199 | 20275 | 19727 | 62201 | Over-range | 12456 | 10341 | 11770 | 34667 | 5017 | 4621 | 4699 | 14604 | 18358 | 17470 | 15859 | 51687 | 18358 | 17470 | 15859 | 51687 | - - - | - - - | - - - | - - -
5/9/2026 | 2:15:00 AM | 285.24 | 282.67 | 281.04 | 493.31 | 486.65 | 490.46 | 79.3497 | 73.4569 | 71.0866 | 0.2477 | 1.431 | 1.429 | 1.424 | 1.959 | 1.941 | 2.079 | Over-range | 59.98 | 18621 | 17803 | 15984 | 52408 | - - - | - - - | - - - | - - - | 18621 | 17803 | 15984 | 52408 | 11462 | 9122 | 10654 | 31238 | - - - | - - - | - - - | - - - | 11462 | 9122 | 10654 | 31238 | 22480 | 20596 | 19830 | 62906 | # # # | # # # | # # # | # # # | 0.828 | 0.864 | 0.806 | 0.833 | # # # | # # # | # # # | - - - | 0.851 | 0.889 | 0.832 | 0.857 | - - - | 0.596 | 1.8 | 1.69 | 1.59 | 1.63 | 1.6 | 1.64 | 22.58 | 23.33 | 24.61 | 0 | - - - | - - - | - - - | - - - | 22480 | 20596 | 19830 | 62906 | Over-range | 12587 | 10343 | 11725 | 34764 | 5119 | 4797 | 4816 | 15022 | 18625 | 17811 | 16036 | 52472 | 18625 | 17811 | 16036 | 52472 | - - - | - - - | - - - | - - -
5/9/2026 | 2:30:00 AM | 285.48 | 282.87 | 281.27 | 493.69 | 487.01 | 490.88 | 77.7977 | 71.8916 | 69.7518 | 0.2461 | 1.431 | 1.428 | 1.424 | 1.962 | 1.955 | 2.091 | Over-range | 60.01 | 18216 | 17373 | 15614 | 51203 | - - - | - - - | - - - | - - - | 18216 | 17373 | 15614 | 51203 | 11240 | 8960 | 10496 | 30696 | - - - | - - - | - - - | - - - | 11240 | 8960 | 10496 | 30696 | 22035 | 20148 | 19450 | 61633 | # # # | # # # | # # # | # # # | 0.827 | 0.862 | 0.803 | 0.831 | # # # | # # # | # # # | - - - | 0.849 | 0.887 | 0.829 | 0.855 | - - - | 0.6 | 1.81 | 1.68 | 1.61 | 1.63 | 1.61 | 1.65 | 23.04 | 23.79 | 25.23 | 0 | - - - | - - - | - - - | - - - | 22035 | 20148 | 19450 | 61633 | Over-range | 12390 | 10189 | 11585 | 34273 | 5123 | 4764 | 4816 | 14987 | 18199 | 17414 | 15659 | 51272 | 18199 | 17414 | 15659 | 51272 | - - - | - - - | - - - | - - -
5/9/2026 | 2:45:00 AM | 285.52 | 282.97 | 281.24 | 493.88 | 487.04 | 490.84 | 78.6416 | 72.7541 | 70.7649 | 0.2407 | 1.431 | 1.429 | 1.424 | 1.95 | 1.933 | 2.066 | Over-range | 59.99 | 18385 | 17533 | 15814 | 51732 | - - - | - - - | - - - | - - - | 18385 | 17533 | 15814 | 51732 | 11495 | 9292 | 10758 | 31545 | - - - | - - - | - - - | - - - | 11495 | 9292 | 10758 | 31545 | 22302 | 20419 | 19752 | 62473 | # # # | # # # | # # # | # # # | 0.824 | 0.859 | 0.801 | 0.828 | # # # | # # # | # # # | - - - | 0.846 | 0.882 | 0.824 | 0.851 | - - - | 0.61 | 1.81 | 1.69 | 1.62 | 1.64 | 1.62 | 1.66 | 22.27 | 22.83 | 24.19 | 0 | - - - | - - - | - - - | - - - | 22302 | 20419 | 19752 | 62473 | Over-range | 12608 | 10444 | 11818 | 34972 | 5067 | 4661 | 4790 | 14787 | 18412 | 17587 | 15792 | 51792 | 18412 | 17587 | 15792 | 51792 | - - - | - - - | - - - | - - -
5/9/2026 | 3:00:00 AM | 285.45 | 282.83 | 281.1 | 493.68 | 486.77 | 490.71 | 78.1223 | 72.3387 | 69.751 | 0.236 | 1.431 | 1.428 | 1.424 | 1.94 | 1.919 | 2.061 | Over-range | 59.98 | 18322 | 17572 | 15692 | 51585 | - - - | - - - | - - - | - - - | 18322 | 17572 | 15692 | 51585 | 11441 | 9107 | 10538 | 31086 | - - - | - - - | - - - | - - - | 11441 | 9107 | 10538 | 31086 | 22172 | 20317 | 19484 | 61973 | # # # | # # # | # # # | # # # | 0.826 | 0.865 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.848 | 0.887 | 0.828 | 0.855 | - - - | 0.603 | 1.79 | 1.68 | 1.61 | 1.63 | 1.61 | 1.65 | 21.74 | 22.19 | 23.74 | 0 | - - - | - - - | - - - | - - - | 22172 | 20317 | 19484 | 61973 | Over-range | 12480 | 10185 | 11539 | 34317 | 4901 | 4484 | 4628 | 14311 | 18361 | 17622 | 15659 | 51643 | 18361 | 17622 | 15659 | 51643 | - - - | - - - | - - - | - - -
5/9/2026 | 3:15:00 AM | 285.49 | 282.93 | 281.14 | 493.81 | 486.93 | 490.72 | 77.6365 | 71.9373 | 69.2006 | 0.2441 | 1.43 | 1.428 | 1.423 | 1.954 | 1.93 | 2.072 | Over-range | 59.99 | 18160 | 17450 | 15527 | 51136 | - - - | - - - | - - - | - - - | 18160 | 17450 | 15527 | 51136 | 11382 | 9027 | 10433 | 30841 | - - - | - - - | - - - | - - - | 11382 | 9027 | 10433 | 30841 | 22023 | 20200 | 19315 | 61537 | # # # | # # # | # # # | # # # | 0.825 | 0.864 | 0.804 | 0.831 | # # # | # # # | # # # | - - - | 0.847 | 0.887 | 0.828 | 0.854 | - - - | 0.603 | 1.77 | 1.69 | 1.6 | 1.63 | 1.6 | 1.64 | 22.19 | 22.8 | 24.31 | 0 | - - - | - - - | - - - | - - - | 22023 | 20200 | 19315 | 61537 | Over-range | 12451 | 10161 | 11477 | 34202 | 4961 | 4580 | 4696 | 14535 | 18206 | 17494 | 15493 | 51193 | 18206 | 17494 | 15493 | 51193 | - - - | - - - | - - - | - - -
5/9/2026 | 3:30:00 AM | 285.81 | 283.22 | 281.49 | 494.35 | 487.45 | 491.35 | 78.1216 | 72.0288 | 70.3986 | 0.2283 | 1.431 | 1.428 | 1.424 | 1.948 | 1.932 | 2.069 | Over-range | 59.98 | 18330 | 17391 | 15749 | 51470 | - - - | - - - | - - - | - - - | 18330 | 17391 | 15749 | 51470 | 11415 | 9221 | 10732 | 31369 | - - - | - - - | - - - | - - - | 11415 | 9221 | 10732 | 31369 | 22183 | 20239 | 19675 | 62097 | # # # | # # # | # # # | # # # | 0.826 | 0.859 | 0.801 | 0.829 | # # # | # # # | # # # | - - - | 0.848 | 0.882 | 0.824 | 0.852 | - - - | 0.61 | 1.8 | 1.68 | 1.61 | 1.62 | 1.6 | 1.64 | 22.17 | 22.75 | 24.14 | 0 | - - - | - - - | - - - | - - - | 22183 | 20239 | 19675 | 62097 | Over-range | 12487 | 10340 | 11780 | 34710 | 4974 | 4593 | 4775 | 14612 | 18401 | 17401 | 15729 | 51531 | 18401 | 17401 | 15729 | 51531 | - - - | - - - | - - - | - - -
5/9/2026 | 3:45:00 AM | 285.73 | 283.24 | 281.45 | 494.27 | 487.5 | 491.18 | 77.9747 | 72.2547 | 70.2346 | 0.2469 | 1.429 | 1.427 | 1.423 | 1.962 | 1.944 | 2.075 | Over-range | 59.98 | 18310 | 17484 | 15787 | 51581 | - - - | - - - | - - - | - - - | 18310 | 17484 | 15787 | 51581 | 11332 | 9162 | 10599 | 31093 | - - - | - - - | - - - | - - - | 11332 | 9162 | 10599 | 31093 | 22164 | 20338 | 19654 | 62155 | # # # | # # # | # # # | # # # | 0.826 | 0.86 | 0.803 | 0.83 | # # # | # # # | # # # | - - - | 0.849 | 0.884 | 0.828 | 0.854 | - - - | 0.603 | 1.77 | 1.68 | 1.58 | 1.61 | 1.58 | 1.62 | 22.78 | 23.41 | 24.72 | 0 | - - - | - - - | - - - | - - - | 22164 | 20338 | 19654 | 62155 | Over-range | 12475 | 10370 | 11692 | 34634 | 5132 | 4780 | 4859 | 15028 | 18337 | 17517 | 15786 | 51640 | 18337 | 17517 | 15786 | 51640 | - - - | - - - | - - - | - - -
5/9/2026 | 4:00:00 AM | 285.85 | 283.35 | 281.57 | 494.45 | 487.69 | 491.42 | 76.397 | 70.7102 | 68.6162 | 0.2227 | 1.43 | 1.428 | 1.423 | 1.976 | 1.96 | 2.092 | Over-range | 59.99 | 17915 | 17105 | 15395 | 50415 | - - - | - - - | - - - | - - - | 17915 | 17105 | 15395 | 50415 | 11055 | 8879 | 10341 | 30276 | - - - | - - - | - - - | - - - | 11055 | 8879 | 10341 | 30276 | 21692 | 19876 | 19183 | 60752 | # # # | # # # | # # # | # # # | 0.826 | 0.861 | 0.803 | 0.83 | # # # | # # # | # # # | - - - | 0.85 | 0.887 | 0.829 | 0.855 | - - - | 0.601 | 1.79 | 1.67 | 1.59 | 1.62 | 1.59 | 1.63 | 23.47 | 24.18 | 25.49 | 0 | - - - | - - - | - - - | - - - | 21692 | 19876 | 19183 | 60752 | Over-range | 12225 | 10109 | 11434 | 33869 | 5145 | 4763 | 4810 | 14978 | 17904 | 17172 | 15406 | 50482 | 17904 | 17172 | 15406 | 50482 | - - - | - - - | - - - | - - -
5/9/2026 | 4:15:00 AM | 285.95 | 283.47 | 281.65 | 494.69 | 487.85 | 491.55 | 77.0435 | 71.454 | 69.3093 | 0.2446 | 1.431 | 1.428 | 1.423 | 1.975 | 1.957 | 2.087 | Over-range | 59.99 | 18055 | 17275 | 15558 | 50889 | - - - | - - - | - - - | - - - | 18055 | 17275 | 15558 | 50889 | 11260 | 9062 | 10480 | 30802 | - - - | - - - | - - - | - - - | 11260 | 9062 | 10480 | 30802 | 21907 | 20117 | 19401 | 61424 | # # # | # # # | # # # | # # # | 0.824 | 0.859 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.848 | 0.884 | 0.829 | 0.854 | - - - | 0.605 | 1.8 | 1.65 | 1.6 | 1.62 | 1.59 | 1.63 | 23.21 | 23.91 | 25.14 | 0 | - - - | - - - | - - - | - - - | 21907 | 20117 | 19401 | 61424 | Over-range | 12400 | 10296 | 11580 | 34372 | 5119 | 4818 | 4853 | 15044 | 18087 | 17262 | 15600 | 50949 | 18087 | 17262 | 15600 | 50949 | - - - | - - - | - - - | - - -
5/9/2026 | 4:30:00 AM | 286.1 | 283.67 | 281.89 | 494.95 | 488.28 | 491.88 | 77.7838 | 72.1842 | 69.9485 | 0.2287 | 1.43 | 1.427 | 1.423 | 1.974 | 1.961 | 2.085 | Over-range | 59.99 | 18251 | 17482 | 15728 | 51461 | - - - | - - - | - - - | - - - | 18251 | 17482 | 15728 | 51461 | 11355 | 9128 | 10534 | 31017 | - - - | - - - | - - - | - - - | 11355 | 9128 | 10534 | 31017 | 22123 | 20334 | 19590 | 62046 | # # # | # # # | # # # | # # # | 0.825 | 0.86 | 0.803 | 0.829 | # # # | # # # | # # # | - - - | 0.849 | 0.885 | 0.83 | 0.855 | - - - | 0.603 | 1.81 | 1.66 | 1.58 | 1.62 | 1.59 | 1.63 | 23.25 | 24.18 | 25.44 | 0 | - - - | - - - | - - - | - - - | 22123 | 20334 | 19590 | 62046 | Over-range | 12497 | 10374 | 11670 | 34639 | 5152 | 4868 | 4962 | 15240 | 18331 | 17475 | 15716 | 51523 | 18331 | 17475 | 15716 | 51523 | - - - | - - - | - - - | - - -
5/9/2026 | 4:45:00 AM | 285.93 | 283.52 | 281.8 | 494.62 | 488.13 | 491.66 | 76.1976 | 70.926 | 68.9902 | 0.2463 | 1.431 | 1.428 | 1.424 | 1.999 | 1.996 | 2.11 | Over-range | 60 | 17864 | 17089 | 15497 | 50451 | - - - | - - - | - - - | - - - | 17864 | 17089 | 15497 | 50451 | 10901 | 8869 | 10197 | 29967 | - - - | - - - | - - - | - - - | 10901 | 8869 | 10197 | 29967 | 21649 | 19957 | 19306 | 60911 | # # # | # # # | # # # | # # # | 0.825 | 0.856 | 0.803 | 0.828 | # # # | # # # | # # # | - - - | 0.853 | 0.886 | 0.833 | 0.857 | - - - | 0.594 | 1.8 | 1.67 | 1.6 | 1.63 | 1.6 | 1.64 | 24.71 | 25.75 | 27.03 | 0 | - - - | - - - | - - - | - - - | 21649 | 19957 | 19306 | 60911 | Over-range | 12211 | 10280 | 11494 | 34070 | 5407 | 5109 | 5213 | 15945 | 17932 | 17119 | 15467 | 50518 | 17932 | 17119 | 15467 | 50518 | - - - | - - - | - - - | - - -
5/9/2026 | 5:00:00 AM | 285.72 | 283.25 | 281.5 | 494.25 | 487.54 | 491.24 | 79.3782 | 74.0943 | 71.9045 | 0.2493 | 1.43 | 1.427 | 1.424 | 1.987 | 1.979 | 2.093 | Over-range | 59.99 | 18691 | 17939 | 16270 | 52900 | - - - | - - - | - - - | - - - | 18691 | 17939 | 16270 | 52900 | 11329 | 9257 | 10582 | 31168 | - - - | - - - | - - - | - - - | 11329 | 9257 | 10582 | 31168 | 22554 | 20847 | 20115 | 63516 | # # # | # # # | # # # | # # # | 0.829 | 0.861 | 0.809 | 0.833 | # # # | # # # | # # # | - - - | 0.855 | 0.888 | 0.837 | 0.86 | - - - | 0.589 | 1.82 | 1.69 | 1.61 | 1.63 | 1.62 | 1.66 | 24.18 | 24.99 | 26.28 | 0 | - - - | - - - | - - - | - - - | 22554 | 20847 | 20115 | 63516 | Over-range | 12616 | 10613 | 11819 | 35133 | 5495 | 5134 | 5211 | 16051 | 18710 | 18017 | 16252 | 52979 | 18710 | 18017 | 16252 | 52979 | - - - | - - - | - - - | - - -
5/9/2026 | 5:15:00 AM | 285.62 | 283.15 | 281.46 | 494.06 | 487.43 | 491.16 | 78.3971 | 72.9468 | 70.6701 | 0.2294 | 1.43 | 1.428 | 1.424 | 1.998 | 1.998 | 2.106 | Over-range | 60 | 18497 | 17719 | 16001 | 52217 | - - - | - - - | - - - | - - - | 18497 | 17719 | 16001 | 52217 | 11067 | 8892 | 10339 | 30298 | - - - | - - - | - - - | - - - | 11067 | 8892 | 10339 | 30298 | 22301 | 20555 | 19802 | 62658 | # # # | # # # | # # # | # # # | 0.829 | 0.862 | 0.808 | 0.833 | # # # | # # # | # # # | - - - | 0.857 | 0.893 | 0.839 | 0.863 | - - - | 0.58 | 1.84 | 1.72 | 1.64 | 1.66 | 1.64 | 1.69 | 24.95 | 26.09 | 27.32 | 0 | - - - | - - - | - - - | - - - | 22301 | 20555 | 19802 | 62658 | Over-range | 12450 | 10405 | 11657 | 34605 | 5645 | 5352 | 5330 | 16561 | 18479 | 17780 | 16043 | 52301 | 18479 | 17780 | 16043 | 52301 | - - - | - - - | - - - | - - -
5/9/2026 | 5:30:00 AM | 285.49 | 283.11 | 281.33 | 493.92 | 487.33 | 490.86 | 79.1811 | 73.9729 | 72.1242 | 0.2494 | 1.431 | 1.428 | 1.425 | 1.996 | 1.997 | 2.094 | Over-range | 60.01 | 18653 | 17847 | 16305 | 52805 | - - - | - - - | - - - | - - - | 18653 | 17847 | 16305 | 52805 | 11144 | 9172 | 10539 | 30855 | - - - | - - - | - - - | - - - | 11144 | 9172 | 10539 | 30855 | 22458 | 20782 | 20147 | 63387 | # # # | # # # | # # # | # # # | 0.831 | 0.859 | 0.809 | 0.833 | # # # | # # # | # # # | - - - | 0.857 | 0.889 | 0.839 | 0.862 | - - - | 0.584 | 1.84 | 1.73 | 1.64 | 1.66 | 1.65 | 1.7 | 24.67 | 25.77 | 26.77 | 0 | - - - | - - - | - - - | - - - | 22458 | 20782 | 20147 | 63387 | Over-range | 12501 | 10636 | 11822 | 35035 | 5591 | 5317 | 5288 | 16393 | 18631 | 17908 | 16352 | 52891 | 18631 | 17908 | 16352 | 52891 | - - - | - - - | - - - | - - -
5/9/2026 | 5:45:00 AM | 285.37 | 282.89 | 281.21 | 493.64 | 486.97 | 490.72 | 79.4695 | 74.0735 | 71.6741 | 0.2468 | 1.43 | 1.427 | 1.424 | 1.971 | 1.97 | 2.079 | Over-range | 60.01 | 18651 | 17902 | 16162 | 52714 | - - - | - - - | - - - | - - - | 18651 | 17902 | 16162 | 52714 | 11385 | 9165 | 10574 | 31124 | - - - | - - - | - - - | - - - | 11385 | 9165 | 10574 | 31124 | 22523 | 20782 | 20007 | 63311 | # # # | # # # | # # # | # # # | 0.828 | 0.861 | 0.808 | 0.833 | # # # | # # # | # # # | - - - | 0.852 | 0.888 | 0.836 | 0.859 | - - - | 0.59 | 1.82 | 1.69 | 1.63 | 1.64 | 1.62 | 1.67 | 23.49 | 24.53 | 25.72 | 0 | - - - | - - - | - - - | - - - | 22523 | 20782 | 20007 | 63311 | Over-range | 12611 | 10532 | 11775 | 35012 | 5343 | 5117 | 5107 | 15818 | 18676 | 17886 | 16225 | 52787 | 18676 | 17886 | 16225 | 52787 | - - - | - - - | - - - | - - -
5/9/2026 | 6:00:00 AM | 285.29 | 282.91 | 281.18 | 493.56 | 487.03 | 490.58 | 76.9275 | 71.5028 | 68.8461 | 0.2412 | 1.43 | 1.428 | 1.424 | 1.977 | 1.974 | 2.091 | Over-range | 60 | 18036 | 17343 | 15500 | 50878 | - - - | - - - | - - - | - - - | 18036 | 17343 | 15500 | 50878 | 11092 | 8778 | 10211 | 30080 | - - - | - - - | - - - | - - - | 11092 | 8778 | 10211 | 30080 | 21815 | 20085 | 19228 | 61127 | # # # | # # # | # # # | # # # | 0.827 | 0.864 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.851 | 0.891 | 0.835 | 0.859 | - - - | 0.591 | 1.8 | 1.71 | 1.62 | 1.64 | 1.62 | 1.67 | 23.56 | 24.75 | 26 | 0 | - - - | - - - | - - - | - - - | 21815 | 20085 | 19228 | 61127 | Over-range | 12264 | 10118 | 11368 | 33853 | 5162 | 4968 | 4932 | 15337 | 18065 | 17327 | 15566 | 50959 | 18065 | 17327 | 15566 | 50959 | - - - | - - - | - - - | - - -
5/9/2026 | 6:15:00 AM | 285.1 | 282.7 | 281 | 493.17 | 486.75 | 490.23 | 79.047 | 73.6332 | 71.7796 | 0.2264 | 1.431 | 1.428 | 1.425 | 1.973 | 1.978 | 2.073 | Over-range | 60 | 18562 | 17746 | 16156 | 52464 | - - - | - - - | - - - | - - - | 18562 | 17746 | 16156 | 52464 | 11332 | 9243 | 10643 | 31218 | - - - | - - - | - - - | - - - | 11332 | 9243 | 10643 | 31218 | 22396 | 20663 | 20034 | 63093 | # # # | # # # | # # # | # # # | 0.829 | 0.859 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.854 | 0.886 | 0.834 | 0.858 | - - - | 0.595 | 1.8 | 1.68 | 1.64 | 1.64 | 1.62 | 1.66 | 23.38 | 24.56 | 25.59 | 0 | - - - | - - - | - - - | - - - | 22396 | 20663 | 20034 | 63093 | Over-range | 12524 | 10574 | 11835 | 35019 | 5255 | 5064 | 5105 | 15650 | 18639 | 17725 | 16181 | 52544 | 18639 | 17725 | 16181 | 52544 | - - - | - - - | - - - | - - -
5/9/2026 | 6:30:00 AM | 284.94 | 282.64 | 280.89 | 493.01 | 486.6 | 489.97 | 80.0732 | 75.0829 | 72.5762 | 0.2489 | 1.43 | 1.428 | 1.424 | 1.976 | 1.981 | 2.08 | Over-range | 60.01 | 18844 | 18180 | 16465 | 53488 | - - - | - - - | - - - | - - - | 18844 | 18180 | 16465 | 53488 | 11377 | 9265 | 10530 | 31172 | - - - | - - - | - - - | - - - | 11377 | 9265 | 10530 | 31172 | 22687 | 21080 | 20261 | 64028 | # # # | # # # | # # # | # # # | 0.831 | 0.862 | 0.813 | 0.835 | # # # | # # # | # # # | - - - | 0.856 | 0.89 | 0.841 | 0.862 | - - - | 0.583 | 1.79 | 1.69 | 1.63 | 1.63 | 1.61 | 1.66 | 23.71 | 24.8 | 26.04 | 0 | - - - | - - - | - - - | - - - | 22687 | 21080 | 20261 | 64028 | Over-range | 12627 | 10659 | 11797 | 35166 | 5402 | 5201 | 5249 | 16068 | 18929 | 18178 | 16459 | 53566 | 18929 | 18178 | 16459 | 53566 | - - - | - - - | - - - | - - -
5/9/2026 | 6:45:00 AM | 285.02 | 282.69 | 281.03 | 493.08 | 486.81 | 490.17 | 79.0429 | 74.1174 | 71.695 | 0.2484 | 1.43 | 1.427 | 1.424 | 1.985 | 1.988 | 2.084 | Over-range | 60.01 | 18517 | 17856 | 16183 | 52557 | - - - | - - - | - - - | - - - | 18517 | 17856 | 16183 | 52557 | 11242 | 9175 | 10421 | 30838 | - - - | - - - | - - - | - - - | 11242 | 9175 | 10421 | 30838 | 22368 | 20781 | 19996 | 63144 | # # # | # # # | # # # | # # # | 0.828 | 0.859 | 0.809 | 0.832 | # # # | # # # | # # # | - - - | 0.854 | 0.888 | 0.838 | 0.86 | - - - | 0.587 | 1.79 | 1.67 | 1.62 | 1.62 | 1.6 | 1.64 | 24.03 | 25.21 | 26.43 | 0 | - - - | - - - | - - - | - - - | 22368 | 20781 | 19996 | 63144 | Over-range | 12527 | 10601 | 11724 | 34933 | 5426 | 5219 | 5281 | 16139 | 18605 | 17873 | 16162 | 52640 | 18605 | 17873 | 16162 | 52640 | - - - | - - - | - - - | - - -
5/9/2026 | 7:00:00 AM | 284.96 | 282.68 | 280.97 | 492.96 | 486.78 | 490.09 | 76.1537 | 71.5893 | 69.3626 | 0.2263 | 1.431 | 1.428 | 1.425 | 1.987 | 1.991 | 2.088 | Over-range | 60.01 | 17843 | 17248 | 15677 | 50768 | - - - | - - - | - - - | - - - | 17843 | 17248 | 15677 | 50768 | 10896 | 8982 | 10136 | 30014 | - - - | - - - | - - - | - - - | 10896 | 8982 | 10136 | 30014 | 21588 | 20113 | 19376 | 61078 | # # # | # # # | # # # | # # # | 0.827 | 0.858 | 0.809 | 0.831 | # # # | # # # | # # # | - - - | 0.853 | 0.886 | 0.838 | 0.859 | - - - | 0.591 | 1.83 | 1.72 | 1.68 | 1.66 | 1.65 | 1.7 | 24.33 | 25.31 | 26.61 | 0 | - - - | - - - | - - - | - - - | 21588 | 20113 | 19376 | 61078 | Over-range | 12146 | 10337 | 11378 | 33935 | 5309 | 5063 | 5117 | 15673 | 17895 | 17296 | 15666 | 50857 | 17895 | 17296 | 15666 | 50857 | - - - | - - - | - - - | - - -
5/9/2026 | 7:15:00 AM | 284.59 | 282.3 | 280.58 | 492.33 | 486.07 | 489.43 | 78.9344 | 74.5131 | 71.7428 | 0.2469 | 1.43 | 1.428 | 1.425 | 1.982 | 1.991 | 2.082 | Over-range | 60 | 18506 | 17982 | 16284 | 52772 | - - - | - - - | - - - | - - - | 18506 | 17982 | 16284 | 52772 | 11177 | 9157 | 10325 | 30660 | - - - | - - - | - - - | - - - | 11177 | 9157 | 10325 | 30660 | 22324 | 20881 | 19997 | 63203 | # # # | # # # | # # # | # # # | 0.829 | 0.861 | 0.814 | 0.835 | # # # | # # # | # # # | - - - | 0.855 | 0.89 | 0.844 | 0.863 | - - - | 0.581 | 1.84 | 1.76 | 1.74 | 1.69 | 1.69 | 1.75 | 24.32 | 25.33 | 26.58 | 0 | - - - | - - - | - - - | - - - | 22324 | 20881 | 19997 | 63203 | Over-range | 12478 | 10603 | 11596 | 34753 | 5484 | 5284 | 5220 | 16185 | 18494 | 18023 | 16347 | 52864 | 18494 | 18023 | 16347 | 52864 | - - - | - - - | - - - | - - -
5/9/2026 | 7:30:00 AM | 284.28 | 281.99 | 280.25 | 491.82 | 485.5 | 488.9 | 78.1213 | 73.6346 | 71.1837 | 0.2436 | 1.43 | 1.429 | 1.425 | 2.001 | 2.015 | 2.107 | Over-range | 60.01 | 18293 | 17711 | 16096 | 52101 | - - - | - - - | - - - | - - - | 18293 | 17711 | 16096 | 52101 | 10952 | 8967 | 10142 | 30061 | - - - | - - - | - - - | - - - | 10952 | 8967 | 10142 | 30061 | 22072 | 20617 | 19814 | 62503 | # # # | # # # | # # # | # # # | 0.829 | 0.859 | 0.812 | 0.834 | # # # | # # # | # # # | - - - | 0.857 | 0.89 | 0.845 | 0.864 | - - - | 0.577 | 1.87 | 1.79 | 1.73 | 1.71 | 1.71 | 1.76 | 25.32 | 26.58 | 27.85 | 0 | - - - | - - - | - - - | - - - | 22072 | 20617 | 19814 | 62503 | Over-range | 12342 | 10538 | 11542 | 34494 | 5614 | 5466 | 5439 | 16703 | 18339 | 17701 | 16160 | 52200 | 18339 | 17701 | 16160 | 52200 | - - - | - - - | - - - | - - -
5/9/2026 | 7:45:00 AM | 283.91 | 281.65 | 279.85 | 491.2 | 484.87 | 488.21 | 80.3103 | 76.1003 | 73.3032 | 0.2341 | 1.43 | 1.429 | 1.425 | 1.999 | 2.005 | 2.088 | Over-range | 60 | 18791 | 18297 | 16620 | 53709 | - - - | - - - | - - - | - - - | 18791 | 18297 | 16620 | 53709 | 11268 | 9279 | 10349 | 30896 | - - - | - - - | - - - | - - - | 11268 | 9279 | 10349 | 30896 | 22668 | 21287 | 20380 | 64335 | # # # | # # # | # # # | # # # | 0.829 | 0.86 | 0.816 | 0.835 | # # # | # # # | # # # | - - - | 0.858 | 0.89 | 0.848 | 0.865 | - - - | 0.575 | 1.89 | 1.81 | 1.77 | 1.73 | 1.75 | 1.8 | 25.12 | 26.34 | 27.53 | 0 | - - - | - - - | - - - | - - - | 22668 | 21287 | 20380 | 64335 | Over-range | 12664 | 10861 | 11781 | 35374 | 5707 | 5577 | 5565 | 17025 | 18893 | 18289 | 16635 | 53817 | 18893 | 18289 | 16635 | 53817 | - - - | - - - | - - - | - - -
5/9/2026 | 8:00:00 AM | 283.58 | 281.24 | 279.56 | 490.56 | 484.22 | 487.71 | 80.4794 | 76.252 | 73.2043 | 0.248 | 1.43 | 1.429 | 1.426 | 2.015 | 2.017 | 2.104 | Over-range | 60.01 | 18860 | 18376 | 16647 | 53884 | - - - | - - - | - - - | - - - | 18860 | 18376 | 16647 | 53884 | 11091 | 9073 | 10136 | 30301 | - - - | - - - | - - - | - - - | 11091 | 9073 | 10136 | 30301 | 22672 | 21285 | 20321 | 64279 | # # # | # # # | # # # | # # # | 0.832 | 0.863 | 0.819 | 0.838 | # # # | # # # | # # # | - - - | 0.862 | 0.896 | 0.853 | 0.87 | - - - | 0.562 | 1.9 | 1.81 | 1.81 | 1.75 | 1.77 | 1.81 | 25.88 | 27.06 | 28.35 | 0 | - - - | - - - | - - - | - - - | 22672 | 21285 | 20321 | 64279 | Over-range | 12576 | 10730 | 11643 | 35019 | 5857 | 5663 | 5667 | 17363 | 18949 | 18420 | 16624 | 53992 | 18949 | 18420 | 16624 | 53992 | - - - | - - - | - - - | - - -
5/9/2026 | 8:15:00 AM | 283.17 | 280.92 | 279.17 | 489.88 | 483.65 | 487.02 | 78.5531 | 74.2405 | 71.5731 | 0.2442 | 1.431 | 1.431 | 1.426 | 2.006 | 2.011 | 2.095 | Over-range | 59.99 | 18361 | 17833 | 16200 | 52394 | - - - | - - - | - - - | - - - | 18361 | 17833 | 16200 | 52394 | 10885 | 8958 | 10037 | 29880 | - - - | - - - | - - - | - - - | 10885 | 8958 | 10037 | 29880 | 22113 | 20718 | 19855 | 62686 | # # # | # # # | # # # | # # # | 0.83 | 0.861 | 0.816 | 0.836 | # # # | # # # | # # # | - - - | 0.86 | 0.893 | 0.848 | 0.867 | - - - | 0.57 | 1.94 | 1.85 | 1.86 | 1.78 | 1.82 | 1.87 | 25.4 | 26.58 | 27.77 | 0 | - - - | - - - | - - - | - - - | 22113 | 20718 | 19855 | 62686 | Over-range | 12315 | 10532 | 11468 | 34384 | 5686 | 5470 | 5480 | 16807 | 18430 | 17900 | 16173 | 52502 | 18430 | 17900 | 16173 | 52502 | - - - | - - - | - - - | - - -
5/9/2026 | 8:30:00 AM | 282.99 | 280.77 | 279.09 | 489.55 | 483.52 | 486.79 | 77.354 | 73.1517 | 70.5998 | 0.2254 | 1.43 | 1.431 | 1.426 | 1.997 | 2.003 | 2.083 | Over-range | 60.01 | 18091 | 17577 | 15997 | 51665 | - - - | - - - | - - - | - - - | 18091 | 17577 | 15997 | 51665 | 10785 | 8894 | 9956 | 29635 | - - - | - - - | - - - | - - - | 10785 | 8894 | 9956 | 29635 | 21776 | 20412 | 19591 | 61778 | # # # | # # # | # # # | # # # | 0.831 | 0.861 | 0.817 | 0.836 | # # # | # # # | # # # | - - - | 0.859 | 0.891 | 0.847 | 0.866 | - - - | 0.574 | 1.92 | 1.88 | 1.86 | 1.78 | 1.81 | 1.86 | 24.82 | 25.96 | 27.1 | 0 | - - - | - - - | - - - | - - - | 21776 | 20412 | 19591 | 61778 | Over-range | 12112 | 10367 | 11300 | 33846 | 5450 | 5268 | 5289 | 16175 | 18187 | 17604 | 15980 | 51771 | 18187 | 17604 | 15980 | 51771 | - - - | - - - | - - - | - - -
5/9/2026 | 8:45:00 AM | 282.52 | 280.25 | 278.5 | 488.77 | 482.46 | 485.89 | 78.769 | 74.639 | 71.4454 | 0.2418 | 1.431 | 1.432 | 1.426 | 2.001 | 2.005 | 2.093 | Over-range | 60 | 18409 | 17976 | 16219 | 52604 | - - - | - - - | - - - | - - - | 18409 | 17976 | 16219 | 52604 | 10872 | 8817 | 9903 | 29592 | - - - | - - - | - - - | - - - | 10872 | 8817 | 9903 | 29592 | 22131 | 20783 | 19777 | 62692 | # # # | # # # | # # # | # # # | 0.832 | 0.865 | 0.82 | 0.839 | # # # | # # # | # # # | - - - | 0.86 | 0.896 | 0.853 | 0.869 | - - - | 0.563 | 1.92 | 1.88 | 1.86 | 1.78 | 1.83 | 1.86 | 25.1 | 26.2 | 27.37 | 0 | - - - | - - - | - - - | - - - | 22131 | 20783 | 19777 | 62692 | Over-range | 12269 | 10412 | 11301 | 34055 | 5623 | 5478 | 5384 | 16677 | 18448 | 17975 | 16287 | 52710 | 18448 | 17975 | 16287 | 52710 | - - - | - - - | - - - | - - -
5/9/2026 | 9:00:00 AM | 282.47 | 280.15 | 278.5 | 488.58 | 482.39 | 485.89 | 79.8814 | 75.5743 | 72.5546 | 0.2457 | 1.431 | 1.432 | 1.427 | 1.989 | 2.004 | 2.086 | Over-range | 60.01 | 18671 | 18179 | 16452 | 53301 | - - - | - - - | - - - | - - - | 18671 | 18179 | 16452 | 53301 | 10964 | 8939 | 10066 | 29970 | - - - | - - - | - - - | - - - | 10964 | 8939 | 10066 | 29970 | 22404 | 21003 | 20054 | 63462 | # # # | # # # | # # # | # # # | 0.833 | 0.866 | 0.82 | 0.84 | # # # | # # # | # # # | - - - | 0.861 | 0.897 | 0.852 | 0.87 | - - - | 0.562 | 1.94 | 1.92 | 1.88 | 1.81 | 1.85 | 1.89 | 24.98 | 26.05 | 27.36 | 0 | - - - | - - - | - - - | - - - | 22404 | 21003 | 20054 | 63462 | Over-range | 12375 | 10505 | 11456 | 34411 | 5663 | 5444 | 5400 | 16696 | 18677 | 18261 | 16473 | 53411 | 18677 | 18261 | 16473 | 53411 | - - - | - - - | - - - | - - -
5/9/2026 | 9:15:00 AM | 282.96 | 280.84 | 279.1 | 489.57 | 483.63 | 486.73 | 77.8337 | 73.6416 | 71.4879 | 0.2436 | 1.432 | 1.432 | 1.427 | 1.982 | 1.988 | 2.066 | Over-range | 60.01 | 18232 | 17662 | 16207 | 52100 | - - - | - - - | - - - | - - - | 18232 | 17662 | 16207 | 52100 | 10800 | 9037 | 10086 | 29923 | - - - | - - - | - - - | - - - | 10800 | 9037 | 10086 | 29923 | 21883 | 20530 | 19812 | 62225 | # # # | # # # | # # # | # # # | 0.833 | 0.86 | 0.818 | 0.837 | # # # | # # # | # # # | - - - | 0.86 | 0.889 | 0.847 | 0.866 | - - - | 0.574 | 1.94 | 1.9 | 1.87 | 1.8 | 1.83 | 1.88 | 24.19 | 25.29 | 26.25 | 0 | - - - | - - - | - - - | - - - | 21883 | 20530 | 19812 | 62225 | Over-range | 12094 | 10454 | 11382 | 33989 | 5369 | 5189 | 5206 | 15914 | 18318 | 17701 | 16191 | 52210 | 18318 | 17701 | 16191 | 52210 | - - - | - - - | - - - | - - -
5/9/2026 | 9:30:00 AM | 282.74 | 280.45 | 278.84 | 489.02 | 482.97 | 486.44 | 79.5795 | 75.2546 | 72.4735 | 0.245 | 1.432 | 1.433 | 1.427 | 1.978 | 1.978 | 2.062 | Over-range | 60.01 | 18627 | 18108 | 16462 | 53196 | - - - | - - - | - - - | - - - | 18627 | 18108 | 16462 | 53196 | 11045 | 9084 | 10166 | 30294 | - - - | - - - | - - - | - - - | 11045 | 9084 | 10166 | 30294 | 22346 | 20938 | 20062 | 63345 | # # # | # # # | # # # | # # # | 0.834 | 0.865 | 0.821 | 0.84 | # # # | # # # | # # # | - - - | 0.86 | 0.893 | 0.849 | 0.867 | - - - | 0.57 | 1.92 | 1.88 | 1.86 | 1.78 | 1.82 | 1.86 | 23.97 | 24.95 | 26.05 | 0 | - - - | - - - | - - - | - - - | 22346 | 20938 | 20062 | 63345 | Over-range | 12336 | 10500 | 11455 | 34362 | 5414 | 5191 | 5208 | 15994 | 18707 | 18159 | 16437 | 53302 | 18707 | 18159 | 16437 | 53302 | - - - | - - - | - - - | - - -
5/9/2026 | 9:45:00 AM | 282.42 | 280.05 | 278.43 | 488.44 | 482.23 | 485.8 | 78.0429 | 73.4906 | 70.8746 | 0.2415 | 1.433 | 1.434 | 1.428 | 1.98 | 1.98 | 2.066 | Over-range | 60.01 | 18201 | 17619 | 15985 | 51805 | - - - | - - - | - - - | - - - | 18201 | 17619 | 15985 | 51805 | 10839 | 8832 | 9998 | 29669 | - - - | - - - | - - - | - - - | 10839 | 8832 | 9998 | 29669 | 21890 | 20418 | 19586 | 61894 | # # # | # # # | # # # | # # # | 0.832 | 0.863 | 0.816 | 0.837 | # # # | # # # | # # # | - - - | 0.858 | 0.892 | 0.846 | 0.866 | - - - | 0.573 | 1.94 | 1.89 | 1.84 | 1.78 | 1.82 | 1.87 | 24.09 | 25.25 | 26.27 | 0 | - - - | - - - | - - - | - - - | 21890 | 20418 | 19586 | 61894 | Over-range | 12143 | 10291 | 11298 | 33807 | 5376 | 5191 | 5168 | 15932 | 18274 | 17640 | 16002 | 51916 | 18274 | 17640 | 16002 | 51916 | - - - | - - - | - - - | - - -
5/9/2026 | 10:00:00 AM | 282.23 | 280.07 | 278.42 | 488.22 | 482.39 | 485.55 | 77.3745 | 72.9547 | 70.6144 | 0.2429 | 1.434 | 1.433 | 1.429 | 1.959 | 1.957 | 2.038 | Over-range | 60.01 | 18087 | 17516 | 15974 | 51578 | - - - | - - - | - - - | - - - | 18087 | 17516 | 15974 | 51578 | 10837 | 8973 | 10113 | 29923 | - - - | - - - | - - - | - - - | 10837 | 8973 | 10113 | 29923 | 21711 | 20294 | 19533 | 61538 | # # # | # # # | # # # | # # # | 0.833 | 0.863 | 0.818 | 0.838 | # # # | # # # | # # # | - - - | 0.857 | 0.89 | 0.844 | 0.864 | - - - | 0.58 | 1.93 | 1.87 | 1.81 | 1.77 | 1.79 | 1.85 | 22.94 | 23.94 | 24.83 | 0 | - - - | - - - | - - - | - - - | 21711 | 20294 | 19533 | 61538 | Over-range | 12002 | 10238 | 11232 | 33540 | 5088 | 4863 | 4822 | 14954 | 18104 | 17590 | 15985 | 51679 | 18104 | 17590 | 15985 | 51679 | - - - | - - - | - - - | - - -
5/9/2026 | 10:15:00 AM | 282.11 | 279.89 | 278.28 | 488.01 | 482.04 | 485.34 | 77.5231 | 72.9175 | 70.1155 | 0.2409 | 1.433 | 1.433 | 1.428 | 1.97 | 1.972 | 2.058 | Over-range | 60 | 18097 | 17545 | 15842 | 51485 | - - - | - - - | - - - | - - - | 18097 | 17545 | 15842 | 51485 | 10767 | 8728 | 9943 | 29438 | - - - | - - - | - - - | - - - | 10767 | 8728 | 9943 | 29438 | 21716 | 20245 | 19364 | 61326 | # # # | # # # | # # # | # # # | 0.833 | 0.867 | 0.818 | 0.84 | # # # | # # # | # # # | - - - | 0.858 | 0.895 | 0.846 | 0.867 | - - - | 0.572 | 1.92 | 1.87 | 1.83 | 1.77 | 1.79 | 1.85 | 23.57 | 24.67 | 25.7 | 0 | - - - | - - - | - - - | - - - | 21716 | 20245 | 19364 | 61326 | Over-range | 11996 | 10088 | 11123 | 33287 | 5214 | 4990 | 4917 | 15333 | 18094 | 17622 | 15871 | 51588 | 18094 | 17622 | 15871 | 51588 | - - - | - - - | - - - | - - -
5/9/2026 | 10:30:00 AM | 281.94 | 279.7 | 278.08 | 487.71 | 481.66 | 485.04 | 75.2294 | 70.7056 | 68.5224 | 0.2381 | 1.433 | 1.434 | 1.428 | 1.987 | 1.988 | 2.076 | Over-range | 60 | 17527 | 16910 | 15414 | 49851 | - - - | - - - | - - - | - - - | 17527 | 16910 | 15414 | 49851 | 10433 | 8572 | 9762 | 28767 | - - - | - - - | - - - | - - - | 10433 | 8572 | 9762 | 28767 | 21065 | 19621 | 18911 | 59597 | # # # | # # # | # # # | # # # | 0.832 | 0.862 | 0.815 | 0.837 | # # # | # # # | # # # | - - - | 0.858 | 0.891 | 0.844 | 0.864 | - - - | 0.577 | 1.91 | 1.85 | 1.82 | 1.75 | 1.78 | 1.84 | 24.14 | 25.23 | 26.12 | 0 | - - - | - - - | - - - | - - - | 21065 | 19621 | 18911 | 59597 | Over-range | 11678 | 9938 | 10946 | 32630 | 5171 | 4956 | 4878 | 15186 | 17517 | 16971 | 15465 | 49953 | 17517 | 16971 | 15465 | 49953 | - - - | - - - | - - - | - - -
5/9/2026 | 10:45:00 AM | 281.69 | 279.41 | 277.81 | 487.21 | 481.2 | 484.6 | 76.7608 | 72.3053 | 69.9528 | 0.2401 | 1.433 | 1.433 | 1.428 | 1.971 | 1.973 | 2.061 | Over-range | 60.02 | 17923 | 17340 | 15799 | 51061 | - - - | - - - | - - - | - - - | 17923 | 17340 | 15799 | 51061 | 10667 | 8762 | 9924 | 29353 | - - - | - - - | - - - | - - - | 10667 | 8762 | 9924 | 29353 | 21502 | 20070 | 19311 | 60883 | # # # | # # # | # # # | # # # | 0.834 | 0.864 | 0.818 | 0.839 | # # # | # # # | # # # | - - - | 0.858 | 0.891 | 0.846 | 0.865 | - - - | 0.575 | 1.91 | 1.86 | 1.81 | 1.75 | 1.78 | 1.83 | 23.34 | 24.3 | 25.33 | 0 | - - - | - - - | - - - | - - - | 21502 | 20070 | 19311 | 60883 | Over-range | 11864 | 10086 | 11090 | 33110 | 5125 | 4932 | 4883 | 15127 | 17942 | 17367 | 15847 | 51156 | 17942 | 17367 | 15847 | 51156 | - - - | - - - | - - - | - - -
5/9/2026 | 11:00:00 AM | 281.67 | 279.35 | 277.74 | 487.2 | 481.01 | 484.56 | 76.5369 | 71.6489 | 68.9377 | 0.2387 | 1.433 | 1.433 | 1.428 | 1.948 | 1.935 | 2.042 | Over-range | 60.01 | 17859 | 17267 | 15549 | 50675 | - - - | - - - | - - - | - - - | 17859 | 17267 | 15549 | 50675 | 10811 | 8690 | 9932 | 29433 | - - - | - - - | - - - | - - - | 10811 | 8690 | 9932 | 29433 | 21456 | 19905 | 19045 | 60406 | # # # | # # # | # # # | # # # | 0.832 | 0.868 | 0.816 | 0.839 | # # # | # # # | # # # | - - - | 0.855 | 0.891 | 0.841 | 0.863 | - - - | 0.581 | 1.89 | 1.83 | 1.83 | 1.74 | 1.78 | 1.82 | 22.06 | 22.94 | 23.9 | 0 | - - - | - - - | - - - | - - - | 21456 | 19905 | 19045 | 60406 | Over-range | 11883 | 9887 | 10986 | 32844 | 4849 | 4643 | 4619 | 14352 | 17921 | 17266 | 15576 | 50764 | 17921 | 17266 | 15576 | 50764 | - - - | - - - | - - - | - - -
5/9/2026 | 11:15:00 AM | 281.53 | 279.22 | 277.66 | 486.95 | 480.83 | 484.37 | 76.9689 | 72.1024 | 70.0014 | 0.2401 | 1.434 | 1.434 | 1.429 | 1.96 | 1.96 | 2.051 | Over-range | 60.01 | 17927 | 17240 | 15719 | 50886 | - - - | - - - | - - - | - - - | 17927 | 17240 | 15719 | 50886 | 10738 | 8814 | 10050 | 29602 | - - - | - - - | - - - | - - - | 10738 | 8814 | 10050 | 29602 | 21520 | 19971 | 19291 | 60782 | # # # | # # # | # # # | # # # | 0.833 | 0.863 | 0.815 | 0.837 | # # # | # # # | # # # | - - - | 0.857 | 0.889 | 0.841 | 0.863 | - - - | 0.582 | 1.89 | 1.85 | 1.84 | 1.75 | 1.78 | 1.84 | 22.96 | 23.91 | 24.87 | 0 | - - - | - - - | - - - | - - - | 21520 | 19971 | 19291 | 60782 | Over-range | 11897 | 10069 | 11170 | 33211 | 5041 | 4788 | 4798 | 14822 | 17963 | 17295 | 15725 | 50982 | 17963 | 17295 | 15725 | 50982 | - - - | - - - | - - - | - - -
5/9/2026 | 11:30:00 AM | 281.45 | 279.23 | 277.59 | 486.87 | 480.87 | 484.18 | 77.1223 | 72.9496 | 70.1649 | 0.2421 | 1.434 | 1.434 | 1.429 | 1.963 | 1.959 | 2.05 | Over-range | 60.02 | 17992 | 17519 | 15893 | 51403 | - - - | - - - | - - - | - - - | 17992 | 17519 | 15893 | 51403 | 10754 | 8831 | 9883 | 29467 | - - - | - - - | - - - | - - - | 10754 | 8831 | 9883 | 29467 | 21573 | 20222 | 19344 | 61139 | # # # | # # # | # # # | # # # | 0.834 | 0.866 | 0.822 | 0.841 | # # # | # # # | # # # | - - - | 0.858 | 0.892 | 0.848 | 0.866 | - - - | 0.573 | 1.91 | 1.84 | 1.82 | 1.75 | 1.78 | 1.84 | 22.95 | 23.82 | 24.84 | 0 | - - - | - - - | - - - | - - - | 21573 | 20222 | 19344 | 61139 | Over-range | 11896 | 10091 | 11017 | 33075 | 5024 | 4821 | 4809 | 14839 | 18052 | 17548 | 15902 | 51501 | 18052 | 17548 | 15902 | 51501 | - - - | - - - | - - - | - - -
5/9/2026 | 11:45:00 AM | 281.26 | 278.96 | 277.39 | 486.5 | 480.36 | 483.89 | 78.4983 | 73.9223 | 70.8658 | 0.2435 | 1.434 | 1.435 | 1.43 | 1.97 | 1.972 | 2.065 | Over-range | 60.01 | 18230 | 17713 | 15950 | 51893 | - - - | - - - | - - - | - - - | 18230 | 17713 | 15950 | 51893 | 10867 | 8779 | 9968 | 29615 | - - - | - - - | - - - | - - - | 10867 | 8779 | 9968 | 29615 | 21899 | 20431 | 19485 | 61815 | # # # | # # # | # # # | # # # | 0.832 | 0.867 | 0.819 | 0.84 | # # # | # # # | # # # | - - - | 0.857 | 0.895 | 0.847 | 0.866 | - - - | 0.571 | 1.91 | 1.86 | 1.83 | 1.76 | 1.79 | 1.84 | 23.53 | 24.52 | 25.67 | 0 | - - - | - - - | - - - | - - - | 21899 | 20431 | 19485 | 61815 | Over-range | 12119 | 10159 | 11176 | 33538 | 5265 | 5018 | 4958 | 15462 | 18224 | 17792 | 15979 | 51995 | 18224 | 17792 | 15979 | 51995 | - - - | - - - | - - - | - - -
5/9/2026 | 12:00:00 PM | 281.05 | 278.83 | 277.24 | 486.19 | 480.15 | 483.59 | 76.9177 | 72.3964 | 70.1474 | 0.241 | 1.434 | 1.434 | 1.429 | 1.955 | 1.955 | 2.046 | Over-range | 60.02 | 17941 | 17341 | 15828 | 51111 | - - - | - - - | - - - | - - - | 17941 | 17341 | 15828 | 51111 | 10703 | 8838 | 9985 | 29526 | - - - | - - - | - - - | - - - | 10703 | 8838 | 9985 | 29526 | 21497 | 20055 | 19327 | 60879 | # # # | # # # | # # # | # # # | 0.835 | 0.865 | 0.819 | 0.84 | # # # | # # # | # # # | - - - | 0.858 | 0.89 | 0.845 | 0.864 | - - - | 0.578 | 1.9 | 1.87 | 1.82 | 1.75 | 1.79 | 1.84 | 22.65 | 23.46 | 24.49 | 0 | - - - | - - - | - - - | - - - | 21497 | 20055 | 19327 | 60879 | Over-range | 11835 | 10063 | 11079 | 33046 | 4988 | 4752 | 4738 | 14661 | 17961 | 17388 | 15856 | 51204 | 17961 | 17388 | 15856 | 51204 | - - - | - - - | - - - | - - -
5/9/2026 | 12:15:00 PM | 281.15 | 278.85 | 277.3 | 486.27 | 480.22 | 483.75 | 76.9923 | 72.6171 | 70.1664 | 0.2417 | 1.435 | 1.435 | 1.43 | 1.978 | 1.978 | 2.064 | Over-range | 60.01 | 17946 | 17383 | 15843 | 51173 | - - - | - - - | - - - | - - - | 17946 | 17383 | 15843 | 51173 | 10630 | 8747 | 9889 | 29266 | - - - | - - - | - - - | - - - | 10630 | 8747 | 9889 | 29266 | 21512 | 20105 | 19326 | 60943 | # # # | # # # | # # # | # # # | 0.834 | 0.865 | 0.82 | 0.84 | # # # | # # # | # # # | - - - | 0.859 | 0.893 | 0.848 | 0.867 | - - - | 0.572 | 1.87 | 1.85 | 1.81 | 1.74 | 1.77 | 1.83 | 23.67 | 24.59 | 25.53 | 0 | - - - | - - - | - - - | - - - | 21512 | 20105 | 19326 | 60943 | Over-range | 11854 | 10089 | 11057 | 33068 | 5176 | 4958 | 4876 | 15189 | 17933 | 17437 | 15897 | 51267 | 17933 | 17437 | 15897 | 51267 | - - - | - - - | - - - | - - -
5/9/2026 | 12:30:00 PM | 281.22 | 278.9 | 277.31 | 486.45 | 480.18 | 483.84 | 78.1225 | 73.499 | 70.5239 | 0.24 | 1.434 | 1.434 | 1.429 | 1.98 | 1.977 | 2.071 | Over-range | 60 | 18227 | 17687 | 15945 | 51859 | - - - | - - - | - - - | - - - | 18227 | 17687 | 15945 | 51859 | 10814 | 8691 | 9897 | 29402 | - - - | - - - | - - - | - - - | 10814 | 8691 | 9897 | 29402 | 21853 | 20374 | 19443 | 61670 | # # # | # # # | # # # | # # # | 0.834 | 0.868 | 0.82 | 0.841 | # # # | # # # | # # # | - - - | 0.859 | 0.896 | 0.849 | 0.868 | - - - | 0.567 | 1.88 | 1.83 | 1.82 | 1.74 | 1.77 | 1.81 | 23.77 | 24.86 | 25.84 | 0 | - - - | - - - | - - - | - - - | 21853 | 20374 | 19443 | 61670 | Over-range | 12048 | 10099 | 11115 | 33344 | 5248 | 5084 | 4999 | 15549 | 18265 | 17684 | 16012 | 51961 | 18265 | 17684 | 16012 | 51961 | - - - | - - - | - - - | - - -
5/9/2026 | 12:45:00 PM | 281.16 | 278.9 | 277.3 | 486.37 | 480.21 | 483.77 | 77.7701 | 73.1359 | 70.9318 | 0.2409 | 1.435 | 1.434 | 1.43 | 1.965 | 1.963 | 2.05 | Over-range | 60 | 18073 | 17427 | 15922 | 51423 | - - - | - - - | - - - | - - - | 18073 | 17427 | 15922 | 51423 | 10773 | 8860 | 10064 | 29698 | - - - | - - - | - - - | - - - | 10773 | 8860 | 10064 | 29698 | 21687 | 20201 | 19494 | 61383 | # # # | # # # | # # # | # # # | 0.833 | 0.863 | 0.817 | 0.838 | # # # | # # # | # # # | - - - | 0.858 | 0.889 | 0.844 | 0.864 | - - - | 0.578 | 1.88 | 1.84 | 1.79 | 1.73 | 1.76 | 1.81 | 23.19 | 24.21 | 25.04 | 0 | - - - | - - - | - - - | - - - | 21687 | 20201 | 19494 | 61383 | Over-range | 11972 | 10195 | 11229 | 33465 | 5125 | 4956 | 4889 | 15161 | 18106 | 17424 | 15989 | 51519 | 18106 | 17424 | 15989 | 51519 | - - - | - - - | - - - | - - -
5/9/2026 | 1:00:00 PM | 281.19 | 278.88 | 277.3 | 486.33 | 480.22 | 483.79 | 79.2886 | 74.7492 | 72.3568 | 0.2441 | 1.435 | 1.435 | 1.43 | 1.969 | 1.97 | 2.049 | Over-range | 60.01 | 18514 | 17903 | 16352 | 52769 | - - - | - - - | - - - | - - - | 18514 | 17903 | 16352 | 52769 | 10927 | 9016 | 10143 | 30086 | - - - | - - - | - - - | - - - | 10927 | 9016 | 10143 | 30086 | 22142 | 20683 | 19914 | 62739 | # # # | # # # | # # # | # # # | 0.836 | 0.866 | 0.821 | 0.841 | # # # | # # # | # # # | - - - | 0.861 | 0.892 | 0.848 | 0.867 | - - - | 0.57 | 1.89 | 1.81 | 1.77 | 1.71 | 1.75 | 1.8 | 23.25 | 24.38 | 25.29 | 0 | - - - | - - - | - - - | - - - | 22142 | 20683 | 19914 | 62739 | Over-range | 12137 | 10346 | 11354 | 33906 | 5215 | 5012 | 5040 | 15446 | 18603 | 17941 | 16328 | 52871 | 18603 | 17941 | 16328 | 52871 | - - - | - - - | - - - | - - -
5/9/2026 | 1:15:00 PM | 281.42 | 279.12 | 277.53 | 486.81 | 480.58 | 484.19 | 76.8068 | 72.2049 | 69.6039 | 0.2391 | 1.435 | 1.434 | 1.43 | 1.984 | 1.978 | 2.076 | Over-range | 60 | 17917 | 17334 | 15711 | 50963 | - - - | - - - | - - - | - - - | 17917 | 17334 | 15711 | 50963 | 10590 | 8620 | 9780 | 28991 | - - - | - - - | - - - | - - - | 10590 | 8620 | 9780 | 28991 | 21488 | 20019 | 19193 | 60700 | # # # | # # # | # # # | # # # | 0.834 | 0.866 | 0.819 | 0.84 | # # # | # # # | # # # | - - - | 0.86 | 0.895 | 0.847 | 0.867 | - - - | 0.569 | 1.82 | 1.78 | 1.76 | 1.69 | 1.72 | 1.76 | 24.08 | 25.04 | 26.12 | 0 | - - - | - - - | - - - | - - - | 21488 | 20019 | 19193 | 60700 | Over-range | 11853 | 10000 | 11014 | 32942 | 5249 | 5002 | 4994 | 15438 | 17958 | 17396 | 15704 | 51058 | 17958 | 17396 | 15704 | 51058 | - - - | - - - | - - - | - - -
5/9/2026 | 1:30:00 PM | 281.38 | 278.97 | 277.43 | 486.64 | 480.33 | 484.11 | 75.7564 | 70.8668 | 68.696 | 0.2377 | 1.435 | 1.433 | 1.429 | 1.991 | 1.983 | 2.082 | Over-range | 60.01 | 17629 | 16944 | 15407 | 49980 | - - - | - - - | - - - | - - - | 17629 | 16944 | 15407 | 49980 | 10511 | 8552 | 9822 | 28885 | - - - | - - - | - - - | - - - | 10511 | 8552 | 9822 | 28885 | 21192 | 19634 | 18934 | 59761 | # # # | # # # | # # # | # # # | 0.832 | 0.863 | 0.814 | 0.836 | # # # | # # # | # # # | - - - | 0.858 | 0.892 | 0.843 | 0.864 | - - - | 0.578 | 1.84 | 1.76 | 1.73 | 1.69 | 1.72 | 1.75 | 24.21 | 25.22 | 26.12 | 0 | - - - | - - - | - - - | - - - | 21192 | 19634 | 18934 | 59761 | Over-range | 11754 | 9910 | 10997 | 32737 | 5206 | 4953 | 4890 | 15246 | 17620 | 16997 | 15460 | 50077 | 17620 | 16997 | 15460 | 50077 | - - - | - - - | - - - | - - -
5/9/2026 | 1:45:00 PM | 281.44 | 279.19 | 277.59 | 486.83 | 480.79 | 484.21 | 76.6865 | 72.1624 | 69.5532 | 0.2413 | 1.434 | 1.433 | 1.429 | 1.972 | 1.962 | 2.057 | Over-range | 60 | 17861 | 17301 | 15682 | 50844 | - - - | - - - | - - - | - - - | 17861 | 17301 | 15682 | 50844 | 10667 | 8694 | 9880 | 29241 | - - - | - - - | - - - | - - - | 10667 | 8694 | 9880 | 29241 | 21447 | 20000 | 19172 | 60619 | # # # | # # # | # # # | # # # | 0.833 | 0.865 | 0.818 | 0.839 | # # # | # # # | # # # | - - - | 0.857 | 0.892 | 0.845 | 0.865 | - - - | 0.575 | 1.82 | 1.76 | 1.71 | 1.68 | 1.7 | 1.74 | 23.22 | 24.19 | 25.04 | 0 | - - - | - - - | - - - | - - - | 21447 | 20000 | 19172 | 60619 | Over-range | 11856 | 10012 | 11013 | 32956 | 5093 | 4889 | 4788 | 14974 | 17859 | 17340 | 15738 | 50936 | 17859 | 17340 | 15738 | 50936 | - - - | - - - | - - - | - - -
5/9/2026 | 2:00:00 PM | 281.53 | 279.21 | 277.71 | 486.92 | 480.85 | 484.45 | 76.2608 | 71.3788 | 69.0841 | 0.2384 | 1.434 | 1.432 | 1.429 | 1.962 | 1.95 | 2.056 | Over-range | 60.01 | 17708 | 17050 | 15479 | 50236 | - - - | - - - | - - - | - - - | 17708 | 17050 | 15479 | 50236 | 10700 | 8691 | 9974 | 29365 | - - - | - - - | - - - | - - - | 10700 | 8691 | 9974 | 29365 | 21287 | 19730 | 19012 | 60029 | # # # | # # # | # # # | # # # | 0.832 | 0.864 | 0.814 | 0.837 | # # # | # # # | # # # | - - - | 0.854 | 0.889 | 0.84 | 0.861 | - - - | 0.585 | 1.76 | 1.71 | 1.66 | 1.63 | 1.64 | 1.68 | 22.63 | 23.46 | 24.35 | 0 | - - - | - - - | - - - | - - - | 21287 | 19730 | 19012 | 60029 | Over-range | 11804 | 9912 | 11024 | 32821 | 4893 | 4679 | 4606 | 14399 | 17707 | 17058 | 15556 | 50320 | 17707 | 17058 | 15556 | 50320 | - - - | - - - | - - - | - - -
5/9/2026 | 2:15:00 PM | 281.44 | 279.15 | 277.62 | 486.8 | 480.73 | 484.29 | 75.2316 | 70.3238 | 68.2172 | 0.2365 | 1.434 | 1.432 | 1.429 | 1.968 | 1.958 | 2.06 | Over-range | 60.01 | 17518 | 16838 | 15310 | 49667 | - - - | - - - | - - - | - - - | 17518 | 16838 | 15310 | 49667 | 10561 | 8595 | 9883 | 29039 | - - - | - - - | - - - | - - - | 10561 | 8595 | 9883 | 29039 | 21049 | 19493 | 18816 | 59358 | # # # | # # # | # # # | # # # | 0.832 | 0.864 | 0.814 | 0.837 | # # # | # # # | # # # | - - - | 0.855 | 0.89 | 0.84 | 0.862 | - - - | 0.585 | 1.75 | 1.69 | 1.65 | 1.62 | 1.63 | 1.66 | 22.87 | 23.76 | 24.64 | 0 | - - - | - - - | - - - | - - - | 21049 | 19493 | 18816 | 59358 | Over-range | 11663 | 9812 | 10927 | 32480 | 4886 | 4671 | 4597 | 14366 | 17510 | 16857 | 15384 | 49750 | 17510 | 16857 | 15384 | 49750 | - - - | - - - | - - - | - - -
5/9/2026 | 2:30:00 PM | 281.2 | 278.95 | 277.44 | 486.36 | 480.46 | 483.93 | 77.3702 | 72.4429 | 70.2841 | 0.2403 | 1.435 | 1.433 | 1.43 | 1.963 | 1.96 | 2.056 | Over-range | 60 | 18024 | 17342 | 15792 | 51158 | - - - | - - - | - - - | - - - | 18024 | 17342 | 15792 | 51158 | 10764 | 8792 | 10087 | 29643 | - - - | - - - | - - - | - - - | 10764 | 8792 | 10087 | 29643 | 21610 | 20050 | 19352 | 61012 | # # # | # # # | # # # | # # # | 0.834 | 0.865 | 0.816 | 0.839 | # # # | # # # | # # # | - - - | 0.857 | 0.891 | 0.842 | 0.864 | - - - | 0.579 | 1.76 | 1.7 | 1.66 | 1.63 | 1.63 | 1.67 | 22.78 | 23.78 | 24.68 | 0 | - - - | - - - | - - - | - - - | 21610 | 20050 | 19352 | 61012 | Over-range | 11912 | 10051 | 11174 | 33215 | 5032 | 4804 | 4741 | 14786 | 18012 | 17392 | 15843 | 51247 | 18012 | 17392 | 15843 | 51247 | - - - | - - - | - - - | - - -
5/9/2026 | 2:45:00 PM | 281.01 | 278.66 | 277.18 | 485.98 | 479.93 | 483.54 | 77.6377 | 72.5652 | 70.5909 | 0.2414 | 1.435 | 1.433 | 1.43 | 1.965 | 1.958 | 2.053 | Over-range | 60.01 | 18073 | 17326 | 15823 | 51222 | - - - | - - - | - - - | - - - | 18073 | 17326 | 15823 | 51222 | 10762 | 8812 | 10133 | 29706 | - - - | - - - | - - - | - - - | 10762 | 8812 | 10133 | 29706 | 21672 | 20065 | 19425 | 61162 | # # # | # # # | # # # | # # # | 0.834 | 0.864 | 0.815 | 0.838 | # # # | # # # | # # # | - - - | 0.857 | 0.89 | 0.841 | 0.863 | - - - | 0.58 | 1.75 | 1.7 | 1.66 | 1.62 | 1.63 | 1.67 | 22.92 | 23.9 | 24.71 | 0 | - - - | - - - | - - - | - - - | 21672 | 20065 | 19425 | 61162 | Over-range | 11944 | 10096 | 11250 | 33369 | 5095 | 4846 | 4802 | 14952 | 18068 | 17387 | 15864 | 51318 | 18068 | 17387 | 15864 | 51318 | - - - | - - - | - - - | - - -
5/9/2026 | 3:00:00 PM | 280.88 | 278.61 | 277.11 | 485.81 | 479.83 | 483.39 | 75.9001 | 70.8393 | 68.9219 | 0.2372 | 1.436 | 1.434 | 1.431 | 1.969 | 1.955 | 2.055 | Over-range | 60 | 17671 | 16942 | 15453 | 50065 | - - - | - - - | - - - | - - - | 17671 | 16942 | 15453 | 50065 | 10601 | 8678 | 9981 | 29259 | - - - | - - - | - - - | - - - | 10601 | 8678 | 9981 | 29259 | 21206 | 19616 | 18986 | 59808 | # # # | # # # | # # # | # # # | 0.833 | 0.864 | 0.814 | 0.837 | # # # | # # # | # # # | - - - | 0.857 | 0.89 | 0.84 | 0.862 | - - - | 0.584 | 1.74 | 1.71 | 1.66 | 1.62 | 1.63 | 1.67 | 22.84 | 23.71 | 24.53 | 0 | - - - | - - - | - - - | - - - | 21206 | 19616 | 18986 | 59808 | Over-range | 11718 | 9878 | 11024 | 32697 | 4940 | 4669 | 4629 | 14442 | 17663 | 17006 | 15488 | 50157 | 17663 | 17006 | 15488 | 50157 | - - - | - - - | - - - | - - -
5/9/2026 | 3:15:00 PM | 280.77 | 278.54 | 277.08 | 485.62 | 479.8 | 483.25 | 76.3965 | 71.5693 | 69.4307 | 0.238 | 1.436 | 1.434 | 1.431 | 1.957 | 1.946 | 2.047 | Over-range | 60 | 17751 | 17098 | 15573 | 50423 | - - - | - - - | - - - | - - - | 17751 | 17098 | 15573 | 50423 | 10720 | 8751 | 9990 | 29461 | - - - | - - - | - - - | - - - | 10720 | 8751 | 9990 | 29461 | 21305 | 19779 | 19091 | 60175 | # # # | # # # | # # # | # # # | 0.833 | 0.865 | 0.816 | 0.838 | # # # | # # # | # # # | - - - | 0.856 | 0.888 | 0.841 | 0.862 | - - - | 0.584 | 1.74 | 1.7 | 1.65 | 1.62 | 1.63 | 1.67 | 22.17 | 23.1 | 23.94 | 0 | - - - | - - - | - - - | - - - | 21305 | 19779 | 19091 | 60175 | Over-range | 11773 | 9930 | 11031 | 32811 | 4789 | 4620 | 4599 | 14218 | 17809 | 17076 | 15622 | 50507 | 17809 | 17076 | 15622 | 50507 | - - - | - - - | - - - | - - -
5/9/2026 | 3:30:00 PM | 280.58 | 278.29 | 276.73 | 485.28 | 479.24 | 482.77 | 77.0178 | 72.1806 | 69.5827 | 0.2381 | 1.436 | 1.434 | 1.431 | 1.945 | 1.929 | 2.036 | Over-range | 60.01 | 17891 | 17298 | 15631 | 50820 | - - - | - - - | - - - | - - - | 17891 | 17298 | 15631 | 50820 | 10891 | 8804 | 10051 | 29745 | - - - | - - - | - - - | - - - | 10891 | 8804 | 10051 | 29745 | 21482 | 19948 | 19130 | 60560 | # # # | # # # | # # # | # # # | 0.833 | 0.867 | 0.817 | 0.839 | # # # | # # # | # # # | - - - | 0.854 | 0.89 | 0.841 | 0.862 | - - - | 0.585 | 1.76 | 1.7 | 1.64 | 1.61 | 1.63 | 1.66 | 21.57 | 22.36 | 23.23 | 0 | - - - | - - - | - - - | - - - | 21482 | 19948 | 19130 | 60560 | Over-range | 11886 | 9925 | 11019 | 32915 | 4691 | 4518 | 4451 | 13899 | 17923 | 17279 | 15700 | 50903 | 17923 | 17279 | 15700 | 50903 | - - - | - - - | - - - | - - -
5/9/2026 | 3:45:00 PM | 280.63 | 278.27 | 276.79 | 485.32 | 479.2 | 482.92 | 76.9617 | 72.0461 | 69.9332 | 0.2372 | 1.436 | 1.434 | 1.431 | 1.979 | 1.975 | 2.071 | Over-range | 60 | 17852 | 17153 | 15639 | 50644 | - - - | - - - | - - - | - - - | 17852 | 17153 | 15639 | 50644 | 10664 | 8680 | 9946 | 29290 | - - - | - - - | - - - | - - - | 10664 | 8680 | 9946 | 29290 | 21432 | 19868 | 19194 | 60494 | # # # | # # # | # # # | # # # | 0.833 | 0.863 | 0.815 | 0.837 | # # # | # # # | # # # | - - - | 0.858 | 0.89 | 0.843 | 0.864 | - - - | 0.578 | 1.73 | 1.7 | 1.65 | 1.61 | 1.63 | 1.65 | 23.49 | 24.52 | 25.42 | 0 | - - - | - - - | - - - | - - - | 21432 | 19868 | 19194 | 60494 | Over-range | 11845 | 10006 | 11113 | 33040 | 5072 | 4899 | 4878 | 15053 | 17913 | 17131 | 15693 | 50737 | 17913 | 17131 | 15693 | 50737 | - - - | - - - | - - - | - - -
5/9/2026 | 4:00:00 PM | 280.61 | 278.29 | 276.74 | 485.37 | 479.15 | 482.84 | 77.5336 | 72.8178 | 69.8598 | 0.2372 | 1.436 | 1.434 | 1.431 | 1.971 | 1.962 | 2.069 | Over-range | 60.01 | 18033 | 17489 | 15741 | 51263 | - - - | - - - | - - - | - - - | 18033 | 17489 | 15741 | 51263 | 10800 | 8652 | 9851 | 29303 | - - - | - - - | - - - | - - - | 10800 | 8652 | 9851 | 29303 | 21637 | 20132 | 19213 | 60981 | # # # | # # # | # # # | # # # | 0.833 | 0.869 | 0.819 | 0.841 | # # # | # # # | # # # | - - - | 0.858 | 0.895 | 0.847 | 0.867 | - - - | 0.572 | 1.74 | 1.68 | 1.61 | 1.6 | 1.61 | 1.64 | 23.17 | 24.14 | 25.24 | 0 | - - - | - - - | - - - | - - - | 21637 | 20132 | 19213 | 60981 | Over-range | 11950 | 9959 | 11006 | 33001 | 5053 | 4875 | 4852 | 15008 | 18111 | 17464 | 15779 | 51354 | 18111 | 17464 | 15779 | 51354 | - - - | - - - | - - - | - - -
5/9/2026 | 4:15:00 PM | 280.56 | 278.23 | 276.71 | 485.22 | 479.18 | 482.72 | 76.375 | 71.6893 | 69.6401 | 0.2378 | 1.436 | 1.434 | 1.431 | 1.982 | 1.979 | 2.077 | Over-range | 60.01 | 17716 | 17047 | 15590 | 50353 | - - - | - - - | - - - | - - - | 17716 | 17047 | 15590 | 50353 | 10517 | 8626 | 9832 | 28975 | - - - | - - - | - - - | - - - | 10517 | 8626 | 9832 | 28975 | 21243 | 19751 | 19095 | 60089 | # # # | # # # | # # # | # # # | 0.834 | 0.863 | 0.817 | 0.838 | # # # | # # # | # # # | - - - | 0.859 | 0.89 | 0.845 | 0.865 | - - - | 0.575 | 1.74 | 1.67 | 1.61 | 1.6 | 1.59 | 1.64 | 23.8 | 24.84 | 25.69 | 0 | - - - | - - - | - - - | - - - | 21243 | 19751 | 19095 | 60089 | Over-range | 11714 | 9959 | 11011 | 32755 | 5066 | 4896 | 4875 | 15025 | 17773 | 17026 | 15641 | 50440 | 17773 | 17026 | 15641 | 50440 | - - - | - - - | - - - | - - -
5/9/2026 | 4:30:00 PM | 280.5 | 278.21 | 276.69 | 485.17 | 479.11 | 482.68 | 79.0202 | 74.147 | 72.0783 | 0.2425 | 1.435 | 1.434 | 1.431 | 1.964 | 1.959 | 2.057 | Over-range | 60 | 18416 | 17718 | 16222 | 52356 | - - - | - - - | - - - | - - - | 18416 | 17718 | 16222 | 52356 | 10930 | 9033 | 10252 | 30215 | - - - | - - - | - - - | - - - | 10930 | 9033 | 10252 | 30215 | 22035 | 20484 | 19816 | 62334 | # # # | # # # | # # # | # # # | 0.836 | 0.865 | 0.819 | 0.84 | # # # | # # # | # # # | - - - | 0.86 | 0.89 | 0.844 | 0.865 | - - - | 0.577 | 1.72 | 1.67 | 1.61 | 1.59 | 1.59 | 1.62 | 22.86 | 23.65 | 24.6 | 0 | - - - | - - - | - - - | - - - | 22035 | 20484 | 19816 | 62334 | Over-range | 12091 | 10270 | 11370 | 33803 | 5109 | 4828 | 4858 | 14983 | 18454 | 17778 | 16216 | 52447 | 18454 | 17778 | 16216 | 52447 | - - - | - - - | - - - | - - -
5/9/2026 | 4:45:00 PM | 280.41 | 278.1 | 276.56 | 485.01 | 478.87 | 482.47 | 78.112 | 73.2889 | 70.5975 | 0.2397 | 1.436 | 1.434 | 1.431 | 1.986 | 1.981 | 2.079 | Over-range | 59.99 | 18126 | 17510 | 15833 | 51468 | - - - | - - - | - - - | - - - | 18126 | 17510 | 15833 | 51468 | 10743 | 8655 | 9876 | 29274 | - - - | - - - | - - - | - - - | 10743 | 8655 | 9876 | 29274 | 21751 | 20217 | 19375 | 61343 | # # # | # # # | # # # | # # # | 0.833 | 0.866 | 0.817 | 0.839 | # # # | # # # | # # # | - - - | 0.859 | 0.894 | 0.846 | 0.867 | - - - | 0.569 | 1.73 | 1.69 | 1.64 | 1.61 | 1.61 | 1.65 | 23.88 | 25.02 | 26.04 | 0 | - - - | - - - | - - - | - - - | 21751 | 20217 | 19375 | 61343 | Over-range | 12006 | 10079 | 11149 | 33316 | 5272 | 5088 | 5092 | 15667 | 18222 | 17511 | 15830 | 51563 | 18222 | 17511 | 15830 | 51563 | - - - | - - - | - - - | - - -
5/9/2026 | 5:00:00 PM | 280.39 | 277.98 | 276.47 | 484.86 | 478.71 | 482.42 | 76.6232 | 71.9602 | 69.9674 | 0.2367 | 1.436 | 1.434 | 1.431 | 1.998 | 2.001 | 2.092 | Over-range | 60.01 | 17859 | 17172 | 15739 | 50769 | - - - | - - - | - - - | - - - | 17859 | 17172 | 15739 | 50769 | 10399 | 8534 | 9755 | 28688 | - - - | - - - | - - - | - - - | 10399 | 8534 | 9755 | 28688 | 21356 | 19866 | 19219 | 60441 | # # # | # # # | # # # | # # # | 0.836 | 0.864 | 0.819 | 0.84 | # # # | # # # | # # # | - - - | 0.863 | 0.894 | 0.85 | 0.869 | - - - | 0.565 | 1.74 | 1.67 | 1.64 | 1.6 | 1.61 | 1.65 | 24.74 | 25.76 | 26.7 | 0 | - - - | - - - | - - - | - - - | 21356 | 19866 | 19219 | 60441 | Over-range | 11705 | 9979 | 11020 | 32771 | 5313 | 5117 | 5070 | 15673 | 17879 | 17182 | 15810 | 50871 | 17879 | 17182 | 15810 | 50871 | - - - | - - - | - - - | - - -
5/9/2026 | 5:15:00 PM | 280.63 | 278.35 | 276.75 | 485.41 | 479.3 | 482.81 | 79.218 | 74.823 | 72.3754 | 0.2422 | 1.435 | 1.434 | 1.431 | 1.992 | 1.985 | 2.079 | Over-range | 60.01 | 18464 | 17892 | 16350 | 52706 | - - - | - - - | - - - | - - - | 18464 | 17892 | 16350 | 52706 | 10847 | 8990 | 10085 | 29922 | - - - | - - - | - - - | - - - | 10847 | 8990 | 10085 | 29922 | 22111 | 20697 | 19911 | 62719 | # # # | # # # | # # # | # # # | 0.835 | 0.865 | 0.821 | 0.84 | # # # | # # # | # # # | - - - | 0.861 | 0.893 | 0.85 | 0.868 | - - - | 0.568 | 1.74 | 1.67 | 1.6 | 1.59 | 1.59 | 1.62 | 24.19 | 25.02 | 26.05 | 0 | - - - | - - - | - - - | - - - | 22111 | 20697 | 19911 | 62719 | Over-range | 12157 | 10392 | 11352 | 33967 | 5429 | 5156 | 5155 | 15905 | 18497 | 17972 | 16339 | 52808 | 18497 | 17972 | 16339 | 52808 | - - - | - - - | - - - | - - -
5/9/2026 | 5:30:00 PM | 280.54 | 278.31 | 276.78 | 485.28 | 479.32 | 482.75 | 78.5946 | 74.1816 | 71.4105 | 0.2415 | 1.436 | 1.434 | 1.431 | 1.996 | 1.995 | 2.089 | Over-range | 60.01 | 18255 | 17722 | 16082 | 52059 | - - - | - - - | - - - | - - - | 18255 | 17722 | 16082 | 52059 | 10729 | 8755 | 9865 | 29349 | - - - | - - - | - - - | - - - | 10729 | 8755 | 9865 | 29349 | 21884 | 20467 | 19606 | 61957 | # # # | # # # | # # # | # # # | 0.834 | 0.866 | 0.82 | 0.84 | # # # | # # # | # # # | - - - | 0.862 | 0.895 | 0.85 | 0.869 | - - - | 0.564 | 1.74 | 1.69 | 1.63 | 1.61 | 1.61 | 1.65 | 24.6 | 25.65 | 26.8 | 0 | - - - | - - - | - - - | - - - | 21884 | 20467 | 19606 | 61957 | Over-range | 12059 | 10225 | 11199 | 33556 | 5420 | 5207 | 5227 | 16039 | 18339 | 17757 | 16065 | 52160 | 18339 | 17757 | 16065 | 52160 | - - - | - - - | - - - | - - -
5/9/2026 | 5:45:00 PM | 280.73 | 278.67 | 277.1 | 485.7 | 479.99 | 483.15 | 76.3668 | 71.8377 | 69.9707 | 0.238 | 1.436 | 1.434 | 1.431 | 1.998 | 1.995 | 2.084 | Over-range | 60.01 | 17748 | 17088 | 15701 | 50537 | - - - | - - - | - - - | - - - | 17748 | 17088 | 15701 | 50537 | 10511 | 8710 | 9890 | 29111 | - - - | - - - | - - - | - - - | 10511 | 8710 | 9890 | 29111 | 21304 | 19868 | 19256 | 60428 | # # # | # # # | # # # | # # # | 0.833 | 0.86 | 0.815 | 0.836 | # # # | # # # | # # # | - - - | 0.86 | 0.889 | 0.845 | 0.865 | - - - | 0.576 | 1.72 | 1.69 | 1.61 | 1.6 | 1.6 | 1.64 | 24.28 | 25.35 | 26.15 | 0 | - - - | - - - | - - - | - - - | 21304 | 19868 | 19256 | 60428 | Over-range | 11767 | 10112 | 11128 | 33071 | 5209 | 5061 | 5023 | 15463 | 17810 | 17072 | 15752 | 50635 | 17810 | 17072 | 15752 | 50635 | - - - | - - - | - - - | - - -
5/9/2026 | 6:00:00 PM | 280.71 | 278.59 | 277 | 485.62 | 479.82 | 483.05 | 76.5903 | 72.0023 | 69.9931 | 0.2402 | 1.435 | 1.434 | 1.431 | 1.972 | 1.959 | 2.061 | Over-range | 60.02 | 17840 | 17209 | 15758 | 50807 | - - - | - - - | - - - | - - - | 17840 | 17209 | 15758 | 50807 | 10650 | 8829 | 10018 | 29497 | - - - | - - - | - - - | - - - | 10650 | 8829 | 10018 | 29497 | 21381 | 19931 | 19267 | 60579 | # # # | # # # | # # # | # # # | 0.834 | 0.863 | 0.818 | 0.839 | # # # | # # # | # # # | - - - | 0.857 | 0.889 | 0.843 | 0.863 | - - - | 0.581 | 1.72 | 1.66 | 1.6 | 1.59 | 1.58 | 1.62 | 22.78 | 23.53 | 24.34 | 0 | - - - | - - - | - - - | - - - | 21381 | 19931 | 19267 | 60579 | Over-range | 11777 | 10044 | 11076 | 32965 | 4965 | 4727 | 4659 | 14531 | 17823 | 17254 | 15812 | 50889 | 17823 | 17254 | 15812 | 50889 | - - - | - - - | - - - | - - -
5/9/2026 | 6:15:00 PM | 280.87 | 278.81 | 277.2 | 485.99 | 480.17 | 483.35 | 76.2745 | 71.3908 | 69.1238 | 0.2368 | 1.435 | 1.434 | 1.431 | 1.966 | 1.95 | 2.058 | Over-range | 60.02 | 17679 | 17035 | 15458 | 50173 | - - - | - - - | - - - | - - - | 17679 | 17035 | 15458 | 50173 | 10692 | 8696 | 9977 | 29365 | - - - | - - - | - - - | - - - | 10692 | 8696 | 9977 | 29365 | 21249 | 19715 | 18989 | 59953 | # # # | # # # | # # # | # # # | 0.832 | 0.864 | 0.814 | 0.837 | # # # | # # # | # # # | - - - | 0.854 | 0.889 | 0.84 | 0.861 | - - - | 0.585 | 1.72 | 1.64 | 1.61 | 1.58 | 1.58 | 1.62 | 22.57 | 23.49 | 24.24 | 0 | - - - | - - - | - - - | - - - | 21249 | 19715 | 18989 | 59953 | Over-range | 11778 | 9910 | 11015 | 32783 | 4854 | 4673 | 4586 | 14336 | 17692 | 17039 | 15526 | 50257 | 17692 | 17039 | 15526 | 50257 | - - - | - - - | - - - | - - -
5/9/2026 | 6:30:00 PM | 280.87 | 278.82 | 277.2 | 486.01 | 480.19 | 483.31 | 77.7069 | 72.7745 | 71.1593 | 0.2402 | 1.435 | 1.433 | 1.431 | 1.944 | 1.926 | 2.028 | Over-range | 60.01 | 18095 | 17352 | 15965 | 51411 | - - - | - - - | - - - | - - - | 18095 | 17352 | 15965 | 51411 | 10934 | 9118 | 10397 | 30449 | - - - | - - - | - - - | - - - | 10934 | 9118 | 10397 | 30449 | 21688 | 20140 | 19588 | 61416 | # # # | # # # | # # # | # # # | 0.834 | 0.862 | 0.815 | 0.837 | # # # | # # # | # # # | - - - | 0.855 | 0.884 | 0.838 | 0.859 | - - - | 0.592 | 1.71 | 1.62 | 1.61 | 1.57 | 1.58 | 1.61 | 21.46 | 22.19 | 22.77 | 0 | - - - | - - - | - - - | - - - | 21688 | 20140 | 19588 | 61416 | Over-range | 11949 | 10213 | 11338 | 33569 | 4742 | 4526 | 4444 | 13907 | 18089 | 17370 | 16035 | 51494 | 18089 | 17370 | 16035 | 51494 | - - - | - - - | - - - | - - -
5/9/2026 | 6:45:00 PM | 280.92 | 278.85 | 277.28 | 486.04 | 480.35 | 483.43 | 75.2987 | 70.6118 | 68.7651 | 0.2381 | 1.435 | 1.433 | 1.43 | 1.946 | 1.926 | 2.033 | Over-range | 60.01 | 17488 | 16835 | 15411 | 49735 | - - - | - - - | - - - | - - - | 17488 | 16835 | 15411 | 49735 | 10689 | 8883 | 10079 | 29651 | - - - | - - - | - - - | - - - | 10689 | 8883 | 10079 | 29651 | 21040 | 19564 | 18953 | 59557 | # # # | # # # | # # # | # # # | 0.831 | 0.861 | 0.813 | 0.835 | # # # | # # # | # # # | - - - | 0.852 | 0.883 | 0.836 | 0.857 | - - - | 0.596 | 1.71 | 1.65 | 1.59 | 1.58 | 1.57 | 1.61 | 21.45 | 22.09 | 22.89 | 0 | - - - | - - - | - - - | - - - | 21040 | 19564 | 18953 | 59557 | Over-range | 11684 | 9946 | 11016 | 32716 | 4640 | 4397 | 4368 | 13600 | 17495 | 16873 | 15445 | 49812 | 17495 | 16873 | 15445 | 49812 | - - - | - - - | - - - | - - -
5/9/2026 | 7:00:00 PM | 281.13 | 279.11 | 277.49 | 486.46 | 480.71 | 483.8 | 76.2476 | 71.6406 | 68.8362 | 0.238 | 1.435 | 1.433 | 1.43 | 1.924 | 1.892 | 2.017 | Over-range | 60.02 | 17647 | 17154 | 15445 | 50246 | - - - | - - - | - - - | - - - | 17647 | 17154 | 15445 | 50246 | 10959 | 8911 | 10081 | 29950 | - - - | - - - | - - - | - - - | 10959 | 8911 | 10081 | 29950 | 21267 | 19809 | 18935 | 60011 | # # # | # # # | # # # | # # # | 0.83 | 0.866 | 0.816 | 0.837 | # # # | # # # | # # # | - - - | 0.849 | 0.886 | 0.837 | 0.857 | - - - | 0.596 | 1.73 | 1.65 | 1.62 | 1.59 | 1.58 | 1.63 | 20.48 | 20.96 | 21.89 | 0 | - - - | - - - | - - - | - - - | 21267 | 19809 | 18935 | 60011 | Over-range | 11861 | 9894 | 10941 | 32781 | 4449 | 4213 | 4169 | 13075 | 17666 | 17166 | 15483 | 50315 | 17666 | 17166 | 15483 | 50315 | - - - | - - - | - - - | - - -
5/9/2026 | 7:15:00 PM | 280.86 | 278.8 | 277.26 | 485.96 | 480.24 | 483.38 | 74.468 | 69.7613 | 67.9296 | 0.2375 | 1.435 | 1.433 | 1.43 | 1.941 | 1.921 | 2.031 | Over-range | 60 | 17258 | 16605 | 15190 | 49053 | - - - | - - - | - - - | - - - | 17258 | 16605 | 15190 | 49053 | 10578 | 8756 | 9968 | 29301 | - - - | - - - | - - - | - - - | 10578 | 8756 | 9968 | 29301 | 20759 | 19279 | 18682 | 58721 | # # # | # # # | # # # | # # # | 0.831 | 0.861 | 0.813 | 0.835 | # # # | # # # | # # # | - - - | 0.852 | 0.883 | 0.836 | 0.857 | - - - | 0.597 | 1.74 | 1.66 | 1.59 | 1.59 | 1.58 | 1.63 | 21.38 | 22 | 22.81 | 0 | - - - | - - - | - - - | - - - | 20759 | 19279 | 18682 | 58721 | Over-range | 11529 | 9785 | 10864 | 32248 | 4509 | 4294 | 4245 | 13248 | 17267 | 16611 | 15254 | 49132 | 17267 | 16611 | 15254 | 49132 | - - - | - - - | - - - | - - -
5/9/2026 | 7:30:00 PM | 280.82 | 278.78 | 277.15 | 485.9 | 480.19 | 483.21 | 75.4785 | 70.8641 | 68.7471 | 0.2377 | 1.435 | 1.433 | 1.43 | 1.928 | 1.9 | 2.01 | Over-range | 60.01 | 17498 | 16907 | 15404 | 49809 | - - - | - - - | - - - | - - - | 17498 | 16907 | 15404 | 49809 | 10789 | 8923 | 10112 | 29825 | - - - | - - - | - - - | - - - | 10789 | 8923 | 10112 | 29825 | 21063 | 19610 | 18918 | 59592 | # # # | # # # | # # # | # # # | 0.831 | 0.862 | 0.814 | 0.836 | # # # | # # # | # # # | - - - | 0.85 | 0.883 | 0.835 | 0.856 | - - - | 0.599 | 1.73 | 1.63 | 1.59 | 1.58 | 1.58 | 1.61 | 20.59 | 21.15 | 21.85 | 0 | - - - | - - - | - - - | - - - | 21063 | 19610 | 18918 | 59592 | Over-range | 11716 | 9923 | 10971 | 32682 | 4474 | 4252 | 4159 | 13096 | 17481 | 16927 | 15468 | 49876 | 17481 | 16927 | 15468 | 49876 | - - - | - - - | - - - | - - -
5/9/2026 | 7:45:00 PM | 280.92 | 278.93 | 277.29 | 486.15 | 480.39 | 483.42 | 76.5562 | 71.9852 | 69.1677 | 0.238 | 1.435 | 1.433 | 1.43 | 1.933 | 1.909 | 2.023 | Over-range | 59.99 | 17658 | 17166 | 15463 | 50287 | - - - | - - - | - - - | - - - | 17658 | 17166 | 15463 | 50287 | 10943 | 8926 | 10090 | 29960 | - - - | - - - | - - - | - - - | 10943 | 8926 | 10090 | 29960 | 21304 | 19859 | 18983 | 60147 | # # # | # # # | # # # | # # # | 0.829 | 0.864 | 0.815 | 0.836 | # # # | # # # | # # # | - - - | 0.849 | 0.886 | 0.836 | 0.857 | - - - | 0.596 | 1.7 | 1.63 | 1.58 | 1.57 | 1.56 | 1.6 | 20.98 | 21.6 | 22.51 | 0 | - - - | - - - | - - - | - - - | 21304 | 19859 | 18983 | 60147 | Over-range | 11903 | 9964 | 10995 | 32946 | 4577 | 4329 | 4264 | 13410 | 17656 | 17215 | 15491 | 50361 | 17656 | 17215 | 15491 | 50361 | - - - | - - - | - - - | - - -
5/9/2026 | 8:00:00 PM | 280.3 | 278.34 | 276.74 | 485.04 | 479.45 | 482.43 | 76.1577 | 71.4762 | 69.8561 | 0.2529 | 1.434 | 1.433 | 1.43 | 1.943 | 1.926 | 2.032 | Over-range | 60 | 17652 | 16969 | 15621 | 50242 | - - - | - - - | - - - | - - - | 17652 | 16969 | 15621 | 50242 | 10696 | 8991 | 10143 | 29830 | - - - | - - - | - - - | - - - | 10696 | 8991 | 10143 | 29830 | 21182 | 19716 | 19168 | 60066 | # # # | # # # | # # # | # # # | 0.833 | 0.861 | 0.815 | 0.836 | # # # | # # # | # # # | - - - | 0.854 | 0.883 | 0.837 | 0.858 | - - - | 0.594 | 1.74 | 1.66 | 1.63 | 1.59 | 1.61 | 1.64 | 21.46 | 22.05 | 22.83 | 0 | - - - | - - - | - - - | - - - | 21182 | 19716 | 19168 | 60066 | Over-range | 11701 | 10027 | 11096 | 32890 | 4657 | 4355 | 4414 | 13601 | 17686 | 17033 | 15599 | 50318 | 17686 | 17033 | 15599 | 50318 | - - - | - - - | - - - | - - -
5/9/2026 | 8:15:00 PM | 280.61 | 278.71 | 277.15 | 485.6 | 480.2 | 483 | 76.9259 | 72.6461 | 70.7214 | 0.2747 | 1.434 | 1.432 | 1.431 | 1.957 | 1.937 | 2.027 | Over-range | 60 | 17904 | 17315 | 15946 | 51165 | - - - | - - - | - - - | - - - | 17904 | 17315 | 15946 | 51165 | 10792 | 9128 | 10202 | 30121 | - - - | - - - | - - - | - - - | 10792 | 9128 | 10202 | 30121 | 21459 | 20107 | 19473 | 61039 | # # # | # # # | # # # | # # # | 0.834 | 0.861 | 0.819 | 0.838 | # # # | # # # | # # # | - - - | 0.855 | 0.884 | 0.841 | 0.86 | - - - | 0.589 | 1.8 | 1.78 | 1.79 | 1.68 | 1.74 | 1.77 | 21.65 | 22.34 | 22.92 | 0 | - - - | - - - | - - - | - - - | 21459 | 20107 | 19473 | 61039 | Over-range | 11822 | 10213 | 11167 | 33260 | 4754 | 4510 | 4473 | 13897 | 17918 | 17384 | 15939 | 51242 | 17918 | 17384 | 15939 | 51242 | - - - | - - - | - - - | - - -
5/9/2026 | 8:30:00 PM | 280.94 | 278.88 | 277.42 | 486.1 | 480.47 | 483.56 | 78.0894 | 73.3555 | 70.8675 | 0.2763 | 1.433 | 1.432 | 1.431 | 1.958 | 1.933 | 2.046 | Over-range | 60 | 18129 | 17533 | 15928 | 51591 | - - - | - - - | - - - | - - - | 18129 | 17533 | 15928 | 51591 | 10965 | 9019 | 10223 | 30207 | - - - | - - - | - - - | - - - | 10965 | 9019 | 10223 | 30207 | 21767 | 20269 | 19493 | 61528 | # # # | # # # | # # # | # # # | 0.833 | 0.865 | 0.817 | 0.839 | # # # | # # # | # # # | - - - | 0.854 | 0.888 | 0.84 | 0.861 | - - - | 0.586 | 1.72 | 1.67 | 1.66 | 1.58 | 1.63 | 1.65 | 21.96 | 22.61 | 23.41 | 0 | - - - | - - - | - - - | - - - | 21767 | 20269 | 19493 | 61528 | Over-range | 12038 | 10155 | 11224 | 33494 | 4884 | 4586 | 4553 | 14232 | 18137 | 17601 | 15936 | 51674 | 18137 | 17601 | 15936 | 51674 | - - - | - - - | - - - | - - -
5/9/2026 | 8:45:00 PM | 281.14 | 279.04 | 277.54 | 486.47 | 480.66 | 483.84 | 76.9815 | 72.1885 | 70.478 | 0.2717 | 1.433 | 1.431 | 1.43 | 1.968 | 1.948 | 2.06 | Over-range | 60 | 17951 | 17232 | 15852 | 51035 | - - - | - - - | - - - | - - - | 17951 | 17232 | 15852 | 51035 | 10702 | 8933 | 10169 | 29804 | - - - | - - - | - - - | - - - | 10702 | 8933 | 10169 | 29804 | 21516 | 20003 | 19432 | 60950 | # # # | # # # | # # # | # # # | 0.834 | 0.862 | 0.816 | 0.837 | # # # | # # # | # # # | - - - | 0.857 | 0.887 | 0.841 | 0.862 | - - - | 0.584 | 1.63 | 1.55 | 1.52 | 1.48 | 1.49 | 1.53 | 22.66 | 23.23 | 24.05 | 0 | - - - | - - - | - - - | - - - | 21516 | 20003 | 19432 | 60950 | Over-range | 11846 | 10138 | 11223 | 33275 | 4998 | 4713 | 4667 | 14559 | 17930 | 17283 | 15900 | 51112 | 17930 | 17283 | 15900 | 51112 | - - - | - - - | - - - | - - -
5/9/2026 | 9:00:00 PM | 281.01 | 278.83 | 277.37 | 486.17 | 480.35 | 483.57 | 78.0626 | 73.0761 | 71.2867 | 0.2737 | 1.433 | 1.431 | 1.43 | 1.956 | 1.942 | 2.048 | Over-range | 60.01 | 18261 | 17512 | 16076 | 51849 | - - - | - - - | - - - | - - - | 18261 | 17512 | 16076 | 51849 | 10857 | 9014 | 10254 | 30125 | - - - | - - - | - - - | - - - | 10857 | 9014 | 10254 | 30125 | 21814 | 20242 | 19649 | 61705 | # # # | # # # | # # # | # # # | 0.837 | 0.865 | 0.818 | 0.84 | # # # | # # # | # # # | - - - | 0.859 | 0.888 | 0.842 | 0.863 | - - - | 0.581 | 1.64 | 1.55 | 1.47 | 1.47 | 1.47 | 1.51 | 21.92 | 22.64 | 23.54 | 0 | - - - | - - - | - - - | - - - | 21814 | 20242 | 19649 | 61705 | Over-range | 11927 | 10142 | 11288 | 33429 | 4864 | 4577 | 4649 | 14281 | 18326 | 17551 | 16052 | 51929 | 18326 | 17551 | 16052 | 51929 | - - - | - - - | - - - | - - -
5/9/2026 | 9:15:00 PM | 281.02 | 278.88 | 277.31 | 486.28 | 480.28 | 483.51 | 77.94 | 72.893 | 70.4576 | 0.2729 | 1.433 | 1.431 | 1.43 | 1.965 | 1.945 | 2.061 | Over-range | 59.97 | 18135 | 17468 | 15823 | 51426 | - - - | - - - | - - - | - - - | 18135 | 17468 | 15823 | 51426 | 10860 | 8841 | 10129 | 29830 | - - - | - - - | - - - | - - - | 10860 | 8841 | 10129 | 29830 | 21742 | 20156 | 19383 | 61281 | # # # | # # # | # # # | # # # | 0.834 | 0.867 | 0.816 | 0.839 | # # # | # # # | # # # | - - - | 0.856 | 0.891 | 0.841 | 0.863 | - - - | 0.58 | 1.66 | 1.54 | 1.47 | 1.48 | 1.48 | 1.52 | 22.41 | 23.2 | 24.09 | 0 | - - - | - - - | - - - | - - - | 21742 | 20156 | 19383 | 61281 | Over-range | 11985 | 10043 | 11182 | 33295 | 4973 | 4678 | 4647 | 14525 | 18137 | 17524 | 15838 | 51500 | 18137 | 17524 | 15838 | 51500 | - - - | - - - | - - - | - - -
5/9/2026 | 9:30:00 PM | 281.33 | 279.2 | 277.68 | 486.8 | 480.9 | 484.11 | 77.8914 | 72.8482 | 71.0058 | 0.2733 | 1.433 | 1.431 | 1.429 | 1.962 | 1.94 | 2.05 | Over-range | 60 | 18213 | 17458 | 16006 | 51676 | - - - | - - - | - - - | - - - | 18213 | 17458 | 16006 | 51676 | 10828 | 8961 | 10253 | 30042 | - - - | - - - | - - - | - - - | 10828 | 8961 | 10253 | 30042 | 21773 | 20185 | 19581 | 61539 | # # # | # # # | # # # | # # # | 0.837 | 0.865 | 0.817 | 0.84 | # # # | # # # | # # # | - - - | 0.859 | 0.889 | 0.841 | 0.863 | - - - | 0.581 | 1.62 | 1.55 | 1.52 | 1.48 | 1.48 | 1.52 | 22.24 | 22.86 | 23.62 | 0 | - - - | - - - | - - - | - - - | 21773 | 20185 | 19581 | 61539 | Over-range | 11924 | 10120 | 11269 | 33387 | 4919 | 4632 | 4603 | 14353 | 18223 | 17493 | 16037 | 51753 | 18223 | 17493 | 16037 | 51753 | - - - | - - - | - - - | - - -
5/9/2026 | 9:45:00 PM | 281.85 | 279.63 | 278.13 | 487.59 | 481.68 | 484.96 | 76.0579 | 70.7829 | 68.9263 | 0.2703 | 1.431 | 1.429 | 1.428 | 1.968 | 1.956 | 2.073 | Over-range | 60 | 17731 | 16949 | 15432 | 50112 | - - - | - - - | - - - | - - - | 17731 | 16949 | 15432 | 50112 | 10661 | 8656 | 10043 | 29360 | - - - | - - - | - - - | - - - | 10661 | 8656 | 10043 | 29360 | 21294 | 19634 | 19027 | 59955 | # # # | # # # | # # # | # # # | 0.833 | 0.863 | 0.811 | 0.836 | # # # | # # # | # # # | - - - | 0.856 | 0.888 | 0.837 | 0.86 | - - - | 0.586 | 1.57 | 1.46 | 1.39 | 1.4 | 1.38 | 1.41 | 22.71 | 23.63 | 24.5 | 0 | - - - | - - - | - - - | - - - | 21294 | 19634 | 19027 | 59955 | Over-range | 11774 | 9888 | 11111 | 32859 | 4905 | 4696 | 4662 | 14495 | 17749 | 16928 | 15499 | 50176 | 17749 | 16928 | 15499 | 50176 | - - - | - - - | - - - | - - -
5/9/2026 | 10:00:00 PM | 282.23 | 280.04 | 278.52 | 488.29 | 482.39 | 485.61 | 75.9334 | 70.2726 | 68.4568 | 0.2678 | 1.431 | 1.428 | 1.426 | 1.956 | 1.946 | 2.067 | Over-range | 60.03 | 17744 | 16909 | 15323 | 49977 | - - - | - - - | - - - | - - - | 17744 | 16909 | 15323 | 49977 | 10802 | 8697 | 10171 | 29670 | - - - | - - - | - - - | - - - | 10802 | 8697 | 10171 | 29670 | 21326 | 19562 | 18961 | 59850 | # # # | # # # | # # # | # # # | 0.832 | 0.864 | 0.808 | 0.835 | # # # | # # # | # # # | - - - | 0.854 | 0.888 | 0.833 | 0.858 | - - - | 0.594 | 1.55 | 1.41 | 1.37 | 1.39 | 1.35 | 1.39 | 22.01 | 22.99 | 23.91 | 0 | - - - | - - - | - - - | - - - | 21326 | 19562 | 18961 | 59850 | Over-range | 11822 | 9825 | 11158 | 32902 | 4740 | 4515 | 4528 | 14046 | 17781 | 16902 | 15360 | 50043 | 17781 | 16902 | 15360 | 50043 | - - - | - - - | - - - | - - -
5/9/2026 | 10:15:00 PM | 281.97 | 279.65 | 278.1 | 487.77 | 481.56 | 485.08 | 77.1477 | 71.2268 | 70.0378 | 0.2696 | 1.433 | 1.43 | 1.428 | 1.948 | 1.94 | 2.056 | Over-range | 60.01 | 18026 | 17044 | 15621 | 50690 | - - - | - - - | - - - | - - - | 18026 | 17044 | 15621 | 50690 | 10908 | 8899 | 10408 | 30215 | - - - | - - - | - - - | - - - | 10908 | 8899 | 10408 | 30215 | 21616 | 19769 | 19342 | 60727 | # # # | # # # | # # # | # # # | 0.834 | 0.862 | 0.808 | 0.835 | # # # | # # # | # # # | - - - | 0.855 | 0.885 | 0.831 | 0.857 | - - - | 0.596 | 1.62 | 1.51 | 1.48 | 1.47 | 1.46 | 1.5 | 21.79 | 22.62 | 23.5 | 0 | - - - | - - - | - - - | - - - | 21616 | 19769 | 19342 | 60727 | Over-range | 11923 | 10005 | 11395 | 33413 | 4736 | 4500 | 4564 | 14043 | 18093 | 17011 | 15655 | 50759 | 18093 | 17011 | 15655 | 50759 | - - - | - - - | - - - | - - -
5/9/2026 | 10:30:00 PM | 282.24 | 279.95 | 278.34 | 488.28 | 482.07 | 485.47 | 77.5464 | 72.0529 | 70.2486 | 0.2712 | 1.433 | 1.43 | 1.429 | 1.952 | 1.931 | 2.055 | Over-range | 60.01 | 18131 | 17312 | 15767 | 51209 | - - - | - - - | - - - | - - - | 18131 | 17312 | 15767 | 51209 | 11007 | 8971 | 10353 | 30331 | - - - | - - - | - - - | - - - | 11007 | 8971 | 10353 | 30331 | 21763 | 20037 | 19430 | 61230 | # # # | # # # | # # # | # # # | 0.833 | 0.864 | 0.812 | 0.836 | # # # | # # # | # # # | - - - | 0.855 | 0.887 | 0.835 | 0.859 | - - - | 0.592 | 1.65 | 1.57 | 1.5 | 1.49 | 1.49 | 1.54 | 21.76 | 22.4 | 23.35 | 0 | - - - | - - - | - - - | - - - | 21763 | 20037 | 19430 | 61230 | Over-range | 12031 | 10080 | 11346 | 33544 | 4787 | 4531 | 4572 | 14124 | 18199 | 17289 | 15791 | 51279 | 18199 | 17289 | 15791 | 51279 | - - - | - - - | - - - | - - -
5/9/2026 | 10:45:00 PM | 282.35 | 279.98 | 278.42 | 488.37 | 482.14 | 485.68 | 76.7053 | 71.1799 | 68.8126 | 0.269 | 1.434 | 1.431 | 1.429 | 1.938 | 1.918 | 2.055 | Over-range | 60.02 | 17833 | 17093 | 15365 | 50291 | - - - | - - - | - - - | - - - | 17833 | 17093 | 15365 | 50291 | 10996 | 8780 | 10178 | 29954 | - - - | - - - | - - - | - - - | 10996 | 8780 | 10178 | 29954 | 21490 | 19743 | 18992 | 60225 | # # # | # # # | # # # | # # # | 0.83 | 0.866 | 0.809 | 0.835 | # # # | # # # | # # # | - - - | 0.851 | 0.887 | 0.832 | 0.857 | - - - | 0.596 | 1.69 | 1.57 | 1.54 | 1.52 | 1.53 | 1.57 | 21.29 | 21.95 | 23.09 | 0 | - - - | - - - | - - - | - - - | 21490 | 19743 | 18992 | 60225 | Over-range | 11976 | 9857 | 11145 | 33081 | 4651 | 4394 | 4457 | 13786 | 17909 | 17067 | 15384 | 50361 | 17909 | 17067 | 15384 | 50361 | - - - | - - - | - - - | - - -
5/9/2026 | 11:00:00 PM | 282.71 | 280.41 | 278.79 | 489.12 | 482.82 | 486.28 | 76.38 | 70.8341 | 68.9335 | 0.2695 | 1.434 | 1.431 | 1.429 | 1.928 | 1.898 | 2.032 | Over-range | 60.01 | 17813 | 17012 | 15425 | 50251 | - - - | - - - | - - - | - - - | 17813 | 17012 | 15425 | 50251 | 11035 | 8949 | 10349 | 30333 | - - - | - - - | - - - | - - - | 11035 | 8949 | 10349 | 30333 | 21448 | 19701 | 19076 | 60226 | # # # | # # # | # # # | # # # | 0.831 | 0.864 | 0.809 | 0.834 | # # # | # # # | # # # | - - - | 0.85 | 0.883 | 0.83 | 0.854 | - - - | 0.604 | 1.72 | 1.61 | 1.59 | 1.54 | 1.57 | 1.61 | 20.63 | 21.07 | 22.01 | 0 | - - - | - - - | - - - | - - - | 21448 | 19701 | 19076 | 60226 | Over-range | 11940 | 9926 | 11213 | 33172 | 4474 | 4214 | 4239 | 13190 | 17865 | 16980 | 15471 | 50316 | 17865 | 16980 | 15471 | 50316 | - - - | - - - | - - - | - - -
5/9/2026 | 11:15:00 PM | 283.1 | 280.78 | 279.25 | 489.72 | 483.56 | 487.04 | 76.5389 | 70.9189 | 69.1408 | 0.2711 | 1.434 | 1.432 | 1.43 | 1.925 | 1.899 | 2.031 | Over-range | 60.01 | 17875 | 17052 | 15478 | 50405 | - - - | - - - | - - - | - - - | 17875 | 17052 | 15478 | 50405 | 11084 | 9016 | 10435 | 30535 | - - - | - - - | - - - | - - - | 11084 | 9016 | 10435 | 30535 | 21533 | 19763 | 19170 | 60466 | # # # | # # # | # # # | # # # | 0.83 | 0.863 | 0.807 | 0.834 | # # # | # # # | # # # | - - - | 0.849 | 0.883 | 0.828 | 0.854 | - - - | 0.606 | 1.73 | 1.63 | 1.62 | 1.57 | 1.58 | 1.63 | 20.59 | 21.01 | 22.04 | 0 | - - - | - - - | - - - | - - - | 21533 | 19763 | 19170 | 60466 | Over-range | 12000 | 9980 | 11298 | 33371 | 4519 | 4205 | 4255 | 13240 | 17905 | 17063 | 15506 | 50474 | 17905 | 17063 | 15506 | 50474 | - - - | - - - | - - - | - - -
5/9/2026 | 11:30:00 PM | 283.35 | 281.08 | 279.42 | 490.23 | 484 | 487.34 | 74.9709 | 69.5625 | 67.0387 | 0.2683 | 1.434 | 1.431 | 1.43 | 1.93 | 1.901 | 2.038 | Over-range | 60.02 | 17476 | 16795 | 15021 | 49291 | - - - | - - - | - - - | - - - | 17476 | 16795 | 15021 | 49291 | 10901 | 8698 | 10043 | 29642 | - - - | - - - | - - - | - - - | 10901 | 8698 | 10043 | 29642 | 21099 | 19394 | 18587 | 59080 | # # # | # # # | # # # | # # # | 0.828 | 0.866 | 0.808 | 0.834 | # # # | # # # | # # # | - - - | 0.848 | 0.887 | 0.83 | 0.855 | - - - | 0.601 | 1.73 | 1.65 | 1.6 | 1.57 | 1.59 | 1.63 | 20.8 | 21.42 | 22.51 | 0 | - - - | - - - | - - - | - - - | 21099 | 19394 | 18587 | 59080 | Over-range | 11815 | 9686 | 10938 | 32543 | 4471 | 4182 | 4253 | 13194 | 17551 | 16797 | 15007 | 49355 | 17551 | 16797 | 15007 | 49355 | - - - | - - - | - - - | - - -
5/9/2026 | 11:45:00 PM | 283.56 | 281.19 | 279.57 | 490.53 | 484.14 | 487.71 | 76.663 | 71.038 | 69.3304 | 0.2721 | 1.434 | 1.431 | 1.429 | 1.949 | 1.926 | 2.053 | Over-range | 60.02 | 17858 | 16997 | 15459 | 50314 | - - - | - - - | - - - | - - - | 17858 | 16997 | 15459 | 50314 | 10971 | 8962 | 10384 | 30318 | - - - | - - - | - - - | - - - | 10971 | 8962 | 10384 | 30318 | 21537 | 19753 | 19187 | 60476 | # # # | # # # | # # # | # # # | 0.829 | 0.861 | 0.806 | 0.832 | # # # | # # # | # # # | - - - | 0.85 | 0.883 | 0.828 | 0.854 | - - - | 0.603 | 1.75 | 1.64 | 1.62 | 1.57 | 1.59 | 1.63 | 21.87 | 22.42 | 23.37 | 0 | - - - | - - - | - - - | - - - | 21537 | 19753 | 19187 | 60476 | Over-range | 12023 | 10044 | 11348 | 33505 | 4827 | 4446 | 4489 | 14006 | 17861 | 17063 | 15466 | 50390 | 17861 | 17063 | 15466 | 50390 | - - - | - - - | - - - | - - -
5/10/2026 | 12:00:00 AM | 283.89 | 281.5 | 279.88 | 491.09 | 484.68 | 488.27 | 78.3549 | 72.6954 | 70.958 | 0.2754 | 1.435 | 1.432 | 1.43 | 1.948 | 1.928 | 2.05 | Over-range | 60.01 | 18378 | 17515 | 15949 | 51842 | - - - | - - - | - - - | - - - | 18378 | 17515 | 15949 | 51842 | 11249 | 9212 | 10640 | 31101 | - - - | - - - | - - - | - - - | 11249 | 9212 | 10640 | 31101 | 22125 | 20331 | 19741 | 62197 | # # # | # # # | # # # | # # # | 0.831 | 0.862 | 0.808 | 0.834 | # # # | # # # | # # # | - - - | 0.852 | 0.884 | 0.831 | 0.856 | - - - | 0.6 | 1.77 | 1.67 | 1.63 | 1.6 | 1.61 | 1.66 | 21.77 | 22.36 | 23.32 | 0 | - - - | - - - | - - - | - - - | 22125 | 20331 | 19741 | 62197 | Over-range | 12314 | 10314 | 11623 | 34339 | 4939 | 4570 | 4606 | 14352 | 18377 | 17581 | 15960 | 51918 | 18377 | 17581 | 15960 | 51918 | - - - | - - - | - - - | - - -
5/10/2026 | 12:15:00 AM | 284 | 281.59 | 279.92 | 491.26 | 484.84 | 488.37 | 78.6749 | 73.1612 | 70.7021 | 0.2751 | 1.435 | 1.432 | 1.429 | 1.942 | 1.921 | 2.044 | Over-range | 60 | 18473 | 17726 | 15963 | 52162 | - - - | - - - | - - - | - - - | 18473 | 17726 | 15963 | 52162 | 11329 | 9110 | 10495 | 30934 | - - - | - - - | - - - | - - - | 11329 | 9110 | 10495 | 30934 | 22220 | 20463 | 19671 | 62355 | # # # | # # # | # # # | # # # | 0.831 | 0.866 | 0.812 | 0.837 | # # # | # # # | # # # | - - - | 0.852 | 0.888 | 0.834 | 0.858 | - - - | 0.593 | 1.78 | 1.66 | 1.62 | 1.6 | 1.6 | 1.65 | 21.38 | 22.14 | 23.13 | 0 | - - - | - - - | - - - | - - - | 22220 | 20463 | 19671 | 62355 | Over-range | 12341 | 10213 | 11485 | 34139 | 4820 | 4550 | 4602 | 14243 | 18554 | 17726 | 15956 | 52236 | 18554 | 17726 | 15956 | 52236 | - - - | - - - | - - - | - - -
5/10/2026 | 12:30:00 AM | 284.53 | 282.03 | 280.44 | 492.13 | 485.57 | 489.34 | 77.1323 | 71.3667 | 69.695 | 0.2724 | 1.434 | 1.431 | 1.429 | 1.956 | 1.938 | 2.069 | Over-range | 60 | 18044 | 17158 | 15593 | 50795 | - - - | - - - | - - - | - - - | 18044 | 17158 | 15593 | 50795 | 11106 | 9050 | 10500 | 30656 | - - - | - - - | - - - | - - - | 11106 | 9050 | 10500 | 30656 | 21793 | 19962 | 19396 | 61152 | # # # | # # # | # # # | # # # | 0.828 | 0.86 | 0.804 | 0.831 | # # # | # # # | # # # | - - - | 0.85 | 0.883 | 0.828 | 0.854 | - - - | 0.604 | 1.78 | 1.65 | 1.59 | 1.59 | 1.6 | 1.64 | 22.36 | 22.92 | 24.04 | 0 | - - - | - - - | - - - | - - - | 21793 | 19962 | 19396 | 61152 | Over-range | 12214 | 10187 | 11524 | 34018 | 4989 | 4588 | 4659 | 14480 | 18047 | 17225 | 15598 | 50870 | 18047 | 17225 | 15598 | 50870 | - - - | - - - | - - - | - - -
5/10/2026 | 12:45:00 AM | 284.82 | 282.5 | 280.82 | 492.77 | 486.4 | 489.86 | 78.6929 | 73.4052 | 71.3692 | 0.2752 | 1.434 | 1.431 | 1.429 | 1.961 | 1.943 | 2.067 | Over-range | 60 | 18432 | 17680 | 16068 | 52180 | - - - | - - - | - - - | - - - | 18432 | 17680 | 16068 | 52180 | 11366 | 9315 | 10680 | 31361 | - - - | - - - | - - - | - - - | 11366 | 9315 | 10680 | 31361 | 22277 | 20586 | 19905 | 62768 | # # # | # # # | # # # | # # # | 0.827 | 0.859 | 0.807 | 0.831 | # # # | # # # | # # # | - - - | 0.85 | 0.883 | 0.832 | 0.855 | - - - | 0.601 | 1.77 | 1.63 | 1.6 | 1.59 | 1.59 | 1.64 | 22.42 | 23.07 | 24.03 | 0 | - - - | - - - | - - - | - - - | 22277 | 20586 | 19905 | 62768 | Over-range | 12496 | 10525 | 11732 | 34837 | 5098 | 4807 | 4760 | 14894 | 18416 | 17703 | 16135 | 52254 | 18416 | 17703 | 16135 | 52254 | - - - | - - - | - - - | - - -
5/10/2026 | 1:00:00 AM | 284.82 | 282.46 | 280.81 | 492.7 | 486.41 | 489.83 | 76.0404 | 70.77 | 68.2216 | 0.2699 | 1.434 | 1.43 | 1.429 | 1.985 | 1.968 | 2.1 | Over-range | 60.01 | 17813 | 17128 | 15368 | 50310 | - - - | - - - | - - - | - - - | 17813 | 17128 | 15368 | 50310 | 10884 | 8695 | 10049 | 29628 | - - - | - - - | - - - | - - - | 10884 | 8695 | 10049 | 29628 | 21509 | 19828 | 19014 | 60351 | # # # | # # # | # # # | # # # | 0.828 | 0.864 | 0.808 | 0.834 | # # # | # # # | # # # | - - - | 0.853 | 0.891 | 0.836 | 0.86 | - - - | 0.589 | 1.76 | 1.64 | 1.57 | 1.58 | 1.57 | 1.62 | 23.56 | 24.52 | 25.72 | 0 | - - - | - - - | - - - | - - - | 21509 | 19828 | 19014 | 60351 | Over-range | 12048 | 9976 | 11185 | 33306 | 5088 | 4820 | 4841 | 15000 | 17866 | 17135 | 15384 | 50385 | 17866 | 17135 | 15384 | 50385 | - - - | - - - | - - - | - - -
5/10/2026 | 1:15:00 AM | 284.77 | 282.32 | 280.72 | 492.58 | 486.09 | 489.77 | 76.6856 | 71.1647 | 69.2755 | 0.2713 | 1.434 | 1.43 | 1.428 | 1.981 | 1.963 | 2.099 | Over-range | 60 | 17994 | 17182 | 15584 | 50760 | - - - | - - - | - - - | - - - | 17994 | 17182 | 15584 | 50760 | 10995 | 8923 | 10289 | 30208 | - - - | - - - | - - - | - - - | 10995 | 8923 | 10289 | 30208 | 21738 | 19981 | 19346 | 61064 | # # # | # # # | # # # | # # # | 0.828 | 0.86 | 0.806 | 0.831 | # # # | # # # | # # # | - - - | 0.853 | 0.886 | 0.833 | 0.857 | - - - | 0.595 | 1.76 | 1.64 | 1.6 | 1.58 | 1.59 | 1.64 | 23.61 | 24.29 | 25.51 | 0 | - - - | - - - | - - - | - - - | 21738 | 19981 | 19346 | 61064 | Over-range | 12189 | 10188 | 11453 | 33919 | 5186 | 4847 | 4958 | 15217 | 18071 | 17192 | 15568 | 50830 | 18071 | 17192 | 15568 | 50830 | - - - | - - - | - - - | - - -
5/10/2026 | 1:30:00 AM | 284.81 | 282.28 | 280.75 | 492.56 | 486.06 | 489.89 | 77.7718 | 72.1573 | 70.4171 | 0.2729 | 1.434 | 1.43 | 1.428 | 1.964 | 1.954 | 2.084 | Over-range | 60.01 | 18283 | 17428 | 15864 | 51575 | - - - | - - - | - - - | - - - | 18283 | 17428 | 15864 | 51575 | 11167 | 9086 | 10477 | 30730 | - - - | - - - | - - - | - - - | 11167 | 9086 | 10477 | 30730 | 22034 | 20240 | 19653 | 61927 | # # # | # # # | # # # | # # # | 0.83 | 0.861 | 0.807 | 0.833 | # # # | # # # | # # # | - - - | 0.854 | 0.886 | 0.833 | 0.858 | - - - | 0.596 | 1.75 | 1.66 | 1.62 | 1.59 | 1.59 | 1.64 | 23 | 23.61 | 24.95 | 0 | - - - | - - - | - - - | - - - | 22034 | 20240 | 19653 | 61927 | Over-range | 12292 | 10284 | 11593 | 34257 | 5079 | 4761 | 4908 | 14976 | 18376 | 17417 | 15859 | 51653 | 18376 | 17417 | 15859 | 51653 | - - - | - - - | - - - | - - -
5/10/2026 | 1:45:00 AM | 285.07 | 282.65 | 281.05 | 493.09 | 486.72 | 490.29 | 78.7097 | 72.9302 | 70.8302 | 0.2759 | 1.434 | 1.43 | 1.429 | 1.948 | 1.934 | 2.066 | Over-range | 60 | 18450 | 17619 | 15908 | 51977 | - - - | - - - | - - - | - - - | 18450 | 17619 | 15908 | 51977 | 11347 | 9160 | 10620 | 31128 | - - - | - - - | - - - | - - - | 11347 | 9160 | 10620 | 31128 | 22278 | 20438 | 19751 | 62467 | # # # | # # # | # # # | # # # | 0.828 | 0.862 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.85 | 0.886 | 0.829 | 0.855 | - - - | 0.599 | 1.77 | 1.63 | 1.61 | 1.59 | 1.59 | 1.64 | 22.18 | 22.86 | 24.06 | 0 | - - - | - - - | - - - | - - - | 22278 | 20438 | 19751 | 62467 | Over-range | 12469 | 10336 | 11689 | 34595 | 5060 | 4687 | 4781 | 14796 | 18486 | 17673 | 15887 | 52046 | 18486 | 17673 | 15887 | 52046 | - - - | - - - | - - - | - - -
5/10/2026 | 2:00:00 AM | 285.31 | 282.88 | 281.25 | 493.55 | 487.03 | 490.69 | 76.2523 | 70.1451 | 68.9799 | 0.2716 | 1.434 | 1.43 | 1.428 | 1.945 | 1.926 | 2.069 | Over-range | 60 | 17867 | 16868 | 15381 | 50116 | - - - | - - - | - - - | - - - | 17867 | 16868 | 15381 | 50116 | 11106 | 9075 | 10616 | 30797 | - - - | - - - | - - - | - - - | 11106 | 9075 | 10616 | 30797 | 21610 | 19681 | 19256 | 60547 | # # # | # # # | # # # | # # # | 0.827 | 0.857 | 0.799 | 0.828 | # # # | # # # | # # # | - - - | 0.848 | 0.88 | 0.822 | 0.85 | - - - | 0.615 | 1.75 | 1.61 | 1.58 | 1.57 | 1.56 | 1.62 | 21.98 | 22.43 | 23.58 | 0 | - - - | - - - | - - - | - - - | 21610 | 19681 | 19256 | 60547 | Over-range | 12149 | 10126 | 11573 | 33944 | 4844 | 4417 | 4532 | 14049 | 17872 | 16926 | 15385 | 50182 | 17872 | 16926 | 15385 | 50182 | - - - | - - - | - - - | - - -
5/10/2026 | 2:15:00 AM | 285.09 | 282.56 | 281.05 | 493.04 | 486.55 | 490.39 | 76.6222 | 70.6074 | 69.0852 | 0.2709 | 1.434 | 1.43 | 1.428 | 1.946 | 1.932 | 2.077 | Over-range | 60 | 17952 | 17019 | 15448 | 50420 | - - - | - - - | - - - | - - - | 17952 | 17019 | 15448 | 50420 | 11138 | 9028 | 10561 | 30727 | - - - | - - - | - - - | - - - | 11138 | 9028 | 10561 | 30727 | 21702 | 19793 | 19278 | 60774 | # # # | # # # | # # # | # # # | 0.827 | 0.86 | 0.801 | 0.83 | # # # | # # # | # # # | - - - | 0.849 | 0.883 | 0.825 | 0.852 | - - - | 0.609 | 1.74 | 1.61 | 1.58 | 1.56 | 1.56 | 1.61 | 22.16 | 22.55 | 23.9 | 0 | - - - | - - - | - - - | - - - | 21702 | 19793 | 19278 | 60774 | Over-range | 12187 | 10095 | 11522 | 33905 | 4882 | 4454 | 4546 | 14147 | 17939 | 17079 | 15476 | 50494 | 17939 | 17079 | 15476 | 50494 | - - - | - - - | - - - | - - -
5/10/2026 | 2:30:00 AM | 285.08 | 282.52 | 280.98 | 493 | 486.49 | 490.29 | 77.6887 | 71.5964 | 69.5593 | 0.2724 | 1.434 | 1.43 | 1.428 | 1.938 | 1.924 | 2.068 | Over-range | 60.01 | 18220 | 17341 | 15588 | 51149 | - - - | - - - | - - - | - - - | 18220 | 17341 | 15588 | 51149 | 11314 | 9000 | 10585 | 30899 | - - - | - - - | - - - | - - - | 11314 | 9000 | 10585 | 30899 | 22018 | 20085 | 19416 | 61519 | # # # | # # # | # # # | # # # | 0.828 | 0.863 | 0.803 | 0.831 | # # # | # # # | # # # | - - - | 0.848 | 0.886 | 0.827 | 0.854 | - - - | 0.604 | 1.77 | 1.62 | 1.57 | 1.57 | 1.56 | 1.62 | 21.71 | 22.35 | 23.63 | 0 | - - - | - - - | - - - | - - - | 22018 | 20085 | 19416 | 61519 | Over-range | 12354 | 10119 | 11564 | 34149 | 4880 | 4552 | 4580 | 14317 | 18221 | 17343 | 15650 | 51214 | 18221 | 17343 | 15650 | 51214 | - - - | - - - | - - - | - - -
5/10/2026 | 2:45:00 AM | 285.44 | 282.8 | 281.15 | 493.63 | 486.79 | 490.76 | 77.2581 | 71.1725 | 69.4147 | 0.2455 | 1.434 | 1.43 | 1.427 | 1.928 | 1.907 | 2.056 | Over-range | 60.01 | 18051 | 17146 | 15470 | 50668 | - - - | - - - | - - - | - - - | 18051 | 17146 | 15470 | 50668 | 11400 | 9155 | 10668 | 31223 | - - - | - - - | - - - | - - - | 11400 | 9155 | 10668 | 31223 | 21906 | 19964 | 19370 | 61239 | # # # | # # # | # # # | # # # | 0.824 | 0.859 | 0.799 | 0.827 | # # # | # # # | # # # | - - - | 0.844 | 0.88 | 0.821 | 0.849 | - - - | 0.616 | 1.75 | 1.64 | 1.59 | 1.59 | 1.57 | 1.62 | 21.33 | 21.71 | 23.1 | 0 | - - - | - - - | - - - | - - - | 21906 | 19964 | 19370 | 61239 | Over-range | 12393 | 10202 | 11638 | 34340 | 4748 | 4396 | 4547 | 13984 | 18120 | 17124 | 15484 | 50728 | 18120 | 17124 | 15484 | 50728 | - - - | - - - | - - - | - - -
5/10/2026 | 3:00:00 AM | 285.56 | 283.01 | 281.26 | 493.93 | 487.08 | 490.92 | 76.079 | 70.2135 | 68.059 | 0.2369 | 1.433 | 1.431 | 1.427 | 1.921 | 1.887 | 2.048 | Over-range | 60 | 17802 | 17006 | 15241 | 50048 | - - - | - - - | - - - | - - - | 17802 | 17006 | 15241 | 50048 | 11315 | 9036 | 10472 | 30823 | - - - | - - - | - - - | - - - | 11315 | 9036 | 10472 | 30823 | 21591 | 19723 | 19012 | 60326 | # # # | # # # | # # # | # # # | 0.825 | 0.862 | 0.802 | 0.83 | # # # | # # # | # # # | - - - | 0.844 | 0.881 | 0.823 | 0.85 | - - - | 0.616 | 1.78 | 1.64 | 1.62 | 1.61 | 1.58 | 1.64 | 20.81 | 21.05 | 22.47 | 0 | - - - | - - - | - - - | - - - | 21591 | 19723 | 19012 | 60326 | Over-range | 12213 | 9981 | 11356 | 33660 | 4523 | 4170 | 4326 | 13322 | 17887 | 16979 | 15242 | 50108 | 17887 | 16979 | 15242 | 50108 | - - - | - - - | - - - | - - -
5/10/2026 | 3:15:00 AM | 285.49 | 282.94 | 281.14 | 493.78 | 486.98 | 490.73 | 77.7732 | 71.9536 | 69.472 | 0.2398 | 1.433 | 1.431 | 1.427 | 1.928 | 1.901 | 2.045 | Over-range | 60 | 18205 | 17443 | 15584 | 51232 | - - - | - - - | - - - | - - - | 18205 | 17443 | 15584 | 51232 | 11503 | 9149 | 10593 | 31244 | - - - | - - - | - - - | - - - | 11503 | 9149 | 10593 | 31244 | 22068 | 20207 | 19402 | 61677 | # # # | # # # | # # # | # # # | 0.825 | 0.863 | 0.803 | 0.831 | # # # | # # # | # # # | - - - | 0.845 | 0.883 | 0.825 | 0.851 | - - - | 0.61 | 1.78 | 1.71 | 1.64 | 1.64 | 1.62 | 1.66 | 21.05 | 21.52 | 22.84 | 0 | - - - | - - - | - - - | - - - | 22068 | 20207 | 19402 | 61677 | Over-range | 12464 | 10186 | 11544 | 34307 | 4695 | 4380 | 4492 | 13880 | 18289 | 17427 | 15581 | 51297 | 18289 | 17427 | 15581 | 51297 | - - - | - - - | - - - | - - -
5/10/2026 | 3:30:00 AM | 285.46 | 282.91 | 281.01 | 493.81 | 486.77 | 490.59 | 77.5503 | 71.5294 | 69.4073 | 0.2391 | 1.433 | 1.431 | 1.427 | 1.93 | 1.891 | 2.044 | Over-range | 60.01 | 18114 | 17273 | 15488 | 50874 | - - - | - - - | - - - | - - - | 18114 | 17273 | 15488 | 50874 | 11519 | 9200 | 10720 | 31439 | - - - | - - - | - - - | - - - | 11519 | 9200 | 10720 | 31439 | 21996 | 20078 | 19365 | 61440 | # # # | # # # | # # # | # # # | 0.824 | 0.86 | 0.8 | 0.828 | # # # | # # # | # # # | - - - | 0.843 | 0.881 | 0.822 | 0.848 | - - - | 0.618 | 1.81 | 1.7 | 1.65 | 1.64 | 1.64 | 1.67 | 21 | 21.42 | 22.47 | 0 | - - - | - - - | - - - | - - - | 21996 | 20078 | 19365 | 61440 | Over-range | 12472 | 10224 | 11613 | 34418 | 4679 | 4366 | 4366 | 13721 | 18141 | 17242 | 15551 | 50933 | 18141 | 17242 | 15551 | 50933 | - - - | - - - | - - - | - - -
5/10/2026 | 3:45:00 AM | 285.48 | 282.88 | 281.06 | 493.78 | 486.78 | 490.67 | 78.7317 | 72.8165 | 70.339 | 0.2402 | 1.433 | 1.431 | 1.427 | 1.942 | 1.908 | 2.052 | Over-range | 60.01 | 18435 | 17636 | 15773 | 51844 | - - - | - - - | - - - | - - - | 18435 | 17636 | 15773 | 51844 | 11551 | 9190 | 10669 | 31411 | - - - | - - - | - - - | - - - | 11551 | 9190 | 10669 | 31411 | 22332 | 20437 | 19626 | 62395 | # # # | # # # | # # # | # # # | 0.826 | 0.863 | 0.804 | 0.831 | # # # | # # # | # # # | - - - | 0.847 | 0.885 | 0.827 | 0.853 | - - - | 0.606 | 1.82 | 1.72 | 1.67 | 1.66 | 1.67 | 1.69 | 21.61 | 22.23 | 23.33 | 0 | - - - | - - - | - - - | - - - | 22332 | 20437 | 19626 | 62395 | Over-range | 12589 | 10304 | 11661 | 34665 | 4918 | 4582 | 4627 | 14429 | 18489 | 17643 | 15779 | 51912 | 18489 | 17643 | 15779 | 51912 | - - - | - - - | - - - | - - -
5/10/2026 | 4:00:00 AM | 285.69 | 283.19 | 281.32 | 494.21 | 487.36 | 491.02 | 78.1124 | 72.3971 | 70.168 | 0.2412 | 1.434 | 1.431 | 1.427 | 1.965 | 1.933 | 2.068 | Over-range | 59.99 | 18263 | 17467 | 15713 | 51444 | - - - | - - - | - - - | - - - | 18263 | 17467 | 15713 | 51444 | 11422 | 9227 | 10654 | 31303 | - - - | - - - | - - - | - - - | 11422 | 9227 | 10654 | 31303 | 22162 | 20336 | 19594 | 62093 | # # # | # # # | # # # | # # # | 0.824 | 0.859 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.846 | 0.883 | 0.826 | 0.852 | - - - | 0.609 | 1.84 | 1.73 | 1.71 | 1.68 | 1.68 | 1.72 | 22.51 | 23.18 | 24.15 | 0 | - - - | - - - | - - - | - - - | 22162 | 20336 | 19594 | 62093 | Over-range | 12546 | 10399 | 11694 | 34738 | 5094 | 4705 | 4729 | 14792 | 18275 | 17539 | 15701 | 51515 | 18275 | 17539 | 15701 | 51515 | - - - | - - - | - - - | - - -
5/10/2026 | 4:15:00 AM | 285.63 | 283.02 | 281.27 | 493.99 | 487.09 | 491.02 | 76.7488 | 70.9073 | 68.7085 | 0.2381 | 1.434 | 1.431 | 1.427 | 1.964 | 1.932 | 2.073 | Over-range | 60 | 17977 | 17163 | 15403 | 50544 | - - - | - - - | - - - | - - - | 17977 | 17163 | 15403 | 50544 | 11245 | 8996 | 10466 | 30706 | - - - | - - - | - - - | - - - | 11245 | 8996 | 10466 | 30706 | 21806 | 19938 | 19213 | 60958 | # # # | # # # | # # # | # # # | 0.824 | 0.861 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.847 | 0.885 | 0.826 | 0.853 | - - - | 0.608 | 1.84 | 1.74 | 1.69 | 1.67 | 1.68 | 1.71 | 22.52 | 23.05 | 24.17 | 0 | - - - | - - - | - - - | - - - | 21806 | 19938 | 19213 | 60958 | Over-range | 12336 | 10137 | 11476 | 34053 | 5001 | 4603 | 4637 | 14517 | 17989 | 17210 | 15414 | 50613 | 17989 | 17210 | 15414 | 50613 | - - - | - - - | - - - | - - -
5/10/2026 | 4:30:00 AM | 285.72 | 283.14 | 281.34 | 494.22 | 487.24 | 491.13 | 75.9561 | 70.0795 | 67.4674 | 0.2351 | 1.434 | 1.432 | 1.428 | 1.964 | 1.926 | 2.078 | Over-range | 60 | 17739 | 16975 | 15084 | 49798 | - - - | - - - | - - - | - - - | 17739 | 16975 | 15084 | 49798 | 11134 | 8730 | 10251 | 30114 | - - - | - - - | - - - | - - - | 11134 | 8730 | 10251 | 30114 | 21536 | 19662 | 18824 | 60022 | # # # | # # # | # # # | # # # | 0.824 | 0.863 | 0.801 | 0.83 | # # # | # # # | # # # | - - - | 0.846 | 0.887 | 0.826 | 0.853 | - - - | 0.605 | 1.87 | 1.75 | 1.7 | 1.69 | 1.7 | 1.73 | 22.46 | 23.18 | 24.24 | 0 | - - - | - - - | - - - | - - - | 21536 | 19662 | 18824 | 60022 | Over-range | 12203 | 9905 | 11247 | 33471 | 4896 | 4591 | 4532 | 14338 | 17742 | 16965 | 15152 | 49860 | 17742 | 16965 | 15152 | 49860 | - - - | - - - | - - - | - - -
5/10/2026 | 4:45:00 AM | 285.74 | 283.19 | 281.35 | 494.24 | 487.34 | 491.12 | 76.4113 | 70.7327 | 68.6993 | 0.2371 | 1.433 | 1.431 | 1.427 | 1.979 | 1.952 | 2.082 | Over-range | 60 | 17875 | 17057 | 15367 | 50299 | - - - | - - - | - - - | - - - | 17875 | 17057 | 15367 | 50299 | 11170 | 8966 | 10433 | 30569 | - - - | - - - | - - - | - - - | 11170 | 8966 | 10433 | 30569 | 21715 | 19898 | 19211 | 60824 | # # # | # # # | # # # | # # # | 0.823 | 0.857 | 0.8 | 0.827 | # # # | # # # | # # # | - - - | 0.847 | 0.883 | 0.827 | 0.853 | - - - | 0.608 | 1.85 | 1.76 | 1.7 | 1.68 | 1.69 | 1.72 | 23.23 | 24.06 | 25.01 | 0 | - - - | - - - | - - - | - - - | 21715 | 19898 | 19211 | 60824 | Over-range | 12315 | 10224 | 11512 | 34147 | 5107 | 4840 | 4788 | 14996 | 17895 | 17040 | 15437 | 50373 | 17895 | 17040 | 15437 | 50373 | - - - | - - - | - - - | - - -
5/10/2026 | 5:00:00 AM | 285.23 | 282.69 | 280.97 | 493.33 | 486.57 | 490.41 | 78.1659 | 72.8286 | 70.3081 | 0.2649 | 1.435 | 1.432 | 1.429 | 1.982 | 1.964 | 2.095 | Over-range | 60.02 | 18336 | 17622 | 15863 | 51820 | - - - | - - - | - - - | - - - | 18336 | 17622 | 15863 | 51820 | 11195 | 8971 | 10344 | 30511 | - - - | - - - | - - - | - - - | 11195 | 8971 | 10344 | 30511 | 22144 | 20422 | 19610 | 62176 | # # # | # # # | # # # | # # # | 0.828 | 0.863 | 0.809 | 0.834 | # # # | # # # | # # # | - - - | 0.853 | 0.889 | 0.837 | 0.86 | - - - | 0.589 | 1.88 | 1.74 | 1.75 | 1.69 | 1.71 | 1.75 | 23.7 | 24.47 | 25.65 | 0 | - - - | - - - | - - - | - - - | 22144 | 20422 | 19610 | 62176 | Over-range | 12408 | 10308 | 11518 | 34328 | 5272 | 5007 | 4993 | 15518 | 18373 | 17592 | 15932 | 51897 | 18373 | 17592 | 15932 | 51897 | - - - | - - - | - - - | - - -
5/10/2026 | 5:15:00 AM | 285.72 | 283.25 | 281.58 | 494.25 | 487.61 | 491.32 | 79.1684 | 73.7175 | 70.9021 | 0.2754 | 1.434 | 1.431 | 1.429 | 1.977 | 1.962 | 2.089 | Over-range | 60.01 | 18573 | 17884 | 16002 | 52459 | - - - | - - - | - - - | - - - | 18573 | 17884 | 16002 | 52459 | 11446 | 9101 | 10504 | 31052 | - - - | - - - | - - - | - - - | 11446 | 9101 | 10504 | 31052 | 22461 | 20708 | 19807 | 62977 | # # # | # # # | # # # | # # # | 0.827 | 0.864 | 0.808 | 0.833 | # # # | # # # | # # # | - - - | 0.851 | 0.89 | 0.835 | 0.859 | - - - | 0.592 | 1.88 | 1.73 | 1.71 | 1.68 | 1.69 | 1.75 | 23.3 | 24.26 | 25.45 | 0 | - - - | - - - | - - - | - - - | 22461 | 20708 | 19807 | 62977 | Over-range | 12624 | 10425 | 11662 | 34813 | 5239 | 5003 | 4983 | 15499 | 18631 | 17858 | 16052 | 52540 | 18631 | 17858 | 16052 | 52540 | - - - | - - - | - - - | - - -
5/10/2026 | 5:30:00 AM | 285.71 | 283.16 | 281.6 | 494.12 | 487.57 | 491.36 | 78.0872 | 72.356 | 70.9135 | 0.275 | 1.434 | 1.43 | 1.428 | 1.974 | 1.973 | 2.087 | Over-range | 60.01 | 18426 | 17495 | 15996 | 51917 | - - - | - - - | - - - | - - - | 18426 | 17495 | 15996 | 51917 | 11223 | 9160 | 10635 | 31019 | - - - | - - - | - - - | - - - | 11223 | 9160 | 10635 | 31019 | 22208 | 20376 | 19868 | 62453 | # # # | # # # | # # # | # # # | 0.83 | 0.859 | 0.805 | 0.831 | # # # | # # # | # # # | - - - | 0.854 | 0.884 | 0.832 | 0.857 | - - - | 0.598 | 1.83 | 1.65 | 1.61 | 1.62 | 1.6 | 1.66 | 23.29 | 24.23 | 25.31 | 0 | - - - | - - - | - - - | - - - | 22208 | 20376 | 19868 | 62453 | Over-range | 12392 | 10436 | 11776 | 34691 | 5194 | 4946 | 5001 | 15368 | 18480 | 17467 | 16047 | 51994 | 18480 | 17467 | 16047 | 51994 | - - - | - - - | - - - | - - -
5/10/2026 | 5:45:00 AM | 285.57 | 283.01 | 281.42 | 493.92 | 487.26 | 491.06 | 78.4742 | 72.8084 | 70.6739 | 0.2743 | 1.433 | 1.429 | 1.427 | 1.968 | 1.964 | 2.088 | Over-range | 60 | 18441 | 17619 | 15913 | 51973 | - - - | - - - | - - - | - - - | 18441 | 17619 | 15913 | 51973 | 11315 | 9096 | 10529 | 30940 | - - - | - - - | - - - | - - - | 11315 | 9096 | 10529 | 30940 | 22284 | 20466 | 19765 | 62516 | # # # | # # # | # # # | # # # | 0.828 | 0.861 | 0.805 | 0.831 | # # # | # # # | # # # | - - - | 0.852 | 0.886 | 0.832 | 0.857 | - - - | 0.595 | 1.78 | 1.64 | 1.59 | 1.6 | 1.58 | 1.64 | 23.16 | 24.08 | 25.37 | 0 | - - - | - - - | - - - | - - - | 22284 | 20466 | 19765 | 62516 | Over-range | 12496 | 10393 | 11708 | 34694 | 5220 | 4955 | 5045 | 15477 | 18526 | 17593 | 15926 | 52045 | 18526 | 17593 | 15926 | 52045 | - - - | - - - | - - - | - - -
5/10/2026 | 6:00:00 AM | 285.71 | 283.19 | 281.66 | 494.16 | 487.64 | 491.41 | 77.1275 | 71.406 | 69.601 | 0.2729 | 1.434 | 1.429 | 1.427 | 1.962 | 1.96 | 2.085 | Over-range | 60.01 | 18098 | 17231 | 15624 | 50954 | - - - | - - - | - - - | - - - | 18098 | 17231 | 15624 | 50954 | 11164 | 9045 | 10469 | 30678 | - - - | - - - | - - - | - - - | 11164 | 9045 | 10469 | 30678 | 21875 | 20047 | 19452 | 61374 | # # # | # # # | # # # | # # # | 0.827 | 0.86 | 0.803 | 0.83 | # # # | # # # | # # # | - - - | 0.851 | 0.884 | 0.829 | 0.855 | - - - | 0.602 | 1.8 | 1.62 | 1.6 | 1.6 | 1.58 | 1.64 | 22.82 | 23.65 | 25 | 0 | - - - | - - - | - - - | - - - | 21875 | 20047 | 19452 | 61374 | Over-range | 12280 | 10230 | 11576 | 34181 | 5026 | 4698 | 4860 | 14832 | 18181 | 17248 | 15600 | 51030 | 18181 | 17248 | 15600 | 51030 | - - - | - - - | - - - | - - -
5/10/2026 | 6:15:00 AM | 285.7 | 283.27 | 281.65 | 494.22 | 487.76 | 491.32 | 77.4747 | 72.0433 | 70.0395 | 0.2753 | 1.433 | 1.43 | 1.427 | 1.962 | 1.961 | 2.073 | Over-range | 60 | 18207 | 17417 | 15784 | 51409 | - - - | - - - | - - - | - - - | 18207 | 17417 | 15784 | 51409 | 11259 | 9167 | 10521 | 30947 | - - - | - - - | - - - | - - - | 11259 | 9167 | 10521 | 30947 | 22006 | 20263 | 19600 | 61870 | # # # | # # # | # # # | # # # | 0.827 | 0.86 | 0.805 | 0.831 | # # # | # # # | # # # | - - - | 0.85 | 0.884 | 0.83 | 0.855 | - - - | 0.602 | 1.78 | 1.65 | 1.59 | 1.6 | 1.58 | 1.63 | 22.55 | 23.42 | 24.68 | 0 | - - - | - - - | - - - | - - - | 22006 | 20263 | 19600 | 61870 | Over-range | 12353 | 10344 | 11609 | 34396 | 5011 | 4724 | 4842 | 14812 | 18288 | 17432 | 15761 | 51481 | 18288 | 17432 | 15761 | 51481 | - - - | - - - | - - - | - - -
5/10/2026 | 6:30:00 AM | 285.39 | 282.91 | 281.33 | 493.64 | 487.13 | 490.84 | 77.3674 | 71.6175 | 69.4278 | 0.2723 | 1.434 | 1.43 | 1.428 | 1.961 | 1.963 | 2.086 | Over-range | 60.01 | 18135 | 17318 | 15580 | 51033 | - - - | - - - | - - - | - - - | 18135 | 17318 | 15580 | 51033 | 11172 | 8927 | 10434 | 30533 | - - - | - - - | - - - | - - - | 11172 | 8927 | 10434 | 30533 | 21927 | 20096 | 19386 | 61408 | # # # | # # # | # # # | # # # | 0.827 | 0.862 | 0.804 | 0.831 | # # # | # # # | # # # | - - - | 0.85 | 0.887 | 0.83 | 0.856 | - - - | 0.598 | 1.77 | 1.63 | 1.59 | 1.59 | 1.58 | 1.63 | 22.86 | 23.8 | 25.07 | 0 | - - - | - - - | - - - | - - - | 21927 | 20096 | 19386 | 61408 | Over-range | 12315 | 10177 | 11522 | 34117 | 5090 | 4803 | 4802 | 14970 | 18125 | 17344 | 15637 | 51106 | 18125 | 17344 | 15637 | 51106 | - - - | - - - | - - - | - - -
5/10/2026 | 6:45:00 AM | 285.5 | 283.04 | 281.46 | 493.87 | 487.34 | 491.03 | 77.0666 | 71.5305 | 69.6267 | 0.2718 | 1.434 | 1.43 | 1.428 | 1.97 | 1.959 | 2.077 | Over-range | 60.01 | 18039 | 17220 | 15607 | 50866 | - - - | - - - | - - - | - - - | 18039 | 17220 | 15607 | 50866 | 11189 | 9083 | 10523 | 30794 | - - - | - - - | - - - | - - - | 11189 | 9083 | 10523 | 30794 | 21856 | 20083 | 19449 | 61388 | # # # | # # # | # # # | # # # | 0.825 | 0.858 | 0.803 | 0.829 | # # # | # # # | # # # | - - - | 0.848 | 0.883 | 0.828 | 0.853 | - - - | 0.605 | 1.76 | 1.64 | 1.63 | 1.6 | 1.6 | 1.64 | 22.78 | 23.58 | 24.62 | 0 | - - - | - - - | - - - | - - - | 21856 | 20083 | 19449 | 61388 | Over-range | 12325 | 10313 | 11589 | 34317 | 5085 | 4809 | 4775 | 14915 | 18030 | 17238 | 15674 | 50942 | 18030 | 17238 | 15674 | 50942 | - - - | - - - | - - - | - - -
5/10/2026 | 7:00:00 AM | 285.54 | 283.14 | 281.59 | 493.91 | 487.64 | 491.15 | 76.6116 | 71.8019 | 69.3333 | 0.275 | 1.434 | 1.43 | 1.428 | 1.945 | 1.938 | 2.06 | Over-range | 60 | 17905 | 17320 | 15642 | 50867 | - - - | - - - | - - - | - - - | 17905 | 17320 | 15642 | 50867 | 11304 | 9273 | 10463 | 31040 | - - - | - - - | - - - | - - - | 11304 | 9273 | 10463 | 31040 | 21744 | 20187 | 19396 | 61328 | # # # | # # # | # # # | # # # | 0.823 | 0.858 | 0.806 | 0.829 | # # # | # # # | # # # | - - - | 0.845 | 0.881 | 0.83 | 0.852 | - - - | 0.61 | 1.78 | 1.66 | 1.61 | 1.61 | 1.59 | 1.65 | 21.87 | 22.41 | 23.79 | 0 | - - - | - - - | - - - | - - - | 21744 | 20187 | 19396 | 61328 | Over-range | 12331 | 10358 | 11459 | 34231 | 4843 | 4539 | 4595 | 14201 | 17924 | 17359 | 15654 | 50938 | 17924 | 17359 | 15654 | 50938 | - - - | - - - | - - - | - - -
5/10/2026 | 7:15:00 AM | 285.51 | 283.22 | 281.6 | 493.97 | 487.72 | 491.09 | 77.2463 | 72.2545 | 69.3738 | 0.274 | 1.433 | 1.43 | 1.428 | 1.935 | 1.929 | 2.05 | Over-range | 60 | 18028 | 17474 | 15626 | 51129 | - - - | - - - | - - - | - - - | 18028 | 17474 | 15626 | 51129 | 11452 | 9225 | 10460 | 31138 | - - - | - - - | - - - | - - - | 11452 | 9225 | 10460 | 31138 | 21902 | 20298 | 19385 | 61585 | # # # | # # # | # # # | # # # | 0.823 | 0.861 | 0.806 | 0.83 | # # # | # # # | # # # | - - - | 0.844 | 0.883 | 0.829 | 0.852 | - - - | 0.609 | 1.76 | 1.64 | 1.61 | 1.6 | 1.57 | 1.63 | 21.37 | 22.17 | 23.49 | 0 | - - - | - - - | - - - | - - - | 21902 | 20298 | 19385 | 61585 | Over-range | 12429 | 10314 | 11459 | 34298 | 4732 | 4525 | 4591 | 14115 | 18112 | 17459 | 15623 | 51193 | 18112 | 17459 | 15623 | 51193 | - - - | - - - | - - - | - - -
5/10/2026 | 7:30:00 AM | 285.3 | 282.99 | 281.33 | 493.63 | 487.23 | 490.71 | 76.2484 | 71.2574 | 69.22 | 0.2723 | 1.434 | 1.43 | 1.428 | 1.941 | 1.929 | 2.053 | Over-range | 60 | 17833 | 17156 | 15583 | 50572 | - - - | - - - | - - - | - - - | 17833 | 17156 | 15583 | 50572 | 11278 | 9286 | 10530 | 31094 | - - - | - - - | - - - | - - - | 11278 | 9286 | 10530 | 31094 | 21634 | 20030 | 19356 | 61020 | # # # | # # # | # # # | # # # | 0.824 | 0.857 | 0.805 | 0.829 | # # # | # # # | # # # | - - - | 0.845 | 0.878 | 0.828 | 0.85 | - - - | 0.615 | 1.77 | 1.64 | 1.6 | 1.6 | 1.57 | 1.64 | 21.5 | 22.04 | 23.22 | 0 | - - - | - - - | - - - | - - - | 21634 | 20030 | 19356 | 61020 | Over-range | 12243 | 10330 | 11473 | 34126 | 4703 | 4466 | 4494 | 13884 | 17871 | 17137 | 15636 | 50643 | 17871 | 17137 | 15636 | 50643 | - - - | - - - | - - - | - - -
5/10/2026 | 7:45:00 AM | 284.97 | 282.61 | 281.04 | 492.95 | 486.71 | 490.19 | 78.3305 | 73.6033 | 71.2282 | 0.2773 | 1.433 | 1.43 | 1.428 | 1.944 | 1.943 | 2.059 | Over-range | 60 | 18258 | 17661 | 16028 | 51947 | - - - | - - - | - - - | - - - | 18258 | 17661 | 16028 | 51947 | 11426 | 9452 | 10645 | 31523 | - - - | - - - | - - - | - - - | 11426 | 9452 | 10645 | 31523 | 22151 | 20615 | 19851 | 62617 | # # # | # # # | # # # | # # # | 0.824 | 0.857 | 0.807 | 0.83 | # # # | # # # | # # # | - - - | 0.846 | 0.88 | 0.832 | 0.853 | - - - | 0.607 | 1.77 | 1.64 | 1.6 | 1.6 | 1.58 | 1.64 | 22.03 | 22.6 | 23.9 | 0 | - - - | - - - | - - - | - - - | 22151 | 20615 | 19851 | 62617 | Over-range | 12526 | 10610 | 11693 | 34906 | 5019 | 4714 | 4731 | 14675 | 18236 | 17721 | 16067 | 52024 | 18236 | 17721 | 16067 | 52024 | - - - | - - - | - - - | - - -
5/10/2026 | 8:00:00 AM | 284.87 | 282.55 | 280.99 | 492.8 | 486.62 | 490.07 | 77.6614 | 72.9071 | 70.4068 | 0.2577 | 1.433 | 1.43 | 1.428 | 1.96 | 1.956 | 2.074 | Over-range | 60.01 | 18185 | 17605 | 15924 | 51714 | - - - | - - - | - - - | - - - | 18185 | 17605 | 15924 | 51714 | 11246 | 9218 | 10437 | 30901 | - - - | - - - | - - - | - - - | 11246 | 9218 | 10437 | 30901 | 22001 | 20467 | 19659 | 62127 | # # # | # # # | # # # | # # # | 0.827 | 0.86 | 0.81 | 0.832 | # # # | # # # | # # # | - - - | 0.849 | 0.885 | 0.835 | 0.857 | - - - | 0.598 | 1.77 | 1.62 | 1.61 | 1.6 | 1.57 | 1.63 | 22.65 | 23.29 | 24.6 | 0 | - - - | - - - | - - - | - - - | 22001 | 20467 | 19659 | 62127 | Over-range | 12375 | 10426 | 11518 | 34401 | 5091 | 4799 | 4797 | 14903 | 18165 | 17665 | 15960 | 51790 | 18165 | 17665 | 15960 | 51790 | - - - | - - - | - - - | - - -
5/10/2026 | 8:15:00 AM | 284.7 | 282.38 | 280.79 | 492.52 | 486.25 | 489.77 | 77.2527 | 72.406 | 70.3146 | 0.2739 | 1.433 | 1.43 | 1.428 | 1.962 | 1.964 | 2.073 | Over-range | 60 | 18035 | 17376 | 15817 | 51228 | - - - | - - - | - - - | - - - | 18035 | 17376 | 15817 | 51228 | 11227 | 9248 | 10479 | 30954 | - - - | - - - | - - - | - - - | 11227 | 9248 | 10479 | 30954 | 21846 | 20284 | 19599 | 61730 | # # # | # # # | # # # | # # # | 0.826 | 0.857 | 0.807 | 0.83 | # # # | # # # | # # # | - - - | 0.848 | 0.881 | 0.833 | 0.854 | - - - | 0.604 | 1.76 | 1.63 | 1.58 | 1.6 | 1.56 | 1.62 | 22.78 | 23.57 | 24.75 | 0 | - - - | - - - | - - - | - - - | 21846 | 20284 | 19599 | 61730 | Over-range | 12321 | 10454 | 11561 | 34412 | 5003 | 4805 | 4812 | 14824 | 18072 | 17357 | 15884 | 51313 | 18072 | 17357 | 15884 | 51313 | - - - | - - - | - - - | - - -
5/10/2026 | 8:30:00 AM | 284.37 | 282.07 | 280.46 | 491.94 | 485.74 | 489.19 | 78.8691 | 74.179 | 71.5155 | 0.2775 | 1.434 | 1.43 | 1.429 | 1.96 | 1.959 | 2.066 | Over-range | 60.01 | 18438 | 17872 | 16169 | 52479 | - - - | - - - | - - - | - - - | 18438 | 17872 | 16169 | 52479 | 11378 | 9294 | 10487 | 31159 | - - - | - - - | - - - | - - - | 11378 | 9294 | 10487 | 31159 | 22274 | 20757 | 19909 | 62940 | # # # | # # # | # # # | # # # | 0.828 | 0.861 | 0.812 | 0.834 | # # # | # # # | # # # | - - - | 0.851 | 0.886 | 0.839 | 0.858 | - - - | 0.594 | 1.75 | 1.61 | 1.58 | 1.59 | 1.55 | 1.61 | 22.66 | 23.57 | 24.71 | 0 | - - - | - - - | - - - | - - - | 22274 | 20757 | 19909 | 62940 | Over-range | 12489 | 10546 | 11604 | 34718 | 5068 | 4909 | 4893 | 15088 | 18497 | 17843 | 16225 | 52564 | 18497 | 17843 | 16225 | 52564 | - - - | - - - | - - - | - - -
5/10/2026 | 8:45:00 AM | 284.31 | 281.97 | 280.45 | 491.79 | 485.63 | 489.15 | 76.0212 | 71.5019 | 69.2948 | 0.2728 | 1.434 | 1.431 | 1.429 | 1.999 | 2.005 | 2.107 | Over-range | 60 | 17705 | 17089 | 15573 | 50366 | - - - | - - - | - - - | - - - | 17705 | 17089 | 15573 | 50366 | 10769 | 8862 | 10047 | 29679 | - - - | - - - | - - - | - - - | 10769 | 8862 | 10047 | 29679 | 21431 | 19961 | 19258 | 60651 | # # # | # # # | # # # | # # # | 0.826 | 0.856 | 0.809 | 0.83 | # # # | # # # | # # # | - - - | 0.852 | 0.885 | 0.839 | 0.859 | - - - | 0.589 | 1.75 | 1.65 | 1.59 | 1.59 | 1.57 | 1.62 | 24.67 | 25.66 | 26.81 | 0 | - - - | - - - | - - - | - - - | 21431 | 19961 | 19258 | 60651 | Over-range | 12060 | 10291 | 11311 | 33732 | 5332 | 5147 | 5109 | 15773 | 17719 | 17090 | 15649 | 50459 | 17719 | 17090 | 15649 | 50459 | - - - | - - - | - - - | - - -
5/10/2026 | 9:00:00 AM | 283.93 | 281.62 | 280.05 | 491.2 | 484.91 | 488.49 | 77.1879 | 72.501 | 70.386 | 0.2751 | 1.433 | 1.431 | 1.429 | 1.98 | 1.978 | 2.085 | Over-range | 60 | 18078 | 17430 | 15912 | 51420 | - - - | - - - | - - - | - - - | 18078 | 17430 | 15912 | 51420 | 10972 | 9061 | 10232 | 30265 | - - - | - - - | - - - | - - - | 10972 | 9061 | 10232 | 30265 | 21796 | 20287 | 19593 | 61676 | # # # | # # # | # # # | # # # | 0.829 | 0.859 | 0.812 | 0.834 | # # # | # # # | # # # | - - - | 0.855 | 0.886 | 0.84 | 0.86 | - - - | 0.589 | 1.72 | 1.63 | 1.57 | 1.56 | 1.55 | 1.6 | 23.68 | 24.51 | 25.65 | 0 | - - - | - - - | - - - | - - - | 21796 | 20287 | 19593 | 61676 | Over-range | 12169 | 10371 | 11421 | 34031 | 5192 | 4979 | 5008 | 15361 | 18141 | 17423 | 15943 | 51507 | 18141 | 17423 | 15943 | 51507 | - - - | - - - | - - - | - - -
5/10/2026 | 9:15:00 AM | 283.5 | 281.05 | 279.6 | 490.26 | 484.04 | 487.79 | 78.8037 | 73.9308 | 71.4826 | 0.2756 | 1.433 | 1.431 | 1.429 | 1.99 | 1.995 | 2.094 | Over-range | 59.99 | 18446 | 17776 | 16155 | 52377 | - - - | - - - | - - - | - - - | 18446 | 17776 | 16155 | 52377 | 10995 | 8927 | 10183 | 30105 | - - - | - - - | - - - | - - - | 10995 | 8927 | 10183 | 30105 | 22172 | 20598 | 19833 | 62604 | # # # | # # # | # # # | # # # | 0.832 | 0.863 | 0.815 | 0.837 | # # # | # # # | # # # | - - - | 0.858 | 0.891 | 0.845 | 0.865 | - - - | 0.575 | 1.72 | 1.63 | 1.56 | 1.57 | 1.56 | 1.6 | 24.35 | 25.5 | 26.61 | 0 | - - - | - - - | - - - | - - - | 22172 | 20598 | 19833 | 62604 | Over-range | 12294 | 10390 | 11492 | 34256 | 5411 | 5240 | 5248 | 16106 | 18524 | 17747 | 16195 | 52466 | 18524 | 17747 | 16195 | 52466 | - - - | - - - | - - - | - - -
5/10/2026 | 9:30:00 AM | 283.12 | 280.72 | 279.26 | 489.67 | 483.48 | 487.14 | 79.5921 | 74.8721 | 72.8234 | 0.2786 | 1.433 | 1.431 | 1.43 | 2.005 | 2.014 | 2.102 | Over-range | 60 | 18640 | 17932 | 16456 | 53028 | - - - | - - - | - - - | - - - | 18640 | 17932 | 16456 | 53028 | 10962 | 9060 | 10260 | 30282 | - - - | - - - | - - - | - - - | 10962 | 9060 | 10260 | 30282 | 22367 | 20839 | 20177 | 63383 | # # # | # # # | # # # | # # # | 0.833 | 0.861 | 0.816 | 0.837 | # # # | # # # | # # # | - - - | 0.862 | 0.891 | 0.848 | 0.867 | - - - | 0.571 | 1.74 | 1.63 | 1.58 | 1.58 | 1.57 | 1.63 | 25.24 | 26.45 | 27.47 | 0 | - - - | - - - | - - - | - - - | 22367 | 20839 | 20177 | 63383 | Over-range | 12356 | 10606 | 11662 | 34690 | 5623 | 5442 | 5474 | 16708 | 18735 | 17925 | 16473 | 53133 | 18735 | 17925 | 16473 | 53133 | - - - | - - - | - - - | - - -
5/10/2026 | 9:45:00 AM | 282.94 | 280.46 | 278.99 | 489.32 | 482.95 | 486.78 | 79.8303 | 74.9829 | 72.212 | 0.2774 | 1.433 | 1.43 | 1.429 | 2.005 | 2.003 | 2.104 | Over-range | 60.01 | 18661 | 18032 | 16313 | 53006 | - - - | - - - | - - - | - - - | 18661 | 18032 | 16313 | 53006 | 11062 | 8949 | 10169 | 30179 | - - - | - - - | - - - | - - - | 11062 | 8949 | 10169 | 30179 | 22439 | 20870 | 20002 | 63311 | # # # | # # # | # # # | # # # | 0.832 | 0.864 | 0.816 | 0.837 | # # # | # # # | # # # | - - - | 0.86 | 0.895 | 0.847 | 0.867 | - - - | 0.569 | 1.71 | 1.64 | 1.58 | 1.56 | 1.57 | 1.61 | 25.03 | 26.14 | 27.4 | 0 | - - - | - - - | - - - | - - - | 22439 | 20870 | 20002 | 63311 | Over-range | 12448 | 10489 | 11559 | 34578 | 5636 | 5405 | 5432 | 16680 | 18749 | 18057 | 16304 | 53109 | 18749 | 18057 | 16304 | 53109 | - - - | - - - | - - - | - - -
5/10/2026 | 10:00:00 AM | 282.54 | 280.05 | 278.67 | 488.56 | 482.35 | 486.18 | 77.9903 | 72.8031 | 70.8529 | 0.2744 | 1.433 | 1.431 | 1.43 | 1.981 | 1.98 | 2.085 | Over-range | 60.02 | 18180 | 17399 | 15883 | 51462 | - - - | - - - | - - - | - - - | 18180 | 17399 | 15883 | 51462 | 10871 | 8867 | 10202 | 29940 | - - - | - - - | - - - | - - - | 10871 | 8867 | 10202 | 29940 | 21852 | 20193 | 19571 | 61617 | # # # | # # # | # # # | # # # | 0.832 | 0.862 | 0.812 | 0.835 | # # # | # # # | # # # | - - - | 0.857 | 0.889 | 0.84 | 0.862 | - - - | 0.582 | 1.71 | 1.65 | 1.56 | 1.55 | 1.57 | 1.6 | 23.91 | 24.98 | 26.06 | 0 | - - - | - - - | - - - | - - - | 21852 | 20193 | 19571 | 61617 | Over-range | 12116 | 10234 | 11421 | 33851 | 5262 | 5028 | 5052 | 15548 | 18222 | 17406 | 15924 | 51551 | 18222 | 17406 | 15924 | 51551 | - - - | - - - | - - - | - - -
5/10/2026 | 10:15:00 AM | 281.96 | 279.43 | 278.04 | 487.49 | 481.26 | 485.17 | 78.4665 | 73.3034 | 71.2304 | 0.2747 | 1.433 | 1.431 | 1.429 | 1.977 | 1.971 | 2.082 | Over-range | 60.01 | 18349 | 17594 | 16045 | 51989 | - - - | - - - | - - - | - - - | 18349 | 17594 | 16045 | 51989 | 10896 | 8904 | 10216 | 30016 | - - - | - - - | - - - | - - - | 10896 | 8904 | 10216 | 30016 | 21994 | 20341 | 19677 | 62011 | # # # | # # # | # # # | # # # | 0.834 | 0.865 | 0.815 | 0.838 | # # # | # # # | # # # | - - - | 0.859 | 0.892 | 0.843 | 0.865 | - - - | 0.577 | 1.67 | 1.62 | 1.57 | 1.53 | 1.55 | 1.58 | 23.53 | 24.23 | 25.46 | 0 | - - - | - - - | - - - | - - - | 21994 | 20341 | 19677 | 62011 | Over-range | 12119 | 10198 | 11380 | 33777 | 5242 | 4911 | 4952 | 15309 | 18352 | 17664 | 16063 | 52078 | 18352 | 17664 | 16063 | 52078 | - - - | - - - | - - - | - - -
5/10/2026 | 10:30:00 AM | 281.68 | 278.95 | 277.72 | 486.82 | 480.46 | 484.78 | 77.2475 | 71.6058 | 69.3545 | 0.2679 | 1.432 | 1.431 | 1.429 | 1.98 | 1.98 | 2.102 | Over-range | 60.01 | 18019 | 17198 | 15541 | 50758 | - - - | - - - | - - - | - - - | 18019 | 17198 | 15541 | 50758 | 10646 | 8440 | 9888 | 28974 | - - - | - - - | - - - | - - - | 10646 | 8440 | 9888 | 28974 | 21594 | 19803 | 19109 | 60507 | # # # | # # # | # # # | # # # | 0.834 | 0.869 | 0.813 | 0.839 | # # # | # # # | # # # | - - - | 0.86 | 0.897 | 0.843 | 0.867 | - - - | 0.571 | 1.65 | 1.6 | 1.57 | 1.51 | 1.55 | 1.55 | 24.07 | 24.95 | 26.34 | 0 | - - - | - - - | - - - | - - - | 21594 | 19803 | 19109 | 60507 | Over-range | 11893 | 9803 | 11107 | 32901 | 5217 | 4914 | 4986 | 15366 | 18063 | 17217 | 15564 | 50843 | 18063 | 17217 | 15564 | 50843 | - - - | - - - | - - - | - - -
5/10/2026 | 10:45:00 AM | 281.31 | 278.51 | 277.31 | 486.11 | 479.68 | 484.15 | 77.5724 | 71.8442 | 70.1199 | 0.2686 | 1.432 | 1.431 | 1.429 | 1.972 | 1.966 | 2.088 | Over-range | 60.01 | 18066 | 17159 | 15653 | 50878 | - - - | - - - | - - - | - - - | 18066 | 17159 | 15653 | 50878 | 10748 | 8640 | 10097 | 29485 | - - - | - - - | - - - | - - - | 10748 | 8640 | 10097 | 29485 | 21664 | 19836 | 19293 | 60793 | # # # | # # # | # # # | # # # | 0.834 | 0.865 | 0.811 | 0.837 | # # # | # # # | # # # | - - - | 0.859 | 0.891 | 0.839 | 0.863 | - - - | 0.58 | 1.62 | 1.59 | 1.53 | 1.48 | 1.53 | 1.53 | 23.44 | 24.17 | 25.46 | 0 | - - - | - - - | - - - | - - - | 21664 | 19836 | 19293 | 60793 | Over-range | 11938 | 9926 | 11259 | 33213 | 5097 | 4793 | 4893 | 15019 | 18124 | 17142 | 15691 | 50957 | 18124 | 17142 | 15691 | 50957 | - - - | - - - | - - - | - - -
5/10/2026 | 11:00:00 AM | 280.96 | 278.11 | 276.94 | 485.43 | 479.05 | 483.53 | 80.2265 | 74.27 | 72.5027 | 0.2757 | 1.432 | 1.431 | 1.429 | 1.923 | 1.915 | 2.036 | Over-range | 60 | 18769 | 17835 | 16273 | 52877 | - - - | - - - | - - - | - - - | 18769 | 17835 | 16273 | 52877 | 11229 | 9091 | 10566 | 30887 | - - - | - - - | - - - | - - - | 11229 | 9091 | 10566 | 30887 | 22416 | 20518 | 19959 | 62892 | # # # | # # # | # # # | # # # | 0.837 | 0.869 | 0.815 | 0.841 | # # # | # # # | # # # | - - - | 0.858 | 0.89 | 0.837 | 0.862 | - - - | 0.584 | 1.62 | 1.59 | 1.48 | 1.47 | 1.51 | 1.51 | 21.04 | 21.49 | 22.85 | 0 | - - - | - - - | - - - | - - - | 22416 | 20518 | 19959 | 62892 | Over-range | 12250 | 10136 | 11546 | 34028 | 4826 | 4412 | 4586 | 14081 | 18807 | 17895 | 16253 | 52955 | 18807 | 17895 | 16253 | 52955 | - - - | - - - | - - - | - - -
5/10/2026 | 11:15:00 AM | 280.66 | 277.81 | 276.66 | 484.95 | 478.49 | 483.05 | 78.3055 | 72.3687 | 70.2876 | 0.2706 | 1.433 | 1.431 | 1.429 | 1.947 | 1.944 | 2.068 | Over-range | 60 | 18227 | 17337 | 15690 | 51254 | - - - | - - - | - - - | - - - | 18227 | 17337 | 15690 | 51254 | 10839 | 8614 | 10094 | 29547 | - - - | - - - | - - - | - - - | 10839 | 8614 | 10094 | 29547 | 21803 | 19919 | 19278 | 61000 | # # # | # # # | # # # | # # # | 0.836 | 0.87 | 0.814 | 0.84 | # # # | # # # | # # # | - - - | 0.859 | 0.895 | 0.839 | 0.865 | - - - | 0.577 | 1.62 | 1.59 | 1.51 | 1.47 | 1.51 | 1.52 | 22.44 | 23.09 | 24.6 | 0 | - - - | - - - | - - - | - - - | 21803 | 19919 | 19278 | 61000 | Over-range | 11955 | 9796 | 11189 | 33045 | 4961 | 4591 | 4752 | 14572 | 18290 | 17374 | 15669 | 51333 | 18290 | 17374 | 15669 | 51333 | - - - | - - - | - - - | - - -
5/10/2026 | 11:30:00 AM | 280.54 | 277.61 | 276.42 | 484.72 | 478.03 | 482.76 | 77.9244 | 71.9548 | 70.1016 | 0.2693 | 1.433 | 1.432 | 1.429 | 1.971 | 1.967 | 2.088 | Over-range | 59.99 | 18150 | 17209 | 15638 | 50998 | - - - | - - - | - - - | - - - | 18150 | 17209 | 15638 | 50998 | 10686 | 8538 | 10029 | 29253 | - - - | - - - | - - - | - - - | 10686 | 8538 | 10029 | 29253 | 21713 | 19815 | 19237 | 60765 | # # # | # # # | # # # | # # # | 0.836 | 0.869 | 0.813 | 0.839 | # # # | # # # | # # # | - - - | 0.861 | 0.895 | 0.84 | 0.866 | - - - | 0.574 | 1.59 | 1.57 | 1.52 | 1.46 | 1.51 | 1.51 | 23.6 | 24.23 | 25.68 | 0 | - - - | - - - | - - - | - - - | 21713 | 19815 | 19237 | 60765 | Over-range | 11910 | 9811 | 11192 | 33011 | 5186 | 4765 | 4902 | 15097 | 18178 | 17284 | 15627 | 51088 | 18178 | 17284 | 15627 | 51088 | - - - | - - - | - - - | - - -
5/10/2026 | 11:45:00 AM | 280.02 | 277.02 | 275.93 | 483.69 | 477.15 | 481.91 | 81.3082 | 75.5414 | 73.1973 | 0.2752 | 1.432 | 1.431 | 1.429 | 1.977 | 1.979 | 2.093 | Over-range | 60 | 18947 | 18076 | 16400 | 53423 | - - - | - - - | - - - | - - - | 18947 | 18076 | 16400 | 53423 | 10953 | 8699 | 10204 | 29856 | - - - | - - - | - - - | - - - | 10953 | 8699 | 10204 | 29856 | 22604 | 20749 | 20039 | 63392 | # # # | # # # | # # # | # # # | 0.838 | 0.871 | 0.818 | 0.843 | # # # | # # # | # # # | - - - | 0.864 | 0.9 | 0.848 | 0.871 | - - - | 0.559 | 1.57 | 1.56 | 1.51 | 1.45 | 1.5 | 1.49 | 24.09 | 24.84 | 26.24 | 0 | - - - | - - - | - - - | - - - | 22604 | 20749 | 20039 | 63392 | Over-range | 12311 | 10164 | 11497 | 34071 | 5519 | 5161 | 5201 | 16131 | 18932 | 18128 | 16453 | 53512 | 18932 | 18128 | 16453 | 53512 | - - - | - - - | - - - | - - -
5/10/2026 | 12:00:00 PM | 281.57 | 278.6 | 277.45 | 486.44 | 479.8 | 484.54 | 79.1863 | 73.3218 | 71.1017 | 0.2714 | 1.432 | 1.431 | 1.429 | 1.989 | 1.994 | 2.111 | Over-range | 60.01 | 18505 | 17628 | 15943 | 52075 | - - - | - - - | - - - | - - - | 18505 | 17628 | 15943 | 52075 | 10865 | 8619 | 10118 | 29602 | - - - | - - - | - - - | - - - | 10865 | 8619 | 10118 | 29602 | 22178 | 20305 | 19612 | 62095 | # # # | # # # | # # # | # # # | 0.834 | 0.868 | 0.813 | 0.839 | # # # | # # # | # # # | - - - | 0.861 | 0.898 | 0.843 | 0.868 | - - - | 0.568 | 1.58 | 1.56 | 1.48 | 1.44 | 1.47 | 1.47 | 24.62 | 25.45 | 26.98 | 0 | - - - | - - - | - - - | - - - | 22178 | 20305 | 19612 | 62095 | Over-range | 12218 | 10066 | 11412 | 33797 | 5528 | 5141 | 5218 | 16132 | 18504 | 17711 | 15956 | 52171 | 18504 | 17711 | 15956 | 52171 | - - - | - - - | - - - | - - -
5/10/2026 | 12:15:00 PM | 282.3 | 279.32 | 278.17 | 487.71 | 481.04 | 485.81 | 77.6241 | 71.6117 | 70.0421 | 0.2696 | 1.433 | 1.432 | 1.429 | 1.991 | 2.001 | 2.116 | Over-range | 60 | 18154 | 17170 | 15655 | 50979 | - - - | - - - | - - - | - - - | 18154 | 17170 | 15655 | 50979 | 10717 | 8593 | 10129 | 29438 | - - - | - - - | - - - | - - - | 10717 | 8593 | 10129 | 29438 | 21804 | 19887 | 19380 | 61071 | # # # | # # # | # # # | # # # | 0.833 | 0.863 | 0.808 | 0.835 | # # # | # # # | # # # | - - - | 0.86 | 0.894 | 0.839 | 0.864 | - - - | 0.578 | 1.59 | 1.56 | 1.44 | 1.45 | 1.46 | 1.47 | 24.83 | 25.67 | 27.17 | 0 | - - - | - - - | - - - | - - - | 21804 | 19887 | 19380 | 61071 | Over-range | 12070 | 10021 | 11415 | 33599 | 5490 | 5097 | 5203 | 16020 | 18152 | 17247 | 15675 | 51073 | 18152 | 17247 | 15675 | 51073 | - - - | - - - | - - - | - - -
5/10/2026 | 12:30:00 PM | 282.14 | 279.26 | 278.09 | 487.48 | 480.97 | 485.56 | 80.4229 | 74.9078 | 72.8389 | 0.2729 | 1.432 | 1.431 | 1.428 | 1.987 | 2.002 | 2.104 | Over-range | 59.99 | 18842 | 17992 | 16407 | 53241 | - - - | - - - | - - - | - - - | 18842 | 17992 | 16407 | 53241 | 11037 | 8888 | 10330 | 30255 | - - - | - - - | - - - | - - - | 11037 | 8888 | 10330 | 30255 | 22560 | 20776 | 20131 | 63468 | # # # | # # # | # # # | # # # | 0.835 | 0.866 | 0.815 | 0.839 | # # # | # # # | # # # | - - - | 0.862 | 0.896 | 0.846 | 0.868 | - - - | 0.568 | 1.58 | 1.52 | 1.41 | 1.44 | 1.42 | 1.44 | 24.73 | 25.71 | 27.07 | 0 | - - - | - - - | - - - | - - - | 22560 | 20776 | 20131 | 63468 | Over-range | 12402 | 10379 | 11654 | 34522 | 5597 | 5305 | 5342 | 16462 | 18848 | 18017 | 16477 | 53341 | 18848 | 18017 | 16477 | 53341 | - - - | - - - | - - - | - - -
5/10/2026 | 12:45:00 PM | 281.89 | 279.04 | 277.85 | 487.09 | 480.58 | 485.13 | 79.0261 | 73.4335 | 71.3254 | 0.2692 | 1.433 | 1.432 | 1.429 | 2.011 | 2.031 | 2.13 | Over-range | 60 | 18489 | 17620 | 16015 | 52124 | - - - | - - - | - - - | - - - | 18489 | 17620 | 16015 | 52124 | 10625 | 8457 | 9945 | 29027 | - - - | - - - | - - - | - - - | 10625 | 8457 | 9945 | 29027 | 22153 | 20361 | 19698 | 62212 | # # # | # # # | # # # | # # # | 0.835 | 0.865 | 0.813 | 0.838 | # # # | # # # | # # # | - - - | 0.865 | 0.9 | 0.848 | 0.871 | - - - | 0.557 | 1.58 | 1.54 | 1.45 | 1.45 | 1.45 | 1.47 | 26.24 | 27.48 | 28.85 | 0 | - - - | - - - | - - - | - - - | 22153 | 20361 | 19698 | 62212 | Over-range | 12185 | 10179 | 11453 | 33906 | 5879 | 5591 | 5600 | 17293 | 18480 | 17675 | 16077 | 52232 | 18480 | 17675 | 16077 | 52232 | - - - | - - - | - - - | - - -
5/10/2026 | 1:00:00 PM | 281.64 | 278.78 | 277.61 | 486.64 | 480.15 | 484.72 | 81.5491 | 76.0389 | 74.1698 | 0.2753 | 1.433 | 1.432 | 1.43 | 2.009 | 2.03 | 2.116 | Over-range | 60 | 19100 | 18197 | 16689 | 53987 | - - - | - - - | - - - | - - - | 19100 | 18197 | 16689 | 53987 | 10908 | 8858 | 10289 | 30055 | - - - | - - - | - - - | - - - | 10908 | 8858 | 10289 | 30055 | 22809 | 21032 | 20438 | 64278 | # # # | # # # | # # # | # # # | 0.837 | 0.865 | 0.817 | 0.84 | # # # | # # # | # # # | - - - | 0.868 | 0.899 | 0.851 | 0.872 | - - - | 0.557 | 1.6 | 1.57 | 1.49 | 1.46 | 1.48 | 1.49 | 26.14 | 27.32 | 28.58 | 0 | - - - | - - - | - - - | - - - | 22809 | 21032 | 20438 | 64278 | Over-range | 12460 | 10535 | 11786 | 34862 | 5959 | 5642 | 5692 | 17485 | 19105 | 18284 | 16716 | 54105 | 19105 | 18284 | 16716 | 54105 | - - - | - - - | - - - | - - -
5/10/2026 | 1:15:00 PM | 281.58 | 278.74 | 277.52 | 486.57 | 480.01 | 484.58 | 82.095 | 76.704 | 74.6243 | 0.276 | 1.434 | 1.433 | 1.431 | 2.004 | 2.024 | 2.106 | Over-range | 60 | 19271 | 18409 | 16861 | 54542 | - - - | - - - | - - - | - - - | 19271 | 18409 | 16861 | 54542 | 10996 | 8935 | 10311 | 30241 | - - - | - - - | - - - | - - - | 10996 | 8935 | 10311 | 30241 | 22984 | 21240 | 20583 | 64808 | # # # | # # # | # # # | # # # | 0.839 | 0.867 | 0.819 | 0.842 | # # # | # # # | # # # | - - - | 0.868 | 0.9 | 0.852 | 0.874 | - - - | 0.555 | 1.59 | 1.6 | 1.47 | 1.47 | 1.49 | 1.5 | 25.7 | 26.87 | 28.15 | 0 | - - - | - - - | - - - | - - - | 22984 | 21240 | 20583 | 64808 | Over-range | 12520 | 10586 | 11797 | 34982 | 5937 | 5629 | 5686 | 17442 | 19305 | 18496 | 16857 | 54658 | 19305 | 18496 | 16857 | 54658 | - - - | - - - | - - - | - - -
5/10/2026 | 1:30:00 PM | 281.36 | 278.61 | 277.36 | 486.22 | 479.85 | 484.22 | 82.0037 | 76.7392 | 74.1227 | 0.2756 | 1.434 | 1.433 | 1.431 | 2.011 | 2.029 | 2.112 | Over-range | 60 | 19178 | 18411 | 16716 | 54305 | - - - | - - - | - - - | - - - | 19178 | 18411 | 16716 | 54305 | 10987 | 8785 | 10154 | 29925 | - - - | - - - | - - - | - - - | 10987 | 8785 | 10154 | 29925 | 22914 | 21214 | 20410 | 64538 | # # # | # # # | # # # | # # # | 0.837 | 0.868 | 0.819 | 0.841 | # # # | # # # | # # # | - - - | 0.867 | 0.902 | 0.853 | 0.874 | - - - | 0.551 | 1.63 | 1.6 | 1.53 | 1.5 | 1.52 | 1.53 | 25.97 | 27.43 | 28.61 | 0 | - - - | - - - | - - - | - - - | 22914 | 21214 | 20410 | 64538 | Over-range | 12532 | 10525 | 11700 | 34842 | 5952 | 5727 | 5744 | 17635 | 19254 | 18452 | 16723 | 54429 | 19254 | 18452 | 16723 | 54429 | - - - | - - - | - - - | - - -
5/10/2026 | 1:45:00 PM | 280.92 | 278.16 | 276.9 | 485.51 | 478.98 | 483.44 | 82.2737 | 76.6073 | 74.7455 | 0.275 | 1.434 | 1.434 | 1.431 | 1.987 | 1.999 | 2.082 | Over-range | 59.99 | 19226 | 18294 | 16776 | 54297 | - - - | - - - | - - - | - - - | 19226 | 18294 | 16776 | 54297 | 11074 | 9000 | 10460 | 30534 | - - - | - - - | - - - | - - - | 11074 | 9000 | 10460 | 30534 | 22947 | 21133 | 20540 | 64620 | # # # | # # # | # # # | # # # | 0.838 | 0.866 | 0.817 | 0.84 | # # # | # # # | # # # | - - - | 0.865 | 0.897 | 0.847 | 0.87 | - - - | 0.562 | 1.65 | 1.61 | 1.52 | 1.5 | 1.53 | 1.54 | 24.74 | 25.93 | 26.93 | 0 | - - - | - - - | - - - | - - - | 22947 | 21133 | 20540 | 64620 | Over-range | 12512 | 10559 | 11835 | 34988 | 5736 | 5436 | 5457 | 16839 | 19247 | 18369 | 16802 | 54417 | 19247 | 18369 | 16802 | 54417 | - - - | - - - | - - - | - - -
5/10/2026 | 2:00:00 PM | 280.5 | 277.75 | 276.5 | 484.79 | 478.28 | 482.75 | 80.7811 | 75.1356 | 72.8535 | 0.2905 | 1.435 | 1.434 | 1.431 | 1.972 | 1.986 | 2.079 | Over-range | 60 | 18878 | 18025 | 16374 | 53276 | - - - | - - - | - - - | - - - | 18878 | 18025 | 16374 | 53276 | 10940 | 8756 | 10188 | 29885 | - - - | - - - | - - - | - - - | 10940 | 8756 | 10188 | 29885 | 22525 | 20725 | 20014 | 63264 | # # # | # # # | # # # | # # # | 0.838 | 0.87 | 0.818 | 0.842 | # # # | # # # | # # # | - - - | 0.864 | 0.899 | 0.848 | 0.87 | - - - | 0.561 | 1.62 | 1.6 | 1.51 | 1.49 | 1.51 | 1.53 | 24.07 | 25.14 | 26.41 | 0 | - - - | - - - | - - - | - - - | 22525 | 20725 | 20014 | 63264 | Over-range | 12281 | 10218 | 11497 | 34087 | 5511 | 5202 | 5263 | 16205 | 18925 | 18084 | 16380 | 53389 | 18925 | 18084 | 16380 | 53389 | - - - | - - - | - - - | - - -
5/10/2026 | 2:15:00 PM | 280.63 | 277.83 | 276.68 | 484.89 | 478.54 | 483.07 | 79.1413 | 73.2772 | 70.9912 | 0.2885 | 1.434 | 1.434 | 1.431 | 1.978 | 1.995 | 2.094 | Over-range | 60 | 18483 | 17606 | 15914 | 52003 | - - - | - - - | - - - | - - - | 18483 | 17606 | 15914 | 52003 | 10789 | 8485 | 9996 | 29270 | - - - | - - - | - - - | - - - | 10789 | 8485 | 9996 | 29270 | 22103 | 20244 | 19538 | 61886 | # # # | # # # | # # # | # # # | 0.836 | 0.87 | 0.815 | 0.84 | # # # | # # # | # # # | - - - | 0.864 | 0.9 | 0.846 | 0.87 | - - - | 0.563 | 1.6 | 1.58 | 1.45 | 1.46 | 1.48 | 1.49 | 24.38 | 25.65 | 26.98 | 0 | - - - | - - - | - - - | - - - | 22103 | 20244 | 19538 | 61886 | Over-range | 12113 | 9978 | 11324 | 33517 | 5444 | 5194 | 5261 | 16155 | 18570 | 17606 | 15941 | 52116 | 18570 | 17606 | 15941 | 52116 | - - - | - - - | - - - | - - -
5/10/2026 | 2:30:00 PM | 280.62 | 277.86 | 276.64 | 484.94 | 478.52 | 483 | 80.077 | 74.3729 | 72.4969 | 0.2926 | 1.434 | 1.434 | 1.43 | 1.977 | 1.997 | 2.086 | Over-range | 59.99 | 18684 | 17767 | 16236 | 52686 | - - - | - - - | - - - | - - - | 18684 | 17767 | 16236 | 52686 | 10818 | 8729 | 10175 | 29722 | - - - | - - - | - - - | - - - | 10818 | 8729 | 10175 | 29722 | 22306 | 20488 | 19900 | 62693 | # # # | # # # | # # # | # # # | 0.838 | 0.867 | 0.816 | 0.84 | # # # | # # # | # # # | - - - | 0.865 | 0.897 | 0.846 | 0.869 | - - - | 0.564 | 1.59 | 1.59 | 1.47 | 1.46 | 1.48 | 1.49 | 24.45 | 25.51 | 26.81 | 0 | - - - | - - - | - - - | - - - | 22306 | 20488 | 19900 | 62693 | Over-range | 12176 | 10189 | 11494 | 33947 | 5509 | 5182 | 5276 | 16184 | 18729 | 17834 | 16234 | 52797 | 18729 | 17834 | 16234 | 52797 | - - - | - - - | - - - | - - -
5/10/2026 | 2:45:00 PM | 280.42 | 277.59 | 276.43 | 484.54 | 478.08 | 482.66 | 81.0847 | 75.286 | 72.9896 | 0.2925 | 1.434 | 1.434 | 1.43 | 1.955 | 1.967 | 2.068 | Over-range | 59.99 | 18887 | 18023 | 16342 | 53252 | - - - | - - - | - - - | - - - | 18887 | 18023 | 16342 | 53252 | 11083 | 8845 | 10325 | 30253 | - - - | - - - | - - - | - - - | 11083 | 8845 | 10325 | 30253 | 22584 | 20734 | 20028 | 63347 | # # # | # # # | # # # | # # # | 0.836 | 0.869 | 0.816 | 0.841 | # # # | # # # | # # # | - - - | 0.861 | 0.897 | 0.844 | 0.867 | - - - | 0.568 | 1.56 | 1.56 | 1.43 | 1.43 | 1.44 | 1.45 | 23.32 | 24.19 | 25.6 | 0 | - - - | - - - | - - - | - - - | 22584 | 20734 | 20028 | 63347 | Over-range | 12365 | 10226 | 11559 | 34248 | 5395 | 5053 | 5117 | 15817 | 18899 | 18090 | 16366 | 53354 | 18899 | 18090 | 16366 | 53354 | - - - | - - - | - - - | - - -
5/10/2026 | 3:00:00 PM | 280.67 | 277.78 | 276.68 | 484.9 | 478.42 | 483.15 | 80.071 | 73.8966 | 71.7106 | 0.2907 | 1.435 | 1.434 | 1.43 | 1.924 | 1.938 | 2.044 | Over-range | 59.99 | 18671 | 17751 | 16029 | 52451 | - - - | - - - | - - - | - - - | 18671 | 17751 | 16029 | 52451 | 11134 | 8775 | 10376 | 30286 | - - - | - - - | - - - | - - - | 11134 | 8775 | 10376 | 30286 | 22334 | 20378 | 19703 | 62414 | # # # | # # # | # # # | # # # | 0.836 | 0.871 | 0.814 | 0.84 | # # # | # # # | # # # | - - - | 0.858 | 0.896 | 0.839 | 0.864 | - - - | 0.577 | 1.58 | 1.56 | 1.46 | 1.44 | 1.46 | 1.47 | 21.99 | 22.8 | 24.22 | 0 | - - - | - - - | - - - | - - - | 22334 | 20378 | 19703 | 62414 | Over-range | 12247 | 9995 | 11446 | 33800 | 5028 | 4715 | 4759 | 14796 | 18668 | 17774 | 16104 | 52547 | 18668 | 17774 | 16104 | 52547 | - - - | - - - | - - - | - - -
5/10/2026 | 3:15:00 PM | 280.7 | 277.84 | 276.63 | 484.98 | 478.48 | 483.08 | 80.7024 | 74.6943 | 72.7419 | 0.2927 | 1.435 | 1.434 | 1.431 | 1.912 | 1.919 | 2.019 | Over-range | 60.01 | 18851 | 17918 | 16303 | 53073 | - - - | - - - | - - - | - - - | 18851 | 17918 | 16303 | 53073 | 11249 | 9017 | 10516 | 30782 | - - - | - - - | - - - | - - - | 11249 | 9017 | 10516 | 30782 | 22508 | 20597 | 19985 | 63091 | # # # | # # # | # # # | # # # | 0.838 | 0.87 | 0.816 | 0.841 | # # # | # # # | # # # | - - - | 0.859 | 0.892 | 0.839 | 0.863 | - - - | 0.58 | 1.57 | 1.53 | 1.45 | 1.43 | 1.44 | 1.46 | 21.15 | 21.95 | 23.16 | 0 | - - - | - - - | - - - | - - - | 22508 | 20597 | 19985 | 63091 | Over-range | 12291 | 10146 | 11548 | 34084 | 4874 | 4581 | 4700 | 14422 | 18933 | 17922 | 16317 | 53173 | 18933 | 17922 | 16317 | 53173 | - - - | - - - | - - - | - - -
5/10/2026 | 3:30:00 PM | 280.51 | 277.62 | 276.54 | 484.61 | 478.18 | 482.9 | 80.7838 | 74.4686 | 72.0671 | 0.2894 | 1.435 | 1.434 | 1.431 | 1.922 | 1.93 | 2.035 | Over-range | 60 | 18869 | 17941 | 16145 | 52955 | - - - | - - - | - - - | - - - | 18869 | 17941 | 16145 | 52955 | 11196 | 8733 | 10384 | 30313 | - - - | - - - | - - - | - - - | 11196 | 8733 | 10384 | 30313 | 22525 | 20528 | 19797 | 62849 | # # # | # # # | # # # | # # # | 0.838 | 0.874 | 0.816 | 0.843 | # # # | # # # | # # # | - - - | 0.859 | 0.898 | 0.841 | 0.866 | - - - | 0.572 | 1.55 | 1.56 | 1.44 | 1.42 | 1.44 | 1.46 | 21.69 | 22.64 | 23.89 | 0 | - - - | - - - | - - - | - - - | 22525 | 20528 | 19797 | 62849 | Over-range | 12294 | 9965 | 11447 | 33824 | 4998 | 4725 | 4739 | 14780 | 18893 | 17945 | 16221 | 53059 | 18893 | 17945 | 16221 | 53059 | - - - | - - - | - - - | - - -
5/10/2026 | 3:45:00 PM | 280.19 | 277.26 | 276.13 | 484.04 | 477.49 | 482.27 | 81.8892 | 75.8826 | 73.8607 | 0.2925 | 1.434 | 1.434 | 1.431 | 1.954 | 1.962 | 2.05 | Over-range | 60.01 | 19120 | 18162 | 16548 | 53830 | - - - | - - - | - - - | - - - | 19120 | 18162 | 16548 | 53830 | 11130 | 8906 | 10454 | 30490 | - - - | - - - | - - - | - - - | 11130 | 8906 | 10454 | 30490 | 22818 | 20898 | 20271 | 63987 | # # # | # # # | # # # | # # # | 0.838 | 0.869 | 0.816 | 0.841 | # # # | # # # | # # # | - - - | 0.863 | 0.897 | 0.844 | 0.868 | - - - | 0.566 | 1.57 | 1.55 | 1.44 | 1.43 | 1.46 | 1.46 | 23.22 | 24.22 | 25.3 | 0 | - - - | - - - | - - - | - - - | 22818 | 20898 | 20271 | 63987 | Over-range | 12437 | 10316 | 11690 | 34540 | 5465 | 5125 | 5151 | 15990 | 19123 | 18233 | 16588 | 53944 | 19123 | 18233 | 16588 | 53944 | - - - | - - - | - - - | - - -
5/10/2026 | 4:00:00 PM | 280.47 | 277.57 | 276.47 | 484.53 | 478.13 | 482.77 | 80.3978 | 74.4615 | 72.0687 | 0.2911 | 1.435 | 1.434 | 1.431 | 1.938 | 1.949 | 2.045 | Over-range | 60 | 18760 | 17891 | 16157 | 52808 | - - - | - - - | - - - | - - - | 18760 | 17891 | 16157 | 52808 | 11037 | 8717 | 10259 | 30014 | - - - | - - - | - - - | - - - | 11037 | 8717 | 10259 | 30014 | 22402 | 20516 | 19781 | 62699 | # # # | # # # | # # # | # # # | 0.837 | 0.872 | 0.817 | 0.842 | # # # | # # # | # # # | - - - | 0.86 | 0.898 | 0.843 | 0.867 | - - - | 0.568 | 1.6 | 1.55 | 1.47 | 1.45 | 1.48 | 1.48 | 22.65 | 23.65 | 24.88 | 0 | - - - | - - - | - - - | - - - | 22402 | 20516 | 19781 | 62699 | Over-range | 12236 | 10029 | 11402 | 33773 | 5212 | 4893 | 4905 | 15285 | 18754 | 17956 | 16209 | 52918 | 18754 | 17956 | 16209 | 52918 | - - - | - - - | - - - | - - -
5/10/2026 | 4:15:00 PM | 280.55 | 277.7 | 276.6 | 484.66 | 478.38 | 482.95 | 80.9295 | 74.8031 | 72.9818 | 0.2929 | 1.435 | 1.435 | 1.431 | 1.928 | 1.945 | 2.036 | Over-range | 60 | 18902 | 17925 | 16335 | 53162 | - - - | - - - | - - - | - - - | 18902 | 17925 | 16335 | 53162 | 11127 | 8921 | 10486 | 30533 | - - - | - - - | - - - | - - - | 11127 | 8921 | 10486 | 30533 | 22550 | 20608 | 20041 | 63199 | # # # | # # # | # # # | # # # | 0.838 | 0.87 | 0.815 | 0.841 | # # # | # # # | # # # | - - - | 0.861 | 0.895 | 0.84 | 0.865 | - - - | 0.574 | 1.6 | 1.57 | 1.48 | 1.46 | 1.47 | 1.49 | 22.25 | 23.16 | 24.42 | 0 | - - - | - - - | - - - | - - - | 22550 | 20608 | 20041 | 63199 | Over-range | 12291 | 10159 | 11600 | 34150 | 5148 | 4794 | 4891 | 15093 | 18916 | 18005 | 16353 | 53274 | 18916 | 18005 | 16353 | 53274 | - - - | - - - | - - - | - - -
5/10/2026 | 4:30:00 PM | 280.37 | 277.63 | 276.47 | 484.5 | 478.2 | 482.63 | 81.3064 | 75.5081 | 73.3373 | 0.2766 | 1.435 | 1.435 | 1.432 | 1.919 | 1.929 | 2.021 | Over-range | 60 | 18994 | 18127 | 16483 | 53604 | - - - | - - - | - - - | - - - | 18994 | 18127 | 16483 | 53604 | 11231 | 9011 | 10467 | 30709 | - - - | - - - | - - - | - - - | 11231 | 9011 | 10467 | 30709 | 22661 | 20821 | 20148 | 63630 | # # # | # # # | # # # | # # # | 0.838 | 0.871 | 0.818 | 0.842 | # # # | # # # | # # # | - - - | 0.86 | 0.894 | 0.843 | 0.866 | - - - | 0.573 | 1.6 | 1.57 | 1.49 | 1.47 | 1.49 | 1.5 | 21.77 | 22.64 | 23.84 | 0 | - - - | - - - | - - - | - - - | 22661 | 20821 | 20148 | 63630 | Over-range | 12351 | 10230 | 11578 | 34256 | 5063 | 4774 | 4878 | 14969 | 19070 | 18155 | 16485 | 53710 | 19070 | 18155 | 16485 | 53710 | - - - | - - - | - - - | - - -
5/10/2026 | 4:45:00 PM | 280.14 | 277.33 | 276.16 | 484.06 | 477.62 | 482.2 | 80.4133 | 74.737 | 72.1574 | 0.2698 | 1.435 | 1.435 | 1.431 | 1.951 | 1.964 | 2.055 | Over-range | 59.99 | 18697 | 17884 | 16142 | 52723 | - - - | - - - | - - - | - - - | 18697 | 17884 | 16142 | 52723 | 10951 | 8632 | 10083 | 29667 | - - - | - - - | - - - | - - - | 10951 | 8632 | 10083 | 29667 | 22350 | 20536 | 19756 | 62642 | # # # | # # # | # # # | # # # | 0.837 | 0.871 | 0.817 | 0.842 | # # # | # # # | # # # | - - - | 0.862 | 0.898 | 0.846 | 0.869 | - - - | 0.563 | 1.57 | 1.57 | 1.45 | 1.44 | 1.46 | 1.47 | 23.45 | 24.58 | 25.89 | 0 | - - - | - - - | - - - | - - - | 22350 | 20536 | 19756 | 62642 | Over-range | 12226 | 10068 | 11369 | 33764 | 5333 | 5095 | 5163 | 15855 | 18802 | 17881 | 16155 | 52838 | 18802 | 17881 | 16155 | 52838 | - - - | - - - | - - - | - - -
5/10/2026 | 5:00:00 PM | 280.16 | 277.34 | 276.18 | 484.02 | 477.7 | 482.25 | 80.4656 | 74.7958 | 72.9977 | 0.2736 | 1.434 | 1.434 | 1.431 | 1.946 | 1.966 | 2.043 | Over-range | 59.99 | 18814 | 17900 | 16392 | 53106 | - - - | - - - | - - - | - - - | 18814 | 17900 | 16392 | 53106 | 10947 | 8865 | 10299 | 30111 | - - - | - - - | - - - | - - - | 10947 | 8865 | 10299 | 30111 | 22416 | 20605 | 20036 | 63057 | # # # | # # # | # # # | # # # | 0.839 | 0.869 | 0.818 | 0.842 | # # # | # # # | # # # | - - - | 0.864 | 0.896 | 0.846 | 0.869 | - - - | 0.567 | 1.57 | 1.53 | 1.42 | 1.42 | 1.43 | 1.44 | 23.16 | 24.22 | 25.39 | 0 | - - - | - - - | - - - | - - - | 22416 | 20605 | 20036 | 63057 | Over-range | 12182 | 10198 | 11511 | 33978 | 5287 | 4987 | 5090 | 15584 | 18874 | 17960 | 16388 | 53222 | 18874 | 17960 | 16388 | 53222 | - - - | - - - | - - - | - - -
5/10/2026 | 5:15:00 PM | 280.35 | 277.94 | 276.64 | 484.72 | 478.76 | 482.66 | 81.4846 | 76.1571 | 73.7596 | 0.274 | 1.434 | 1.434 | 1.431 | 1.941 | 1.956 | 2.03 | Over-range | 60.01 | 19062 | 18302 | 16647 | 54011 | - - - | - - - | - - - | - - - | 19062 | 18302 | 16647 | 54011 | 11103 | 8979 | 10350 | 30432 | - - - | - - - | - - - | - - - | 11103 | 8979 | 10350 | 30432 | 22710 | 21025 | 20272 | 64006 | # # # | # # # | # # # | # # # | 0.839 | 0.871 | 0.821 | 0.844 | # # # | # # # | # # # | - - - | 0.863 | 0.897 | 0.848 | 0.87 | - - - | 0.563 | 1.55 | 1.54 | 1.39 | 1.42 | 1.41 | 1.43 | 22.73 | 23.95 | 24.99 | 0 | - - - | - - - | - - - | - - - | 22710 | 21025 | 20272 | 64006 | Over-range | 12335 | 10338 | 11558 | 34318 | 5299 | 5051 | 5070 | 15646 | 19097 | 18388 | 16640 | 54125 | 19097 | 18388 | 16640 | 54125 | - - - | - - - | - - - | - - -
5/10/2026 | 5:30:00 PM | 280.08 | 277.57 | 276.33 | 484.16 | 478.12 | 482.19 | 80.5857 | 75.0819 | 73.5844 | 0.2731 | 1.434 | 1.434 | 1.431 | 1.942 | 1.954 | 2.027 | Over-range | 60 | 18862 | 17951 | 16553 | 53365 | - - - | - - - | - - - | - - - | 18862 | 17951 | 16553 | 53365 | 10956 | 8999 | 10433 | 30389 | - - - | - - - | - - - | - - - | 10956 | 8999 | 10433 | 30389 | 22457 | 20719 | 20220 | 63396 | # # # | # # # | # # # | # # # | 0.84 | 0.866 | 0.819 | 0.842 | # # # | # # # | # # # | - - - | 0.864 | 0.893 | 0.846 | 0.867 | - - - | 0.57 | 1.57 | 1.53 | 1.41 | 1.42 | 1.42 | 1.44 | 22.78 | 23.89 | 24.7 | 0 | - - - | - - - | - - - | - - - | 22457 | 20719 | 20220 | 63396 | Over-range | 12181 | 10337 | 11603 | 34197 | 5257 | 5023 | 5010 | 15493 | 18872 | 17991 | 16620 | 53483 | 18872 | 17991 | 16620 | 53483 | - - - | - - - | - - - | - - -
5/10/2026 | 5:45:00 PM | 279.98 | 277.54 | 276.29 | 484.04 | 478.12 | 482.03 | 80.3469 | 74.9864 | 72.6997 | 0.2722 | 1.434 | 1.434 | 1.431 | 1.91 | 1.916 | 2.006 | Over-range | 59.99 | 18693 | 17942 | 16310 | 52945 | - - - | - - - | - - - | - - - | 18693 | 17942 | 16310 | 52945 | 11132 | 9020 | 10409 | 30561 | - - - | - - - | - - - | - - - | 11132 | 9020 | 10409 | 30561 | 22337 | 20640 | 19927 | 62904 | # # # | # # # | # # # | # # # | 0.837 | 0.869 | 0.819 | 0.842 | # # # | # # # | # # # | - - - | 0.857 | 0.892 | 0.842 | 0.864 | - - - | 0.577 | 1.56 | 1.51 | 1.43 | 1.42 | 1.41 | 1.44 | 21.18 | 21.98 | 23.06 | 0 | - - - | - - - | - - - | - - - | 22337 | 20640 | 19927 | 62904 | Over-range | 12210 | 10181 | 11430 | 33912 | 4924 | 4636 | 4635 | 14442 | 18682 | 18013 | 16353 | 53049 | 18682 | 18013 | 16353 | 53049 | - - - | - - - | - - - | - - -
5/10/2026 | 6:00:00 PM | 279.96 | 277.66 | 276.35 | 484.12 | 478.34 | 482.02 | 78.1646 | 72.7419 | 70.9839 | 0.2688 | 1.434 | 1.434 | 1.431 | 1.917 | 1.923 | 2.011 | Over-range | 60 | 18181 | 17361 | 15877 | 51419 | - - - | - - - | - - - | - - - | 18181 | 17361 | 15877 | 51419 | 10865 | 8854 | 10271 | 29990 | - - - | - - - | - - - | - - - | 10865 | 8854 | 10271 | 29990 | 21738 | 20041 | 19476 | 61256 | # # # | # # # | # # # | # # # | 0.836 | 0.866 | 0.815 | 0.839 | # # # | # # # | # # # | - - - | 0.857 | 0.89 | 0.839 | 0.862 | - - - | 0.583 | 1.54 | 1.5 | 1.41 | 1.41 | 1.39 | 1.43 | 21.38 | 22.26 | 23.18 | 0 | - - - | - - - | - - - | - - - | 21738 | 20041 | 19476 | 61256 | Over-range | 11908 | 9999 | 11269 | 33260 | 4791 | 4569 | 4553 | 14148 | 18191 | 17380 | 15949 | 51520 | 18191 | 17380 | 15949 | 51520 | - - - | - - - | - - - | - - -
5/10/2026 | 6:15:00 PM | 280.22 | 278 | 276.76 | 484.6 | 479.05 | 482.56 | 76.3314 | 71.0534 | 69.3936 | 0.2664 | 1.435 | 1.434 | 1.432 | 1.92 | 1.93 | 2.014 | Over-range | 60.01 | 17828 | 17025 | 15592 | 50446 | - - - | - - - | - - - | - - - | 17828 | 17025 | 15592 | 50446 | 10610 | 8645 | 10038 | 29293 | - - - | - - - | - - - | - - - | 10610 | 8645 | 10038 | 29293 | 21285 | 19639 | 19099 | 60024 | # # # | # # # | # # # | # # # | 0.838 | 0.867 | 0.816 | 0.84 | # # # | # # # | # # # | - - - | 0.859 | 0.89 | 0.841 | 0.863 | - - - | 0.581 | 1.58 | 1.56 | 1.43 | 1.45 | 1.44 | 1.47 | 21.45 | 22.46 | 23.32 | 0 | - - - | - - - | - - - | - - - | 21285 | 19639 | 19099 | 60024 | Over-range | 11621 | 9779 | 11021 | 32503 | 4678 | 4514 | 4490 | 13909 | 17860 | 17015 | 15670 | 50545 | 17860 | 17015 | 15670 | 50545 | - - - | - - - | - - - | - - -
5/10/2026 | 6:30:00 PM | 280.26 | 278.02 | 276.81 | 484.66 | 479.08 | 482.65 | 75.9825 | 70.5288 | 68.7845 | 0.2671 | 1.434 | 1.434 | 1.431 | 1.927 | 1.937 | 2.023 | Over-range | 59.99 | 17689 | 16867 | 15378 | 49934 | - - - | - - - | - - - | - - - | 17689 | 16867 | 15378 | 49934 | 10590 | 8563 | 9958 | 29111 | - - - | - - - | - - - | - - - | 10590 | 8563 | 9958 | 29111 | 21169 | 19471 | 18914 | 59554 | # # # | # # # | # # # | # # # | 0.836 | 0.866 | 0.813 | 0.839 | # # # | # # # | # # # | - - - | 0.858 | 0.89 | 0.838 | 0.862 | - - - | 0.583 | 1.55 | 1.52 | 1.43 | 1.42 | 1.41 | 1.44 | 21.81 | 22.96 | 23.89 | 0 | - - - | - - - | - - - | - - - | 21169 | 19471 | 18914 | 59554 | Over-range | 11623 | 9716 | 11001 | 32427 | 4714 | 4525 | 4605 | 14081 | 17785 | 16864 | 15383 | 50031 | 17785 | 16864 | 15383 | 50031 | - - - | - - - | - - - | - - -
5/10/2026 | 6:45:00 PM | 280.54 | 278.34 | 277.05 | 485.17 | 479.64 | 483.05 | 75.8608 | 70.7979 | 69.3326 | 0.2681 | 1.434 | 1.434 | 1.431 | 1.922 | 1.934 | 2.017 | Over-range | 59.99 | 17659 | 16869 | 15520 | 50048 | - - - | - - - | - - - | - - - | 17659 | 16869 | 15520 | 50048 | 10582 | 8754 | 10034 | 29370 | - - - | - - - | - - - | - - - | 10582 | 8754 | 10034 | 29370 | 21160 | 19572 | 19085 | 59817 | # # # | # # # | # # # | # # # | 0.835 | 0.862 | 0.813 | 0.837 | # # # | # # # | # # # | - - - | 0.857 | 0.886 | 0.838 | 0.86 | - - - | 0.587 | 1.56 | 1.51 | 1.45 | 1.43 | 1.42 | 1.45 | 21.92 | 22.88 | 23.79 | 0 | - - - | - - - | - - - | - - - | 21160 | 19572 | 19085 | 59817 | Over-range | 11641 | 9904 | 11091 | 32709 | 4773 | 4557 | 4652 | 14178 | 17743 | 16887 | 15517 | 50147 | 17743 | 16887 | 15517 | 50147 | - - - | - - - | - - - | - - -
5/10/2026 | 7:00:00 PM | 281.07 | 279.02 | 277.75 | 486.21 | 480.87 | 484.1 | 78.4189 | 73.1335 | 71.1021 | 0.2721 | 1.434 | 1.433 | 1.431 | 1.903 | 1.912 | 2.004 | Over-range | 60 | 18303 | 17564 | 15993 | 51861 | - - - | - - - | - - - | - - - | 18303 | 17564 | 15993 | 51861 | 11036 | 8971 | 10330 | 30336 | - - - | - - - | - - - | - - - | 11036 | 8971 | 10330 | 30336 | 21902 | 20258 | 19609 | 61769 | # # # | # # # | # # # | # # # | 0.836 | 0.867 | 0.816 | 0.84 | # # # | # # # | # # # | - - - | 0.856 | 0.889 | 0.839 | 0.862 | - - - | 0.585 | 1.58 | 1.52 | 1.42 | 1.44 | 1.41 | 1.44 | 20.89 | 21.97 | 22.93 | 0 | - - - | - - - | - - - | - - - | 21902 | 20258 | 19609 | 61769 | Over-range | 12022 | 10081 | 11335 | 33526 | 4679 | 4518 | 4582 | 14022 | 18396 | 17558 | 16005 | 51958 | 18396 | 17558 | 16005 | 51958 | - - - | - - - | - - - | - - -
5/10/2026 | 7:15:00 PM | 281.39 | 279.49 | 278.14 | 486.92 | 481.66 | 484.63 | 77.1832 | 72.1902 | 71.0498 | 0.2705 | 1.434 | 1.433 | 1.431 | 1.921 | 1.929 | 2.01 | Over-range | 60 | 18006 | 17192 | 15940 | 51138 | - - - | - - - | - - - | - - - | 18006 | 17192 | 15940 | 51138 | 10840 | 9102 | 10414 | 30356 | - - - | - - - | - - - | - - - | 10840 | 9102 | 10414 | 30356 | 21573 | 20017 | 19615 | 61205 | # # # | # # # | # # # | # # # | 0.835 | 0.859 | 0.813 | 0.836 | # # # | # # # | # # # | - - - | 0.856 | 0.882 | 0.837 | 0.859 | - - - | 0.594 | 1.59 | 1.55 | 1.41 | 1.45 | 1.41 | 1.45 | 21.7 | 22.76 | 23.42 | 0 | - - - | - - - | - - - | - - - | 21573 | 20017 | 19615 | 61205 | Over-range | 11874 | 10245 | 11421 | 33605 | 4771 | 4631 | 4618 | 14203 | 18046 | 17187 | 16006 | 51239 | 18046 | 17187 | 16006 | 51239 | - - - | - - - | - - - | - - -
5/10/2026 | 7:30:00 PM | 281.59 | 279.66 | 278.32 | 487.24 | 481.94 | 484.98 | 77.5589 | 72.6683 | 70.6344 | 0.2686 | 1.434 | 1.434 | 1.431 | 1.922 | 1.926 | 2.019 | Over-range | 60 | 18077 | 17410 | 15899 | 51387 | - - - | - - - | - - - | - - - | 18077 | 17410 | 15899 | 51387 | 10927 | 8972 | 10252 | 30151 | - - - | - - - | - - - | - - - | 10927 | 8972 | 10252 | 30151 | 21683 | 20154 | 19505 | 61343 | # # # | # # # | # # # | # # # | 0.834 | 0.864 | 0.815 | 0.838 | # # # | # # # | # # # | - - - | 0.855 | 0.887 | 0.84 | 0.861 | - - - | 0.587 | 1.6 | 1.53 | 1.43 | 1.45 | 1.42 | 1.45 | 21.67 | 22.72 | 23.61 | 0 | - - - | - - - | - - - | - - - | 21683 | 20154 | 19505 | 61343 | Over-range | 11965 | 10140 | 11287 | 33470 | 4790 | 4649 | 4641 | 14295 | 18136 | 17398 | 15958 | 51493 | 18136 | 17398 | 15958 | 51493 | - - - | - - - | - - - | - - -
5/10/2026 | 7:45:00 PM | 282.08 | 280.29 | 278.82 | 488.23 | 483.02 | 485.73 | 77.8846 | 73.3665 | 71.4077 | 0.2719 | 1.434 | 1.433 | 1.431 | 1.938 | 1.946 | 2.025 | Over-range | 60 | 18127 | 17510 | 16068 | 51705 | - - - | - - - | - - - | - - - | 18127 | 17510 | 16068 | 51705 | 10996 | 9184 | 10387 | 30566 | - - - | - - - | - - - | - - - | 10996 | 9184 | 10387 | 30566 | 21817 | 20396 | 19759 | 61972 | # # # | # # # | # # # | # # # | 0.831 | 0.859 | 0.813 | 0.834 | # # # | # # # | # # # | - - - | 0.853 | 0.884 | 0.839 | 0.859 | - - - | 0.591 | 1.6 | 1.52 | 1.42 | 1.46 | 1.41 | 1.45 | 22.35 | 23.43 | 24.2 | 0 | - - - | - - - | - - - | - - - | 21817 | 20396 | 19759 | 61972 | Over-range | 12123 | 10437 | 11482 | 34108 | 5014 | 4878 | 4809 | 14888 | 18138 | 17530 | 16136 | 51804 | 18138 | 17530 | 16136 | 51804 | - - - | - - - | - - - | - - -
5/10/2026 | 8:00:00 PM | 282.52 | 280.63 | 279.17 | 488.91 | 483.54 | 486.47 | 79.8001 | 75.3418 | 73.1977 | 0.2721 | 1.434 | 1.433 | 1.431 | 1.943 | 1.946 | 2.032 | Over-range | 60.01 | 18680 | 18089 | 16607 | 53376 | - - - | - - - | - - - | - - - | 18680 | 18089 | 16607 | 53376 | 11226 | 9385 | 10563 | 31174 | - - - | - - - | - - - | - - - | 11226 | 9385 | 10563 | 31174 | 22414 | 21000 | 20308 | 63722 | # # # | # # # | # # # | # # # | 0.833 | 0.861 | 0.818 | 0.838 | # # # | # # # | # # # | - - - | 0.856 | 0.887 | 0.844 | 0.862 | - - - | 0.584 | 1.6 | 1.52 | 1.41 | 1.46 | 1.41 | 1.45 | 22.54 | 23.46 | 24.3 | 0 | - - - | - - - | - - - | - - - | 22414 | 21000 | 20308 | 63722 | Over-range | 12381 | 10657 | 11678 | 34782 | 5157 | 4984 | 4917 | 15235 | 18686 | 18117 | 16682 | 53484 | 18686 | 18117 | 16682 | 53484 | - - - | - - - | - - - | - - -
5/10/2026 | 8:15:00 PM | 282.41 | 280.46 | 279.04 | 488.66 | 483.25 | 486.3 | 76.0345 | 71.1077 | 69.1995 | 0.2651 | 1.434 | 1.433 | 1.43 | 1.964 | 1.972 | 2.063 | Over-range | 60 | 17696 | 17008 | 15511 | 50215 | - - - | - - - | - - - | - - - | 17696 | 17008 | 15511 | 50215 | 10766 | 8813 | 10124 | 29703 | - - - | - - - | - - - | - - - | 10766 | 8813 | 10124 | 29703 | 21349 | 19806 | 19184 | 60339 | # # # | # # # | # # # | # # # | 0.829 | 0.859 | 0.809 | 0.832 | # # # | # # # | # # # | - - - | 0.853 | 0.886 | 0.837 | 0.859 | - - - | 0.592 | 1.58 | 1.52 | 1.38 | 1.44 | 1.39 | 1.43 | 23.39 | 24.62 | 25.53 | 0 | - - - | - - - | - - - | - - - | 21349 | 19806 | 19184 | 60339 | Over-range | 11934 | 10135 | 11276 | 33421 | 5070 | 4934 | 4888 | 15098 | 17727 | 16999 | 15585 | 50311 | 17727 | 16999 | 15585 | 50311 | - - - | - - - | - - - | - - -
5/10/2026 | 8:30:00 PM | 282.67 | 280.78 | 279.31 | 489.18 | 483.81 | 486.69 | 77.5237 | 72.9723 | 71.3559 | 0.2718 | 1.434 | 1.433 | 1.43 | 1.95 | 1.956 | 2.04 | Over-range | 60 | 18110 | 17444 | 16096 | 51650 | - - - | - - - | - - - | - - - | 18110 | 17444 | 16096 | 51650 | 11017 | 9308 | 10453 | 30778 | - - - | - - - | - - - | - - - | 11017 | 9308 | 10453 | 30778 | 21796 | 20359 | 19811 | 61966 | # # # | # # # | # # # | # # # | 0.831 | 0.857 | 0.813 | 0.834 | # # # | # # # | # # # | - - - | 0.854 | 0.882 | 0.837 | 0.858 | - - - | 0.596 | 1.58 | 1.49 | 1.37 | 1.43 | 1.37 | 1.41 | 22.54 | 23.47 | 24.34 | 0 | - - - | - - - | - - - | - - - | 21796 | 20359 | 19811 | 61966 | Over-range | 12122 | 10489 | 11540 | 34212 | 4992 | 4772 | 4825 | 14751 | 18159 | 17494 | 16090 | 51744 | 18159 | 17494 | 16090 | 51744 | - - - | - - - | - - - | - - -
5/10/2026 | 8:45:00 PM | 282.78 | 280.74 | 279.33 | 489.28 | 483.73 | 486.84 | 79.6959 | 74.4157 | 72.4393 | 0.2725 | 1.433 | 1.432 | 1.429 | 1.961 | 1.97 | 2.062 | Over-range | 60 | 18634 | 17862 | 16296 | 52791 | - - - | - - - | - - - | - - - | 18634 | 17862 | 16296 | 52791 | 11125 | 9095 | 10457 | 30677 | - - - | - - - | - - - | - - - | 11125 | 9095 | 10457 | 30677 | 22379 | 20721 | 20078 | 63177 | # # # | # # # | # # # | # # # | 0.833 | 0.862 | 0.812 | 0.836 | # # # | # # # | # # # | - - - | 0.858 | 0.889 | 0.839 | 0.862 | - - - | 0.581 | 1.58 | 1.49 | 1.37 | 1.43 | 1.37 | 1.41 | 23.34 | 24.6 | 25.61 | 0 | - - - | - - - | - - - | - - - | 22379 | 20721 | 20078 | 63177 | Over-range | 12377 | 10481 | 11713 | 34654 | 5319 | 5114 | 5180 | 15832 | 18724 | 17888 | 16275 | 52887 | 18724 | 17888 | 16275 | 52887 | - - - | - - - | - - - | - - -
5/10/2026 | 9:00:00 PM | 283.03 | 280.97 | 279.45 | 489.76 | 483.99 | 487.14 | 78.5432 | 73.3785 | 72.2166 | 0.2718 | 1.433 | 1.432 | 1.429 | 1.977 | 1.99 | 2.075 | Over-range | 60.01 | 18467 | 17585 | 16300 | 52352 | - - - | - - - | - - - | - - - | 18467 | 17585 | 16300 | 52352 | 10824 | 9078 | 10396 | 30298 | - - - | - - - | - - - | - - - | 10824 | 9078 | 10396 | 30298 | 22094 | 20470 | 20049 | 62613 | # # # | # # # | # # # | # # # | 0.836 | 0.859 | 0.813 | 0.836 | # # # | # # # | # # # | - - - | 0.862 | 0.888 | 0.841 | 0.864 | - - - | 0.579 | 1.6 | 1.49 | 1.36 | 1.44 | 1.38 | 1.41 | 24.11 | 25.33 | 26.16 | 0 | - - - | - - - | - - - | - - - | 22094 | 20470 | 20049 | 62613 | Over-range | 12124 | 10468 | 11664 | 34322 | 5391 | 5145 | 5223 | 15926 | 18529 | 17640 | 16281 | 52450 | 18529 | 17640 | 16281 | 52450 | - - - | - - - | - - - | - - -
5/10/2026 | 9:15:00 PM | 283.32 | 281.29 | 279.79 | 490.24 | 484.62 | 487.66 | 80.8507 | 75.8335 | 74.4139 | 0.2767 | 1.433 | 1.432 | 1.429 | 1.961 | 1.973 | 2.06 | Over-range | 59.99 | 19032 | 18222 | 16864 | 54118 | - - - | - - - | - - - | - - - | 19032 | 18222 | 16864 | 54118 | 11266 | 9499 | 10788 | 31553 | - - - | - - - | - - - | - - - | 11266 | 9499 | 10788 | 31553 | 22781 | 21194 | 20695 | 64669 | # # # | # # # | # # # | # # # | 0.835 | 0.86 | 0.815 | 0.837 | # # # | # # # | # # # | - - - | 0.86 | 0.887 | 0.841 | 0.863 | - - - | 0.583 | 1.62 | 1.53 | 1.39 | 1.47 | 1.4 | 1.44 | 23.25 | 24.22 | 25.18 | 0 | - - - | - - - | - - - | - - - | 22781 | 21194 | 20695 | 64669 | Over-range | 12514 | 10814 | 11986 | 35381 | 5386 | 5108 | 5166 | 15829 | 19049 | 18310 | 16861 | 54220 | 19049 | 18310 | 16861 | 54220 | - - - | - - - | - - - | - - -
5/10/2026 | 9:30:00 PM | 283.69 | 281.6 | 280.12 | 490.81 | 485.19 | 488.29 | 80.3551 | 75.3376 | 73.2871 | 0.2748 | 1.433 | 1.431 | 1.428 | 1.972 | 1.985 | 2.077 | Over-range | 60.02 | 18888 | 18166 | 16607 | 53662 | - - - | - - - | - - - | - - - | 18888 | 18166 | 16607 | 53662 | 11195 | 9235 | 10549 | 30979 | - - - | - - - | - - - | - - - | 11195 | 9235 | 10549 | 30979 | 22656 | 21063 | 20392 | 64112 | # # # | # # # | # # # | # # # | 0.834 | 0.862 | 0.814 | 0.837 | # # # | # # # | # # # | - - - | 0.859 | 0.891 | 0.843 | 0.864 | - - - | 0.577 | 1.6 | 1.5 | 1.39 | 1.46 | 1.38 | 1.42 | 23.85 | 24.91 | 26.03 | 0 | - - - | - - - | - - - | - - - | 22656 | 21063 | 20392 | 64112 | Over-range | 12503 | 10649 | 11823 | 35052 | 5489 | 5226 | 5266 | 16177 | 18905 | 18245 | 16606 | 53755 | 18905 | 18245 | 16606 | 53755 | - - - | - - - | - - - | - - -
5/10/2026 | 9:45:00 PM | 283.72 | 281.72 | 280.2 | 490.99 | 485.34 | 488.36 | 77.565 | 72.4108 | 71.153 | 0.2698 | 1.433 | 1.431 | 1.428 | 1.983 | 1.993 | 2.083 | Over-range | 60 | 18196 | 17345 | 16013 | 51554 | - - - | - - - | - - - | - - - | 18196 | 17345 | 16013 | 51554 | 10832 | 9055 | 10401 | 30289 | - - - | - - - | - - - | - - - | 10832 | 9055 | 10401 | 30289 | 21875 | 20251 | 19807 | 61933 | # # # | # # # | # # # | # # # | 0.832 | 0.857 | 0.809 | 0.832 | # # # | # # # | # # # | - - - | 0.858 | 0.885 | 0.837 | 0.86 | - - - | 0.588 | 1.62 | 1.5 | 1.38 | 1.46 | 1.38 | 1.43 | 24.19 | 25.32 | 26.22 | 0 | - - - | - - - | - - - | - - - | 21875 | 20251 | 19807 | 61933 | Over-range | 12126 | 10432 | 11640 | 34269 | 5372 | 5103 | 5152 | 15808 | 18210 | 17417 | 16019 | 51645 | 18210 | 17417 | 16019 | 51645 | - - - | - - - | - - - | - - -
5/10/2026 | 10:00:00 PM | 284.18 | 282.05 | 280.59 | 491.66 | 485.93 | 489.14 | 79.6659 | 74.2333 | 72.8972 | 0.2722 | 1.432 | 1.431 | 1.427 | 1.967 | 1.979 | 2.076 | Over-range | 60.02 | 18746 | 17867 | 16452 | 53065 | - - - | - - - | - - - | - - - | 18746 | 17867 | 16452 | 53065 | 11264 | 9315 | 10756 | 31335 | - - - | - - - | - - - | - - - | 11264 | 9315 | 10756 | 31335 | 22526 | 20813 | 20340 | 63679 | # # # | # # # | # # # | # # # | 0.832 | 0.859 | 0.809 | 0.833 | # # # | # # # | # # # | - - - | 0.857 | 0.885 | 0.837 | 0.86 | - - - | 0.591 | 1.64 | 1.51 | 1.37 | 1.46 | 1.39 | 1.42 | 23.44 | 24.57 | 25.52 | 0 | - - - | - - - | - - - | - - - | 22526 | 20813 | 20340 | 63679 | Over-range | 12484 | 10665 | 11952 | 35179 | 5320 | 5136 | 5150 | 15810 | 18778 | 17845 | 16526 | 53150 | 18778 | 17845 | 16526 | 53150 | - - - | - - - | - - - | - - -
5/10/2026 | 10:15:00 PM | 283.52 | 281.33 | 279.96 | 490.39 | 484.78 | 488.06 | 79.3609 | 73.7646 | 72.1388 | 0.2725 | 1.431 | 1.43 | 1.426 | 1.969 | 1.987 | 2.084 | Over-range | 60 | 18615 | 17739 | 16223 | 52578 | - - - | - - - | - - - | - - - | 18615 | 17739 | 16223 | 52578 | 11068 | 9000 | 10486 | 30554 | - - - | - - - | - - - | - - - | 11068 | 9000 | 10486 | 30554 | 22329 | 20572 | 20033 | 62934 | # # # | # # # | # # # | # # # | 0.834 | 0.862 | 0.81 | 0.835 | # # # | # # # | # # # | - - - | 0.859 | 0.89 | 0.839 | 0.863 | - - - | 0.581 | 1.62 | 1.5 | 1.38 | 1.46 | 1.39 | 1.42 | 23.8 | 25.08 | 26.17 | 0 | - - - | - - - | - - - | - - - | 22329 | 20572 | 20033 | 62934 | Over-range | 12324 | 10405 | 11741 | 34558 | 5332 | 5145 | 5201 | 15907 | 18671 | 17725 | 16262 | 52658 | 18671 | 17725 | 16262 | 52658 | - - - | - - - | - - - | - - -
5/10/2026 | 10:30:00 PM | 283.51 | 281.33 | 279.84 | 490.49 | 484.6 | 487.92 | 78.3163 | 72.6631 | 71.464 | 0.2707 | 1.431 | 1.43 | 1.426 | 1.963 | 1.971 | 2.074 | Over-range | 60.01 | 18352 | 17415 | 16020 | 51786 | - - - | - - - | - - - | - - - | 18352 | 17415 | 16020 | 51786 | 11010 | 9114 | 10565 | 30689 | - - - | - - - | - - - | - - - | 11010 | 9114 | 10565 | 30689 | 22046 | 20272 | 19846 | 62164 | # # # | # # # | # # # | # # # | 0.832 | 0.859 | 0.807 | 0.833 | # # # | # # # | # # # | - - - | 0.857 | 0.886 | 0.833 | 0.859 | - - - | 0.593 | 1.62 | 1.52 | 1.39 | 1.47 | 1.4 | 1.44 | 23.3 | 24.25 | 25.34 | 0 | - - - | - - - | - - - | - - - | 22046 | 20272 | 19846 | 62164 | Over-range | 12209 | 10366 | 11705 | 34361 | 5195 | 4858 | 4960 | 15223 | 18362 | 17494 | 16013 | 51869 | 18362 | 17494 | 16013 | 51869 | - - - | - - - | - - - | - - -
5/10/2026 | 10:45:00 PM | 284.1 | 281.76 | 280.34 | 491.38 | 485.33 | 488.94 | 79.9709 | 74.1445 | 72.9056 | 0.2725 | 1.431 | 1.43 | 1.426 | 1.934 | 1.943 | 2.048 | Over-range | 60.01 | 18807 | 17847 | 16403 | 53057 | - - - | - - - | - - - | - - - | 18807 | 17847 | 16403 | 53057 | 11413 | 9394 | 10919 | 31725 | - - - | - - - | - - - | - - - | 11413 | 9394 | 10919 | 31725 | 22601 | 20759 | 20319 | 63680 | # # # | # # # | # # # | # # # | 0.832 | 0.86 | 0.807 | 0.833 | # # # | # # # | # # # | - - - | 0.854 | 0.883 | 0.832 | 0.857 | - - - | 0.598 | 1.65 | 1.51 | 1.42 | 1.48 | 1.43 | 1.47 | 21.99 | 22.83 | 23.91 | 0 | - - - | - - - | - - - | - - - | 22601 | 20759 | 20319 | 63680 | Over-range | 12519 | 10585 | 11978 | 35169 | 5060 | 4796 | 4843 | 14935 | 18813 | 17856 | 16467 | 53135 | 18813 | 17856 | 16467 | 53135 | - - - | - - - | - - - | - - -
5/10/2026 | 11:00:00 PM | 284.44 | 282.13 | 280.64 | 492 | 485.94 | 489.45 | 78.7138 | 72.8429 | 70.9828 | 0.2703 | 1.432 | 1.43 | 1.426 | 1.92 | 1.918 | 2.033 | Over-range | 60.02 | 18431 | 17566 | 15918 | 51915 | - - - | - - - | - - - | - - - | 18431 | 17566 | 15918 | 51915 | 11412 | 9212 | 10745 | 31369 | - - - | - - - | - - - | - - - | 11412 | 9212 | 10745 | 31369 | 22214 | 20362 | 19754 | 62330 | # # # | # # # | # # # | # # # | 0.83 | 0.863 | 0.806 | 0.833 | # # # | # # # | # # # | - - - | 0.849 | 0.884 | 0.828 | 0.854 | - - - | 0.604 | 1.65 | 1.53 | 1.43 | 1.49 | 1.44 | 1.48 | 21.05 | 21.87 | 22.92 | 0 | - - - | - - - | - - - | - - - | 22214 | 20362 | 19754 | 62330 | Over-range | 12391 | 10283 | 11686 | 34462 | 4739 | 4490 | 4509 | 14024 | 18450 | 17559 | 15979 | 51988 | 18450 | 17559 | 15979 | 51988 | - - - | - - - | - - - | - - -
5/10/2026 | 11:15:00 PM | 284.62 | 282.2 | 280.73 | 492.26 | 486.01 | 489.72 | 76.7797 | 70.8972 | 69.415 | 0.2682 | 1.432 | 1.431 | 1.426 | 1.925 | 1.923 | 2.041 | Over-range | 60.02 | 17952 | 17042 | 15506 | 50501 | - - - | - - - | - - - | - - - | 17952 | 17042 | 15506 | 50501 | 11189 | 9085 | 10560 | 30834 | - - - | - - - | - - - | - - - | 11189 | 9085 | 10560 | 30834 | 21690 | 19831 | 19331 | 60851 | # # # | # # # | # # # | # # # | 0.828 | 0.859 | 0.802 | 0.83 | # # # | # # # | # # # | - - - | 0.848 | 0.881 | 0.825 | 0.852 | - - - | 0.611 | 1.67 | 1.56 | 1.45 | 1.51 | 1.45 | 1.5 | 21.33 | 22.03 | 23.29 | 0 | - - - | - - - | - - - | - - - | 21690 | 19831 | 19331 | 60851 | Over-range | 12165 | 10130 | 11533 | 33924 | 4682 | 4396 | 4551 | 13891 | 18036 | 17022 | 15512 | 50570 | 18036 | 17022 | 15512 | 50570 | - - - | - - - | - - - | - - -
5/10/2026 | 11:30:00 PM | 285.06 | 282.62 | 281.21 | 493 | 486.79 | 490.52 | 78.8573 | 73.0681 | 71.3746 | 0.2707 | 1.433 | 1.431 | 1.427 | 1.909 | 1.906 | 2.02 | Over-range | 60.01 | 18516 | 17648 | 16057 | 52220 | - - - | - - - | - - - | - - - | 18516 | 17648 | 16057 | 52220 | 11594 | 9439 | 10908 | 31941 | - - - | - - - | - - - | - - - | 11594 | 9439 | 10908 | 31941 | 22346 | 20503 | 19941 | 62791 | # # # | # # # | # # # | # # # | 0.829 | 0.861 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.848 | 0.881 | 0.827 | 0.852 | - - - | 0.612 | 1.71 | 1.57 | 1.49 | 1.54 | 1.48 | 1.54 | 20.55 | 21.19 | 22.38 | 0 | - - - | - - - | - - - | - - - | 22346 | 20503 | 19941 | 62791 | Over-range | 12506 | 10430 | 11816 | 34847 | 4625 | 4375 | 4482 | 13752 | 18588 | 17615 | 16097 | 52299 | 18588 | 17615 | 16097 | 52299 | - - - | - - - | - - - | - - -
5/10/2026 | 11:45:00 PM | 285.38 | 282.95 | 281.42 | 493.61 | 487.25 | 490.96 | 77.5477 | 71.736 | 69.5921 | 0.2682 | 1.433 | 1.431 | 1.427 | 1.935 | 1.931 | 2.047 | Over-range | 60.02 | 18124 | 17308 | 15576 | 51009 | - - - | - - - | - - - | - - - | 18124 | 17308 | 15576 | 51009 | 11320 | 9089 | 10546 | 30955 | - - - | - - - | - - - | - - - | 11320 | 9089 | 10546 | 30955 | 21958 | 20114 | 19424 | 61497 | # # # | # # # | # # # | # # # | 0.825 | 0.861 | 0.802 | 0.83 | # # # | # # # | # # # | - - - | 0.847 | 0.884 | 0.826 | 0.853 | - - - | 0.607 | 1.71 | 1.59 | 1.49 | 1.55 | 1.49 | 1.54 | 21.81 | 22.71 | 23.94 | 0 | - - - | - - - | - - - | - - - | 21958 | 20114 | 19424 | 61497 | Over-range | 12382 | 10225 | 11588 | 34299 | 4900 | 4578 | 4696 | 14459 | 18187 | 17345 | 15553 | 51085 | 18187 | 17345 | 15553 | 51085 | - - - | - - - | - - - | - - -
5/11/2026 | 12:00:00 AM | 285.05 | 282.57 | 281.1 | 492.97 | 486.64 | 490.4 | 78.6144 | 72.765 | 71.2561 | 0.2727 | 1.433 | 1.431 | 1.427 | 1.927 | 1.93 | 2.042 | Over-range | 60.01 | 18413 | 17499 | 15953 | 51865 | - - - | - - - | - - - | - - - | 18413 | 17499 | 15953 | 51865 | 11455 | 9394 | 10860 | 31709 | - - - | - - - | - - - | - - - | 11455 | 9394 | 10860 | 31709 | 22260 | 20397 | 19885 | 62542 | # # # | # # # | # # # | # # # | 0.827 | 0.858 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.848 | 0.88 | 0.825 | 0.851 | - - - | 0.611 | 1.73 | 1.59 | 1.49 | 1.55 | 1.5 | 1.55 | 21.5 | 22.16 | 23.43 | 0 | - - - | - - - | - - - | - - - | 22260 | 20397 | 19885 | 62542 | Over-range | 12500 | 10467 | 11859 | 34918 | 4904 | 4520 | 4673 | 14344 | 18437 | 17570 | 15932 | 51938 | 18437 | 17570 | 15932 | 51938 | - - - | - - - | - - - | - - -
5/11/2026 | 12:15:00 AM | 283.76 | 281.23 | 279.8 | 490.7 | 484.3 | 488.19 | 77.7833 | 72.0374 | 70.2585 | 0.269 | 1.432 | 1.43 | 1.426 | 1.943 | 1.94 | 2.065 | Over-range | 60 | 18210 | 17341 | 15758 | 51310 | - - - | - - - | - - - | - - - | 18210 | 17341 | 15758 | 51310 | 11132 | 9013 | 10450 | 30595 | - - - | - - - | - - - | - - - | 11132 | 9013 | 10450 | 30595 | 21917 | 20090 | 19510 | 61517 | # # # | # # # | # # # | # # # | 0.831 | 0.863 | 0.808 | 0.834 | # # # | # # # | # # # | - - - | 0.853 | 0.886 | 0.832 | 0.857 | - - - | 0.596 | 1.69 | 1.58 | 1.47 | 1.53 | 1.49 | 1.53 | 22.15 | 22.78 | 24.17 | 0 | - - - | - - - | - - - | - - - | 21917 | 20090 | 19510 | 61517 | Over-range | 12189 | 10133 | 11492 | 33910 | 4884 | 4558 | 4712 | 14405 | 18282 | 17344 | 15757 | 51383 | 18282 | 17344 | 15757 | 51383 | - - - | - - - | - - - | - - -
5/11/2026 | 12:30:00 AM | 284.02 | 281.53 | 280.12 | 491.18 | 484.89 | 488.66 | 77.6432 | 71.6031 | 70.1353 | 0.2688 | 1.432 | 1.429 | 1.425 | 1.917 | 1.915 | 2.045 | Over-range | 60 | 18193 | 17241 | 15698 | 51131 | - - - | - - - | - - - | - - - | 18193 | 17241 | 15698 | 51131 | 11191 | 9048 | 10608 | 30846 | - - - | - - - | - - - | - - - | 11191 | 9048 | 10608 | 30846 | 21883 | 19979 | 19488 | 61350 | # # # | # # # | # # # | # # # | 0.831 | 0.863 | 0.806 | 0.833 | # # # | # # # | # # # | - - - | 0.851 | 0.884 | 0.828 | 0.854 | - - - | 0.603 | 1.66 | 1.58 | 1.47 | 1.52 | 1.48 | 1.52 | 21.06 | 21.62 | 22.96 | 0 | - - - | - - - | - - - | - - - | 21883 | 19979 | 19488 | 61350 | Over-range | 12154 | 10082 | 11538 | 33875 | 4652 | 4365 | 4451 | 13749 | 18214 | 17218 | 15764 | 51196 | 18214 | 17218 | 15764 | 51196 | - - - | - - - | - - - | - - -
5/11/2026 | 12:45:00 AM | 284.25 | 281.83 | 280.32 | 491.63 | 485.38 | 488.98 | 78.8477 | 73.1408 | 71.7396 | 0.2725 | 1.432 | 1.43 | 1.426 | 1.932 | 1.934 | 2.047 | Over-range | 60 | 18463 | 17548 | 16067 | 52078 | - - - | - - - | - - - | - - - | 18463 | 17548 | 16067 | 52078 | 11348 | 9316 | 10777 | 31441 | - - - | - - - | - - - | - - - | 11348 | 9316 | 10777 | 31441 | 22250 | 20434 | 19950 | 62633 | # # # | # # # | # # # | # # # | 0.83 | 0.859 | 0.805 | 0.832 | # # # | # # # | # # # | - - - | 0.851 | 0.881 | 0.829 | 0.854 | - - - | 0.604 | 1.68 | 1.58 | 1.47 | 1.53 | 1.48 | 1.53 | 21.67 | 22.36 | 23.53 | 0 | - - - | - - - | - - - | - - - | 22250 | 20434 | 19950 | 62633 | Over-range | 12402 | 10450 | 11810 | 34750 | 4911 | 4652 | 4742 | 14545 | 18509 | 17526 | 16107 | 52141 | 18509 | 17526 | 16107 | 52141 | - - - | - - - | - - - | - - -
5/11/2026 | 1:00:00 AM | 284.48 | 282.04 | 280.52 | 492.07 | 485.67 | 489.37 | 78.0078 | 72.3476 | 70.2179 | 0.2681 | 1.432 | 1.43 | 1.426 | 1.943 | 1.942 | 2.065 | Over-range | 60.02 | 18301 | 17502 | 15804 | 51608 | - - - | - - - | - - - | - - - | 18301 | 17502 | 15804 | 51608 | 11261 | 9041 | 10500 | 30802 | - - - | - - - | - - - | - - - | 11261 | 9041 | 10500 | 30802 | 22066 | 20270 | 19578 | 61914 | # # # | # # # | # # # | # # # | 0.829 | 0.864 | 0.807 | 0.834 | # # # | # # # | # # # | - - - | 0.851 | 0.887 | 0.832 | 0.857 | - - - | 0.597 | 1.7 | 1.58 | 1.47 | 1.54 | 1.49 | 1.53 | 22.14 | 22.91 | 24.23 | 0 | - - - | - - - | - - - | - - - | 22066 | 20270 | 19578 | 61914 | Over-range | 12323 | 10214 | 11546 | 34182 | 4928 | 4684 | 4732 | 14613 | 18344 | 17473 | 15863 | 51680 | 18344 | 17473 | 15863 | 51680 | - - - | - - - | - - - | - - -
5/11/2026 | 1:15:00 AM | 284.43 | 281.95 | 280.59 | 491.86 | 485.69 | 489.42 | 76.9275 | 71.4169 | 69.5398 | 0.2685 | 1.432 | 1.429 | 1.426 | 1.936 | 1.941 | 2.062 | Over-range | 60.01 | 18031 | 17228 | 15636 | 50894 | - - - | - - - | - - - | - - - | 18031 | 17228 | 15636 | 50894 | 11114 | 9015 | 10392 | 30521 | - - - | - - - | - - - | - - - | 11114 | 9015 | 10392 | 30521 | 21745 | 19987 | 19380 | 61112 | # # # | # # # | # # # | # # # | 0.829 | 0.862 | 0.807 | 0.833 | # # # | # # # | # # # | - - - | 0.851 | 0.884 | 0.831 | 0.856 | - - - | 0.6 | 1.7 | 1.58 | 1.51 | 1.54 | 1.49 | 1.54 | 21.9 | 22.55 | 24.07 | 0 | - - - | - - - | - - - | - - - | 21745 | 19987 | 19380 | 61112 | Over-range | 12146 | 10118 | 11438 | 33797 | 4816 | 4516 | 4701 | 14282 | 18114 | 17225 | 15626 | 50965 | 18114 | 17225 | 15626 | 50965 | - - - | - - - | - - - | - - -
5/11/2026 | 1:30:00 AM | 284.54 | 282.06 | 280.67 | 492.04 | 485.9 | 489.56 | 76.6143 | 70.9437 | 69.6295 | 0.2689 | 1.432 | 1.429 | 1.426 | 1.95 | 1.952 | 2.068 | Over-range | 60.01 | 17942 | 17031 | 15584 | 50557 | - - - | - - - | - - - | - - - | 17942 | 17031 | 15584 | 50557 | 11046 | 9036 | 10476 | 30559 | - - - | - - - | - - - | - - - | 11046 | 9036 | 10476 | 30559 | 21651 | 19849 | 19398 | 60898 | # # # | # # # | # # # | # # # | 0.829 | 0.858 | 0.803 | 0.83 | # # # | # # # | # # # | - - - | 0.851 | 0.881 | 0.829 | 0.854 | - - - | 0.604 | 1.71 | 1.58 | 1.48 | 1.54 | 1.49 | 1.54 | 22.39 | 23.19 | 24.43 | 0 | - - - | - - - | - - - | - - - | 21651 | 19849 | 19398 | 60898 | Over-range | 12111 | 10183 | 11539 | 33921 | 4878 | 4612 | 4755 | 14478 | 18015 | 17004 | 15605 | 50624 | 18015 | 17004 | 15605 | 50624 | - - - | - - - | - - - | - - -
5/11/2026 | 1:45:00 AM | 284.72 | 282.17 | 280.91 | 492.29 | 486.15 | 489.98 | 78.3191 | 72.2892 | 70.6089 | 0.2702 | 1.432 | 1.429 | 1.426 | 1.932 | 1.933 | 2.057 | Over-range | 60.01 | 18374 | 17450 | 15838 | 51662 | - - - | - - - | - - - | - - - | 18374 | 17450 | 15838 | 51662 | 11316 | 9102 | 10645 | 31063 | - - - | - - - | - - - | - - - | 11316 | 9102 | 10645 | 31063 | 22152 | 20241 | 19694 | 62087 | # # # | # # # | # # # | # # # | 0.829 | 0.862 | 0.804 | 0.832 | # # # | # # # | # # # | - - - | 0.851 | 0.885 | 0.829 | 0.855 | - - - | 0.601 | 1.69 | 1.58 | 1.49 | 1.54 | 1.5 | 1.54 | 21.72 | 22.45 | 23.88 | 0 | - - - | - - - | - - - | - - - | 22152 | 20241 | 19694 | 62087 | Over-range | 12359 | 10233 | 11690 | 34386 | 4857 | 4574 | 4729 | 14443 | 18445 | 17428 | 15853 | 51726 | 18445 | 17428 | 15853 | 51726 | - - - | - - - | - - - | - - -
5/11/2026 | 2:00:00 AM | 284.93 | 282.4 | 281.04 | 492.72 | 486.42 | 490.26 | 75.4302 | 69.3149 | 68.1464 | 0.2663 | 1.432 | 1.429 | 1.426 | 1.938 | 1.936 | 2.067 | Over-range | 60.01 | 17660 | 16670 | 15188 | 49518 | - - - | - - - | - - - | - - - | 17660 | 16670 | 15188 | 49518 | 11007 | 8940 | 10463 | 30410 | - - - | - - - | - - - | - - - | 11007 | 8940 | 10463 | 30410 | 21367 | 19438 | 19031 | 59836 | # # # | # # # | # # # | # # # | 0.827 | 0.858 | 0.798 | 0.828 | # # # | # # # | # # # | - - - | 0.848 | 0.88 | 0.822 | 0.85 | - - - | 0.614 | 1.7 | 1.58 | 1.5 | 1.54 | 1.5 | 1.54 | 21.81 | 22.44 | 23.83 | 0 | - - - | - - - | - - - | - - - | 21367 | 19438 | 19031 | 59836 | Over-range | 12020 | 9984 | 11457 | 33560 | 4745 | 4367 | 4586 | 13962 | 17727 | 16695 | 15160 | 49581 | 17727 | 16695 | 15160 | 49581 | - - - | - - - | - - - | - - -
5/11/2026 | 2:15:00 AM | 284.93 | 282.38 | 281.04 | 492.64 | 486.48 | 490.26 | 78.5725 | 72.5821 | 71.1984 | 0.2722 | 1.432 | 1.429 | 1.426 | 1.922 | 1.923 | 2.04 | Over-range | 60 | 18458 | 17501 | 15974 | 51933 | - - - | - - - | - - - | - - - | 18458 | 17501 | 15974 | 51933 | 11430 | 9356 | 10878 | 31664 | - - - | - - - | - - - | - - - | 11430 | 9356 | 10878 | 31664 | 22256 | 20347 | 19880 | 62483 | # # # | # # # | # # # | # # # | 0.829 | 0.86 | 0.804 | 0.831 | # # # | # # # | # # # | - - - | 0.849 | 0.881 | 0.825 | 0.852 | - - - | 0.61 | 1.72 | 1.59 | 1.52 | 1.56 | 1.51 | 1.56 | 21.01 | 21.55 | 22.89 | 0 | - - - | - - - | - - - | - - - | 22256 | 20347 | 19880 | 62483 | Over-range | 12427 | 10368 | 11822 | 34714 | 4791 | 4387 | 4549 | 13989 | 18464 | 17568 | 15961 | 51994 | 18464 | 17568 | 15961 | 51994 | - - - | - - - | - - - | - - -
5/11/2026 | 2:30:00 AM | 285.12 | 282.61 | 281.23 | 493.04 | 486.81 | 490.56 | 77.6265 | 71.3817 | 69.7826 | 0.2693 | 1.432 | 1.429 | 1.426 | 1.925 | 1.925 | 2.047 | Over-range | 60.01 | 18250 | 17285 | 15644 | 51179 | - - - | - - - | - - - | - - - | 18250 | 17285 | 15644 | 51179 | 11314 | 9102 | 10721 | 31137 | - - - | - - - | - - - | - - - | 11314 | 9102 | 10721 | 31137 | 22027 | 20055 | 19521 | 61603 | # # # | # # # | # # # | # # # | 0.829 | 0.862 | 0.801 | 0.831 | # # # | # # # | # # # | - - - | 0.848 | 0.884 | 0.824 | 0.852 | - - - | 0.608 | 1.73 | 1.6 | 1.53 | 1.56 | 1.52 | 1.57 | 21.21 | 21.92 | 23.19 | 0 | - - - | - - - | - - - | - - - | 22027 | 20055 | 19521 | 61603 | Over-range | 12328 | 10157 | 11667 | 34262 | 4822 | 4437 | 4528 | 14083 | 18228 | 17352 | 15658 | 51239 | 18228 | 17352 | 15658 | 51239 | - - - | - - - | - - - | - - -
5/11/2026 | 2:45:00 AM | 285.18 | 282.58 | 281.16 | 493.14 | 486.64 | 490.58 | 76.4134 | 70.2862 | 69.0248 | 0.2683 | 1.432 | 1.429 | 1.426 | 1.931 | 1.928 | 2.059 | Over-range | 60.01 | 17897 | 16905 | 15389 | 50191 | - - - | - - - | - - - | - - - | 17897 | 16905 | 15389 | 50191 | 11119 | 9033 | 10602 | 30754 | - - - | - - - | - - - | - - - | 11119 | 9033 | 10602 | 30754 | 21649 | 19702 | 19266 | 60618 | # # # | # # # | # # # | # # # | 0.827 | 0.858 | 0.799 | 0.828 | # # # | # # # | # # # | - - - | 0.847 | 0.88 | 0.822 | 0.85 | - - - | 0.613 | 1.75 | 1.62 | 1.55 | 1.58 | 1.54 | 1.59 | 21.65 | 22.15 | 23.55 | 0 | - - - | - - - | - - - | - - - | 21649 | 19702 | 19266 | 60618 | Over-range | 12164 | 10096 | 11572 | 33933 | 4843 | 4422 | 4548 | 14084 | 17877 | 16969 | 15412 | 50258 | 17877 | 16969 | 15412 | 50258 | - - - | - - - | - - - | - - -
5/11/2026 | 3:00:00 AM | 285.11 | 282.52 | 281.13 | 492.96 | 486.63 | 490.49 | 80.4754 | 74.492 | 72.8528 | 0.2758 | 1.432 | 1.429 | 1.426 | 1.882 | 1.871 | 2.002 | Over-range | 60.01 | 18925 | 18018 | 16404 | 53347 | - - - | - - - | - - - | - - - | 18925 | 18018 | 16404 | 53347 | 11856 | 9706 | 11223 | 32786 | - - - | - - - | - - - | - - - | 11856 | 9706 | 11223 | 32786 | 22806 | 20898 | 20345 | 64049 | # # # | # # # | # # # | # # # | 0.83 | 0.862 | 0.806 | 0.833 | # # # | # # # | # # # | - - - | 0.846 | 0.88 | 0.825 | 0.851 | - - - | 0.615 | 1.74 | 1.6 | 1.54 | 1.57 | 1.53 | 1.58 | 19.29 | 19.55 | 20.9 | 0 | - - - | - - - | - - - | - - - | 22806 | 20898 | 20345 | 64049 | Over-range | 12720 | 10577 | 12025 | 35421 | 4532 | 4128 | 4242 | 13190 | 18903 | 18067 | 16436 | 53405 | 18903 | 18067 | 16436 | 53405 | - - - | - - - | - - - | - - -
5/11/2026 | 3:15:00 AM | 285.23 | 282.72 | 281.24 | 493.29 | 486.9 | 490.65 | 76.1604 | 70.1226 | 68.1907 | 0.266 | 1.432 | 1.429 | 1.426 | 1.914 | 1.899 | 2.039 | Over-range | 59.99 | 17795 | 16933 | 15215 | 49942 | - - - | - - - | - - - | - - - | 17795 | 16933 | 15215 | 49942 | 11228 | 8992 | 10530 | 30750 | - - - | - - - | - - - | - - - | 11228 | 8992 | 10530 | 30750 | 21559 | 19648 | 19019 | 60226 | # # # | # # # | # # # | # # # | 0.825 | 0.862 | 0.8 | 0.829 | # # # | # # # | # # # | - - - | 0.844 | 0.882 | 0.821 | 0.849 | - - - | 0.616 | 1.75 | 1.62 | 1.55 | 1.58 | 1.54 | 1.59 | 20.56 | 21.06 | 22.43 | 0 | - - - | - - - | - - - | - - - | 21559 | 19648 | 19019 | 60226 | Over-range | 12163 | 9951 | 11399 | 33626 | 4575 | 4167 | 4269 | 13324 | 17781 | 16997 | 15222 | 50000 | 17781 | 16997 | 15222 | 50000 | - - - | - - - | - - - | - - -
5/11/2026 | 3:30:00 AM | 285.09 | 282.58 | 281.16 | 493.03 | 486.69 | 490.49 | 76.0021 | 69.9322 | 68.5315 | 0.2677 | 1.431 | 1.429 | 1.425 | 1.904 | 1.893 | 2.03 | Over-range | 60 | 17774 | 16832 | 15276 | 49883 | - - - | - - - | - - - | - - - | 17774 | 16832 | 15276 | 49883 | 11247 | 9138 | 10650 | 31035 | - - - | - - - | - - - | - - - | 11247 | 9138 | 10650 | 31035 | 21529 | 19603 | 19132 | 60264 | # # # | # # # | # # # | # # # | 0.826 | 0.859 | 0.799 | 0.828 | # # # | # # # | # # # | - - - | 0.844 | 0.878 | 0.818 | 0.847 | - - - | 0.622 | 1.73 | 1.64 | 1.56 | 1.58 | 1.55 | 1.6 | 20.26 | 20.57 | 22.04 | 0 | - - - | - - - | - - - | - - - | 21529 | 19603 | 19132 | 60264 | Over-range | 12140 | 10034 | 11505 | 33782 | 4473 | 4053 | 4263 | 13077 | 17809 | 16874 | 15254 | 49937 | 17809 | 16874 | 15254 | 49937 | - - - | - - - | - - - | - - -
5/11/2026 | 3:45:00 AM | 285.05 | 282.63 | 281.12 | 493.03 | 486.77 | 490.37 | 75.0594 | 69.4979 | 67.7236 | 0.2662 | 1.431 | 1.429 | 1.425 | 1.921 | 1.914 | 2.04 | Over-range | 60.02 | 17548 | 16735 | 15154 | 49436 | - - - | - - - | - - - | - - - | 17548 | 16735 | 15154 | 49436 | 11046 | 8936 | 10367 | 30350 | - - - | - - - | - - - | - - - | 11046 | 8936 | 10367 | 30350 | 21250 | 19480 | 18898 | 59629 | # # # | # # # | # # # | # # # | 0.826 | 0.859 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.845 | 0.88 | 0.825 | 0.85 | - - - | 0.614 | 1.75 | 1.62 | 1.59 | 1.59 | 1.56 | 1.6 | 20.95 | 21.62 | 22.82 | 0 | - - - | - - - | - - - | - - - | 21250 | 19480 | 18898 | 59629 | Over-range | 11973 | 9952 | 11278 | 33298 | 4521 | 4291 | 4349 | 13432 | 17586 | 16700 | 15212 | 49498 | 17586 | 16700 | 15212 | 49498 | - - - | - - - | - - - | - - -
5/11/2026 | 4:00:00 AM | 285.04 | 282.56 | 281.13 | 492.93 | 486.69 | 490.4 | 75.9761 | 70.1812 | 68.4636 | 0.267 | 1.431 | 1.429 | 1.425 | 1.921 | 1.914 | 2.04 | Over-range | 60.01 | 17793 | 16923 | 15331 | 50047 | - - - | - - - | - - - | - - - | 17793 | 16923 | 15331 | 50047 | 11101 | 8964 | 10478 | 30544 | - - - | - - - | - - - | - - - | 11101 | 8964 | 10478 | 30544 | 21485 | 19644 | 19085 | 60214 | # # # | # # # | # # # | # # # | 0.828 | 0.862 | 0.803 | 0.831 | # # # | # # # | # # # | - - - | 0.847 | 0.882 | 0.825 | 0.852 | - - - | 0.61 | 1.76 | 1.63 | 1.57 | 1.59 | 1.56 | 1.6 | 20.93 | 21.58 | 22.79 | 0 | - - - | - - - | - - - | - - - | 21485 | 19644 | 19085 | 60214 | Over-range | 12035 | 9962 | 11355 | 33452 | 4567 | 4269 | 4300 | 13420 | 17778 | 16938 | 15394 | 50110 | 17778 | 16938 | 15394 | 50110 | - - - | - - - | - - - | - - -
5/11/2026 | 4:15:00 AM | 284.85 | 282.44 | 280.99 | 492.68 | 486.47 | 490.1 | 77.0343 | 71.102 | 69.8633 | 0.2702 | 1.432 | 1.43 | 1.426 | 1.91 | 1.904 | 2.022 | Over-range | 60.02 | 18064 | 17111 | 15632 | 50807 | - - - | - - - | - - - | - - - | 18064 | 17111 | 15632 | 50807 | 11301 | 9264 | 10796 | 31361 | - - - | - - - | - - - | - - - | 11301 | 9264 | 10796 | 31361 | 21815 | 19940 | 19504 | 61259 | # # # | # # # | # # # | # # # | 0.828 | 0.858 | 0.802 | 0.829 | # # # | # # # | # # # | - - - | 0.846 | 0.878 | 0.822 | 0.849 | - - - | 0.617 | 1.78 | 1.64 | 1.59 | 1.6 | 1.58 | 1.63 | 20.29 | 20.93 | 21.99 | 0 | - - - | - - - | - - - | - - - | 21815 | 19940 | 19504 | 61259 | Over-range | 12223 | 10226 | 11652 | 34195 | 4569 | 4247 | 4297 | 13380 | 18042 | 17143 | 15679 | 50864 | 18042 | 17143 | 15679 | 50864 | - - - | - - - | - - - | - - -
5/11/2026 | 4:30:00 AM | 284.54 | 282.21 | 280.82 | 492.15 | 486.18 | 489.68 | 76.2216 | 70.49 | 69.0965 | 0.2669 | 1.432 | 1.43 | 1.426 | 1.913 | 1.915 | 2.026 | Over-range | 60.01 | 17873 | 16980 | 15490 | 50343 | - - - | - - - | - - - | - - - | 17873 | 16980 | 15490 | 50343 | 11146 | 9088 | 10561 | 30795 | - - - | - - - | - - - | - - - | 11146 | 9088 | 10561 | 30795 | 21557 | 19751 | 19273 | 60581 | # # # | # # # | # # # | # # # | 0.829 | 0.86 | 0.804 | 0.831 | # # # | # # # | # # # | - - - | 0.848 | 0.88 | 0.826 | 0.851 | - - - | 0.612 | 1.76 | 1.67 | 1.64 | 1.62 | 1.6 | 1.65 | 20.47 | 21.33 | 22.43 | 0 | - - - | - - - | - - - | - - - | 21557 | 19751 | 19273 | 60581 | Over-range | 12044 | 10078 | 11458 | 33672 | 4475 | 4276 | 4362 | 13375 | 17931 | 16948 | 15531 | 50410 | 17931 | 16948 | 15531 | 50410 | - - - | - - - | - - - | - - -
5/11/2026 | 4:45:00 AM | 284.61 | 282.2 | 280.72 | 492.25 | 486.05 | 489.65 | 76.9711 | 71.6471 | 69.7364 | 0.2479 | 1.431 | 1.429 | 1.426 | 1.939 | 1.938 | 2.047 | Over-range | 60.01 | 17976 | 17199 | 15628 | 50803 | - - - | - - - | - - - | - - - | 17976 | 17199 | 15628 | 50803 | 11146 | 9075 | 10433 | 30654 | - - - | - - - | - - - | - - - | 11146 | 9075 | 10433 | 30654 | 21714 | 20006 | 19389 | 61108 | # # # | # # # | # # # | # # # | 0.828 | 0.86 | 0.806 | 0.831 | # # # | # # # | # # # | - - - | 0.849 | 0.882 | 0.83 | 0.854 | - - - | 0.603 | 1.81 | 1.71 | 1.65 | 1.64 | 1.63 | 1.68 | 21.73 | 22.67 | 23.8 | 0 | - - - | - - - | - - - | - - - | 21714 | 20006 | 19389 | 61108 | Over-range | 12165 | 10197 | 11458 | 33909 | 4772 | 4558 | 4646 | 14221 | 18051 | 17175 | 15650 | 50876 | 18051 | 17175 | 15650 | 50876 | - - - | - - - | - - - | - - -
5/11/2026 | 5:00:00 AM | 284.37 | 281.97 | 280.42 | 491.9 | 485.54 | 489.17 | 80.8101 | 75.61 | 73.3327 | 0.2459 | 1.431 | 1.429 | 1.426 | 1.922 | 1.918 | 2.023 | Over-range | 60.01 | 18988 | 18273 | 16612 | 53873 | - - - | - - - | - - - | - - - | 18988 | 18273 | 16612 | 53873 | 11684 | 9573 | 10875 | 32131 | - - - | - - - | - - - | - - - | 11684 | 9573 | 10875 | 32131 | 22835 | 21159 | 20424 | 64417 | # # # | # # # | # # # | # # # | 0.832 | 0.864 | 0.813 | 0.836 | # # # | # # # | # # # | - - - | 0.852 | 0.885 | 0.836 | 0.858 | - - - | 0.596 | 1.83 | 1.73 | 1.72 | 1.67 | 1.68 | 1.72 | 21.02 | 21.76 | 22.85 | 0 | - - - | - - - | - - - | - - - | 22835 | 21159 | 20424 | 64417 | Over-range | 12677 | 10658 | 11871 | 35293 | 4846 | 4614 | 4694 | 14393 | 19063 | 18261 | 16624 | 53948 | 19063 | 18261 | 16624 | 53948 | - - - | - - - | - - - | - - -
5/11/2026 | 5:15:00 AM | 283.71 | 281.25 | 279.74 | 490.68 | 484.31 | 488.04 | 79.3907 | 74.0041 | 71.5204 | 0.2431 | 1.43 | 1.43 | 1.426 | 1.922 | 1.924 | 2.028 | Over-range | 60 | 18630 | 17909 | 16158 | 52697 | - - - | - - - | - - - | - - - | 18630 | 17909 | 16158 | 52697 | 11343 | 9155 | 10505 | 31004 | - - - | - - - | - - - | - - - | 11343 | 9155 | 10505 | 31004 | 22372 | 20651 | 19857 | 62880 | # # # | # # # | # # # | # # # | 0.833 | 0.867 | 0.814 | 0.838 | # # # | # # # | # # # | - - - | 0.854 | 0.89 | 0.837 | 0.86 | - - - | 0.588 | 1.87 | 1.78 | 1.77 | 1.71 | 1.73 | 1.78 | 21.32 | 22.24 | 23.48 | 0 | - - - | - - - | - - - | - - - | 22372 | 20651 | 19857 | 62880 | Over-range | 12379 | 10270 | 11531 | 34278 | 4880 | 4581 | 4683 | 14404 | 18685 | 17966 | 16124 | 52775 | 18685 | 17966 | 16124 | 52775 | - - - | - - - | - - - | - - -
5/11/2026 | 5:30:00 AM | 283.35 | 280.94 | 279.41 | 490.12 | 483.81 | 487.39 | 74.3764 | 69.2867 | 67.4427 | 0.2362 | 1.43 | 1.43 | 1.426 | 1.946 | 1.941 | 2.049 | Over-range | 60.01 | 17405 | 16654 | 15159 | 49217 | - - - | - - - | - - - | - - - | 17405 | 16654 | 15159 | 49217 | 10535 | 8612 | 9924 | 29071 | - - - | - - - | - - - | - - - | 10535 | 8612 | 9924 | 29071 | 20931 | 19310 | 18703 | 58944 | # # # | # # # | # # # | # # # | 0.832 | 0.862 | 0.811 | 0.835 | # # # | # # # | # # # | - - - | 0.854 | 0.887 | 0.835 | 0.859 | - - - | 0.591 | 1.91 | 1.85 | 1.8 | 1.76 | 1.78 | 1.83 | 22.31 | 23.1 | 24.2 | 0 | - - - | - - - | - - - | - - - | 20931 | 19310 | 18703 | 58944 | Over-range | 11617 | 9757 | 10942 | 32398 | 4801 | 4497 | 4517 | 14032 | 17399 | 16718 | 15181 | 49298 | 17399 | 16718 | 15181 | 49298 | - - - | - - - | - - - | - - -
5/11/2026 | 5:45:00 AM | 282.93 | 280.49 | 279.07 | 489.35 | 483.07 | 486.8 | 77.1371 | 71.767 | 69.7564 | 0.239 | 1.431 | 1.43 | 1.427 | 1.916 | 1.915 | 2.02 | Over-range | 60 | 18043 | 17266 | 15679 | 50989 | - - - | - - - | - - - | - - - | 18043 | 17266 | 15679 | 50989 | 10995 | 8915 | 10319 | 30229 | - - - | - - - | - - - | - - - | 10995 | 8915 | 10319 | 30229 | 21687 | 19976 | 19329 | 60992 | # # # | # # # | # # # | # # # | 0.832 | 0.864 | 0.811 | 0.836 | # # # | # # # | # # # | - - - | 0.852 | 0.887 | 0.835 | 0.858 | - - - | 0.593 | 2.02 | 1.96 | 1.92 | 1.85 | 1.89 | 1.94 | 21.2 | 21.95 | 23.06 | 0 | - - - | - - - | - - - | - - - | 21687 | 19976 | 19329 | 60992 | Over-range | 12015 | 10023 | 11287 | 33415 | 4751 | 4494 | 4484 | 13981 | 18043 | 17288 | 15743 | 51073 | 18043 | 17288 | 15743 | 51073 | - - - | - - - | - - - | - - -
5/11/2026 | 6:00:00 AM | 282.66 | 280.24 | 278.78 | 488.93 | 482.6 | 486.29 | 76.5208 | 70.8575 | 68.6434 | 0.2372 | 1.432 | 1.431 | 1.427 | 1.917 | 1.915 | 2.025 | Over-range | 60.01 | 17886 | 17088 | 15394 | 50368 | - - - | - - - | - - - | - - - | 17886 | 17088 | 15394 | 50368 | 10852 | 8659 | 10144 | 29655 | - - - | - - - | - - - | - - - | 10852 | 8659 | 10144 | 29655 | 21474 | 19691 | 18985 | 60150 | # # # | # # # | # # # | # # # | 0.833 | 0.868 | 0.811 | 0.837 | # # # | # # # | # # # | - - - | 0.853 | 0.891 | 0.834 | 0.86 | - - - | 0.589 | 2.01 | 2 | 1.94 | 1.86 | 1.91 | 1.96 | 21.18 | 22.04 | 23.16 | 0 | - - - | - - - | - - - | - - - | 21474 | 19691 | 18985 | 60150 | Over-range | 11873 | 9766 | 11099 | 32842 | 4723 | 4431 | 4410 | 13849 | 17872 | 17144 | 15442 | 50457 | 17872 | 17144 | 15442 | 50457 | - - - | - - - | - - - | - - -
5/11/2026 | 6:15:00 AM | 282.25 | 279.93 | 278.42 | 488.22 | 482.13 | 485.59 | 75.5932 | 70.1245 | 68.6271 | 0.2367 | 1.432 | 1.431 | 1.428 | 1.925 | 1.926 | 2.028 | Over-range | 59.99 | 17675 | 16815 | 15373 | 49863 | - - - | - - - | - - - | - - - | 17675 | 16815 | 15373 | 49863 | 10664 | 8707 | 10099 | 29471 | - - - | - - - | - - - | - - - | 10664 | 8707 | 10099 | 29471 | 21187 | 19467 | 18959 | 59613 | # # # | # # # | # # # | # # # | 0.834 | 0.864 | 0.811 | 0.836 | # # # | # # # | # # # | - - - | 0.856 | 0.887 | 0.835 | 0.859 | - - - | 0.591 | 2.04 | 2.01 | 1.99 | 1.88 | 1.93 | 1.99 | 21.57 | 22.5 | 23.52 | 0 | - - - | - - - | - - - | - - - | 21187 | 19467 | 18959 | 59613 | Over-range | 11675 | 9797 | 11086 | 32644 | 4682 | 4424 | 4504 | 13838 | 17748 | 16832 | 15374 | 49954 | 17748 | 16832 | 15374 | 49954 | - - - | - - - | - - - | - - -
5/11/2026 | 6:30:00 AM | 281.72 | 279.43 | 277.88 | 487.38 | 481.18 | 484.68 | 76.3212 | 71.1315 | 69.2282 | 0.2375 | 1.432 | 1.431 | 1.428 | 1.913 | 1.914 | 2.024 | Over-range | 60 | 17880 | 17125 | 15610 | 50616 | - - - | - - - | - - - | - - - | 17880 | 17125 | 15610 | 50616 | 10685 | 8728 | 10014 | 29427 | - - - | - - - | - - - | - - - | 10685 | 8728 | 10014 | 29427 | 21380 | 19743 | 19115 | 60239 | # # # | # # # | # # # | # # # | 0.836 | 0.867 | 0.817 | 0.84 | # # # | # # # | # # # | - - - | 0.858 | 0.89 | 0.84 | 0.863 | - - - | 0.581 | 2.1 | 2.04 | 2.03 | 1.92 | 1.98 | 2.03 | 21.45 | 22.13 | 23.39 | 0 | - - - | - - - | - - - | - - - | 21380 | 19743 | 19115 | 60239 | Over-range | 11714 | 9814 | 11023 | 32635 | 4730 | 4420 | 4540 | 13908 | 17963 | 17164 | 15583 | 50711 | 17963 | 17164 | 15583 | 50711 | - - - | - - - | - - - | - - -

## Energy and Cost
Energy and Cost
Date | Time | Ep (15 min) | Ep+ (15 min) | Ep- (15 min) | Eq (15 min) | Eq/q1 (15 min) | Eq/q2 (15 min) | Eq/q3 (15 min) | Eq/q4 (15 min) | Es (15 min) | Es+ (15 min) | Es- (15 min)
|  | kWh | kWh | kWh | kvarh | kvarh | kvarh | kvarh | kvarh | kVAh | kVAh | kVAh
5/1/2026 | 12:15:00 PM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5/1/2026 | 12:30:00 PM | 13.26 | 13.26 | 0 | 7.898 | 7.898 | 0 | 0 | 0 | 15.796 | 15.796 | 0
5/1/2026 | 12:45:00 PM | 26.795 | 26.795 | 0 | 15.802 | 15.802 | 0 | 0 | 0 | 31.929 | 31.929 | 0
5/1/2026 | 1:00:00 PM | 40.485 | 40.485 | 0 | 23.635 | 23.635 | 0 | 0 | 0 | 48.182 | 48.182 | 0
5/1/2026 | 1:15:00 PM | 54.046 | 54.046 | 0 | 31.587 | 31.587 | 0 | 0 | 0 | 64.344 | 64.344 | 0
5/1/2026 | 1:30:00 PM | 67.289 | 67.289 | 0 | 39.353 | 39.353 | 0 | 0 | 0 | 80.149 | 80.149 | 0
5/1/2026 | 1:45:00 PM | 81.071 | 81.071 | 0 | 47.307 | 47.307 | 0 | 0 | 0 | 96.519 | 96.519 | 0
5/1/2026 | 2:00:00 PM | 94.214 | 94.214 | 0 | 54.964 | 54.964 | 0 | 0 | 0 | 112.207 | 112.207 | 0
5/1/2026 | 2:15:00 PM | 107.959 | 107.959 | 0 | 62.977 | 62.977 | 0 | 0 | 0 | 128.545 | 128.545 | 0
5/1/2026 | 2:30:00 PM | 121.111 | 121.111 | 0 | 70.777 | 70.777 | 0 | 0 | 0 | 144.263 | 144.263 | 0
5/1/2026 | 2:45:00 PM | 134.92 | 134.92 | 0 | 78.826 | 78.826 | 0 | 0 | 0 | 160.683 | 160.683 | 0
5/1/2026 | 3:00:00 PM | 148.13 | 148.13 | 0 | 86.799 | 86.799 | 0 | 0 | 0 | 176.493 | 176.493 | 0
5/1/2026 | 3:15:00 PM | 161.576 | 161.576 | 0 | 94.788 | 94.788 | 0 | 0 | 0 | 192.516 | 192.516 | 0
5/1/2026 | 3:30:00 PM | 174.773 | 174.773 | 0 | 102.604 | 102.604 | 0 | 0 | 0 | 208.286 | 208.286 | 0
5/1/2026 | 3:45:00 PM | 188.571 | 188.571 | 0 | 110.538 | 110.538 | 0 | 0 | 0 | 224.69 | 224.69 | 0
5/1/2026 | 4:00:00 PM | 202.109 | 202.109 | 0 | 118.473 | 118.473 | 0 | 0 | 0 | 240.863 | 240.863 | 0
5/1/2026 | 4:15:00 PM | 216.017 | 216.017 | 0 | 126.552 | 126.552 | 0 | 0 | 0 | 257.4 | 257.4 | 0
5/1/2026 | 4:30:00 PM | 229.441 | 229.441 | 0 | 134.527 | 134.527 | 0 | 0 | 0 | 273.448 | 273.448 | 0
5/1/2026 | 4:45:00 PM | 243.167 | 243.167 | 0 | 142.588 | 142.588 | 0 | 0 | 0 | 289.827 | 289.827 | 0
5/1/2026 | 5:00:00 PM | 256.857 | 256.857 | 0 | 150.592 | 150.592 | 0 | 0 | 0 | 306.145 | 306.145 | 0
5/1/2026 | 5:15:00 PM | 270.181 | 270.181 | 0 | 158.488 | 158.488 | 0 | 0 | 0 | 322.031 | 322.031 | 0
5/1/2026 | 5:30:00 PM | 283.703 | 283.703 | 0 | 166.515 | 166.515 | 0 | 0 | 0 | 338.158 | 338.158 | 0
5/1/2026 | 5:45:00 PM | 297.084 | 297.084 | 0 | 174.42 | 174.42 | 0 | 0 | 0 | 354.139 | 354.139 | 0
5/1/2026 | 6:00:00 PM | 310.704 | 310.704 | 0 | 182.597 | 182.597 | 0 | 0 | 0 | 370.407 | 370.407 | 0
5/1/2026 | 6:15:00 PM | 324 | 324 | 0 | 190.68 | 190.68 | 0 | 0 | 0 | 386.364 | 386.364 | 0
5/1/2026 | 6:30:00 PM | 337.61 | 337.61 | 0 | 198.974 | 198.974 | 0 | 0 | 0 | 402.664 | 402.664 | 0
5/1/2026 | 6:45:00 PM | 350.822 | 350.822 | 0 | 207.093 | 207.093 | 0 | 0 | 0 | 418.563 | 418.563 | 0
5/1/2026 | 7:00:00 PM | 364.057 | 364.057 | 0 | 215.184 | 215.184 | 0 | 0 | 0 | 434.429 | 434.429 | 0
5/1/2026 | 7:15:00 PM | 377.04 | 377.04 | 0 | 223.246 | 223.246 | 0 | 0 | 0 | 450.062 | 450.062 | 0
5/1/2026 | 7:30:00 PM | 390.455 | 390.455 | 0 | 231.488 | 231.488 | 0 | 0 | 0 | 466.154 | 466.154 | 0
5/1/2026 | 7:45:00 PM | 403.842 | 403.842 | 0 | 239.75 | 239.75 | 0 | 0 | 0 | 482.256 | 482.256 | 0
5/1/2026 | 8:00:00 PM | 417.586 | 417.586 | 0 | 248.134 | 248.134 | 0 | 0 | 0 | 498.729 | 498.729 | 0
5/1/2026 | 8:15:00 PM | 431.076 | 431.076 | 0 | 256.398 | 256.398 | 0 | 0 | 0 | 514.937 | 514.937 | 0
5/1/2026 | 8:30:00 PM | 444.703 | 444.703 | 0 | 264.705 | 264.705 | 0 | 0 | 0 | 531.258 | 531.258 | 0
5/1/2026 | 8:45:00 PM | 458.244 | 458.244 | 0 | 272.928 | 272.928 | 0 | 0 | 0 | 547.507 | 547.507 | 0
5/1/2026 | 9:00:00 PM | 471.69 | 471.69 | 0 | 280.982 | 280.982 | 0 | 0 | 0 | 563.597 | 563.597 | 0
5/1/2026 | 9:15:00 PM | 485.667 | 485.667 | 0 | 289.313 | 289.313 | 0 | 0 | 0 | 580.288 | 580.288 | 0
5/1/2026 | 9:30:00 PM | 499.105 | 499.105 | 0 | 297.444 | 297.444 | 0 | 0 | 0 | 596.43 | 596.43 | 0
5/1/2026 | 9:45:00 PM | 512.844 | 512.844 | 0 | 305.782 | 305.782 | 0 | 0 | 0 | 612.912 | 612.912 | 0
5/1/2026 | 10:00:00 PM | 526.429 | 526.429 | 0 | 314.192 | 314.192 | 0 | 0 | 0 | 629.263 | 629.263 | 0
5/1/2026 | 10:15:00 PM | 539.913 | 539.913 | 0 | 322.514 | 322.514 | 0 | 0 | 0 | 645.497 | 645.497 | 0
5/1/2026 | 10:30:00 PM | 553.197 | 553.197 | 0 | 330.712 | 330.712 | 0 | 0 | 0 | 661.482 | 661.482 | 0
5/1/2026 | 10:45:00 PM | 566.81 | 566.81 | 0 | 339.007 | 339.007 | 0 | 0 | 0 | 677.801 | 677.801 | 0
5/1/2026 | 11:00:00 PM | 580.153 | 580.153 | 0 | 347.238 | 347.238 | 0 | 0 | 0 | 693.855 | 693.855 | 0
5/1/2026 | 11:15:00 PM | 593.336 | 593.336 | 0 | 355.353 | 355.353 | 0 | 0 | 0 | 709.708 | 709.708 | 0
5/1/2026 | 11:30:00 PM | 607.027 | 607.027 | 0 | 363.817 | 363.817 | 0 | 0 | 0 | 726.166 | 726.166 | 0
5/1/2026 | 11:45:00 PM | 620.436 | 620.436 | 0 | 372.125 | 372.125 | 0 | 0 | 0 | 742.362 | 742.362 | 0
5/2/2026 | 12:00:00 AM | 634.319 | 634.319 | 0 | 380.609 | 380.609 | 0 | 0 | 0 | 759.042 | 759.042 | 0
5/2/2026 | 12:15:00 AM | 647.707 | 647.707 | 0 | 388.881 | 388.881 | 0 | 0 | 0 | 775.212 | 775.212 | 0
5/2/2026 | 12:30:00 AM | 661.479 | 661.479 | 0 | 397.307 | 397.307 | 0 | 0 | 0 | 791.786 | 791.786 | 0
5/2/2026 | 12:45:00 AM | 675.274 | 675.274 | 0 | 405.724 | 405.724 | 0 | 0 | 0 | 808.421 | 808.421 | 0
5/2/2026 | 1:00:00 AM | 689.11 | 689.11 | 0 | 414.068 | 414.068 | 0 | 0 | 0 | 825.054 | 825.054 | 0
5/2/2026 | 1:15:00 AM | 702.974 | 702.974 | 0 | 422.542 | 422.542 | 0 | 0 | 0 | 841.77 | 841.77 | 0
5/2/2026 | 1:30:00 AM | 716.879 | 716.879 | 0 | 430.774 | 430.774 | 0 | 0 | 0 | 858.4 | 858.4 | 0
5/2/2026 | 1:45:00 AM | 730.665 | 730.665 | 0 | 439.077 | 439.077 | 0 | 0 | 0 | 874.967 | 874.967 | 0
5/2/2026 | 2:00:00 AM | 744.038 | 744.038 | 0 | 447.194 | 447.194 | 0 | 0 | 0 | 891.042 | 891.042 | 0
5/2/2026 | 2:15:00 AM | 757.768 | 757.768 | 0 | 455.545 | 455.545 | 0 | 0 | 0 | 907.525 | 907.525 | 0
5/2/2026 | 2:30:00 AM | 771.03 | 771.03 | 0 | 463.62 | 463.62 | 0 | 0 | 0 | 923.47 | 923.47 | 0
5/2/2026 | 2:45:00 AM | 784.492 | 784.492 | 0 | 471.848 | 471.848 | 0 | 0 | 0 | 939.65 | 939.65 | 0
5/2/2026 | 3:00:00 AM | 797.742 | 797.742 | 0 | 480.041 | 480.041 | 0 | 0 | 0 | 955.604 | 955.604 | 0
5/2/2026 | 3:15:00 AM | 811.259 | 811.259 | 0 | 488.33 | 488.33 | 0 | 0 | 0 | 971.835 | 971.835 | 0
5/2/2026 | 3:30:00 AM | 824.659 | 824.659 | 0 | 496.576 | 496.576 | 0 | 0 | 0 | 987.945 | 987.945 | 0
5/2/2026 | 3:45:00 AM | 838.288 | 838.288 | 0 | 504.819 | 504.819 | 0 | 0 | 0 | 1004.302 | 1004.302 | 0
5/2/2026 | 4:00:00 AM | 851.767 | 851.767 | 0 | 513.069 | 513.069 | 0 | 0 | 0 | 1020.527 | 1020.527 | 0
5/2/2026 | 4:15:00 AM | 865.304 | 865.304 | 0 | 521.326 | 521.326 | 0 | 0 | 0 | 1036.794 | 1036.794 | 0
5/2/2026 | 4:30:00 AM | 878.828 | 878.828 | 0 | 529.626 | 529.626 | 0 | 0 | 0 | 1053.07 | 1053.07 | 0
5/2/2026 | 4:45:00 AM | 892.52 | 892.52 | 0 | 537.832 | 537.832 | 0 | 0 | 0 | 1069.493 | 1069.493 | 0
5/2/2026 | 5:00:00 AM | 906.313 | 906.313 | 0 | 546.087 | 546.087 | 0 | 0 | 0 | 1086.029 | 1086.029 | 0
5/2/2026 | 5:15:00 AM | 920.072 | 920.072 | 0 | 554.353 | 554.353 | 0 | 0 | 0 | 1102.528 | 1102.528 | 0
5/2/2026 | 5:30:00 AM | 933.84 | 933.84 | 0 | 562.627 | 562.627 | 0 | 0 | 0 | 1119.032 | 1119.032 | 0
5/2/2026 | 5:45:00 AM | 947.521 | 947.521 | 0 | 570.961 | 570.961 | 0 | 0 | 0 | 1135.484 | 1135.484 | 0
5/2/2026 | 6:00:00 AM | 961.247 | 961.247 | 0 | 579.278 | 579.278 | 0 | 0 | 0 | 1151.926 | 1151.926 | 0
5/2/2026 | 6:15:00 AM | 974.419 | 974.419 | 0 | 587.371 | 587.371 | 0 | 0 | 0 | 1167.792 | 1167.792 | 0
5/2/2026 | 6:30:00 AM | 987.966 | 987.966 | 0 | 595.582 | 595.582 | 0 | 0 | 0 | 1184.024 | 1184.024 | 0
5/2/2026 | 6:45:00 AM | 1001.245 | 1001.245 | 0 | 603.78 | 603.78 | 0 | 0 | 0 | 1199.99 | 1199.99 | 0
5/2/2026 | 7:00:00 AM | 1014.733 | 1014.733 | 0 | 612.035 | 612.035 | 0 | 0 | 0 | 1216.123 | 1216.123 | 0
5/2/2026 | 7:15:00 AM | 1027.883 | 1027.883 | 0 | 620.255 | 620.255 | 0 | 0 | 0 | 1231.944 | 1231.944 | 0
5/2/2026 | 7:30:00 AM | 1041.092 | 1041.092 | 0 | 628.394 | 628.394 | 0 | 0 | 0 | 1247.78 | 1247.78 | 0
5/2/2026 | 7:45:00 AM | 1054.432 | 1054.432 | 0 | 636.598 | 636.598 | 0 | 0 | 0 | 1263.799 | 1263.799 | 0
5/2/2026 | 8:00:00 AM | 1067.746 | 1067.746 | 0 | 644.732 | 644.732 | 0 | 0 | 0 | 1279.745 | 1279.745 | 0
5/2/2026 | 8:15:00 AM | 1081.223 | 1081.223 | 0 | 652.968 | 652.968 | 0 | 0 | 0 | 1295.871 | 1295.871 | 0
5/2/2026 | 8:30:00 AM | 1094.537 | 1094.537 | 0 | 660.989 | 660.989 | 0 | 0 | 0 | 1311.751 | 1311.751 | 0
5/2/2026 | 8:45:00 AM | 1108.239 | 1108.239 | 0 | 669.143 | 669.143 | 0 | 0 | 0 | 1328.072 | 1328.072 | 0
5/2/2026 | 9:00:00 AM | 1121.533 | 1121.533 | 0 | 677.129 | 677.129 | 0 | 0 | 0 | 1343.962 | 1343.962 | 0
5/2/2026 | 9:15:00 AM | 1135.402 | 1135.402 | 0 | 685.42 | 685.42 | 0 | 0 | 0 | 1360.468 | 1360.468 | 0
5/2/2026 | 9:30:00 AM | 1148.406 | 1148.406 | 0 | 693.295 | 693.295 | 0 | 0 | 0 | 1376.027 | 1376.027 | 0
5/2/2026 | 9:45:00 AM | 1161.731 | 1161.731 | 0 | 701.255 | 701.255 | 0 | 0 | 0 | 1391.915 | 1391.915 | 0
5/2/2026 | 10:00:00 AM | 1175.061 | 1175.061 | 0 | 709.323 | 709.323 | 0 | 0 | 0 | 1407.829 | 1407.829 | 0
5/2/2026 | 10:15:00 AM | 1188.332 | 1188.332 | 0 | 717.278 | 717.278 | 0 | 0 | 0 | 1423.638 | 1423.638 | 0
5/2/2026 | 10:30:00 AM | 1201.689 | 1201.689 | 0 | 725.323 | 725.323 | 0 | 0 | 0 | 1439.565 | 1439.565 | 0
5/2/2026 | 10:45:00 AM | 1214.993 | 1214.993 | 0 | 733.312 | 733.312 | 0 | 0 | 0 | 1455.42 | 1455.42 | 0
5/2/2026 | 11:00:00 AM | 1228.175 | 1228.175 | 0 | 741.244 | 741.244 | 0 | 0 | 0 | 1471.12 | 1471.12 | 0
5/2/2026 | 11:15:00 AM | 1241.214 | 1241.214 | 0 | 749.116 | 749.116 | 0 | 0 | 0 | 1486.646 | 1486.646 | 0
5/2/2026 | 11:30:00 AM | 1254.427 | 1254.427 | 0 | 757.021 | 757.021 | 0 | 0 | 0 | 1502.343 | 1502.343 | 0
5/2/2026 | 11:45:00 AM | 1267.661 | 1267.661 | 0 | 764.913 | 764.913 | 0 | 0 | 0 | 1518.09 | 1518.09 | 0
5/2/2026 | 12:00:00 PM | 1281.411 | 1281.411 | 0 | 772.96 | 772.96 | 0 | 0 | 0 | 1534.358 | 1534.358 | 0
5/2/2026 | 12:15:00 PM | 1294.257 | 1294.257 | 0 | 780.792 | 780.792 | 0 | 0 | 0 | 1549.746 | 1549.746 | 0
5/2/2026 | 12:30:00 PM | 1307.523 | 1307.523 | 0 | 788.763 | 788.763 | 0 | 0 | 0 | 1565.562 | 1565.562 | 0
5/2/2026 | 12:45:00 PM | 1320.696 | 1320.696 | 0 | 796.784 | 796.784 | 0 | 0 | 0 | 1581.324 | 1581.324 | 0
5/2/2026 | 1:00:00 PM | 1333.938 | 1333.938 | 0 | 804.736 | 804.736 | 0 | 0 | 0 | 1597.104 | 1597.104 | 0
5/2/2026 | 1:15:00 PM | 1347.29 | 1347.29 | 0 | 812.893 | 812.893 | 0 | 0 | 0 | 1613.07 | 1613.07 | 0
5/2/2026 | 1:30:00 PM | 1360.681 | 1360.681 | 0 | 820.933 | 820.933 | 0 | 0 | 0 | 1629.046 | 1629.046 | 0
5/2/2026 | 1:45:00 PM | 1374.2 | 1374.2 | 0 | 829.114 | 829.114 | 0 | 0 | 0 | 1645.238 | 1645.238 | 0
5/2/2026 | 2:00:00 PM | 1387.436 | 1387.436 | 0 | 837.031 | 837.031 | 0 | 0 | 0 | 1661.047 | 1661.047 | 0
5/2/2026 | 2:15:00 PM | 1400.708 | 1400.708 | 0 | 845.023 | 845.023 | 0 | 0 | 0 | 1676.914 | 1676.914 | 0
5/2/2026 | 2:30:00 PM | 1413.867 | 1413.867 | 0 | 852.999 | 852.999 | 0 | 0 | 0 | 1692.645 | 1692.645 | 0
5/2/2026 | 2:45:00 PM | 1427.078 | 1427.078 | 0 | 861.046 | 861.046 | 0 | 0 | 0 | 1708.453 | 1708.453 | 0
5/2/2026 | 3:00:00 PM | 1440.057 | 1440.057 | 0 | 869.073 | 869.073 | 0 | 0 | 0 | 1724.024 | 1724.024 | 0
5/2/2026 | 3:15:00 PM | 1453.426 | 1453.426 | 0 | 877.23 | 877.23 | 0 | 0 | 0 | 1740.001 | 1740.001 | 0
5/2/2026 | 3:30:00 PM | 1466.291 | 1466.291 | 0 | 885.165 | 885.165 | 0 | 0 | 0 | 1755.438 | 1755.438 | 0
5/2/2026 | 3:45:00 PM | 1479.887 | 1479.887 | 0 | 893.412 | 893.412 | 0 | 0 | 0 | 1771.686 | 1771.686 | 0
5/2/2026 | 4:00:00 PM | 1492.857 | 1492.857 | 0 | 901.359 | 901.359 | 0 | 0 | 0 | 1787.249 | 1787.249 | 0
5/2/2026 | 4:15:00 PM | 1506.237 | 1506.237 | 0 | 909.397 | 909.397 | 0 | 0 | 0 | 1803.2 | 1803.2 | 0
5/2/2026 | 4:30:00 PM | 1519.23 | 1519.23 | 0 | 917.338 | 917.338 | 0 | 0 | 0 | 1818.793 | 1818.793 | 0
5/2/2026 | 4:45:00 PM | 1532.818 | 1532.818 | 0 | 925.413 | 925.413 | 0 | 0 | 0 | 1834.991 | 1834.991 | 0
5/2/2026 | 5:00:00 PM | 1546.153 | 1546.153 | 0 | 933.379 | 933.379 | 0 | 0 | 0 | 1850.905 | 1850.905 | 0
5/2/2026 | 5:15:00 PM | 1559.72 | 1559.72 | 0 | 941.493 | 941.493 | 0 | 0 | 0 | 1867.089 | 1867.089 | 0
5/2/2026 | 5:30:00 PM | 1573.245 | 1573.245 | 0 | 949.644 | 949.644 | 0 | 0 | 0 | 1883.24 | 1883.24 | 0
5/2/2026 | 5:45:00 PM | 1586.485 | 1586.485 | 0 | 957.66 | 957.66 | 0 | 0 | 0 | 1899.077 | 1899.077 | 0
5/2/2026 | 6:00:00 PM | 1599.522 | 1599.522 | 0 | 965.603 | 965.603 | 0 | 0 | 0 | 1914.682 | 1914.682 | 0
5/2/2026 | 6:15:00 PM | 1612.54 | 1612.54 | 0 | 973.532 | 973.532 | 0 | 0 | 0 | 1930.243 | 1930.243 | 0
5/2/2026 | 6:30:00 PM | 1625.808 | 1625.808 | 0 | 981.643 | 981.643 | 0 | 0 | 0 | 1946.116 | 1946.116 | 0
5/2/2026 | 6:45:00 PM | 1638.747 | 1638.747 | 0 | 989.686 | 989.686 | 0 | 0 | 0 | 1961.67 | 1961.67 | 0
5/2/2026 | 7:00:00 PM | 1651.794 | 1651.794 | 0 | 997.803 | 997.803 | 0 | 0 | 0 | 1977.323 | 1977.323 | 0
5/2/2026 | 7:15:00 PM | 1664.552 | 1664.552 | 0 | 1005.937 | 1005.937 | 0 | 0 | 0 | 1992.71 | 1992.71 | 0
5/2/2026 | 7:30:00 PM | 1677.358 | 1677.358 | 0 | 1014.02 | 1014.02 | 0 | 0 | 0 | 2008.112 | 2008.112 | 0
5/2/2026 | 7:45:00 PM | 1690.145 | 1690.145 | 0 | 1022.142 | 1022.142 | 0 | 0 | 0 | 2023.541 | 2023.541 | 0
5/2/2026 | 8:00:00 PM | 1703.181 | 1703.181 | 0 | 1030.328 | 1030.328 | 0 | 0 | 0 | 2039.207 | 2039.207 | 0
5/2/2026 | 8:15:00 PM | 1716.125 | 1716.125 | 0 | 1038.55 | 1038.55 | 0 | 0 | 0 | 2054.823 | 2054.823 | 0
5/2/2026 | 8:30:00 PM | 1729.051 | 1729.051 | 0 | 1046.72 | 1046.72 | 0 | 0 | 0 | 2070.399 | 2070.399 | 0
5/2/2026 | 8:45:00 PM | 1742.57 | 1742.57 | 0 | 1055.112 | 1055.112 | 0 | 0 | 0 | 2086.616 | 2086.616 | 0
5/2/2026 | 9:00:00 PM | 1755.62 | 1755.62 | 0 | 1063.289 | 1063.289 | 0 | 0 | 0 | 2102.328 | 2102.328 | 0
5/2/2026 | 9:15:00 PM | 1768.921 | 1768.921 | 0 | 1071.555 | 1071.555 | 0 | 0 | 0 | 2118.311 | 2118.311 | 0
5/2/2026 | 9:30:00 PM | 1781.986 | 1781.986 | 0 | 1079.726 | 1079.726 | 0 | 0 | 0 | 2134.037 | 2134.037 | 0
5/2/2026 | 9:45:00 PM | 1795.158 | 1795.158 | 0 | 1088.016 | 1088.016 | 0 | 0 | 0 | 2149.913 | 2149.913 | 0
5/2/2026 | 10:00:00 PM | 1808.395 | 1808.395 | 0 | 1096.422 | 1096.422 | 0 | 0 | 0 | 2165.877 | 2165.877 | 0
5/2/2026 | 10:15:00 PM | 1821.399 | 1821.399 | 0 | 1104.657 | 1104.657 | 0 | 0 | 0 | 2181.561 | 2181.561 | 0
5/2/2026 | 10:30:00 PM | 1834.823 | 1834.823 | 0 | 1113.152 | 1113.152 | 0 | 0 | 0 | 2197.734 | 2197.734 | 0
5/2/2026 | 10:45:00 PM | 1847.824 | 1847.824 | 0 | 1121.51 | 1121.51 | 0 | 0 | 0 | 2213.48 | 2213.48 | 0
5/2/2026 | 11:00:00 PM | 1860.907 | 1860.907 | 0 | 1129.977 | 1129.977 | 0 | 0 | 0 | 2229.311 | 2229.311 | 0
5/2/2026 | 11:15:00 PM | 1873.671 | 1873.671 | 0 | 1138.329 | 1138.329 | 0 | 0 | 0 | 2244.804 | 2244.804 | 0
5/2/2026 | 11:30:00 PM | 1886.789 | 1886.789 | 0 | 1146.801 | 1146.801 | 0 | 0 | 0 | 2260.665 | 2260.665 | 0
5/2/2026 | 11:45:00 PM | 1899.751 | 1899.751 | 0 | 1155.256 | 1155.256 | 0 | 0 | 0 | 2276.415 | 2276.415 | 0
5/3/2026 | 12:00:00 AM | 1912.851 | 1912.851 | 0 | 1163.716 | 1163.716 | 0 | 0 | 0 | 2292.284 | 2292.284 | 0
5/3/2026 | 12:15:00 AM | 1926.248 | 1926.248 | 0 | 1172.435 | 1172.435 | 0 | 0 | 0 | 2308.531 | 2308.531 | 0
5/3/2026 | 12:30:00 AM | 1939.376 | 1939.376 | 0 | 1180.931 | 1180.931 | 0 | 0 | 0 | 2324.431 | 2324.431 | 0
5/3/2026 | 12:45:00 AM | 1952.599 | 1952.599 | 0 | 1189.316 | 1189.316 | 0 | 0 | 0 | 2340.383 | 2340.383 | 0
5/3/2026 | 1:00:00 AM | 1965.72 | 1965.72 | 0 | 1197.673 | 1197.673 | 0 | 0 | 0 | 2356.227 | 2356.227 | 0
5/3/2026 | 1:15:00 AM | 1979.172 | 1979.172 | 0 | 1206.128 | 1206.128 | 0 | 0 | 0 | 2372.406 | 2372.406 | 0
5/3/2026 | 1:30:00 AM | 1992.245 | 1992.245 | 0 | 1214.425 | 1214.425 | 0 | 0 | 0 | 2388.194 | 2388.194 | 0
5/3/2026 | 1:45:00 AM | 2005.488 | 2005.488 | 0 | 1222.822 | 1222.822 | 0 | 0 | 0 | 2404.184 | 2404.184 | 0
5/3/2026 | 2:00:00 AM | 2018.665 | 2018.665 | 0 | 1231.261 | 1231.261 | 0 | 0 | 0 | 2420.113 | 2420.113 | 0
5/3/2026 | 2:15:00 AM | 2031.967 | 2031.967 | 0 | 1239.772 | 1239.772 | 0 | 0 | 0 | 2436.18 | 2436.18 | 0
5/3/2026 | 2:30:00 AM | 2045.229 | 2045.229 | 0 | 1248.335 | 1248.335 | 0 | 0 | 0 | 2452.25 | 2452.25 | 0
5/3/2026 | 2:45:00 AM | 2058.076 | 2058.076 | 0 | 1256.697 | 1256.697 | 0 | 0 | 0 | 2467.854 | 2467.854 | 0
5/3/2026 | 3:00:00 AM | 2071.423 | 2071.423 | 0 | 1265.331 | 1265.331 | 0 | 0 | 0 | 2483.997 | 2483.997 | 0
5/3/2026 | 3:15:00 AM | 2084.108 | 2084.108 | 0 | 1273.661 | 1273.661 | 0 | 0 | 0 | 2499.429 | 2499.429 | 0
5/3/2026 | 3:30:00 AM | 2097.119 | 2097.119 | 0 | 1282.121 | 1282.121 | 0 | 0 | 0 | 2515.191 | 2515.191 | 0
5/3/2026 | 3:45:00 AM | 2110.384 | 2110.384 | 0 | 1290.725 | 1290.725 | 0 | 0 | 0 | 2531.278 | 2531.278 | 0
5/3/2026 | 4:00:00 AM | 2123.611 | 2123.611 | 0 | 1299.245 | 1299.245 | 0 | 0 | 0 | 2547.296 | 2547.296 | 0
5/3/2026 | 4:15:00 AM | 2136.859 | 2136.859 | 0 | 1307.864 | 1307.864 | 0 | 0 | 0 | 2563.382 | 2563.382 | 0
5/3/2026 | 4:30:00 AM | 2150.187 | 2150.187 | 0 | 1316.433 | 1316.433 | 0 | 0 | 0 | 2579.503 | 2579.503 | 0
5/3/2026 | 4:45:00 AM | 2163.51 | 2163.51 | 0 | 1324.972 | 1324.972 | 0 | 0 | 0 | 2595.639 | 2595.639 | 0
5/3/2026 | 5:00:00 AM | 2176.535 | 2176.535 | 0 | 1333.337 | 1333.337 | 0 | 0 | 0 | 2611.424 | 2611.424 | 0
5/3/2026 | 5:15:00 AM | 2190.183 | 2190.183 | 0 | 1341.966 | 1341.966 | 0 | 0 | 0 | 2627.869 | 2627.869 | 0
5/3/2026 | 5:30:00 AM | 2203.389 | 2203.389 | 0 | 1350.42 | 1350.42 | 0 | 0 | 0 | 2643.853 | 2643.853 | 0
5/3/2026 | 5:45:00 AM | 2216.724 | 2216.724 | 0 | 1358.876 | 1358.876 | 0 | 0 | 0 | 2659.964 | 2659.964 | 0
5/3/2026 | 6:00:00 AM | 2230.14 | 2230.14 | 0 | 1367.459 | 1367.459 | 0 | 0 | 0 | 2676.176 | 2676.176 | 0
5/3/2026 | 6:15:00 AM | 2243.37 | 2243.37 | 0 | 1375.911 | 1375.911 | 0 | 0 | 0 | 2692.163 | 2692.163 | 0
5/3/2026 | 6:30:00 AM | 2256.619 | 2256.619 | 0 | 1384.337 | 1384.337 | 0 | 0 | 0 | 2708.152 | 2708.152 | 0
5/3/2026 | 6:45:00 AM | 2269.735 | 2269.735 | 0 | 1393.062 | 1393.062 | 0 | 0 | 0 | 2724.175 | 2724.175 | 0
5/3/2026 | 7:00:00 AM | 2282.705 | 2282.705 | 0 | 1401.811 | 1401.811 | 0 | 0 | 0 | 2740.062 | 2740.062 | 0
5/3/2026 | 7:15:00 AM | 2295.558 | 2295.558 | 0 | 1410.47 | 1410.47 | 0 | 0 | 0 | 2755.795 | 2755.795 | 0
5/3/2026 | 7:30:00 AM | 2308.61 | 2308.61 | 0 | 1419.182 | 1419.182 | 0 | 0 | 0 | 2771.71 | 2771.71 | 0
5/3/2026 | 7:45:00 AM | 2321.707 | 2321.707 | 0 | 1427.905 | 1427.905 | 0 | 0 | 0 | 2787.701 | 2787.701 | 0
5/3/2026 | 8:00:00 AM | 2334.576 | 2334.576 | 0 | 1436.512 | 1436.512 | 0 | 0 | 0 | 2803.432 | 2803.432 | 0
5/3/2026 | 8:15:00 AM | 2347.819 | 2347.819 | 0 | 1445.318 | 1445.318 | 0 | 0 | 0 | 2819.56 | 2819.56 | 0
5/3/2026 | 8:30:00 AM | 2360.532 | 2360.532 | 0 | 1453.845 | 1453.845 | 0 | 0 | 0 | 2835.112 | 2835.112 | 0
5/3/2026 | 8:45:00 AM | 2373.585 | 2373.585 | 0 | 1462.459 | 1462.459 | 0 | 0 | 0 | 2851.021 | 2851.021 | 0
5/3/2026 | 9:00:00 AM | 2386.711 | 2386.711 | 0 | 1471.017 | 1471.017 | 0 | 0 | 0 | 2866.964 | 2866.964 | 0
5/3/2026 | 9:15:00 AM | 2399.859 | 2399.859 | 0 | 1479.274 | 1479.274 | 0 | 0 | 0 | 2882.764 | 2882.764 | 0
5/3/2026 | 9:30:00 AM | 2413.068 | 2413.068 | 0 | 1487.496 | 1487.496 | 0 | 0 | 0 | 2898.623 | 2898.623 | 0
5/3/2026 | 9:45:00 AM | 2426.142 | 2426.142 | 0 | 1495.684 | 1495.684 | 0 | 0 | 0 | 2914.349 | 2914.349 | 0
5/3/2026 | 10:00:00 AM | 2439.376 | 2439.376 | 0 | 1504.027 | 1504.027 | 0 | 0 | 0 | 2930.264 | 2930.264 | 0
5/3/2026 | 10:15:00 AM | 2452.414 | 2452.414 | 0 | 1512.211 | 1512.211 | 0 | 0 | 0 | 2945.936 | 2945.936 | 0
5/3/2026 | 10:30:00 AM | 2465.731 | 2465.731 | 0 | 1520.426 | 1520.426 | 0 | 0 | 0 | 2961.869 | 2961.869 | 0
5/3/2026 | 10:45:00 AM | 2478.865 | 2478.865 | 0 | 1528.605 | 1528.605 | 0 | 0 | 0 | 2977.644 | 2977.644 | 0
5/3/2026 | 11:00:00 AM | 2491.743 | 2491.743 | 0 | 1536.586 | 1536.586 | 0 | 0 | 0 | 2993.079 | 2993.079 | 0
5/3/2026 | 11:15:00 AM | 2504.977 | 2504.977 | 0 | 1544.782 | 1544.782 | 0 | 0 | 0 | 3008.916 | 3008.916 | 0
5/3/2026 | 11:30:00 AM | 2517.728 | 2517.728 | 0 | 1552.753 | 1552.753 | 0 | 0 | 0 | 3024.225 | 3024.225 | 0
5/3/2026 | 11:45:00 AM | 2530.909 | 2530.909 | 0 | 1560.927 | 1560.927 | 0 | 0 | 0 | 3040.025 | 3040.025 | 0
5/3/2026 | 12:00:00 PM | 2544.062 | 2544.062 | 0 | 1569.081 | 1569.081 | 0 | 0 | 0 | 3055.784 | 3055.784 | 0
5/3/2026 | 12:15:00 PM | 2557.212 | 2557.212 | 0 | 1577.176 | 1577.176 | 0 | 0 | 0 | 3071.521 | 3071.521 | 0
5/3/2026 | 12:30:00 PM | 2570.215 | 2570.215 | 0 | 1585.239 | 1585.239 | 0 | 0 | 0 | 3087.113 | 3087.113 | 0
5/3/2026 | 12:45:00 PM | 2583.327 | 2583.327 | 0 | 1593.265 | 1593.265 | 0 | 0 | 0 | 3102.788 | 3102.788 | 0
5/3/2026 | 1:00:00 PM | 2596.595 | 2596.595 | 0 | 1601.371 | 1601.371 | 0 | 0 | 0 | 3118.637 | 3118.637 | 0
5/3/2026 | 1:15:00 PM | 2609.505 | 2609.505 | 0 | 1609.239 | 1609.239 | 0 | 0 | 0 | 3134.064 | 3134.064 | 0
5/3/2026 | 1:30:00 PM | 2622.971 | 2622.971 | 0 | 1617.409 | 1617.409 | 0 | 0 | 0 | 3150.11 | 3150.11 | 0
5/3/2026 | 1:45:00 PM | 2636.224 | 2636.224 | 0 | 1625.563 | 1625.563 | 0 | 0 | 0 | 3165.984 | 3165.984 | 0
5/3/2026 | 2:00:00 PM | 2649.306 | 2649.306 | 0 | 1633.533 | 1633.533 | 0 | 0 | 0 | 3181.599 | 3181.599 | 0
5/3/2026 | 2:15:00 PM | 2662.433 | 2662.433 | 0 | 1641.588 | 1641.588 | 0 | 0 | 0 | 3197.294 | 3197.294 | 0
5/3/2026 | 2:30:00 PM | 2675.49 | 2675.49 | 0 | 1649.604 | 1649.604 | 0 | 0 | 0 | 3212.912 | 3212.912 | 0
5/3/2026 | 2:45:00 PM | 2688.59 | 2688.59 | 0 | 1657.626 | 1657.626 | 0 | 0 | 0 | 3228.569 | 3228.569 | 0
5/3/2026 | 3:00:00 PM | 2701.389 | 2701.389 | 0 | 1665.585 | 1665.585 | 0 | 0 | 0 | 3243.895 | 3243.895 | 0
5/3/2026 | 3:15:00 PM | 2714.608 | 2714.608 | 0 | 1673.756 | 1673.756 | 0 | 0 | 0 | 3259.672 | 3259.672 | 0
5/3/2026 | 3:30:00 PM | 2727.436 | 2727.436 | 0 | 1681.832 | 1681.832 | 0 | 0 | 0 | 3275.074 | 3275.074 | 0
5/3/2026 | 3:45:00 PM | 2740.544 | 2740.544 | 0 | 1689.891 | 1689.891 | 0 | 0 | 0 | 3290.735 | 3290.735 | 0
5/3/2026 | 4:00:00 PM | 2753.28 | 2753.28 | 0 | 1697.803 | 1697.803 | 0 | 0 | 0 | 3305.989 | 3305.989 | 0
5/3/2026 | 4:15:00 PM | 2766.249 | 2766.249 | 0 | 1705.765 | 1705.765 | 0 | 0 | 0 | 3321.457 | 3321.457 | 0
5/3/2026 | 4:30:00 PM | 2779.128 | 2779.128 | 0 | 1713.763 | 1713.763 | 0 | 0 | 0 | 3336.87 | 3336.87 | 0
5/3/2026 | 4:45:00 PM | 2792.131 | 2792.131 | 0 | 1721.689 | 1721.689 | 0 | 0 | 0 | 3352.381 | 3352.381 | 0
5/3/2026 | 5:00:00 PM | 2805.345 | 2805.345 | 0 | 1729.754 | 1729.754 | 0 | 0 | 0 | 3368.132 | 3368.132 | 0
5/3/2026 | 5:15:00 PM | 2818.361 | 2818.361 | 0 | 1737.7 | 1737.7 | 0 | 0 | 0 | 3383.654 | 3383.654 | 0
5/3/2026 | 5:30:00 PM | 2831.66 | 2831.66 | 0 | 1745.761 | 1745.761 | 0 | 0 | 0 | 3399.481 | 3399.481 | 0
5/3/2026 | 5:45:00 PM | 2844.479 | 2844.479 | 0 | 1753.601 | 1753.601 | 0 | 0 | 0 | 3414.794 | 3414.794 | 0
5/3/2026 | 6:00:00 PM | 2857.669 | 2857.669 | 0 | 1761.565 | 1761.565 | 0 | 0 | 0 | 3430.474 | 3430.474 | 0
5/3/2026 | 6:15:00 PM | 2870.466 | 2870.466 | 0 | 1769.409 | 1769.409 | 0 | 0 | 0 | 3445.771 | 3445.771 | 0
5/3/2026 | 6:30:00 PM | 2883.577 | 2883.577 | 0 | 1777.35 | 1777.35 | 0 | 0 | 0 | 3461.376 | 3461.376 | 0
5/3/2026 | 6:45:00 PM | 2896.553 | 2896.553 | 0 | 1785.345 | 1785.345 | 0 | 0 | 0 | 3476.896 | 3476.896 | 0
5/3/2026 | 7:00:00 PM | 2909.699 | 2909.699 | 0 | 1793.372 | 1793.372 | 0 | 0 | 0 | 3492.573 | 3492.573 | 0
5/3/2026 | 7:15:00 PM | 2922.865 | 2922.865 | 0 | 1801.468 | 1801.468 | 0 | 0 | 0 | 3508.286 | 3508.286 | 0
5/3/2026 | 7:30:00 PM | 2935.989 | 2935.989 | 0 | 1809.503 | 1809.503 | 0 | 0 | 0 | 3523.93 | 3523.93 | 0
5/3/2026 | 7:45:00 PM | 2949.008 | 2949.008 | 0 | 1817.497 | 1817.497 | 0 | 0 | 0 | 3539.506 | 3539.506 | 0
5/3/2026 | 8:00:00 PM | 2962.015 | 2962.015 | 0 | 1825.46 | 1825.46 | 0 | 0 | 0 | 3555.036 | 3555.036 | 0
5/3/2026 | 8:15:00 PM | 2975.221 | 2975.221 | 0 | 1833.556 | 1833.556 | 0 | 0 | 0 | 3570.809 | 3570.809 | 0
5/3/2026 | 8:30:00 PM | 2988.359 | 2988.359 | 0 | 1841.673 | 1841.673 | 0 | 0 | 0 | 3586.545 | 3586.545 | 0
5/3/2026 | 8:45:00 PM | 3001.802 | 3001.802 | 0 | 1849.81 | 1849.81 | 0 | 0 | 0 | 3602.561 | 3602.561 | 0
5/3/2026 | 9:00:00 PM | 3015.095 | 3015.095 | 0 | 1857.953 | 1857.953 | 0 | 0 | 0 | 3618.438 | 3618.438 | 0
5/3/2026 | 9:15:00 PM | 3028.628 | 3028.628 | 0 | 1866.107 | 1866.107 | 0 | 0 | 0 | 3634.551 | 3634.551 | 0
5/3/2026 | 9:30:00 PM | 3041.965 | 3041.965 | 0 | 1874.227 | 1874.227 | 0 | 0 | 0 | 3650.485 | 3650.485 | 0
5/3/2026 | 9:45:00 PM | 3055.254 | 3055.254 | 0 | 1882.331 | 1882.331 | 0 | 0 | 0 | 3666.372 | 3666.372 | 0
5/3/2026 | 10:00:00 PM | 3068.589 | 3068.589 | 0 | 1890.54 | 1890.54 | 0 | 0 | 0 | 3682.326 | 3682.326 | 0
5/3/2026 | 10:15:00 PM | 3081.585 | 3081.585 | 0 | 1898.604 | 1898.604 | 0 | 0 | 0 | 3697.913 | 3697.913 | 0
5/3/2026 | 10:30:00 PM | 3094.867 | 3094.867 | 0 | 1906.845 | 1906.845 | 0 | 0 | 0 | 3713.836 | 3713.836 | 0
5/3/2026 | 10:45:00 PM | 3108.122 | 3108.122 | 0 | 1915.261 | 1915.261 | 0 | 0 | 0 | 3729.809 | 3729.809 | 0
5/3/2026 | 11:00:00 PM | 3121.151 | 3121.151 | 0 | 1923.478 | 1923.478 | 0 | 0 | 0 | 3745.466 | 3745.466 | 0
5/3/2026 | 11:15:00 PM | 3134.121 | 3134.121 | 0 | 1931.776 | 1931.776 | 0 | 0 | 0 | 3761.11 | 3761.11 | 0
5/3/2026 | 11:30:00 PM | 3146.807 | 3146.807 | 0 | 1939.846 | 1939.846 | 0 | 0 | 0 | 3776.382 | 3776.382 | 0
5/3/2026 | 11:45:00 PM | 3160.059 | 3160.059 | 0 | 1948.259 | 1948.259 | 0 | 0 | 0 | 3792.34 | 3792.34 | 0
5/4/2026 | 12:00:00 AM | 3172.81 | 3172.81 | 0 | 1956.427 | 1956.427 | 0 | 0 | 0 | 3807.754 | 3807.754 | 0
5/4/2026 | 12:15:00 AM | 3186.109 | 3186.109 | 0 | 1964.906 | 1964.906 | 0 | 0 | 0 | 3823.787 | 3823.787 | 0
5/4/2026 | 12:30:00 AM | 3199.17 | 3199.17 | 0 | 1973.27 | 1973.27 | 0 | 0 | 0 | 3839.559 | 3839.559 | 0
5/4/2026 | 12:45:00 AM | 3212.34 | 3212.34 | 0 | 1981.592 | 1981.592 | 0 | 0 | 0 | 3855.423 | 3855.423 | 0
5/4/2026 | 1:00:00 AM | 3225.908 | 3225.908 | 0 | 1990.092 | 1990.092 | 0 | 0 | 0 | 3871.731 | 3871.731 | 0
5/4/2026 | 1:15:00 AM | 3238.989 | 3238.989 | 0 | 1998.317 | 1998.317 | 0 | 0 | 0 | 3887.502 | 3887.502 | 0
5/4/2026 | 1:30:00 AM | 3252.225 | 3252.225 | 0 | 2006.574 | 2006.574 | 0 | 0 | 0 | 3903.411 | 3903.411 | 0
5/4/2026 | 1:45:00 AM | 3265.553 | 3265.553 | 0 | 2014.951 | 2014.951 | 0 | 0 | 0 | 3919.465 | 3919.465 | 0
5/4/2026 | 2:00:00 AM | 3278.532 | 3278.532 | 0 | 2023.165 | 2023.165 | 0 | 0 | 0 | 3935.125 | 3935.125 | 0
5/4/2026 | 2:15:00 AM | 3291.883 | 3291.883 | 0 | 2031.602 | 2031.602 | 0 | 0 | 0 | 3951.207 | 3951.207 | 0
5/4/2026 | 2:30:00 AM | 3305.083 | 3305.083 | 0 | 2039.986 | 2039.986 | 0 | 0 | 0 | 3967.135 | 3967.135 | 0
5/4/2026 | 2:45:00 AM | 3318.157 | 3318.157 | 0 | 2048.276 | 2048.276 | 0 | 0 | 0 | 3982.906 | 3982.906 | 0
5/4/2026 | 3:00:00 AM | 3331.297 | 3331.297 | 0 | 2056.669 | 2056.669 | 0 | 0 | 0 | 3998.755 | 3998.755 | 0
5/4/2026 | 3:15:00 AM | 3344.312 | 3344.312 | 0 | 2065.038 | 2065.038 | 0 | 0 | 0 | 4014.49 | 4014.49 | 0
5/4/2026 | 3:30:00 AM | 3357.251 | 3357.251 | 0 | 2073.325 | 2073.325 | 0 | 0 | 0 | 4030.112 | 4030.112 | 0
5/4/2026 | 3:45:00 AM | 3370.56 | 3370.56 | 0 | 2081.812 | 2081.812 | 0 | 0 | 0 | 4046.164 | 4046.164 | 0
5/4/2026 | 4:00:00 AM | 3383.457 | 3383.457 | 0 | 2089.988 | 2089.988 | 0 | 0 | 0 | 4061.714 | 4061.714 | 0
5/4/2026 | 4:15:00 AM | 3396.803 | 3396.803 | 0 | 2098.414 | 2098.414 | 0 | 0 | 0 | 4077.779 | 4077.779 | 0
5/4/2026 | 4:30:00 AM | 3409.961 | 3409.961 | 0 | 2106.782 | 2106.782 | 0 | 0 | 0 | 4093.652 | 4093.652 | 0
5/4/2026 | 4:45:00 AM | 3423.367 | 3423.367 | 0 | 2115.156 | 2115.156 | 0 | 0 | 0 | 4109.759 | 4109.759 | 0
5/4/2026 | 5:00:00 AM | 3436.791 | 3436.791 | 0 | 2123.506 | 2123.506 | 0 | 0 | 0 | 4125.87 | 4125.87 | 0
5/4/2026 | 5:15:00 AM | 3450.063 | 3450.063 | 0 | 2131.816 | 2131.816 | 0 | 0 | 0 | 4141.833 | 4141.833 | 0
5/4/2026 | 5:30:00 AM | 3463.45 | 3463.45 | 0 | 2140.112 | 2140.112 | 0 | 0 | 0 | 4157.886 | 4157.886 | 0
5/4/2026 | 5:45:00 AM | 3476.933 | 3476.933 | 0 | 2148.402 | 2148.402 | 0 | 0 | 0 | 4174.033 | 4174.033 | 0
5/4/2026 | 6:00:00 AM | 3489.98 | 3489.98 | 0 | 2156.464 | 2156.464 | 0 | 0 | 0 | 4189.666 | 4189.666 | 0
5/4/2026 | 6:15:00 AM | 3503.253 | 3503.253 | 0 | 2164.545 | 2164.545 | 0 | 0 | 0 | 4205.501 | 4205.501 | 0
5/4/2026 | 6:30:00 AM | 3516.598 | 3516.598 | 0 | 2172.529 | 2172.529 | 0 | 0 | 0 | 4221.359 | 4221.359 | 0
5/4/2026 | 6:45:00 AM | 3529.681 | 3529.681 | 0 | 2180.431 | 2180.431 | 0 | 0 | 0 | 4236.959 | 4236.959 | 0
5/4/2026 | 7:00:00 AM | 3542.831 | 3542.831 | 0 | 2188.488 | 2188.488 | 0 | 0 | 0 | 4252.654 | 4252.654 | 0
5/4/2026 | 7:15:00 AM | 3556.006 | 3556.006 | 0 | 2196.532 | 2196.532 | 0 | 0 | 0 | 4268.364 | 4268.364 | 0
5/4/2026 | 7:30:00 AM | 3568.817 | 3568.817 | 0 | 2204.318 | 2204.318 | 0 | 0 | 0 | 4283.651 | 4283.651 | 0
5/4/2026 | 7:45:00 AM | 3582.401 | 3582.401 | 0 | 2212.373 | 2212.373 | 0 | 0 | 0 | 4299.779 | 4299.779 | 0
5/4/2026 | 8:00:00 AM | 3595.916 | 3595.916 | 0 | 2220.418 | 2220.418 | 0 | 0 | 0 | 4315.833 | 4315.833 | 0
5/4/2026 | 8:15:00 AM | 3609.243 | 3609.243 | 0 | 2228.281 | 2228.281 | 0 | 0 | 0 | 4331.647 | 4331.647 | 0
5/4/2026 | 8:30:00 AM | 3622.837 | 3622.837 | 0 | 2236.23 | 2236.23 | 0 | 0 | 0 | 4347.754 | 4347.754 | 0
5/4/2026 | 8:45:00 AM | 3636.254 | 3636.254 | 0 | 2244.011 | 2244.011 | 0 | 0 | 0 | 4363.693 | 4363.693 | 0
5/4/2026 | 9:00:00 AM | 3650.002 | 3650.002 | 0 | 2251.851 | 2251.851 | 0 | 0 | 0 | 4379.946 | 4379.946 | 0
5/4/2026 | 9:15:00 AM | 3663.701 | 3663.701 | 0 | 2259.685 | 2259.685 | 0 | 0 | 0 | 4396.144 | 4396.144 | 0
5/4/2026 | 9:30:00 AM | 3677.071 | 3677.071 | 0 | 2267.26 | 2267.26 | 0 | 0 | 0 | 4411.939 | 4411.939 | 0
5/4/2026 | 9:45:00 AM | 3690.823 | 3690.823 | 0 | 2275.118 | 2275.118 | 0 | 0 | 0 | 4428.209 | 4428.209 | 0
5/4/2026 | 10:00:00 AM | 3704.016 | 3704.016 | 0 | 2282.86 | 2282.86 | 0 | 0 | 0 | 4443.901 | 4443.901 | 0
5/4/2026 | 10:15:00 AM | 3717.678 | 3717.678 | 0 | 2290.675 | 2290.675 | 0 | 0 | 0 | 4460.055 | 4460.055 | 0
5/4/2026 | 10:30:00 AM | 3731.281 | 3731.281 | 0 | 2298.559 | 2298.559 | 0 | 0 | 0 | 4476.193 | 4476.193 | 0
5/4/2026 | 10:45:00 AM | 3744.686 | 3744.686 | 0 | 2306.223 | 2306.223 | 0 | 0 | 0 | 4492.08 | 4492.08 | 0
5/4/2026 | 11:00:00 AM | 3758.52 | 3758.52 | 0 | 2314.165 | 2314.165 | 0 | 0 | 0 | 4508.432 | 4508.432 | 0
5/4/2026 | 11:15:00 AM | 3771.686 | 3771.686 | 0 | 2321.775 | 2321.775 | 0 | 0 | 0 | 4524.065 | 4524.065 | 0
5/4/2026 | 11:30:00 AM | 3785.276 | 3785.276 | 0 | 2329.497 | 2329.497 | 0 | 0 | 0 | 4540.092 | 4540.092 | 0
5/4/2026 | 11:45:00 AM | 3799.038 | 3799.038 | 0 | 2337.307 | 2337.307 | 0 | 0 | 0 | 4556.373 | 4556.373 | 0
5/4/2026 | 12:00:00 PM | 3812.959 | 3812.959 | 0 | 2345.099 | 2345.099 | 0 | 0 | 0 | 4572.811 | 4572.811 | 0
5/4/2026 | 12:15:00 PM | 3826.705 | 3826.705 | 0 | 2352.822 | 2352.822 | 0 | 0 | 0 | 4589.063 | 4589.063 | 0
5/4/2026 | 12:30:00 PM | 3840.503 | 3840.503 | 0 | 2360.615 | 2360.615 | 0 | 0 | 0 | 4605.382 | 4605.382 | 0
5/4/2026 | 12:45:00 PM | 3854.378 | 3854.378 | 0 | 2368.269 | 2368.269 | 0 | 0 | 0 | 4621.741 | 4621.741 | 0
5/4/2026 | 1:00:00 PM | 3867.766 | 3867.766 | 0 | 2375.736 | 2375.736 | 0 | 0 | 0 | 4637.581 | 4637.581 | 0
5/4/2026 | 1:15:00 PM | 3881.756 | 3881.756 | 0 | 2383.389 | 2383.389 | 0 | 0 | 0 | 4654.067 | 4654.067 | 0
5/4/2026 | 1:30:00 PM | 3895.586 | 3895.586 | 0 | 2390.86 | 2390.86 | 0 | 0 | 0 | 4670.391 | 4670.391 | 0
5/4/2026 | 1:45:00 PM | 3909.922 | 3909.922 | 0 | 2398.66 | 2398.66 | 0 | 0 | 0 | 4687.303 | 4687.303 | 0
5/4/2026 | 2:00:00 PM | 3923.944 | 3923.944 | 0 | 2406.379 | 2406.379 | 0 | 0 | 0 | 4703.86 | 4703.86 | 0
5/4/2026 | 2:15:00 PM | 3938.02 | 3938.02 | 0 | 2414.028 | 2414.028 | 0 | 0 | 0 | 4720.441 | 4720.441 | 0
5/4/2026 | 2:30:00 PM | 3951.966 | 3951.966 | 0 | 2421.752 | 2421.752 | 0 | 0 | 0 | 4736.916 | 4736.916 | 0
5/4/2026 | 2:45:00 PM | 3965.489 | 3965.489 | 0 | 2429.321 | 2429.321 | 0 | 0 | 0 | 4752.92 | 4752.92 | 0
5/4/2026 | 3:00:00 PM | 3979.248 | 3979.248 | 0 | 2437.128 | 2437.128 | 0 | 0 | 0 | 4769.159 | 4769.159 | 0
5/4/2026 | 3:15:00 PM | 3992.238 | 3992.238 | 0 | 2444.65 | 2444.65 | 0 | 0 | 0 | 4784.566 | 4784.566 | 0
5/4/2026 | 3:30:00 PM | 4005.746 | 4005.746 | 0 | 2452.52 | 2452.52 | 0 | 0 | 0 | 4800.532 | 4800.532 | 0
5/4/2026 | 3:45:00 PM | 4019.049 | 4019.049 | 0 | 2460.342 | 2460.342 | 0 | 0 | 0 | 4816.333 | 4816.333 | 0
5/4/2026 | 4:00:00 PM | 4033.002 | 4033.002 | 0 | 2468.199 | 2468.199 | 0 | 0 | 0 | 4832.77 | 4832.77 | 0
5/4/2026 | 4:15:00 PM | 4046.349 | 4046.349 | 0 | 2475.833 | 2475.833 | 0 | 0 | 0 | 4848.565 | 4848.565 | 0
5/4/2026 | 4:30:00 PM | 4059.927 | 4059.927 | 0 | 2483.616 | 2483.616 | 0 | 0 | 0 | 4864.599 | 4864.599 | 0
5/4/2026 | 4:45:00 PM | 4073.451 | 4073.451 | 0 | 2491.52 | 2491.52 | 0 | 0 | 0 | 4880.669 | 4880.669 | 0
5/4/2026 | 5:00:00 PM | 4086.925 | 4086.925 | 0 | 2499.426 | 2499.426 | 0 | 0 | 0 | 4896.678 | 4896.678 | 0
5/4/2026 | 5:15:00 PM | 4100.536 | 4100.536 | 0 | 2507.503 | 2507.503 | 0 | 0 | 0 | 4912.887 | 4912.887 | 0
5/4/2026 | 5:30:00 PM | 4113.819 | 4113.819 | 0 | 2515.424 | 2515.424 | 0 | 0 | 0 | 4928.722 | 4928.722 | 0
5/4/2026 | 5:45:00 PM | 4127.667 | 4127.667 | 0 | 2523.648 | 2523.648 | 0 | 0 | 0 | 4945.188 | 4945.188 | 0
5/4/2026 | 6:00:00 PM | 4140.576 | 4140.576 | 0 | 2531.543 | 2531.543 | 0 | 0 | 0 | 4960.651 | 4960.651 | 0
5/4/2026 | 6:15:00 PM | 4153.991 | 4153.991 | 0 | 2539.766 | 2539.766 | 0 | 0 | 0 | 4976.704 | 4976.704 | 0
5/4/2026 | 6:30:00 PM | 4167.101 | 4167.101 | 0 | 2547.864 | 2547.864 | 0 | 0 | 0 | 4992.446 | 4992.446 | 0
5/4/2026 | 6:45:00 PM | 4180.358 | 4180.358 | 0 | 2555.988 | 2555.988 | 0 | 0 | 0 | 5008.333 | 5008.333 | 0
5/4/2026 | 7:00:00 PM | 4193.638 | 4193.638 | 0 | 2564.248 | 2564.248 | 0 | 0 | 0 | 5024.289 | 5024.289 | 0
5/4/2026 | 7:15:00 PM | 4207.028 | 4207.028 | 0 | 2572.524 | 2572.524 | 0 | 0 | 0 | 5040.349 | 5040.349 | 0
5/4/2026 | 7:30:00 PM | 4220.294 | 4220.294 | 0 | 2580.805 | 2580.805 | 0 | 0 | 0 | 5056.303 | 5056.303 | 0
5/4/2026 | 7:45:00 PM | 4233.577 | 4233.577 | 0 | 2589.088 | 2589.088 | 0 | 0 | 0 | 5072.315 | 5072.315 | 0
5/4/2026 | 8:00:00 PM | 4247.135 | 4247.135 | 0 | 2597.412 | 2597.412 | 0 | 0 | 0 | 5088.58 | 5088.58 | 0
5/4/2026 | 8:15:00 PM | 4260.275 | 4260.275 | 0 | 2605.673 | 2605.673 | 0 | 0 | 0 | 5104.458 | 5104.458 | 0
5/4/2026 | 8:30:00 PM | 4273.845 | 4273.845 | 0 | 2614.055 | 2614.055 | 0 | 0 | 0 | 5120.756 | 5120.756 | 0
5/4/2026 | 8:45:00 PM | 4287.523 | 4287.523 | 0 | 2622.49 | 2622.49 | 0 | 0 | 0 | 5137.215 | 5137.215 | 0
5/4/2026 | 9:00:00 PM | 4301.261 | 4301.261 | 0 | 2630.816 | 2630.816 | 0 | 0 | 0 | 5153.686 | 5153.686 | 0
5/4/2026 | 9:15:00 PM | 4315.29 | 4315.29 | 0 | 2639.324 | 2639.324 | 0 | 0 | 0 | 5170.514 | 5170.514 | 0
5/4/2026 | 9:30:00 PM | 4328.75 | 4328.75 | 0 | 2647.525 | 2647.525 | 0 | 0 | 0 | 5186.716 | 5186.716 | 0
5/4/2026 | 9:45:00 PM | 4342.452 | 4342.452 | 0 | 2655.884 | 2655.884 | 0 | 0 | 0 | 5203.177 | 5203.177 | 0
5/4/2026 | 10:00:00 PM | 4355.872 | 4355.872 | 0 | 2664.11 | 2664.11 | 0 | 0 | 0 | 5219.288 | 5219.288 | 0
5/4/2026 | 10:15:00 PM | 4369.482 | 4369.482 | 0 | 2672.444 | 2672.444 | 0 | 0 | 0 | 5235.586 | 5235.586 | 0
5/4/2026 | 10:30:00 PM | 4382.996 | 4382.996 | 0 | 2680.661 | 2680.661 | 0 | 0 | 0 | 5251.762 | 5251.762 | 0
5/4/2026 | 10:45:00 PM | 4396.361 | 4396.361 | 0 | 2688.928 | 2688.928 | 0 | 0 | 0 | 5267.827 | 5267.827 | 0
5/4/2026 | 11:00:00 PM | 4409.9 | 4409.9 | 0 | 2697.333 | 2697.333 | 0 | 0 | 0 | 5284.06 | 5284.06 | 0
5/4/2026 | 11:15:00 PM | 4423.044 | 4423.044 | 0 | 2705.616 | 2705.616 | 0 | 0 | 0 | 5299.913 | 5299.913 | 0
5/4/2026 | 11:30:00 PM | 4436.381 | 4436.381 | 0 | 2713.919 | 2713.919 | 0 | 0 | 0 | 5315.941 | 5315.941 | 0
5/4/2026 | 11:45:00 PM | 4449.827 | 4449.827 | 0 | 2722.278 | 2722.278 | 0 | 0 | 0 | 5332.141 | 5332.141 | 0
5/5/2026 | 12:00:00 AM | 4463.194 | 4463.194 | 0 | 2730.518 | 2730.518 | 0 | 0 | 0 | 5348.212 | 5348.212 | 0
5/5/2026 | 12:15:00 AM | 4476.789 | 4476.789 | 0 | 2738.91 | 2738.91 | 0 | 0 | 0 | 5364.559 | 5364.559 | 0
5/5/2026 | 12:30:00 AM | 4490.409 | 4490.409 | 0 | 2747.393 | 2747.393 | 0 | 0 | 0 | 5380.957 | 5380.957 | 0
5/5/2026 | 12:45:00 AM | 4504.091 | 4504.091 | 0 | 2755.841 | 2755.841 | 0 | 0 | 0 | 5397.423 | 5397.423 | 0
5/5/2026 | 1:00:00 AM | 4517.963 | 4517.963 | 0 | 2764.381 | 2764.381 | 0 | 0 | 0 | 5414.092 | 5414.092 | 0
5/5/2026 | 1:15:00 AM | 4531.264 | 4531.264 | 0 | 2772.576 | 2772.576 | 0 | 0 | 0 | 5430.105 | 5430.105 | 0
5/5/2026 | 1:30:00 AM | 4544.935 | 4544.935 | 0 | 2780.939 | 2780.939 | 0 | 0 | 0 | 5446.511 | 5446.511 | 0
5/5/2026 | 1:45:00 AM | 4558.297 | 4558.297 | 0 | 2789.254 | 2789.254 | 0 | 0 | 0 | 5462.633 | 5462.633 | 0
5/5/2026 | 2:00:00 AM | 4571.826 | 4571.826 | 0 | 2797.743 | 2797.743 | 0 | 0 | 0 | 5478.96 | 5478.96 | 0
5/5/2026 | 2:15:00 AM | 4585.426 | 4585.426 | 0 | 2806.25 | 2806.25 | 0 | 0 | 0 | 5495.362 | 5495.362 | 0
5/5/2026 | 2:30:00 AM | 4598.907 | 4598.907 | 0 | 2814.701 | 2814.701 | 0 | 0 | 0 | 5511.652 | 5511.652 | 0
5/5/2026 | 2:45:00 AM | 4612.461 | 4612.461 | 0 | 2823.212 | 2823.212 | 0 | 0 | 0 | 5528.023 | 5528.023 | 0
5/5/2026 | 3:00:00 AM | 4625.984 | 4625.984 | 0 | 2831.767 | 2831.767 | 0 | 0 | 0 | 5544.365 | 5544.365 | 0
5/5/2026 | 3:15:00 AM | 4639.248 | 4639.248 | 0 | 2840.13 | 2840.13 | 0 | 0 | 0 | 5560.38 | 5560.38 | 0
5/5/2026 | 3:30:00 AM | 4652.575 | 4652.575 | 0 | 2848.509 | 2848.509 | 0 | 0 | 0 | 5576.464 | 5576.464 | 0
5/5/2026 | 3:45:00 AM | 4666.017 | 4666.017 | 0 | 2857.013 | 2857.013 | 0 | 0 | 0 | 5592.73 | 5592.73 | 0
5/5/2026 | 4:00:00 AM | 4679.553 | 4679.553 | 0 | 2865.488 | 2865.488 | 0 | 0 | 0 | 5609.057 | 5609.057 | 0
5/5/2026 | 4:15:00 AM | 4693.332 | 4693.332 | 0 | 2874.149 | 2874.149 | 0 | 0 | 0 | 5625.681 | 5625.681 | 0
5/5/2026 | 4:30:00 AM | 4706.643 | 4706.643 | 0 | 2882.529 | 2882.529 | 0 | 0 | 0 | 5641.77 | 5641.77 | 0
5/5/2026 | 4:45:00 AM | 4720.395 | 4720.395 | 0 | 2890.993 | 2890.993 | 0 | 0 | 0 | 5658.308 | 5658.308 | 0
5/5/2026 | 5:00:00 AM | 4733.965 | 4733.965 | 0 | 2899.315 | 2899.315 | 0 | 0 | 0 | 5674.624 | 5674.624 | 0
5/5/2026 | 5:15:00 AM | 4747.748 | 4747.748 | 0 | 2907.704 | 2907.704 | 0 | 0 | 0 | 5691.145 | 5691.145 | 0
5/5/2026 | 5:30:00 AM | 4761.643 | 4761.643 | 0 | 2916.037 | 2916.037 | 0 | 0 | 0 | 5707.733 | 5707.733 | 0
5/5/2026 | 5:45:00 AM | 4775.02 | 4775.02 | 0 | 2924.214 | 2924.214 | 0 | 0 | 0 | 5723.818 | 5723.818 | 0
5/5/2026 | 6:00:00 AM | 4788.629 | 4788.629 | 0 | 2932.529 | 2932.529 | 0 | 0 | 0 | 5740.121 | 5740.121 | 0
5/5/2026 | 6:15:00 AM | 4802.057 | 4802.057 | 0 | 2940.648 | 2940.648 | 0 | 0 | 0 | 5756.181 | 5756.181 | 0
5/5/2026 | 6:30:00 AM | 4815.503 | 4815.503 | 0 | 2948.779 | 2948.779 | 0 | 0 | 0 | 5772.245 | 5772.245 | 0
5/5/2026 | 6:45:00 AM | 4828.737 | 4828.737 | 0 | 2956.871 | 2956.871 | 0 | 0 | 0 | 5788.083 | 5788.083 | 0
5/5/2026 | 7:00:00 AM | 4841.862 | 4841.862 | 0 | 2964.975 | 2964.975 | 0 | 0 | 0 | 5803.819 | 5803.819 | 0
5/5/2026 | 7:15:00 AM | 4854.956 | 4854.956 | 0 | 2972.983 | 2972.983 | 0 | 0 | 0 | 5819.473 | 5819.473 | 0
5/5/2026 | 7:30:00 AM | 4868.427 | 4868.427 | 0 | 2981.188 | 2981.188 | 0 | 0 | 0 | 5835.568 | 5835.568 | 0
5/5/2026 | 7:45:00 AM | 4881.722 | 4881.722 | 0 | 2989.204 | 2989.204 | 0 | 0 | 0 | 5851.465 | 5851.465 | 0
5/5/2026 | 8:00:00 AM | 4895.444 | 4895.444 | 0 | 2997.351 | 2997.351 | 0 | 0 | 0 | 5867.808 | 5867.808 | 0
5/5/2026 | 8:15:00 AM | 4909.122 | 4909.122 | 0 | 3005.5 | 3005.5 | 0 | 0 | 0 | 5884.126 | 5884.126 | 0
5/5/2026 | 8:30:00 AM | 4922.64 | 4922.64 | 0 | 3013.495 | 3013.495 | 0 | 0 | 0 | 5900.231 | 5900.231 | 0
5/5/2026 | 8:45:00 AM | 4936.323 | 4936.323 | 0 | 3021.545 | 3021.545 | 0 | 0 | 0 | 5916.523 | 5916.523 | 0
5/5/2026 | 9:00:00 AM | 4950.012 | 4950.012 | 0 | 3029.439 | 3029.439 | 0 | 0 | 0 | 5932.757 | 5932.757 | 0
5/5/2026 | 9:15:00 AM | 4963.837 | 4963.837 | 0 | 3037.339 | 3037.339 | 0 | 0 | 0 | 5949.118 | 5949.118 | 0
5/5/2026 | 9:30:00 AM | 4977.571 | 4977.571 | 0 | 3045.181 | 3045.181 | 0 | 0 | 0 | 5965.437 | 5965.437 | 0
5/5/2026 | 9:45:00 AM | 4991.656 | 4991.656 | 0 | 3053.143 | 3053.143 | 0 | 0 | 0 | 5982.112 | 5982.112 | 0
5/5/2026 | 10:00:00 AM | 5005.301 | 5005.301 | 0 | 3060.988 | 3060.988 | 0 | 0 | 0 | 5998.303 | 5998.303 | 0
5/5/2026 | 10:15:00 AM | 5019.057 | 5019.057 | 0 | 3068.827 | 3068.827 | 0 | 0 | 0 | 6014.558 | 6014.558 | 0
5/5/2026 | 10:30:00 AM | 5032.821 | 5032.821 | 0 | 3076.62 | 3076.62 | 0 | 0 | 0 | 6030.836 | 6030.836 | 0
5/5/2026 | 10:45:00 AM | 5046.364 | 5046.364 | 0 | 3084.184 | 3084.184 | 0 | 0 | 0 | 6046.863 | 6046.863 | 0
5/5/2026 | 11:00:00 AM | 5060.553 | 5060.553 | 0 | 3092.108 | 3092.108 | 0 | 0 | 0 | 6063.568 | 6063.568 | 0
5/5/2026 | 11:15:00 AM | 5074.462 | 5074.462 | 0 | 3099.704 | 3099.704 | 0 | 0 | 0 | 6080.02 | 6080.02 | 0
5/5/2026 | 11:30:00 AM | 5088.878 | 5088.878 | 0 | 3107.34 | 3107.34 | 0 | 0 | 0 | 6096.97 | 6096.97 | 0
5/5/2026 | 11:45:00 AM | 5102.957 | 5102.957 | 0 | 3114.956 | 3114.956 | 0 | 0 | 0 | 6113.632 | 6113.632 | 0
5/5/2026 | 12:00:00 PM | 5117.16 | 5117.16 | 0 | 3122.532 | 3122.532 | 0 | 0 | 0 | 6130.372 | 6130.372 | 0
5/5/2026 | 12:15:00 PM | 5131.363 | 5131.363 | 0 | 3130.146 | 3130.146 | 0 | 0 | 0 | 6147.132 | 6147.132 | 0
5/5/2026 | 12:30:00 PM | 5145.634 | 5145.634 | 0 | 3137.73 | 3137.73 | 0 | 0 | 0 | 6163.929 | 6163.929 | 0
5/5/2026 | 12:45:00 PM | 5160.148 | 5160.148 | 0 | 3145.654 | 3145.654 | 0 | 0 | 0 | 6181.109 | 6181.109 | 0
5/5/2026 | 1:00:00 PM | 5174.179 | 5174.179 | 0 | 3153.208 | 3153.208 | 0 | 0 | 0 | 6197.707 | 6197.707 | 0
5/5/2026 | 1:15:00 PM | 5188.815 | 5188.815 | 0 | 3161.137 | 3161.137 | 0 | 0 | 0 | 6214.98 | 6214.98 | 0
5/5/2026 | 1:30:00 PM | 5202.692 | 5202.692 | 0 | 3168.708 | 3168.708 | 0 | 0 | 0 | 6231.451 | 6231.451 | 0
5/5/2026 | 1:45:00 PM | 5217.069 | 5217.069 | 0 | 3176.523 | 3176.523 | 0 | 0 | 0 | 6248.464 | 6248.464 | 0
5/5/2026 | 2:00:00 PM | 5231.193 | 5231.193 | 0 | 3184.268 | 3184.268 | 0 | 0 | 0 | 6265.221 | 6265.221 | 0
5/5/2026 | 2:15:00 PM | 5245.6 | 5245.6 | 0 | 3192.071 | 3192.071 | 0 | 0 | 0 | 6282.245 | 6282.245 | 0
5/5/2026 | 2:30:00 PM | 5260.149 | 5260.149 | 0 | 3200.059 | 3200.059 | 0 | 0 | 0 | 6299.467 | 6299.467 | 0
5/5/2026 | 2:45:00 PM | 5274.223 | 5274.223 | 0 | 3207.815 | 3207.815 | 0 | 0 | 0 | 6316.13 | 6316.13 | 0
5/5/2026 | 3:00:00 PM | 5288.272 | 5288.272 | 0 | 3215.717 | 3215.717 | 0 | 0 | 0 | 6332.774 | 6332.774 | 0
5/5/2026 | 3:15:00 PM | 5302.048 | 5302.048 | 0 | 3223.328 | 3223.328 | 0 | 0 | 0 | 6349.103 | 6349.103 | 0
5/5/2026 | 3:30:00 PM | 5316.196 | 5316.196 | 0 | 3231.252 | 3231.252 | 0 | 0 | 0 | 6365.837 | 6365.837 | 0
5/5/2026 | 3:45:00 PM | 5329.891 | 5329.891 | 0 | 3238.908 | 3238.908 | 0 | 0 | 0 | 6382.125 | 6382.125 | 0
5/5/2026 | 4:00:00 PM | 5344.152 | 5344.152 | 0 | 3246.767 | 3246.767 | 0 | 0 | 0 | 6398.982 | 6398.982 | 0
5/5/2026 | 4:15:00 PM | 5357.781 | 5357.781 | 0 | 3254.521 | 3254.521 | 0 | 0 | 0 | 6415.152 | 6415.152 | 0
5/5/2026 | 4:30:00 PM | 5372.115 | 5372.115 | 0 | 3262.474 | 3262.474 | 0 | 0 | 0 | 6432.056 | 6432.056 | 0
5/5/2026 | 4:45:00 PM | 5385.928 | 5385.928 | 0 | 3270.123 | 3270.123 | 0 | 0 | 0 | 6448.421 | 6448.421 | 0
5/5/2026 | 5:00:00 PM | 5400.051 | 5400.051 | 0 | 3277.833 | 3277.833 | 0 | 0 | 0 | 6465.084 | 6465.084 | 0
5/5/2026 | 5:15:00 PM | 5414.094 | 5414.094 | 0 | 3285.722 | 3285.722 | 0 | 0 | 0 | 6481.712 | 6481.712 | 0
5/5/2026 | 5:30:00 PM | 5427.621 | 5427.621 | 0 | 3293.418 | 3293.418 | 0 | 0 | 0 | 6497.755 | 6497.755 | 0
5/5/2026 | 5:45:00 PM | 5441.343 | 5441.343 | 0 | 3301.377 | 3301.377 | 0 | 0 | 0 | 6514.075 | 6514.075 | 0
5/5/2026 | 6:00:00 PM | 5454.902 | 5454.902 | 0 | 3309.289 | 3309.289 | 0 | 0 | 0 | 6530.201 | 6530.201 | 0
5/5/2026 | 6:15:00 PM | 5468.683 | 5468.683 | 0 | 3317.455 | 3317.455 | 0 | 0 | 0 | 6546.609 | 6546.609 | 0
5/5/2026 | 6:30:00 PM | 5482.05 | 5482.05 | 0 | 3325.446 | 3325.446 | 0 | 0 | 0 | 6562.59 | 6562.59 | 0
5/5/2026 | 6:45:00 PM | 5495.654 | 5495.654 | 0 | 3333.604 | 3333.604 | 0 | 0 | 0 | 6578.833 | 6578.833 | 0
5/5/2026 | 7:00:00 PM | 5509.016 | 5509.016 | 0 | 3341.744 | 3341.744 | 0 | 0 | 0 | 6594.855 | 6594.855 | 0
5/5/2026 | 7:15:00 PM | 5522.617 | 5522.617 | 0 | 3349.936 | 3349.936 | 0 | 0 | 0 | 6611.1 | 6611.1 | 0
5/5/2026 | 7:30:00 PM | 5535.933 | 5535.933 | 0 | 3358.151 | 3358.151 | 0 | 0 | 0 | 6627.105 | 6627.105 | 0
5/5/2026 | 7:45:00 PM | 5549.434 | 5549.434 | 0 | 3366.277 | 3366.277 | 0 | 0 | 0 | 6643.271 | 6643.271 | 0
5/5/2026 | 8:00:00 PM | 5563.105 | 5563.105 | 0 | 3374.602 | 3374.602 | 0 | 0 | 0 | 6659.682 | 6659.682 | 0
5/5/2026 | 8:15:00 PM | 5576.271 | 5576.271 | 0 | 3382.655 | 3382.655 | 0 | 0 | 0 | 6675.521 | 6675.521 | 0
5/5/2026 | 8:30:00 PM | 5590.024 | 5590.024 | 0 | 3391.015 | 3391.015 | 0 | 0 | 0 | 6691.98 | 6691.98 | 0
5/5/2026 | 8:45:00 PM | 5603.466 | 5603.466 | 0 | 3399.128 | 3399.128 | 0 | 0 | 0 | 6708.094 | 6708.094 | 0
5/5/2026 | 9:00:00 PM | 5617.343 | 5617.343 | 0 | 3407.398 | 3407.398 | 0 | 0 | 0 | 6724.646 | 6724.646 | 0
5/5/2026 | 9:15:00 PM | 5630.749 | 5630.749 | 0 | 3415.572 | 3415.572 | 0 | 0 | 0 | 6740.732 | 6740.732 | 0
5/5/2026 | 9:30:00 PM | 5644.308 | 5644.308 | 0 | 3423.812 | 3423.812 | 0 | 0 | 0 | 6756.966 | 6756.966 | 0
5/5/2026 | 9:45:00 PM | 5657.797 | 5657.797 | 0 | 3432.166 | 3432.166 | 0 | 0 | 0 | 6773.194 | 6773.194 | 0
5/5/2026 | 10:00:00 PM | 5670.874 | 5670.874 | 0 | 3440.336 | 3440.336 | 0 | 0 | 0 | 6788.939 | 6788.939 | 0
5/5/2026 | 10:15:00 PM | 5684.242 | 5684.242 | 0 | 3448.664 | 3448.664 | 0 | 0 | 0 | 6805.02 | 6805.02 | 0
5/5/2026 | 10:30:00 PM | 5697.277 | 5697.277 | 0 | 3456.845 | 3456.845 | 0 | 0 | 0 | 6820.745 | 6820.745 | 0
5/5/2026 | 10:45:00 PM | 5710.81 | 5710.81 | 0 | 3465.259 | 3465.259 | 0 | 0 | 0 | 6837.011 | 6837.011 | 0
5/5/2026 | 11:00:00 PM | 5723.974 | 5723.974 | 0 | 3473.55 | 3473.55 | 0 | 0 | 0 | 6852.901 | 6852.901 | 0
5/5/2026 | 11:15:00 PM | 5737.276 | 5737.276 | 0 | 3481.839 | 3481.839 | 0 | 0 | 0 | 6868.917 | 6868.917 | 0
5/5/2026 | 11:30:00 PM | 5750.453 | 5750.453 | 0 | 3490.155 | 3490.155 | 0 | 0 | 0 | 6884.828 | 6884.828 | 0
5/5/2026 | 11:45:00 PM | 5763.801 | 5763.801 | 0 | 3498.491 | 3498.491 | 0 | 0 | 0 | 6900.92 | 6900.92 | 0
5/6/2026 | 12:00:00 AM | 5777.409 | 5777.409 | 0 | 3506.985 | 3506.985 | 0 | 0 | 0 | 6917.299 | 6917.299 | 0
5/6/2026 | 12:15:00 AM | 5790.485 | 5790.485 | 0 | 3515.181 | 3515.181 | 0 | 0 | 0 | 6933.084 | 6933.084 | 0
5/6/2026 | 12:30:00 AM | 5804.131 | 5804.131 | 0 | 3523.711 | 3523.711 | 0 | 0 | 0 | 6949.507 | 6949.507 | 0
5/6/2026 | 12:45:00 AM | 5817.399 | 5817.399 | 0 | 3532.076 | 3532.076 | 0 | 0 | 0 | 6965.556 | 6965.556 | 0
5/6/2026 | 1:00:00 AM | 5830.91 | 5830.91 | 0 | 3540.464 | 3540.464 | 0 | 0 | 0 | 6981.81 | 6981.81 | 0
5/6/2026 | 1:15:00 AM | 5844.21 | 5844.21 | 0 | 3548.845 | 3548.845 | 0 | 0 | 0 | 6997.873 | 6997.873 | 0
5/6/2026 | 1:30:00 AM | 5857.502 | 5857.502 | 0 | 3557.174 | 3557.174 | 0 | 0 | 0 | 7013.893 | 7013.893 | 0
5/6/2026 | 1:45:00 AM | 5870.817 | 5870.817 | 0 | 3565.616 | 3565.616 | 0 | 0 | 0 | 7029.999 | 7029.999 | 0
5/6/2026 | 2:00:00 AM | 5883.995 | 5883.995 | 0 | 3574.011 | 3574.011 | 0 | 0 | 0 | 7045.944 | 7045.944 | 0
5/6/2026 | 2:15:00 AM | 5897.54 | 5897.54 | 0 | 3582.55 | 3582.55 | 0 | 0 | 0 | 7062.275 | 7062.275 | 0
5/6/2026 | 2:30:00 AM | 5910.674 | 5910.674 | 0 | 3590.941 | 3590.941 | 0 | 0 | 0 | 7078.195 | 7078.195 | 0
5/6/2026 | 2:45:00 AM | 5924.078 | 5924.078 | 0 | 3599.387 | 3599.387 | 0 | 0 | 0 | 7094.376 | 7094.376 | 0
5/6/2026 | 3:00:00 AM | 5937.334 | 5937.334 | 0 | 3607.93 | 3607.93 | 0 | 0 | 0 | 7110.443 | 7110.443 | 0
5/6/2026 | 3:15:00 AM | 5950.537 | 5950.537 | 0 | 3616.346 | 3616.346 | 0 | 0 | 0 | 7126.405 | 7126.405 | 0
5/6/2026 | 3:30:00 AM | 5963.723 | 5963.723 | 0 | 3624.811 | 3624.811 | 0 | 0 | 0 | 7142.377 | 7142.377 | 0
5/6/2026 | 3:45:00 AM | 5977.092 | 5977.092 | 0 | 3633.291 | 3633.291 | 0 | 0 | 0 | 7158.526 | 7158.526 | 0
5/6/2026 | 4:00:00 AM | 5990.545 | 5990.545 | 0 | 3641.859 | 3641.859 | 0 | 0 | 0 | 7174.806 | 7174.806 | 0
5/6/2026 | 4:15:00 AM | 6003.855 | 6003.855 | 0 | 3650.277 | 3650.277 | 0 | 0 | 0 | 7190.877 | 7190.877 | 0
5/6/2026 | 4:30:00 AM | 6017.45 | 6017.45 | 0 | 3658.834 | 3658.834 | 0 | 0 | 0 | 7207.258 | 7207.258 | 0
5/6/2026 | 4:45:00 AM | 6030.666 | 6030.666 | 0 | 3667.177 | 3667.177 | 0 | 0 | 0 | 7223.245 | 7223.245 | 0
5/6/2026 | 5:00:00 AM | 6044.231 | 6044.231 | 0 | 3675.524 | 3675.524 | 0 | 0 | 0 | 7239.54 | 7239.54 | 0
5/6/2026 | 5:15:00 AM | 6057.712 | 6057.712 | 0 | 3683.897 | 3683.897 | 0 | 0 | 0 | 7255.764 | 7255.764 | 0
5/6/2026 | 5:30:00 AM | 6071.519 | 6071.519 | 0 | 3692.305 | 3692.305 | 0 | 0 | 0 | 7272.3 | 7272.3 | 0
5/6/2026 | 5:45:00 AM | 6085.149 | 6085.149 | 0 | 3700.648 | 3700.648 | 0 | 0 | 0 | 7288.671 | 7288.671 | 0
5/6/2026 | 6:00:00 AM | 6098.748 | 6098.748 | 0 | 3708.883 | 3708.883 | 0 | 0 | 0 | 7304.946 | 7304.946 | 0
5/6/2026 | 6:15:00 AM | 6112.377 | 6112.377 | 0 | 3717.127 | 3717.127 | 0 | 0 | 0 | 7321.24 | 7321.24 | 0
5/6/2026 | 6:30:00 AM | 6125.872 | 6125.872 | 0 | 3725.198 | 3725.198 | 0 | 0 | 0 | 7337.365 | 7337.365 | 0
5/6/2026 | 6:45:00 AM | 6139.75 | 6139.75 | 0 | 3733.433 | 3733.433 | 0 | 0 | 0 | 7353.917 | 7353.917 | 0
5/6/2026 | 7:00:00 AM | 6153.098 | 6153.098 | 0 | 3741.471 | 3741.471 | 0 | 0 | 0 | 7369.911 | 7369.911 | 0
5/6/2026 | 7:15:00 AM | 6166.996 | 6166.996 | 0 | 3749.699 | 3749.699 | 0 | 0 | 0 | 7386.482 | 7386.482 | 0
5/6/2026 | 7:30:00 AM | 6180.489 | 6180.489 | 0 | 3757.755 | 3757.755 | 0 | 0 | 0 | 7402.628 | 7402.628 | 0
5/6/2026 | 7:45:00 AM | 6194.416 | 6194.416 | 0 | 3765.881 | 3765.881 | 0 | 0 | 0 | 7419.221 | 7419.221 | 0
5/6/2026 | 8:00:00 AM | 6208.37 | 6208.37 | 0 | 3774.056 | 3774.056 | 0 | 0 | 0 | 7435.832 | 7435.832 | 0
5/6/2026 | 8:15:00 AM | 6222.071 | 6222.071 | 0 | 3781.978 | 3781.978 | 0 | 0 | 0 | 7452.087 | 7452.087 | 0
5/6/2026 | 8:30:00 AM | 6235.748 | 6235.748 | 0 | 3789.906 | 3789.906 | 0 | 0 | 0 | 7468.355 | 7468.355 | 0
5/6/2026 | 8:45:00 AM | 6249.837 | 6249.837 | 0 | 3797.908 | 3797.908 | 0 | 0 | 0 | 7485.074 | 7485.074 | 0
5/6/2026 | 9:00:00 AM | 6263.971 | 6263.971 | 0 | 3805.846 | 3805.846 | 0 | 0 | 0 | 7501.819 | 7501.819 | 0
5/6/2026 | 9:15:00 AM | 6277.859 | 6277.859 | 0 | 3813.578 | 3813.578 | 0 | 0 | 0 | 7518.269 | 7518.269 | 0
5/6/2026 | 9:30:00 AM | 6292.282 | 6292.282 | 0 | 3821.525 | 3821.525 | 0 | 0 | 0 | 7535.284 | 7535.284 | 0
5/6/2026 | 9:45:00 AM | 6306.043 | 6306.043 | 0 | 3829.103 | 3829.103 | 0 | 0 | 0 | 7551.591 | 7551.591 | 0
5/6/2026 | 10:00:00 AM | 6320.055 | 6320.055 | 0 | 3836.6 | 3836.6 | 0 | 0 | 0 | 7568.112 | 7568.112 | 0
5/6/2026 | 10:15:00 AM | 6334.197 | 6334.197 | 0 | 3844.239 | 3844.239 | 0 | 0 | 0 | 7584.81 | 7584.81 | 0
5/6/2026 | 10:30:00 AM | 6348.339 | 6348.339 | 0 | 3851.943 | 3851.943 | 0 | 0 | 0 | 7601.532 | 7601.532 | 0
5/6/2026 | 10:45:00 AM | 6362.325 | 6362.325 | 0 | 3859.819 | 3859.819 | 0 | 0 | 0 | 7618.159 | 7618.159 | 0
5/6/2026 | 11:00:00 AM | 6376.512 | 6376.512 | 0 | 3867.728 | 3867.728 | 0 | 0 | 0 | 7634.943 | 7634.943 | 0
5/6/2026 | 11:15:00 AM | 6390.403 | 6390.403 | 0 | 3875.607 | 3875.607 | 0 | 0 | 0 | 7651.442 | 7651.442 | 0
5/6/2026 | 11:30:00 AM | 6404.264 | 6404.264 | 0 | 3883.566 | 3883.566 | 0 | 0 | 0 | 7667.879 | 7667.879 | 0
5/6/2026 | 11:45:00 AM | 6418.44 | 6418.44 | 0 | 3891.413 | 3891.413 | 0 | 0 | 0 | 7684.631 | 7684.631 | 0
5/6/2026 | 12:00:00 PM | 6432.569 | 6432.569 | 0 | 3899.212 | 3899.212 | 0 | 0 | 0 | 7701.33 | 7701.33 | 0
5/6/2026 | 12:15:00 PM | 6446.802 | 6446.802 | 0 | 3907.117 | 3907.117 | 0 | 0 | 0 | 7718.147 | 7718.147 | 0
5/6/2026 | 12:30:00 PM | 6460.895 | 6460.895 | 0 | 3914.965 | 3914.965 | 0 | 0 | 0 | 7734.771 | 7734.771 | 0
5/6/2026 | 12:45:00 PM | 6475.218 | 6475.218 | 0 | 3922.927 | 3922.927 | 0 | 0 | 0 | 7751.693 | 7751.693 | 0
5/6/2026 | 1:00:00 PM | 6489.535 | 6489.535 | 0 | 3930.797 | 3930.797 | 0 | 0 | 0 | 7768.57 | 7768.57 | 0
5/6/2026 | 1:15:00 PM | 6503.841 | 6503.841 | 0 | 3938.701 | 3938.701 | 0 | 0 | 0 | 7785.425 | 7785.425 | 0
5/6/2026 | 1:30:00 PM | 6517.823 | 6517.823 | 0 | 3946.47 | 3946.47 | 0 | 0 | 0 | 7801.933 | 7801.933 | 0
5/6/2026 | 1:45:00 PM | 6532.514 | 6532.514 | 0 | 3954.372 | 3954.372 | 0 | 0 | 0 | 7819.199 | 7819.199 | 0
5/6/2026 | 2:00:00 PM | 6546.579 | 6546.579 | 0 | 3962.137 | 3962.137 | 0 | 0 | 0 | 7835.779 | 7835.779 | 0
5/6/2026 | 2:15:00 PM | 6560.941 | 6560.941 | 0 | 3970.133 | 3970.133 | 0 | 0 | 0 | 7852.685 | 7852.685 | 0
5/6/2026 | 2:30:00 PM | 6574.92 | 6574.92 | 0 | 3977.915 | 3977.915 | 0 | 0 | 0 | 7869.169 | 7869.169 | 0
5/6/2026 | 2:45:00 PM | 6589.38 | 6589.38 | 0 | 3985.896 | 3985.896 | 0 | 0 | 0 | 7886.22 | 7886.22 | 0
5/6/2026 | 3:00:00 PM | 6603.772 | 6603.772 | 0 | 3993.785 | 3993.785 | 0 | 0 | 0 | 7903.149 | 7903.149 | 0
5/6/2026 | 3:15:00 PM | 6617.826 | 6617.826 | 0 | 4001.677 | 4001.677 | 0 | 0 | 0 | 7919.737 | 7919.737 | 0
5/6/2026 | 3:30:00 PM | 6631.779 | 6631.779 | 0 | 4009.525 | 4009.525 | 0 | 0 | 0 | 7936.189 | 7936.189 | 0
5/6/2026 | 3:45:00 PM | 6646.093 | 6646.093 | 0 | 4017.527 | 4017.527 | 0 | 0 | 0 | 7953.028 | 7953.028 | 0
5/6/2026 | 4:00:00 PM | 6659.751 | 6659.751 | 0 | 4025.312 | 4025.312 | 0 | 0 | 0 | 7969.169 | 7969.169 | 0
5/6/2026 | 4:15:00 PM | 6674.084 | 6674.084 | 0 | 4033.481 | 4033.481 | 0 | 0 | 0 | 7986.046 | 7986.046 | 0
5/6/2026 | 4:30:00 PM | 6687.932 | 6687.932 | 0 | 4041.321 | 4041.321 | 0 | 0 | 0 | 8002.397 | 8002.397 | 0
5/6/2026 | 4:45:00 PM | 6701.961 | 6701.961 | 0 | 4049.305 | 4049.305 | 0 | 0 | 0 | 8018.985 | 8018.985 | 0
5/6/2026 | 5:00:00 PM | 6715.955 | 6715.955 | 0 | 4057.277 | 4057.277 | 0 | 0 | 0 | 8035.499 | 8035.499 | 0
5/6/2026 | 5:15:00 PM | 6729.697 | 6729.697 | 0 | 4065.22 | 4065.22 | 0 | 0 | 0 | 8051.777 | 8051.777 | 0
5/6/2026 | 5:30:00 PM | 6744.019 | 6744.019 | 0 | 4073.353 | 4073.353 | 0 | 0 | 0 | 8068.66 | 8068.66 | 0
5/6/2026 | 5:45:00 PM | 6757.768 | 6757.768 | 0 | 4081.205 | 4081.205 | 0 | 0 | 0 | 8084.927 | 8084.927 | 0
5/6/2026 | 6:00:00 PM | 6771.741 | 6771.741 | 0 | 4089.388 | 4089.388 | 0 | 0 | 0 | 8101.502 | 8101.502 | 0
5/6/2026 | 6:15:00 PM | 6785.578 | 6785.578 | 0 | 4097.534 | 4097.534 | 0 | 0 | 0 | 8117.931 | 8117.931 | 0
5/6/2026 | 6:30:00 PM | 6799.282 | 6799.282 | 0 | 4105.726 | 4105.726 | 0 | 0 | 0 | 8134.273 | 8134.273 | 0
5/6/2026 | 6:45:00 PM | 6813.002 | 6813.002 | 0 | 4113.891 | 4113.891 | 0 | 0 | 0 | 8150.601 | 8150.601 | 0
5/6/2026 | 7:00:00 PM | 6826.416 | 6826.416 | 0 | 4122.077 | 4122.077 | 0 | 0 | 0 | 8166.639 | 8166.639 | 0
5/6/2026 | 7:15:00 PM | 6839.779 | 6839.779 | 0 | 4130.293 | 4130.293 | 0 | 0 | 0 | 8182.643 | 8182.643 | 0
5/6/2026 | 7:30:00 PM | 6853.437 | 6853.437 | 0 | 4138.623 | 4138.623 | 0 | 0 | 0 | 8198.962 | 8198.962 | 0
5/6/2026 | 7:45:00 PM | 6866.856 | 6866.856 | 0 | 4146.841 | 4146.841 | 0 | 0 | 0 | 8215.067 | 8215.067 | 0
5/6/2026 | 8:00:00 PM | 6880.785 | 6880.785 | 0 | 4155.265 | 4155.265 | 0 | 0 | 0 | 8231.696 | 8231.696 | 0
5/6/2026 | 8:15:00 PM | 6894.438 | 6894.438 | 0 | 4163.558 | 4163.558 | 0 | 0 | 0 | 8248.033 | 8248.033 | 0
5/6/2026 | 8:30:00 PM | 6908.139 | 6908.139 | 0 | 4171.801 | 4171.801 | 0 | 0 | 0 | 8264.405 | 8264.405 | 0
5/6/2026 | 8:45:00 PM | 6922.338 | 6922.338 | 0 | 4180.159 | 4180.159 | 0 | 0 | 0 | 8281.311 | 8281.311 | 0
5/6/2026 | 9:00:00 PM | 6936.389 | 6936.389 | 0 | 4188.285 | 4188.285 | 0 | 0 | 0 | 8298.011 | 8298.011 | 0
5/6/2026 | 9:15:00 PM | 6950.52 | 6950.52 | 0 | 4196.439 | 4196.439 | 0 | 0 | 0 | 8314.79 | 8314.79 | 0
5/6/2026 | 9:30:00 PM | 6964.455 | 6964.455 | 0 | 4204.544 | 4204.544 | 0 | 0 | 0 | 8331.35 | 8331.35 | 0
5/6/2026 | 9:45:00 PM | 6978.476 | 6978.476 | 0 | 4212.801 | 4212.801 | 0 | 0 | 0 | 8348.039 | 8348.039 | 0
5/6/2026 | 10:00:00 PM | 6992.435 | 6992.435 | 0 | 4221.075 | 4221.075 | 0 | 0 | 0 | 8364.663 | 8364.663 | 0
5/6/2026 | 10:15:00 PM | 7006.269 | 7006.269 | 0 | 4229.261 | 4229.261 | 0 | 0 | 0 | 8381.133 | 8381.133 | 0
5/6/2026 | 10:30:00 PM | 7020.152 | 7020.152 | 0 | 4237.387 | 4237.387 | 0 | 0 | 0 | 8397.628 | 8397.628 | 0
5/6/2026 | 10:45:00 PM | 7033.782 | 7033.782 | 0 | 4245.506 | 4245.506 | 0 | 0 | 0 | 8413.881 | 8413.881 | 0
5/6/2026 | 11:00:00 PM | 7047.488 | 7047.488 | 0 | 4253.755 | 4253.755 | 0 | 0 | 0 | 8430.236 | 8430.236 | 0
5/6/2026 | 11:15:00 PM | 7061.345 | 7061.345 | 0 | 4261.925 | 4261.925 | 0 | 0 | 0 | 8446.731 | 8446.731 | 0
5/6/2026 | 11:30:00 PM | 7075.246 | 7075.246 | 0 | 4270.24 | 4270.24 | 0 | 0 | 0 | 8463.329 | 8463.329 | 0
5/6/2026 | 11:45:00 PM | 7089.27 | 7089.27 | 0 | 4278.474 | 4278.474 | 0 | 0 | 0 | 8480.04 | 8480.04 | 0
5/7/2026 | 12:00:00 AM | 7103.35 | 7103.35 | 0 | 4286.756 | 4286.756 | 0 | 0 | 0 | 8496.82 | 8496.82 | 0
5/7/2026 | 12:15:00 AM | 7117.097 | 7117.097 | 0 | 4295.022 | 4295.022 | 0 | 0 | 0 | 8513.275 | 8513.275 | 0
5/7/2026 | 12:30:00 AM | 7131.103 | 7131.103 | 0 | 4303.421 | 4303.421 | 0 | 0 | 0 | 8530.01 | 8530.01 | 0
5/7/2026 | 12:45:00 AM | 7144.873 | 7144.873 | 0 | 4311.636 | 4311.636 | 0 | 0 | 0 | 8546.501 | 8546.501 | 0
5/7/2026 | 1:00:00 AM | 7158.96 | 7158.96 | 0 | 4320.012 | 4320.012 | 0 | 0 | 0 | 8563.326 | 8563.326 | 0
5/7/2026 | 1:15:00 AM | 7173.083 | 7173.083 | 0 | 4328.392 | 4328.392 | 0 | 0 | 0 | 8580.187 | 8580.187 | 0
5/7/2026 | 1:30:00 AM | 7186.962 | 7186.962 | 0 | 4336.637 | 4336.637 | 0 | 0 | 0 | 8596.776 | 8596.776 | 0
5/7/2026 | 1:45:00 AM | 7201.109 | 7201.109 | 0 | 4345.291 | 4345.291 | 0 | 0 | 0 | 8613.726 | 8613.726 | 0
5/7/2026 | 2:00:00 AM | 7214.949 | 7214.949 | 0 | 4353.754 | 4353.754 | 0 | 0 | 0 | 8630.295 | 8630.295 | 0
5/7/2026 | 2:15:00 AM | 7228.678 | 7228.678 | 0 | 4362.205 | 4362.205 | 0 | 0 | 0 | 8646.778 | 8646.778 | 0
5/7/2026 | 2:30:00 AM | 7242.347 | 7242.347 | 0 | 4370.679 | 4370.679 | 0 | 0 | 0 | 8663.202 | 8663.202 | 0
5/7/2026 | 2:45:00 AM | 7256.225 | 7256.225 | 0 | 4379.228 | 4379.228 | 0 | 0 | 0 | 8679.851 | 8679.851 | 0
5/7/2026 | 3:00:00 AM | 7269.717 | 7269.717 | 0 | 4387.588 | 4387.588 | 0 | 0 | 0 | 8696.069 | 8696.069 | 0
5/7/2026 | 3:15:00 AM | 7283.671 | 7283.671 | 0 | 4396.234 | 4396.234 | 0 | 0 | 0 | 8712.827 | 8712.827 | 0
5/7/2026 | 3:30:00 AM | 7297.433 | 7297.433 | 0 | 4404.656 | 4404.656 | 0 | 0 | 0 | 8729.328 | 8729.328 | 0
5/7/2026 | 3:45:00 AM | 7311.075 | 7311.075 | 0 | 4413.012 | 4413.012 | 0 | 0 | 0 | 8745.726 | 8745.726 | 0
5/7/2026 | 4:00:00 AM | 7325.175 | 7325.175 | 0 | 4421.612 | 4421.612 | 0 | 0 | 0 | 8762.618 | 8762.618 | 0
5/7/2026 | 4:15:00 AM | 7339.184 | 7339.184 | 0 | 4430.123 | 4430.123 | 0 | 0 | 0 | 8779.392 | 8779.392 | 0
5/7/2026 | 4:30:00 AM | 7352.831 | 7352.831 | 0 | 4438.454 | 4438.454 | 0 | 0 | 0 | 8795.782 | 8795.782 | 0
5/7/2026 | 4:45:00 AM | 7367.061 | 7367.061 | 0 | 4446.848 | 4446.848 | 0 | 0 | 0 | 8812.767 | 8812.767 | 0
5/7/2026 | 5:00:00 AM | 7381.341 | 7381.341 | 0 | 4455.333 | 4455.333 | 0 | 0 | 0 | 8829.832 | 8829.832 | 0
5/7/2026 | 5:15:00 AM | 7395.503 | 7395.503 | 0 | 4463.792 | 4463.792 | 0 | 0 | 0 | 8846.768 | 8846.768 | 0
5/7/2026 | 5:30:00 AM | 7409.714 | 7409.714 | 0 | 4472.228 | 4472.228 | 0 | 0 | 0 | 8863.724 | 8863.724 | 0
5/7/2026 | 5:45:00 AM | 7423.615 | 7423.615 | 0 | 4480.526 | 4480.526 | 0 | 0 | 0 | 8880.34 | 8880.34 | 0
5/7/2026 | 6:00:00 AM | 7437.636 | 7437.636 | 0 | 4488.844 | 4488.844 | 0 | 0 | 0 | 8897.048 | 8897.048 | 0
5/7/2026 | 6:15:00 AM | 7451.516 | 7451.516 | 0 | 4496.926 | 4496.926 | 0 | 0 | 0 | 8913.562 | 8913.562 | 0
5/7/2026 | 6:30:00 AM | 7465.614 | 7465.614 | 0 | 4505.076 | 4505.076 | 0 | 0 | 0 | 8930.29 | 8930.29 | 0
5/7/2026 | 6:45:00 AM | 7479.808 | 7479.808 | 0 | 4513.222 | 4513.222 | 0 | 0 | 0 | 8947.127 | 8947.127 | 0
5/7/2026 | 7:00:00 AM | 7493.784 | 7493.784 | 0 | 4521.325 | 4521.325 | 0 | 0 | 0 | 8963.719 | 8963.719 | 0
5/7/2026 | 7:15:00 AM | 7507.996 | 7507.996 | 0 | 4529.465 | 4529.465 | 0 | 0 | 0 | 8980.565 | 8980.565 | 0
5/7/2026 | 7:30:00 AM | 7521.779 | 7521.779 | 0 | 4537.464 | 4537.464 | 0 | 0 | 0 | 8996.969 | 8996.969 | 0
5/7/2026 | 7:45:00 AM | 7536.14 | 7536.14 | 0 | 4545.665 | 4545.665 | 0 | 0 | 0 | 9014.038 | 9014.038 | 0
5/7/2026 | 8:00:00 AM | 7550.455 | 7550.455 | 0 | 4553.719 | 4553.719 | 0 | 0 | 0 | 9030.996 | 9030.996 | 0
5/7/2026 | 8:15:00 AM | 7564.559 | 7564.559 | 0 | 4561.757 | 4561.757 | 0 | 0 | 0 | 9047.751 | 9047.751 | 0
5/7/2026 | 8:30:00 AM | 7579.064 | 7579.064 | 0 | 4570.016 | 4570.016 | 0 | 0 | 0 | 9064.947 | 9064.947 | 0
5/7/2026 | 8:45:00 AM | 7593.431 | 7593.431 | 0 | 4578.108 | 4578.108 | 0 | 0 | 0 | 9081.984 | 9081.984 | 0
5/7/2026 | 9:00:00 AM | 7607.675 | 7607.675 | 0 | 4586.176 | 4586.176 | 0 | 0 | 0 | 9098.878 | 9098.878 | 0
5/7/2026 | 9:15:00 AM | 7622.083 | 7622.083 | 0 | 4594.288 | 4594.288 | 0 | 0 | 0 | 9115.939 | 9115.939 | 0
5/7/2026 | 9:30:00 AM | 7636.499 | 7636.499 | 0 | 4602.257 | 4602.257 | 0 | 0 | 0 | 9132.997 | 9132.997 | 0
5/7/2026 | 9:45:00 AM | 7650.744 | 7650.744 | 0 | 4610.21 | 4610.21 | 0 | 0 | 0 | 9149.891 | 9149.891 | 0
5/7/2026 | 10:00:00 AM | 7665.397 | 7665.397 | 0 | 4618.33 | 4618.33 | 0 | 0 | 0 | 9167.223 | 9167.223 | 0
5/7/2026 | 10:15:00 AM | 7679.926 | 7679.926 | 0 | 4626.34 | 4626.34 | 0 | 0 | 0 | 9184.388 | 9184.388 | 0
5/7/2026 | 10:30:00 AM | 7694.059 | 7694.059 | 0 | 4634.238 | 4634.238 | 0 | 0 | 0 | 9201.14 | 9201.14 | 0
5/7/2026 | 10:45:00 AM | 7708.475 | 7708.475 | 0 | 4642.396 | 4642.396 | 0 | 0 | 0 | 9218.211 | 9218.211 | 0
5/7/2026 | 11:00:00 AM | 7722.709 | 7722.709 | 0 | 4650.444 | 4650.444 | 0 | 0 | 0 | 9235.05 | 9235.05 | 0
5/7/2026 | 11:15:00 AM | 7736.998 | 7736.998 | 0 | 4658.433 | 4658.433 | 0 | 0 | 0 | 9251.947 | 9251.947 | 0
5/7/2026 | 11:30:00 AM | 7751.264 | 7751.264 | 0 | 4666.617 | 4666.617 | 0 | 0 | 0 | 9268.866 | 9268.866 | 0
5/7/2026 | 11:45:00 AM | 7765.331 | 7765.331 | 0 | 4674.67 | 4674.67 | 0 | 0 | 0 | 9285.57 | 9285.57 | 0
5/7/2026 | 12:00:00 PM | 7778.993 | 7778.993 | 0 | 4682.675 | 4682.675 | 0 | 0 | 0 | 9301.835 | 9301.835 | 0
5/7/2026 | 12:15:00 PM | 7793.242 | 7793.242 | 0 | 4690.776 | 4690.776 | 0 | 0 | 0 | 9318.726 | 9318.726 | 0
5/7/2026 | 12:30:00 PM | 7807.408 | 7807.408 | 0 | 4698.858 | 4698.858 | 0 | 0 | 0 | 9335.517 | 9335.517 | 0
5/7/2026 | 12:45:00 PM | 7821.684 | 7821.684 | 0 | 4706.991 | 4706.991 | 0 | 0 | 0 | 9352.454 | 9352.454 | 0
5/7/2026 | 1:00:00 PM | 7835.942 | 7835.942 | 0 | 4715.1 | 4715.1 | 0 | 0 | 0 | 9369.339 | 9369.339 | 0
5/7/2026 | 1:15:00 PM | 7849.82 | 7849.82 | 0 | 4723.042 | 4723.042 | 0 | 0 | 0 | 9385.78 | 9385.78 | 0
5/7/2026 | 1:30:00 PM | 7863.874 | 7863.874 | 0 | 4731.037 | 4731.037 | 0 | 0 | 0 | 9402.421 | 9402.421 | 0
5/7/2026 | 1:45:00 PM | 7878.017 | 7878.017 | 0 | 4739.03 | 4739.03 | 0 | 0 | 0 | 9419.174 | 9419.174 | 0
5/7/2026 | 2:00:00 PM | 7891.98 | 7891.98 | 0 | 4746.927 | 4746.927 | 0 | 0 | 0 | 9435.726 | 9435.726 | 0
5/7/2026 | 2:15:00 PM | 7906.046 | 7906.046 | 0 | 4754.941 | 4754.941 | 0 | 0 | 0 | 9452.416 | 9452.416 | 0
5/7/2026 | 2:30:00 PM | 7920.127 | 7920.127 | 0 | 4762.985 | 4762.985 | 0 | 0 | 0 | 9469.123 | 9469.123 | 0
5/7/2026 | 2:45:00 PM | 7934.242 | 7934.242 | 0 | 4771.097 | 4771.097 | 0 | 0 | 0 | 9485.899 | 9485.899 | 0
5/7/2026 | 3:00:00 PM | 7948.182 | 7948.182 | 0 | 4779.225 | 4779.225 | 0 | 0 | 0 | 9502.45 | 9502.45 | 0
5/7/2026 | 3:15:00 PM | 7961.862 | 7961.862 | 0 | 4787.182 | 4787.182 | 0 | 0 | 0 | 9518.707 | 9518.707 | 0
5/7/2026 | 3:30:00 PM | 7975.416 | 7975.416 | 0 | 4795.093 | 4795.093 | 0 | 0 | 0 | 9534.832 | 9534.832 | 0
5/7/2026 | 3:45:00 PM | 7989.572 | 7989.572 | 0 | 4803.264 | 4803.264 | 0 | 0 | 0 | 9551.631 | 9551.631 | 0
5/7/2026 | 4:00:00 PM | 8003.48 | 8003.48 | 0 | 4811.179 | 4811.179 | 0 | 0 | 0 | 9568.137 | 9568.137 | 0
5/7/2026 | 4:15:00 PM | 8017.783 | 8017.783 | 0 | 4819.293 | 4819.293 | 0 | 0 | 0 | 9585.103 | 9585.103 | 0
5/7/2026 | 4:30:00 PM | 8031.917 | 8031.917 | 0 | 4827.411 | 4827.411 | 0 | 0 | 0 | 9601.891 | 9601.891 | 0
5/7/2026 | 4:45:00 PM | 8045.861 | 8045.861 | 0 | 4835.416 | 4835.416 | 0 | 0 | 0 | 9618.471 | 9618.471 | 0
5/7/2026 | 5:00:00 PM | 8059.901 | 8059.901 | 0 | 4843.471 | 4843.471 | 0 | 0 | 0 | 9635.146 | 9635.146 | 0
5/7/2026 | 5:15:00 PM | 8073.974 | 8073.974 | 0 | 4851.552 | 4851.552 | 0 | 0 | 0 | 9651.847 | 9651.847 | 0
5/7/2026 | 5:30:00 PM | 8087.837 | 8087.837 | 0 | 4859.593 | 4859.593 | 0 | 0 | 0 | 9668.34 | 9668.34 | 0
5/7/2026 | 5:45:00 PM | 8101.72 | 8101.72 | 0 | 4867.809 | 4867.809 | 0 | 0 | 0 | 9684.9 | 9684.9 | 0
5/7/2026 | 6:00:00 PM | 8115.489 | 8115.489 | 0 | 4876.041 | 4876.041 | 0 | 0 | 0 | 9701.308 | 9701.308 | 0
5/7/2026 | 6:15:00 PM | 8129.096 | 8129.096 | 0 | 4884.28 | 4884.28 | 0 | 0 | 0 | 9717.606 | 9717.606 | 0
5/7/2026 | 6:30:00 PM | 8142.699 | 8142.699 | 0 | 4892.556 | 4892.556 | 0 | 0 | 0 | 9733.907 | 9733.907 | 0
5/7/2026 | 6:45:00 PM | 8156.377 | 8156.377 | 0 | 4900.785 | 4900.785 | 0 | 0 | 0 | 9750.283 | 9750.283 | 0
5/7/2026 | 7:00:00 PM | 8169.795 | 8169.795 | 0 | 4909.054 | 4909.054 | 0 | 0 | 0 | 9766.397 | 9766.397 | 0
5/7/2026 | 7:15:00 PM | 8183.003 | 8183.003 | 0 | 4917.279 | 4917.279 | 0 | 0 | 0 | 9782.301 | 9782.301 | 0
5/7/2026 | 7:30:00 PM | 8195.438 | 8195.438 | 0 | 4924.936 | 4924.936 | 0 | 0 | 0 | 9797.307 | 9797.307 | 0
5/7/2026 | 7:45:00 PM | 8208.056 | 8208.056 | 0 | 4932.674 | 4932.674 | 0 | 0 | 0 | 9812.558 | 9812.558 | 0
5/7/2026 | 8:00:00 PM | 8220.835 | 8220.835 | 0 | 4940.373 | 4940.373 | 0 | 0 | 0 | 9827.921 | 9827.921 | 0
5/7/2026 | 8:15:00 PM | 8233.722 | 8233.722 | 0 | 4948.049 | 4948.049 | 0 | 0 | 0 | 9843.38 | 9843.38 | 0
5/7/2026 | 8:30:00 PM | 8246.254 | 8246.254 | 0 | 4955.548 | 4955.548 | 0 | 0 | 0 | 9858.45 | 9858.45 | 0
5/7/2026 | 8:45:00 PM | 8259.226 | 8259.226 | 0 | 4963.127 | 4963.127 | 0 | 0 | 0 | 9873.989 | 9873.989 | 0
5/7/2026 | 9:00:00 PM | 8272.333 | 8272.333 | 0 | 4970.676 | 4970.676 | 0 | 0 | 0 | 9889.648 | 9889.648 | 0
5/7/2026 | 9:15:00 PM | 8284.973 | 8284.973 | 0 | 4978.109 | 4978.109 | 0 | 0 | 0 | 9904.831 | 9904.831 | 0
5/7/2026 | 9:30:00 PM | 8297.862 | 8297.862 | 0 | 4985.754 | 4985.754 | 0 | 0 | 0 | 9920.305 | 9920.305 | 0
5/7/2026 | 9:45:00 PM | 8310.895 | 8310.895 | 0 | 4993.511 | 4993.511 | 0 | 0 | 0 | 9935.97 | 9935.97 | 0
5/7/2026 | 10:00:00 PM | 8323.637 | 8323.637 | 0 | 5001.234 | 5001.234 | 0 | 0 | 0 | 9951.323 | 9951.323 | 0
5/7/2026 | 10:15:00 PM | 8336.19 | 8336.19 | 0 | 5008.845 | 5008.845 | 0 | 0 | 0 | 9966.423 | 9966.423 | 0
5/7/2026 | 10:30:00 PM | 8348.744 | 8348.744 | 0 | 5016.399 | 5016.399 | 0 | 0 | 0 | 9981.483 | 9981.483 | 0
5/7/2026 | 10:45:00 PM | 8361.084 | 8361.084 | 0 | 5023.993 | 5023.993 | 0 | 0 | 0 | 9996.372 | 9996.372 | 0
5/7/2026 | 11:00:00 PM | 8373.566 | 8373.566 | 0 | 5031.727 | 5031.727 | 0 | 0 | 0 | 10011.422 | 10011.422 | 0
5/7/2026 | 11:15:00 PM | 8386.063 | 8386.063 | 0 | 5039.367 | 5039.367 | 0 | 0 | 0 | 10026.471 | 10026.471 | 0
5/7/2026 | 11:30:00 PM | 8398.4 | 8398.4 | 0 | 5047.043 | 5047.043 | 0 | 0 | 0 | 10041.39 | 10041.39 | 0
5/7/2026 | 11:45:00 PM | 8411.234 | 8411.234 | 0 | 5054.923 | 5054.923 | 0 | 0 | 0 | 10056.867 | 10056.867 | 0
5/8/2026 | 12:00:00 AM | 8423.612 | 8423.612 | 0 | 5062.647 | 5062.647 | 0 | 0 | 0 | 10071.846 | 10071.846 | 0
5/8/2026 | 12:15:00 AM | 8436.069 | 8436.069 | 0 | 5070.318 | 5070.318 | 0 | 0 | 0 | 10086.851 | 10086.851 | 0
5/8/2026 | 12:30:00 AM | 8448.567 | 8448.567 | 0 | 5077.859 | 5077.859 | 0 | 0 | 0 | 10101.837 | 10101.837 | 0
5/8/2026 | 12:45:00 AM | 8461.305 | 8461.305 | 0 | 5085.564 | 5085.564 | 0 | 0 | 0 | 10117.15 | 10117.15 | 0
5/8/2026 | 1:00:00 AM | 8473.881 | 8473.881 | 0 | 5093.18 | 5093.18 | 0 | 0 | 0 | 10132.271 | 10132.271 | 0
5/8/2026 | 1:15:00 AM | 8486.714 | 8486.714 | 0 | 5100.893 | 5100.893 | 0 | 0 | 0 | 10147.656 | 10147.656 | 0
5/8/2026 | 1:30:00 AM | 8498.897 | 8498.897 | 0 | 5108.278 | 5108.278 | 0 | 0 | 0 | 10162.33 | 10162.33 | 0
5/8/2026 | 1:45:00 AM | 8511.114 | 8511.114 | 0 | 5115.702 | 5115.702 | 0 | 0 | 0 | 10177.048 | 10177.048 | 0
5/8/2026 | 2:00:00 AM | 8523.587 | 8523.587 | 0 | 5123.356 | 5123.356 | 0 | 0 | 0 | 10192.068 | 10192.068 | 0
5/8/2026 | 2:15:00 AM | 8535.891 | 8535.891 | 0 | 5130.947 | 5130.947 | 0 | 0 | 0 | 10206.909 | 10206.909 | 0
5/8/2026 | 2:30:00 AM | 8548.487 | 8548.487 | 0 | 5138.626 | 5138.626 | 0 | 0 | 0 | 10222.057 | 10222.057 | 0
5/8/2026 | 2:45:00 AM | 8561.155 | 8561.155 | 0 | 5146.33 | 5146.33 | 0 | 0 | 0 | 10237.302 | 10237.302 | 0
5/8/2026 | 3:00:00 AM | 8573.615 | 8573.615 | 0 | 5154.021 | 5154.021 | 0 | 0 | 0 | 10252.331 | 10252.331 | 0
5/8/2026 | 3:15:00 AM | 8586.025 | 8586.025 | 0 | 5161.676 | 5161.676 | 0 | 0 | 0 | 10267.283 | 10267.283 | 0
5/8/2026 | 3:30:00 AM | 8598.209 | 8598.209 | 0 | 5169.253 | 5169.253 | 0 | 0 | 0 | 10282.011 | 10282.011 | 0
5/8/2026 | 3:45:00 AM | 8610.469 | 8610.469 | 0 | 5176.812 | 5176.812 | 0 | 0 | 0 | 10296.833 | 10296.833 | 0
5/8/2026 | 4:00:00 AM | 8623.269 | 8623.269 | 0 | 5184.656 | 5184.656 | 0 | 0 | 0 | 10312.244 | 10312.244 | 0
5/8/2026 | 4:15:00 AM | 8635.636 | 8635.636 | 0 | 5192.244 | 5192.244 | 0 | 0 | 0 | 10327.169 | 10327.169 | 0
5/8/2026 | 4:30:00 AM | 8648.406 | 8648.406 | 0 | 5200.096 | 5200.096 | 0 | 0 | 0 | 10342.566 | 10342.566 | 0
5/8/2026 | 4:45:00 AM | 8661.099 | 8661.099 | 0 | 5207.736 | 5207.736 | 0 | 0 | 0 | 10357.84 | 10357.84 | 0
5/8/2026 | 5:00:00 AM | 8673.495 | 8673.495 | 0 | 5215.143 | 5215.143 | 0 | 0 | 0 | 10372.76 | 10372.76 | 0
5/8/2026 | 5:15:00 AM | 8686.181 | 8686.181 | 0 | 5222.705 | 5222.705 | 0 | 0 | 0 | 10387.988 | 10387.988 | 0
5/8/2026 | 5:30:00 AM | 8698.825 | 8698.825 | 0 | 5230.292 | 5230.292 | 0 | 0 | 0 | 10403.16 | 10403.16 | 0
5/8/2026 | 5:45:00 AM | 8711.195 | 8711.195 | 0 | 5237.776 | 5237.776 | 0 | 0 | 0 | 10418.061 | 10418.061 | 0
5/8/2026 | 6:00:00 AM | 8723.881 | 8723.881 | 0 | 5245.408 | 5245.408 | 0 | 0 | 0 | 10433.279 | 10433.279 | 0
5/8/2026 | 6:15:00 AM | 8736.445 | 8736.445 | 0 | 5252.847 | 5252.847 | 0 | 0 | 0 | 10448.297 | 10448.297 | 0
5/8/2026 | 6:30:00 AM | 8749.209 | 8749.209 | 0 | 5260.286 | 5260.286 | 0 | 0 | 0 | 10463.569 | 10463.569 | 0
5/8/2026 | 6:45:00 AM | 8762.1 | 8762.1 | 0 | 5267.78 | 5267.78 | 0 | 0 | 0 | 10478.981 | 10478.981 | 0
5/8/2026 | 7:00:00 AM | 8774.594 | 8774.594 | 0 | 5275.027 | 5275.027 | 0 | 0 | 0 | 10493.95 | 10493.95 | 0
5/8/2026 | 7:15:00 AM | 8787.335 | 8787.335 | 0 | 5282.523 | 5282.523 | 0 | 0 | 0 | 10509.218 | 10509.218 | 0
5/8/2026 | 7:30:00 AM | 8799.869 | 8799.869 | 0 | 5289.887 | 5289.887 | 0 | 0 | 0 | 10524.224 | 10524.224 | 0
5/8/2026 | 7:45:00 AM | 8812.277 | 8812.277 | 0 | 5297.23 | 5297.23 | 0 | 0 | 0 | 10539.13 | 10539.13 | 0
5/8/2026 | 8:00:00 AM | 8824.966 | 8824.966 | 0 | 5304.613 | 5304.613 | 0 | 0 | 0 | 10554.32 | 10554.32 | 0
5/8/2026 | 8:15:00 AM | 8837.893 | 8837.893 | 0 | 5311.938 | 5311.938 | 0 | 0 | 0 | 10569.728 | 10569.728 | 0
5/8/2026 | 8:30:00 AM | 8850.658 | 8850.658 | 0 | 5319.326 | 5319.326 | 0 | 0 | 0 | 10585.004 | 10585.004 | 0
5/8/2026 | 8:45:00 AM | 8863.85 | 8863.85 | 0 | 5326.803 | 5326.803 | 0 | 0 | 0 | 10600.757 | 10600.757 | 0
5/8/2026 | 9:00:00 AM | 8877.098 | 8877.098 | 0 | 5334.126 | 5334.126 | 0 | 0 | 0 | 10616.52 | 10616.52 | 0
5/8/2026 | 9:15:00 AM | 8890.343 | 8890.343 | 0 | 5341.44 | 5341.44 | 0 | 0 | 0 | 10632.288 | 10632.288 | 0
5/8/2026 | 9:30:00 AM | 8903.518 | 8903.518 | 0 | 5348.594 | 5348.594 | 0 | 0 | 0 | 10647.959 | 10647.959 | 0
5/8/2026 | 9:45:00 AM | 8916.592 | 8916.592 | 0 | 5355.943 | 5355.943 | 0 | 0 | 0 | 10663.599 | 10663.599 | 0
5/8/2026 | 10:00:00 AM | 8929.734 | 8929.734 | 0 | 5363.215 | 5363.215 | 0 | 0 | 0 | 10679.252 | 10679.252 | 0
5/8/2026 | 10:15:00 AM | 8942.568 | 8942.568 | 0 | 5370.444 | 5370.444 | 0 | 0 | 0 | 10694.559 | 10694.559 | 0
5/8/2026 | 10:30:00 AM | 8955.467 | 8955.467 | 0 | 5377.773 | 5377.773 | 0 | 0 | 0 | 10709.946 | 10709.946 | 0
5/8/2026 | 10:45:00 AM | 8968.53 | 8968.53 | 0 | 5385.157 | 5385.157 | 0 | 0 | 0 | 10725.489 | 10725.489 | 0
5/8/2026 | 11:00:00 AM | 8981.414 | 8981.414 | 0 | 5392.431 | 5392.431 | 0 | 0 | 0 | 10740.836 | 10740.836 | 0
5/8/2026 | 11:15:00 AM | 8995.084 | 8995.084 | 0 | 5399.937 | 5399.937 | 0 | 0 | 0 | 10757.04 | 10757.04 | 0
5/8/2026 | 11:30:00 AM | 9008.433 | 9008.433 | 0 | 5407.217 | 5407.217 | 0 | 0 | 0 | 10772.876 | 10772.876 | 0
5/8/2026 | 11:45:00 AM | 9021.512 | 9021.512 | 0 | 5414.506 | 5414.506 | 0 | 0 | 0 | 10788.461 | 10788.461 | 0
5/8/2026 | 12:00:00 PM | 9034.62 | 9034.62 | 0 | 5421.717 | 5421.717 | 0 | 0 | 0 | 10804.008 | 10804.008 | 0
5/8/2026 | 12:15:00 PM | 9048.01 | 9048.01 | 0 | 5429.075 | 5429.075 | 0 | 0 | 0 | 10819.875 | 10819.875 | 0
5/8/2026 | 12:30:00 PM | 9061.347 | 9061.347 | 0 | 5436.39 | 5436.39 | 0 | 0 | 0 | 10835.716 | 10835.716 | 0
5/8/2026 | 12:45:00 PM | 9074.918 | 9074.918 | 0 | 5443.803 | 5443.803 | 0 | 0 | 0 | 10851.813 | 10851.813 | 0
5/8/2026 | 1:00:00 PM | 9088.105 | 9088.105 | 0 | 5450.976 | 5450.976 | 0 | 0 | 0 | 10867.468 | 10867.468 | 0
5/8/2026 | 1:15:00 PM | 9101.625 | 9101.625 | 0 | 5458.403 | 5458.403 | 0 | 0 | 0 | 10883.505 | 10883.505 | 0
5/8/2026 | 1:30:00 PM | 9114.698 | 9114.698 | 0 | 5465.639 | 5465.639 | 0 | 0 | 0 | 10899.009 | 10899.009 | 0
5/8/2026 | 1:45:00 PM | 9127.478 | 9127.478 | 0 | 5472.731 | 5472.731 | 0 | 0 | 0 | 10914.212 | 10914.212 | 0
5/8/2026 | 2:00:00 PM | 9140.38 | 9140.38 | 0 | 5479.884 | 5479.884 | 0 | 0 | 0 | 10929.532 | 10929.532 | 0
5/8/2026 | 2:15:00 PM | 9153.278 | 9153.278 | 0 | 5487.079 | 5487.079 | 0 | 0 | 0 | 10944.85 | 10944.85 | 0
5/8/2026 | 2:30:00 PM | 9166.409 | 9166.409 | 0 | 5494.426 | 5494.426 | 0 | 0 | 0 | 10960.454 | 10960.454 | 0
5/8/2026 | 2:45:00 PM | 9179.785 | 9179.785 | 0 | 5501.73 | 5501.73 | 0 | 0 | 0 | 10976.324 | 10976.324 | 0
5/8/2026 | 3:00:00 PM | 9192.87 | 9192.87 | 0 | 5508.85 | 5508.85 | 0 | 0 | 0 | 10991.828 | 10991.828 | 0
5/8/2026 | 3:15:00 PM | 9205.698 | 9205.698 | 0 | 5516.037 | 5516.037 | 0 | 0 | 0 | 11007.103 | 11007.103 | 0
5/8/2026 | 3:30:00 PM | 9218.743 | 9218.743 | 0 | 5523.285 | 5523.285 | 0 | 0 | 0 | 11022.576 | 11022.576 | 0
5/8/2026 | 3:45:00 PM | 9232.121 | 9232.121 | 0 | 5530.728 | 5530.728 | 0 | 0 | 0 | 11038.468 | 11038.468 | 0
5/8/2026 | 4:00:00 PM | 9245.066 | 9245.066 | 0 | 5537.831 | 5537.831 | 0 | 0 | 0 | 11053.869 | 11053.869 | 0
5/8/2026 | 4:15:00 PM | 9258.321 | 9258.321 | 0 | 5545.212 | 5545.212 | 0 | 0 | 0 | 11069.609 | 11069.609 | 0
5/8/2026 | 4:30:00 PM | 9271.172 | 9271.172 | 0 | 5552.462 | 5552.462 | 0 | 0 | 0 | 11084.88 | 11084.88 | 0
5/8/2026 | 4:45:00 PM | 9284.169 | 9284.169 | 0 | 5559.805 | 5559.805 | 0 | 0 | 0 | 11100.362 | 11100.362 | 0
5/8/2026 | 5:00:00 PM | 9297.706 | 9297.706 | 0 | 5567.169 | 5567.169 | 0 | 0 | 0 | 11116.393 | 11116.393 | 0
5/8/2026 | 5:15:00 PM | 9310.914 | 9310.914 | 0 | 5574.358 | 5574.358 | 0 | 0 | 0 | 11132.073 | 11132.073 | 0
5/8/2026 | 5:30:00 PM | 9324.045 | 9324.045 | 0 | 5581.598 | 5581.598 | 0 | 0 | 0 | 11147.69 | 11147.69 | 0
5/8/2026 | 5:45:00 PM | 9337.662 | 9337.662 | 0 | 5589.114 | 5589.114 | 0 | 0 | 0 | 11163.843 | 11163.843 | 0
5/8/2026 | 6:00:00 PM | 9350.728 | 9350.728 | 0 | 5596.616 | 5596.616 | 0 | 0 | 0 | 11179.431 | 11179.431 | 0
5/8/2026 | 6:15:00 PM | 9363.887 | 9363.887 | 0 | 5604.14 | 5604.14 | 0 | 0 | 0 | 11195.092 | 11195.092 | 0
5/8/2026 | 6:30:00 PM | 9376.985 | 9376.985 | 0 | 5611.616 | 5611.616 | 0 | 0 | 0 | 11210.669 | 11210.669 | 0
5/8/2026 | 6:45:00 PM | 9389.737 | 9389.737 | 0 | 5619.038 | 5619.038 | 0 | 0 | 0 | 11225.909 | 11225.909 | 0
5/8/2026 | 7:00:00 PM | 9402.229 | 9402.229 | 0 | 5626.402 | 5626.402 | 0 | 0 | 0 | 11240.841 | 11240.841 | 0
5/8/2026 | 7:15:00 PM | 9414.588 | 9414.588 | 0 | 5633.649 | 5633.649 | 0 | 0 | 0 | 11255.608 | 11255.608 | 0
5/8/2026 | 7:30:00 PM | 9426.847 | 9426.847 | 0 | 5640.958 | 5640.958 | 0 | 0 | 0 | 11270.289 | 11270.289 | 0
5/8/2026 | 7:45:00 PM | 9439.58 | 9439.58 | 0 | 5648.56 | 5648.56 | 0 | 0 | 0 | 11285.534 | 11285.534 | 0
5/8/2026 | 8:00:00 PM | 9452.442 | 9452.442 | 0 | 5656.081 | 5656.081 | 0 | 0 | 0 | 11300.855 | 11300.855 | 0
5/8/2026 | 8:15:00 PM | 9464.649 | 9464.649 | 0 | 5663.434 | 5663.434 | 0 | 0 | 0 | 11315.516 | 11315.516 | 0
5/8/2026 | 8:30:00 PM | 9477.128 | 9477.128 | 0 | 5670.858 | 5670.858 | 0 | 0 | 0 | 11330.435 | 11330.435 | 0
5/8/2026 | 8:45:00 PM | 9489.777 | 9489.777 | 0 | 5678.199 | 5678.199 | 0 | 0 | 0 | 11345.527 | 11345.527 | 0
5/8/2026 | 9:00:00 PM | 9502.448 | 9502.448 | 0 | 5685.61 | 5685.61 | 0 | 0 | 0 | 11360.642 | 11360.642 | 0
5/8/2026 | 9:15:00 PM | 9515.392 | 9515.392 | 0 | 5693.18 | 5693.18 | 0 | 0 | 0 | 11376.049 | 11376.049 | 0
5/8/2026 | 9:30:00 PM | 9528.162 | 9528.162 | 0 | 5700.613 | 5700.613 | 0 | 0 | 0 | 11391.26 | 11391.26 | 0
5/8/2026 | 9:45:00 PM | 9540.941 | 9540.941 | 0 | 5708.212 | 5708.212 | 0 | 0 | 0 | 11406.561 | 11406.561 | 0
5/8/2026 | 10:00:00 PM | 9553.626 | 9553.626 | 0 | 5715.752 | 5715.752 | 0 | 0 | 0 | 11421.714 | 11421.714 | 0
5/8/2026 | 10:15:00 PM | 9566.294 | 9566.294 | 0 | 5723.331 | 5723.331 | 0 | 0 | 0 | 11436.877 | 11436.877 | 0
5/8/2026 | 10:30:00 PM | 9578.788 | 9578.788 | 0 | 5730.814 | 5730.814 | 0 | 0 | 0 | 11451.85 | 11451.85 | 0
5/8/2026 | 10:45:00 PM | 9591.358 | 9591.358 | 0 | 5738.315 | 5738.315 | 0 | 0 | 0 | 11466.911 | 11466.911 | 0
5/8/2026 | 11:00:00 PM | 9603.659 | 9603.659 | 0 | 5745.779 | 5745.779 | 0 | 0 | 0 | 11481.662 | 11481.662 | 0
5/8/2026 | 11:15:00 PM | 9616.011 | 9616.011 | 0 | 5753.308 | 5753.308 | 0 | 0 | 0 | 11496.5 | 11496.5 | 0
5/8/2026 | 11:30:00 PM | 9628.471 | 9628.471 | 0 | 5760.804 | 5760.804 | 0 | 0 | 0 | 11511.417 | 11511.417 | 0
5/8/2026 | 11:45:00 PM | 9641.198 | 9641.198 | 0 | 5768.52 | 5768.52 | 0 | 0 | 0 | 11526.731 | 11526.731 | 0
5/9/2026 | 12:00:00 AM | 9654.109 | 9654.109 | 0 | 5776.27 | 5776.27 | 0 | 0 | 0 | 11542.223 | 11542.223 | 0
5/9/2026 | 12:15:00 AM | 9667.2 | 9667.2 | 0 | 5784.06 | 5784.06 | 0 | 0 | 0 | 11557.895 | 11557.895 | 0
5/9/2026 | 12:30:00 AM | 9679.882 | 9679.882 | 0 | 5791.673 | 5791.673 | 0 | 0 | 0 | 11573.134 | 11573.134 | 0
5/9/2026 | 12:45:00 AM | 9692.974 | 9692.974 | 0 | 5799.423 | 5799.423 | 0 | 0 | 0 | 11588.824 | 11588.824 | 0
5/9/2026 | 1:00:00 AM | 9706.037 | 9706.037 | 0 | 5807.136 | 5807.136 | 0 | 0 | 0 | 11604.503 | 11604.503 | 0
5/9/2026 | 1:15:00 AM | 9718.93 | 9718.93 | 0 | 5814.834 | 5814.834 | 0 | 0 | 0 | 11620.027 | 11620.027 | 0
5/9/2026 | 1:30:00 AM | 9732.189 | 9732.189 | 0 | 5822.629 | 5822.629 | 0 | 0 | 0 | 11635.904 | 11635.904 | 0
5/9/2026 | 1:45:00 AM | 9745.237 | 9745.237 | 0 | 5830.486 | 5830.486 | 0 | 0 | 0 | 11651.615 | 11651.615 | 0
5/9/2026 | 2:00:00 AM | 9758.144 | 9758.144 | 0 | 5838.318 | 5838.318 | 0 | 0 | 0 | 11667.165 | 11667.165 | 0
5/9/2026 | 2:15:00 AM | 9771.246 | 9771.246 | 0 | 5846.127 | 5846.127 | 0 | 0 | 0 | 11682.892 | 11682.892 | 0
5/9/2026 | 2:30:00 AM | 9784.046 | 9784.046 | 0 | 5853.801 | 5853.801 | 0 | 0 | 0 | 11698.3 | 11698.3 | 0
5/9/2026 | 2:45:00 AM | 9796.979 | 9796.979 | 0 | 5861.687 | 5861.687 | 0 | 0 | 0 | 11713.918 | 11713.918 | 0
5/9/2026 | 3:00:00 AM | 9809.876 | 9809.876 | 0 | 5869.459 | 5869.459 | 0 | 0 | 0 | 11729.411 | 11729.411 | 0
5/9/2026 | 3:15:00 AM | 9822.66 | 9822.66 | 0 | 5877.169 | 5877.169 | 0 | 0 | 0 | 11744.796 | 11744.796 | 0
5/9/2026 | 3:30:00 AM | 9835.527 | 9835.527 | 0 | 5885.011 | 5885.011 | 0 | 0 | 0 | 11760.32 | 11760.32 | 0
5/9/2026 | 3:45:00 AM | 9848.422 | 9848.422 | 0 | 5892.785 | 5892.785 | 0 | 0 | 0 | 11775.859 | 11775.859 | 0
5/9/2026 | 4:00:00 AM | 9861.026 | 9861.026 | 0 | 5900.354 | 5900.354 | 0 | 0 | 0 | 11791.047 | 11791.047 | 0
5/9/2026 | 4:15:00 AM | 9873.748 | 9873.748 | 0 | 5908.054 | 5908.054 | 0 | 0 | 0 | 11806.403 | 11806.403 | 0
5/9/2026 | 4:30:00 AM | 9886.614 | 9886.614 | 0 | 5915.808 | 5915.808 | 0 | 0 | 0 | 11821.914 | 11821.914 | 0
5/9/2026 | 4:45:00 AM | 9899.226 | 9899.226 | 0 | 5923.3 | 5923.3 | 0 | 0 | 0 | 11837.142 | 11837.142 | 0
5/9/2026 | 5:00:00 AM | 9912.451 | 9912.451 | 0 | 5931.092 | 5931.092 | 0 | 0 | 0 | 11853.021 | 11853.021 | 0
5/9/2026 | 5:15:00 AM | 9925.506 | 9925.506 | 0 | 5938.667 | 5938.667 | 0 | 0 | 0 | 11868.685 | 11868.685 | 0
5/9/2026 | 5:30:00 AM | 9938.707 | 9938.707 | 0 | 5946.38 | 5946.38 | 0 | 0 | 0 | 11884.532 | 11884.532 | 0
5/9/2026 | 5:45:00 AM | 9951.885 | 9951.885 | 0 | 5954.161 | 5954.161 | 0 | 0 | 0 | 11900.36 | 11900.36 | 0
5/9/2026 | 6:00:00 AM | 9964.605 | 9964.605 | 0 | 5961.681 | 5961.681 | 0 | 0 | 0 | 11915.642 | 11915.642 | 0
5/9/2026 | 6:15:00 AM | 9977.721 | 9977.721 | 0 | 5969.486 | 5969.486 | 0 | 0 | 0 | 11931.415 | 11931.415 | 0
5/9/2026 | 6:30:00 AM | 9991.093 | 9991.093 | 0 | 5977.279 | 5977.279 | 0 | 0 | 0 | 11947.422 | 11947.422 | 0
5/9/2026 | 6:45:00 AM | 10004.232 | 10004.232 | 0 | 5984.988 | 5984.988 | 0 | 0 | 0 | 11963.208 | 11963.208 | 0
5/9/2026 | 7:00:00 AM | 10016.924 | 10016.924 | 0 | 5992.492 | 5992.492 | 0 | 0 | 0 | 11978.477 | 11978.477 | 0
5/9/2026 | 7:15:00 AM | 10030.117 | 10030.117 | 0 | 6000.157 | 6000.157 | 0 | 0 | 0 | 11994.278 | 11994.278 | 0
5/9/2026 | 7:30:00 AM | 10043.142 | 10043.142 | 0 | 6007.672 | 6007.672 | 0 | 0 | 0 | 12009.904 | 12009.904 | 0
5/9/2026 | 7:45:00 AM | 10056.57 | 10056.57 | 0 | 6015.396 | 6015.396 | 0 | 0 | 0 | 12025.987 | 12025.987 | 0
5/9/2026 | 8:00:00 AM | 10070.04 | 10070.04 | 0 | 6022.971 | 6022.971 | 0 | 0 | 0 | 12042.057 | 12042.057 | 0
5/9/2026 | 8:15:00 AM | 10083.139 | 10083.139 | 0 | 6030.441 | 6030.441 | 0 | 0 | 0 | 12057.729 | 12057.729 | 0
5/9/2026 | 8:30:00 AM | 10096.055 | 10096.055 | 0 | 6037.85 | 6037.85 | 0 | 0 | 0 | 12073.173 | 12073.173 | 0
5/9/2026 | 8:45:00 AM | 10109.206 | 10109.206 | 0 | 6045.248 | 6045.248 | 0 | 0 | 0 | 12088.846 | 12088.846 | 0
5/9/2026 | 9:00:00 AM | 10122.531 | 10122.531 | 0 | 6052.741 | 6052.741 | 0 | 0 | 0 | 12104.712 | 12104.712 | 0
5/9/2026 | 9:15:00 AM | 10135.557 | 10135.557 | 0 | 6060.221 | 6060.221 | 0 | 0 | 0 | 12120.268 | 12120.268 | 0
5/9/2026 | 9:30:00 AM | 10148.856 | 10148.856 | 0 | 6067.795 | 6067.795 | 0 | 0 | 0 | 12136.104 | 12136.104 | 0
5/9/2026 | 9:45:00 AM | 10161.807 | 10161.807 | 0 | 6075.212 | 6075.212 | 0 | 0 | 0 | 12151.578 | 12151.578 | 0
5/9/2026 | 10:00:00 AM | 10174.701 | 10174.701 | 0 | 6082.693 | 6082.693 | 0 | 0 | 0 | 12166.962 | 12166.962 | 0
5/9/2026 | 10:15:00 AM | 10187.573 | 10187.573 | 0 | 6090.052 | 6090.052 | 0 | 0 | 0 | 12182.294 | 12182.294 | 0
5/9/2026 | 10:30:00 AM | 10200.035 | 10200.035 | 0 | 6097.244 | 6097.244 | 0 | 0 | 0 | 12197.193 | 12197.193 | 0
5/9/2026 | 10:45:00 AM | 10212.801 | 10212.801 | 0 | 6104.582 | 6104.582 | 0 | 0 | 0 | 12212.414 | 12212.414 | 0
5/9/2026 | 11:00:00 AM | 10225.469 | 10225.469 | 0 | 6111.941 | 6111.941 | 0 | 0 | 0 | 12227.515 | 12227.515 | 0
5/9/2026 | 11:15:00 AM | 10238.191 | 10238.191 | 0 | 6119.341 | 6119.341 | 0 | 0 | 0 | 12242.711 | 12242.711 | 0
5/9/2026 | 11:30:00 AM | 10251.042 | 10251.042 | 0 | 6126.708 | 6126.708 | 0 | 0 | 0 | 12257.996 | 12257.996 | 0
5/9/2026 | 11:45:00 AM | 10264.015 | 10264.015 | 0 | 6134.112 | 6134.112 | 0 | 0 | 0 | 12273.449 | 12273.449 | 0
5/9/2026 | 12:00:00 PM | 10276.793 | 10276.793 | 0 | 6141.493 | 6141.493 | 0 | 0 | 0 | 12288.669 | 12288.669 | 0
5/9/2026 | 12:15:00 PM | 10289.586 | 10289.586 | 0 | 6148.81 | 6148.81 | 0 | 0 | 0 | 12303.905 | 12303.905 | 0
5/9/2026 | 12:30:00 PM | 10302.551 | 10302.551 | 0 | 6156.16 | 6156.16 | 0 | 0 | 0 | 12319.322 | 12319.322 | 0
5/9/2026 | 12:45:00 PM | 10315.406 | 10315.406 | 0 | 6163.585 | 6163.585 | 0 | 0 | 0 | 12334.668 | 12334.668 | 0
5/9/2026 | 1:00:00 PM | 10328.599 | 10328.599 | 0 | 6171.106 | 6171.106 | 0 | 0 | 0 | 12350.353 | 12350.353 | 0
5/9/2026 | 1:15:00 PM | 10341.339 | 10341.339 | 0 | 6178.354 | 6178.354 | 0 | 0 | 0 | 12365.528 | 12365.528 | 0
5/9/2026 | 1:30:00 PM | 10353.834 | 10353.834 | 0 | 6185.575 | 6185.575 | 0 | 0 | 0 | 12380.468 | 12380.468 | 0
5/9/2026 | 1:45:00 PM | 10366.545 | 10366.545 | 0 | 6192.885 | 6192.885 | 0 | 0 | 0 | 12395.623 | 12395.623 | 0
5/9/2026 | 2:00:00 PM | 10379.104 | 10379.104 | 0 | 6200.227 | 6200.227 | 0 | 0 | 0 | 12410.63 | 12410.63 | 0
5/9/2026 | 2:15:00 PM | 10391.521 | 10391.521 | 0 | 6207.486 | 6207.486 | 0 | 0 | 0 | 12425.469 | 12425.469 | 0
5/9/2026 | 2:30:00 PM | 10404.311 | 10404.311 | 0 | 6214.897 | 6214.897 | 0 | 0 | 0 | 12440.723 | 12440.723 | 0
5/9/2026 | 2:45:00 PM | 10417.116 | 10417.116 | 0 | 6222.324 | 6222.324 | 0 | 0 | 0 | 12456.013 | 12456.013 | 0
5/9/2026 | 3:00:00 PM | 10429.632 | 10429.632 | 0 | 6229.638 | 6229.638 | 0 | 0 | 0 | 12470.965 | 12470.965 | 0
5/9/2026 | 3:15:00 PM | 10442.238 | 10442.238 | 0 | 6237.004 | 6237.004 | 0 | 0 | 0 | 12486.009 | 12486.009 | 0
5/9/2026 | 3:30:00 PM | 10454.943 | 10454.943 | 0 | 6244.44 | 6244.44 | 0 | 0 | 0 | 12501.149 | 12501.149 | 0
5/9/2026 | 3:45:00 PM | 10467.604 | 10467.604 | 0 | 6251.762 | 6251.762 | 0 | 0 | 0 | 12516.272 | 12516.272 | 0
5/9/2026 | 4:00:00 PM | 10480.42 | 10480.42 | 0 | 6259.088 | 6259.088 | 0 | 0 | 0 | 12531.518 | 12531.518 | 0
5/9/2026 | 4:15:00 PM | 10493.008 | 10493.008 | 0 | 6266.332 | 6266.332 | 0 | 0 | 0 | 12546.54 | 12546.54 | 0
5/9/2026 | 4:30:00 PM | 10506.097 | 10506.097 | 0 | 6273.886 | 6273.886 | 0 | 0 | 0 | 12562.123 | 12562.123 | 0
5/9/2026 | 4:45:00 PM | 10518.964 | 10518.964 | 0 | 6281.204 | 6281.204 | 0 | 0 | 0 | 12577.459 | 12577.459 | 0
5/9/2026 | 5:00:00 PM | 10531.656 | 10531.656 | 0 | 6288.376 | 6288.376 | 0 | 0 | 0 | 12592.569 | 12592.569 | 0
5/9/2026 | 5:15:00 PM | 10544.833 | 10544.833 | 0 | 6295.857 | 6295.857 | 0 | 0 | 0 | 12608.249 | 12608.249 | 0
5/9/2026 | 5:30:00 PM | 10557.848 | 10557.848 | 0 | 6303.194 | 6303.194 | 0 | 0 | 0 | 12623.738 | 12623.738 | 0
5/9/2026 | 5:45:00 PM | 10570.482 | 10570.482 | 0 | 6310.471 | 6310.471 | 0 | 0 | 0 | 12638.845 | 12638.845 | 0
5/9/2026 | 6:00:00 PM | 10583.183 | 10583.183 | 0 | 6317.846 | 6317.846 | 0 | 0 | 0 | 12653.99 | 12653.99 | 0
5/9/2026 | 6:15:00 PM | 10595.727 | 10595.727 | 0 | 6325.187 | 6325.187 | 0 | 0 | 0 | 12668.978 | 12668.978 | 0
5/9/2026 | 6:30:00 PM | 10608.58 | 10608.58 | 0 | 6332.799 | 6332.799 | 0 | 0 | 0 | 12684.332 | 12684.332 | 0
5/9/2026 | 6:45:00 PM | 10621.013 | 10621.013 | 0 | 6340.212 | 6340.212 | 0 | 0 | 0 | 12699.222 | 12699.222 | 0
5/9/2026 | 7:00:00 PM | 10633.575 | 10633.575 | 0 | 6347.7 | 6347.7 | 0 | 0 | 0 | 12714.224 | 12714.224 | 0
5/9/2026 | 7:15:00 PM | 10645.838 | 10645.838 | 0 | 6355.025 | 6355.025 | 0 | 0 | 0 | 12728.905 | 12728.905 | 0
5/9/2026 | 7:30:00 PM | 10658.29 | 10658.29 | 0 | 6362.481 | 6362.481 | 0 | 0 | 0 | 12743.803 | 12743.803 | 0
5/9/2026 | 7:45:00 PM | 10670.862 | 10670.862 | 0 | 6369.971 | 6369.971 | 0 | 0 | 0 | 12758.839 | 12758.839 | 0
5/9/2026 | 8:00:00 PM | 10683.423 | 10683.423 | 0 | 6377.429 | 6377.429 | 0 | 0 | 0 | 12773.856 | 12773.856 | 0
5/9/2026 | 8:15:00 PM | 10696.214 | 10696.214 | 0 | 6384.959 | 6384.959 | 0 | 0 | 0 | 12789.116 | 12789.116 | 0
5/9/2026 | 8:30:00 PM | 10709.112 | 10709.112 | 0 | 6392.511 | 6392.511 | 0 | 0 | 0 | 12804.498 | 12804.498 | 0
5/9/2026 | 8:45:00 PM | 10721.87 | 10721.87 | 0 | 6399.962 | 6399.962 | 0 | 0 | 0 | 12819.735 | 12819.735 | 0
5/9/2026 | 9:00:00 PM | 10734.833 | 10734.833 | 0 | 6407.493 | 6407.493 | 0 | 0 | 0 | 12835.161 | 12835.161 | 0
5/9/2026 | 9:15:00 PM | 10747.689 | 10747.689 | 0 | 6414.95 | 6414.95 | 0 | 0 | 0 | 12850.482 | 12850.482 | 0
5/9/2026 | 9:30:00 PM | 10760.608 | 10760.608 | 0 | 6422.461 | 6422.461 | 0 | 0 | 0 | 12865.866 | 12865.866 | 0
5/9/2026 | 9:45:00 PM | 10773.136 | 10773.136 | 0 | 6429.801 | 6429.801 | 0 | 0 | 0 | 12880.855 | 12880.855 | 0
5/9/2026 | 10:00:00 PM | 10785.63 | 10785.63 | 0 | 6437.218 | 6437.218 | 0 | 0 | 0 | 12895.817 | 12895.817 | 0
5/9/2026 | 10:15:00 PM | 10798.303 | 10798.303 | 0 | 6444.772 | 6444.772 | 0 | 0 | 0 | 12910.999 | 12910.999 | 0
5/9/2026 | 10:30:00 PM | 10811.105 | 10811.105 | 0 | 6452.355 | 6452.355 | 0 | 0 | 0 | 12926.307 | 12926.307 | 0
5/9/2026 | 10:45:00 PM | 10823.678 | 10823.678 | 0 | 6459.843 | 6459.843 | 0 | 0 | 0 | 12941.363 | 12941.363 | 0
5/9/2026 | 11:00:00 PM | 10836.241 | 10836.241 | 0 | 6467.426 | 6467.426 | 0 | 0 | 0 | 12956.42 | 12956.42 | 0
5/9/2026 | 11:15:00 PM | 10848.842 | 10848.842 | 0 | 6475.06 | 6475.06 | 0 | 0 | 0 | 12971.536 | 12971.536 | 0
5/9/2026 | 11:30:00 PM | 10861.165 | 10861.165 | 0 | 6482.471 | 6482.471 | 0 | 0 | 0 | 12986.306 | 12986.306 | 0
5/9/2026 | 11:45:00 PM | 10873.743 | 10873.743 | 0 | 6490.05 | 6490.05 | 0 | 0 | 0 | 13001.425 | 13001.425 | 0
5/10/2026 | 12:00:00 AM | 10886.704 | 10886.704 | 0 | 6497.826 | 6497.826 | 0 | 0 | 0 | 13016.974 | 13016.974 | 0
5/10/2026 | 12:15:00 AM | 10899.744 | 10899.744 | 0 | 6505.559 | 6505.559 | 0 | 0 | 0 | 13032.563 | 13032.563 | 0
5/10/2026 | 12:30:00 AM | 10912.443 | 10912.443 | 0 | 6513.223 | 6513.223 | 0 | 0 | 0 | 13047.851 | 13047.851 | 0
5/10/2026 | 12:45:00 AM | 10925.488 | 10925.488 | 0 | 6521.063 | 6521.063 | 0 | 0 | 0 | 13063.543 | 13063.543 | 0
5/10/2026 | 1:00:00 AM | 10938.065 | 10938.065 | 0 | 6528.47 | 6528.47 | 0 | 0 | 0 | 13078.631 | 13078.631 | 0
5/10/2026 | 1:15:00 AM | 10950.755 | 10950.755 | 0 | 6536.022 | 6536.022 | 0 | 0 | 0 | 13093.897 | 13093.897 | 0
5/10/2026 | 1:30:00 AM | 10963.649 | 10963.649 | 0 | 6543.705 | 6543.705 | 0 | 0 | 0 | 13109.379 | 13109.379 | 0
5/10/2026 | 1:45:00 AM | 10976.643 | 10976.643 | 0 | 6551.487 | 6551.487 | 0 | 0 | 0 | 13124.995 | 13124.995 | 0
5/10/2026 | 2:00:00 AM | 10989.172 | 10989.172 | 0 | 6559.186 | 6559.186 | 0 | 0 | 0 | 13140.132 | 13140.132 | 0
5/10/2026 | 2:15:00 AM | 11001.777 | 11001.777 | 0 | 6566.868 | 6566.868 | 0 | 0 | 0 | 13155.326 | 13155.326 | 0
5/10/2026 | 2:30:00 AM | 11014.565 | 11014.565 | 0 | 6574.593 | 6574.593 | 0 | 0 | 0 | 13170.705 | 13170.705 | 0
5/10/2026 | 2:45:00 AM | 11027.232 | 11027.232 | 0 | 6582.398 | 6582.398 | 0 | 0 | 0 | 13186.015 | 13186.015 | 0
5/10/2026 | 3:00:00 AM | 11039.744 | 11039.744 | 0 | 6590.104 | 6590.104 | 0 | 0 | 0 | 13201.097 | 13201.097 | 0
5/10/2026 | 3:15:00 AM | 11052.552 | 11052.552 | 0 | 6597.915 | 6597.915 | 0 | 0 | 0 | 13216.516 | 13216.516 | 0
5/10/2026 | 3:30:00 AM | 11065.27 | 11065.27 | 0 | 6605.775 | 6605.775 | 0 | 0 | 0 | 13231.876 | 13231.876 | 0
5/10/2026 | 3:45:00 AM | 11078.231 | 11078.231 | 0 | 6613.627 | 6613.627 | 0 | 0 | 0 | 13247.475 | 13247.475 | 0
5/10/2026 | 4:00:00 AM | 11091.092 | 11091.092 | 0 | 6621.453 | 6621.453 | 0 | 0 | 0 | 13262.998 | 13262.998 | 0
5/10/2026 | 4:15:00 AM | 11103.728 | 11103.728 | 0 | 6629.13 | 6629.13 | 0 | 0 | 0 | 13278.237 | 13278.237 | 0
5/10/2026 | 4:30:00 AM | 11116.178 | 11116.178 | 0 | 6636.658 | 6636.658 | 0 | 0 | 0 | 13293.243 | 13293.243 | 0
5/10/2026 | 4:45:00 AM | 11128.752 | 11128.752 | 0 | 6644.301 | 6644.301 | 0 | 0 | 0 | 13308.449 | 13308.449 | 0
5/10/2026 | 5:00:00 AM | 11141.707 | 11141.707 | 0 | 6651.928 | 6651.928 | 0 | 0 | 0 | 13323.993 | 13323.993 | 0
5/10/2026 | 5:15:00 AM | 11154.822 | 11154.822 | 0 | 6659.691 | 6659.691 | 0 | 0 | 0 | 13339.737 | 13339.737 | 0
5/10/2026 | 5:30:00 AM | 11167.801 | 11167.801 | 0 | 6667.446 | 6667.446 | 0 | 0 | 0 | 13355.35 | 13355.35 | 0
5/10/2026 | 5:45:00 AM | 11180.795 | 11180.795 | 0 | 6675.181 | 6675.181 | 0 | 0 | 0 | 13370.979 | 13370.979 | 0
5/10/2026 | 6:00:00 AM | 11193.533 | 11193.533 | 0 | 6682.85 | 6682.85 | 0 | 0 | 0 | 13386.323 | 13386.323 | 0
5/10/2026 | 6:15:00 AM | 11206.385 | 11206.385 | 0 | 6690.587 | 6690.587 | 0 | 0 | 0 | 13401.79 | 13401.79 | 0
5/10/2026 | 6:30:00 AM | 11219.144 | 11219.144 | 0 | 6698.221 | 6698.221 | 0 | 0 | 0 | 13417.142 | 13417.142 | 0
5/10/2026 | 6:45:00 AM | 11231.86 | 11231.86 | 0 | 6705.919 | 6705.919 | 0 | 0 | 0 | 13432.489 | 13432.489 | 0
5/10/2026 | 7:00:00 AM | 11244.577 | 11244.577 | 0 | 6713.679 | 6713.679 | 0 | 0 | 0 | 13447.821 | 13447.821 | 0
5/10/2026 | 7:15:00 AM | 11257.359 | 11257.359 | 0 | 6721.464 | 6721.464 | 0 | 0 | 0 | 13463.218 | 13463.218 | 0
5/10/2026 | 7:30:00 AM | 11270.002 | 11270.002 | 0 | 6729.237 | 6729.237 | 0 | 0 | 0 | 13478.473 | 13478.473 | 0
5/10/2026 | 7:45:00 AM | 11282.989 | 11282.989 | 0 | 6737.118 | 6737.118 | 0 | 0 | 0 | 13494.127 | 13494.127 | 0
5/10/2026 | 8:00:00 AM | 11295.917 | 11295.917 | 0 | 6744.843 | 6744.843 | 0 | 0 | 0 | 13509.659 | 13509.659 | 0
5/10/2026 | 8:15:00 AM | 11308.724 | 11308.724 | 0 | 6752.582 | 6752.582 | 0 | 0 | 0 | 13525.091 | 13525.091 | 0
5/10/2026 | 8:30:00 AM | 11321.844 | 11321.844 | 0 | 6760.371 | 6760.371 | 0 | 0 | 0 | 13540.826 | 13540.826 | 0
5/10/2026 | 8:45:00 AM | 11334.436 | 11334.436 | 0 | 6767.791 | 6767.791 | 0 | 0 | 0 | 13555.989 | 13555.989 | 0
5/10/2026 | 9:00:00 AM | 11347.29 | 11347.29 | 0 | 6775.357 | 6775.357 | 0 | 0 | 0 | 13571.408 | 13571.408 | 0
5/10/2026 | 9:15:00 AM | 11360.385 | 11360.385 | 0 | 6782.884 | 6782.884 | 0 | 0 | 0 | 13587.059 | 13587.059 | 0
5/10/2026 | 9:30:00 AM | 11373.642 | 11373.642 | 0 | 6790.454 | 6790.454 | 0 | 0 | 0 | 13602.905 | 13602.905 | 0
5/10/2026 | 9:45:00 AM | 11386.893 | 11386.893 | 0 | 6797.999 | 6797.999 | 0 | 0 | 0 | 13618.732 | 13618.732 | 0
5/10/2026 | 10:00:00 AM | 11399.759 | 11399.759 | 0 | 6805.484 | 6805.484 | 0 | 0 | 0 | 13634.137 | 13634.137 | 0
5/10/2026 | 10:15:00 AM | 11412.756 | 11412.756 | 0 | 6812.988 | 6812.988 | 0 | 0 | 0 | 13649.639 | 13649.639 | 0
5/10/2026 | 10:30:00 AM | 11425.446 | 11425.446 | 0 | 6820.231 | 6820.231 | 0 | 0 | 0 | 13664.766 | 13664.766 | 0
5/10/2026 | 10:45:00 AM | 11438.165 | 11438.165 | 0 | 6827.603 | 6827.603 | 0 | 0 | 0 | 13679.964 | 13679.964 | 0
5/10/2026 | 11:00:00 AM | 11451.384 | 11451.384 | 0 | 6835.324 | 6835.324 | 0 | 0 | 0 | 13695.687 | 13695.687 | 0
5/10/2026 | 11:15:00 AM | 11464.198 | 11464.198 | 0 | 6842.711 | 6842.711 | 0 | 0 | 0 | 13710.937 | 13710.937 | 0
5/10/2026 | 11:30:00 AM | 11476.947 | 11476.947 | 0 | 6850.024 | 6850.024 | 0 | 0 | 0 | 13726.129 | 13726.129 | 0
5/10/2026 | 11:45:00 AM | 11490.303 | 11490.303 | 0 | 6857.488 | 6857.488 | 0 | 0 | 0 | 13741.977 | 13741.977 | 0
5/10/2026 | 12:00:00 PM | 11503.322 | 11503.322 | 0 | 6864.889 | 6864.889 | 0 | 0 | 0 | 13757.5 | 13757.5 | 0
5/10/2026 | 12:15:00 PM | 11516.067 | 11516.067 | 0 | 6872.248 | 6872.248 | 0 | 0 | 0 | 13772.768 | 13772.768 | 0
5/10/2026 | 12:30:00 PM | 11529.377 | 11529.377 | 0 | 6879.812 | 6879.812 | 0 | 0 | 0 | 13788.635 | 13788.635 | 0
5/10/2026 | 12:45:00 PM | 11542.408 | 11542.408 | 0 | 6887.069 | 6887.069 | 0 | 0 | 0 | 13804.188 | 13804.188 | 0
5/10/2026 | 1:00:00 PM | 11555.905 | 11555.905 | 0 | 6894.583 | 6894.583 | 0 | 0 | 0 | 13820.258 | 13820.258 | 0
5/10/2026 | 1:15:00 PM | 11569.54 | 11569.54 | 0 | 6902.143 | 6902.143 | 0 | 0 | 0 | 13836.46 | 13836.46 | 0
5/10/2026 | 1:30:00 PM | 11583.116 | 11583.116 | 0 | 6909.624 | 6909.624 | 0 | 0 | 0 | 13852.594 | 13852.594 | 0
5/10/2026 | 1:45:00 PM | 11596.691 | 11596.691 | 0 | 6917.258 | 6917.258 | 0 | 0 | 0 | 13868.749 | 13868.749 | 0
5/10/2026 | 2:00:00 PM | 11610.01 | 11610.01 | 0 | 6924.729 | 6924.729 | 0 | 0 | 0 | 13884.565 | 13884.565 | 0
5/10/2026 | 2:15:00 PM | 11623.01 | 11623.01 | 0 | 6932.046 | 6932.046 | 0 | 0 | 0 | 13900.037 | 13900.037 | 0
5/10/2026 | 2:30:00 PM | 11636.182 | 11636.182 | 0 | 6939.477 | 6939.477 | 0 | 0 | 0 | 13915.71 | 13915.71 | 0
5/10/2026 | 2:45:00 PM | 11649.495 | 11649.495 | 0 | 6947.04 | 6947.04 | 0 | 0 | 0 | 13931.547 | 13931.547 | 0
5/10/2026 | 3:00:00 PM | 11662.608 | 11662.608 | 0 | 6954.612 | 6954.612 | 0 | 0 | 0 | 13947.15 | 13947.15 | 0
5/10/2026 | 3:15:00 PM | 11675.876 | 11675.876 | 0 | 6962.307 | 6962.307 | 0 | 0 | 0 | 13962.923 | 13962.923 | 0
5/10/2026 | 3:30:00 PM | 11689.115 | 11689.115 | 0 | 6969.885 | 6969.885 | 0 | 0 | 0 | 13978.635 | 13978.635 | 0
5/10/2026 | 3:45:00 PM | 11702.572 | 11702.572 | 0 | 6977.508 | 6977.508 | 0 | 0 | 0 | 13994.632 | 13994.632 | 0
5/10/2026 | 4:00:00 PM | 11715.774 | 11715.774 | 0 | 6985.011 | 6985.011 | 0 | 0 | 0 | 14010.307 | 14010.307 | 0
5/10/2026 | 4:15:00 PM | 11729.065 | 11729.065 | 0 | 6992.645 | 6992.645 | 0 | 0 | 0 | 14026.106 | 14026.106 | 0
5/10/2026 | 4:30:00 PM | 11742.466 | 11742.466 | 0 | 7000.322 | 7000.322 | 0 | 0 | 0 | 14042.014 | 14042.014 | 0
5/10/2026 | 4:45:00 PM | 11755.646 | 11755.646 | 0 | 7007.739 | 7007.739 | 0 | 0 | 0 | 14057.674 | 14057.674 | 0
5/10/2026 | 5:00:00 PM | 11768.923 | 11768.923 | 0 | 7015.266 | 7015.266 | 0 | 0 | 0 | 14073.439 | 14073.439 | 0
5/10/2026 | 5:15:00 PM | 11782.426 | 11782.426 | 0 | 7022.874 | 7022.874 | 0 | 0 | 0 | 14089.44 | 14089.44 | 0
5/10/2026 | 5:30:00 PM | 11795.767 | 11795.767 | 0 | 7030.471 | 7030.471 | 0 | 0 | 0 | 14105.289 | 14105.289 | 0
5/10/2026 | 5:45:00 PM | 11809.003 | 11809.003 | 0 | 7038.112 | 7038.112 | 0 | 0 | 0 | 14121.015 | 14121.015 | 0
5/10/2026 | 6:00:00 PM | 11821.858 | 11821.858 | 0 | 7045.609 | 7045.609 | 0 | 0 | 0 | 14136.329 | 14136.329 | 0
5/10/2026 | 6:15:00 PM | 11834.469 | 11834.469 | 0 | 7052.933 | 7052.933 | 0 | 0 | 0 | 14151.335 | 14151.335 | 0
5/10/2026 | 6:30:00 PM | 11846.953 | 11846.953 | 0 | 7060.21 | 7060.21 | 0 | 0 | 0 | 14166.224 | 14166.224 | 0
5/10/2026 | 6:45:00 PM | 11859.465 | 11859.465 | 0 | 7067.553 | 7067.553 | 0 | 0 | 0 | 14181.178 | 14181.178 | 0
5/10/2026 | 7:00:00 PM | 11872.43 | 11872.43 | 0 | 7075.137 | 7075.137 | 0 | 0 | 0 | 14196.62 | 14196.62 | 0
5/10/2026 | 7:15:00 PM | 11885.215 | 11885.215 | 0 | 7082.726 | 7082.726 | 0 | 0 | 0 | 14211.921 | 14211.921 | 0
5/10/2026 | 7:30:00 PM | 11898.061 | 11898.061 | 0 | 7090.264 | 7090.264 | 0 | 0 | 0 | 14227.257 | 14227.257 | 0
5/10/2026 | 7:45:00 PM | 11910.987 | 11910.987 | 0 | 7097.905 | 7097.905 | 0 | 0 | 0 | 14242.75 | 14242.75 | 0
5/10/2026 | 8:00:00 PM | 11924.332 | 11924.332 | 0 | 7105.699 | 7105.699 | 0 | 0 | 0 | 14258.681 | 14258.681 | 0
5/10/2026 | 8:15:00 PM | 11936.885 | 11936.885 | 0 | 7113.124 | 7113.124 | 0 | 0 | 0 | 14273.765 | 14273.765 | 0
5/10/2026 | 8:30:00 PM | 11949.798 | 11949.798 | 0 | 7120.819 | 7120.819 | 0 | 0 | 0 | 14289.257 | 14289.257 | 0
5/10/2026 | 8:45:00 PM | 11962.996 | 11962.996 | 0 | 7128.488 | 7128.488 | 0 | 0 | 0 | 14305.051 | 14305.051 | 0
5/10/2026 | 9:00:00 PM | 11976.084 | 11976.084 | 0 | 7136.063 | 7136.063 | 0 | 0 | 0 | 14320.704 | 14320.704 | 0
5/10/2026 | 9:15:00 PM | 11989.613 | 11989.613 | 0 | 7143.951 | 7143.951 | 0 | 0 | 0 | 14336.871 | 14336.871 | 0
5/10/2026 | 9:30:00 PM | 12003.029 | 12003.029 | 0 | 7151.696 | 7151.696 | 0 | 0 | 0 | 14352.9 | 14352.9 | 0
5/10/2026 | 9:45:00 PM | 12015.917 | 12015.917 | 0 | 7159.268 | 7159.268 | 0 | 0 | 0 | 14368.383 | 14368.383 | 0
5/10/2026 | 10:00:00 PM | 12029.183 | 12029.183 | 0 | 7167.102 | 7167.102 | 0 | 0 | 0 | 14384.303 | 14384.303 | 0
5/10/2026 | 10:15:00 PM | 12042.328 | 12042.328 | 0 | 7174.74 | 7174.74 | 0 | 0 | 0 | 14400.036 | 14400.036 | 0
5/10/2026 | 10:30:00 PM | 12055.274 | 12055.274 | 0 | 7182.412 | 7182.412 | 0 | 0 | 0 | 14415.577 | 14415.577 | 0
5/10/2026 | 10:45:00 PM | 12068.539 | 12068.539 | 0 | 7190.344 | 7190.344 | 0 | 0 | 0 | 14431.497 | 14431.497 | 0
5/10/2026 | 11:00:00 PM | 12081.517 | 12081.517 | 0 | 7198.186 | 7198.186 | 0 | 0 | 0 | 14447.08 | 14447.08 | 0
5/10/2026 | 11:15:00 PM | 12094.143 | 12094.143 | 0 | 7205.894 | 7205.894 | 0 | 0 | 0 | 14462.292 | 14462.292 | 0
5/10/2026 | 11:30:00 PM | 12107.198 | 12107.198 | 0 | 7213.88 | 7213.88 | 0 | 0 | 0 | 14477.99 | 14477.99 | 0
5/10/2026 | 11:45:00 PM | 12119.95 | 12119.95 | 0 | 7221.618 | 7221.618 | 0 | 0 | 0 | 14493.364 | 14493.364 | 0
5/11/2026 | 12:00:00 AM | 12132.916 | 12132.916 | 0 | 7229.546 | 7229.546 | 0 | 0 | 0 | 14509 | 14509 | 0
5/11/2026 | 12:15:00 AM | 12145.744 | 12145.744 | 0 | 7237.194 | 7237.194 | 0 | 0 | 0 | 14524.379 | 14524.379 | 0
5/11/2026 | 12:30:00 AM | 12158.526 | 12158.526 | 0 | 7244.906 | 7244.906 | 0 | 0 | 0 | 14539.717 | 14539.717 | 0
5/11/2026 | 12:45:00 AM | 12171.546 | 12171.546 | 0 | 7252.766 | 7252.766 | 0 | 0 | 0 | 14555.375 | 14555.375 | 0
5/11/2026 | 1:00:00 AM | 12184.448 | 12184.448 | 0 | 7260.467 | 7260.467 | 0 | 0 | 0 | 14570.853 | 14570.853 | 0
5/11/2026 | 1:15:00 AM | 12197.171 | 12197.171 | 0 | 7268.097 | 7268.097 | 0 | 0 | 0 | 14586.131 | 14586.131 | 0
5/11/2026 | 1:30:00 AM | 12209.811 | 12209.811 | 0 | 7275.737 | 7275.737 | 0 | 0 | 0 | 14601.356 | 14601.356 | 0
5/11/2026 | 1:45:00 AM | 12222.726 | 12222.726 | 0 | 7283.502 | 7283.502 | 0 | 0 | 0 | 14616.878 | 14616.878 | 0
5/11/2026 | 2:00:00 AM | 12235.106 | 12235.106 | 0 | 7291.105 | 7291.105 | 0 | 0 | 0 | 14631.837 | 14631.837 | 0
5/11/2026 | 2:15:00 AM | 12248.089 | 12248.089 | 0 | 7299.021 | 7299.021 | 0 | 0 | 0 | 14647.457 | 14647.457 | 0
5/11/2026 | 2:30:00 AM | 12260.884 | 12260.884 | 0 | 7306.805 | 7306.805 | 0 | 0 | 0 | 14662.858 | 14662.858 | 0
5/11/2026 | 2:45:00 AM | 12273.431 | 12273.431 | 0 | 7314.493 | 7314.493 | 0 | 0 | 0 | 14678.013 | 14678.013 | 0
5/11/2026 | 3:00:00 AM | 12286.768 | 12286.768 | 0 | 7322.69 | 7322.69 | 0 | 0 | 0 | 14694.025 | 14694.025 | 0
5/11/2026 | 3:15:00 AM | 12299.254 | 12299.254 | 0 | 7330.377 | 7330.377 | 0 | 0 | 0 | 14709.081 | 14709.081 | 0
5/11/2026 | 3:30:00 AM | 12311.724 | 12311.724 | 0 | 7338.136 | 7338.136 | 0 | 0 | 0 | 14724.147 | 14724.147 | 0
5/11/2026 | 3:45:00 AM | 12324.083 | 12324.083 | 0 | 7345.724 | 7345.724 | 0 | 0 | 0 | 14739.055 | 14739.055 | 0
5/11/2026 | 4:00:00 AM | 12336.595 | 12336.595 | 0 | 7353.36 | 7353.36 | 0 | 0 | 0 | 14754.108 | 14754.108 | 0
5/11/2026 | 4:15:00 AM | 12349.297 | 12349.297 | 0 | 7361.2 | 7361.2 | 0 | 0 | 0 | 14769.423 | 14769.423 | 0
5/11/2026 | 4:30:00 AM | 12361.883 | 12361.883 | 0 | 7368.899 | 7368.899 | 0 | 0 | 0 | 14784.568 | 14784.568 | 0
5/11/2026 | 4:45:00 AM | 12374.583 | 12374.583 | 0 | 7376.562 | 7376.562 | 0 | 0 | 0 | 14799.845 | 14799.845 | 0
5/11/2026 | 5:00:00 AM | 12388.052 | 12388.052 | 0 | 7384.595 | 7384.595 | 0 | 0 | 0 | 14815.949 | 14815.949 | 0
5/11/2026 | 5:15:00 AM | 12401.226 | 12401.226 | 0 | 7392.346 | 7392.346 | 0 | 0 | 0 | 14831.669 | 14831.669 | 0
5/11/2026 | 5:30:00 AM | 12413.53 | 12413.53 | 0 | 7399.614 | 7399.614 | 0 | 0 | 0 | 14846.405 | 14846.405 | 0
5/11/2026 | 5:45:00 AM | 12426.277 | 12426.277 | 0 | 7407.171 | 7407.171 | 0 | 0 | 0 | 14861.653 | 14861.653 | 0
5/11/2026 | 6:00:00 AM | 12438.869 | 12438.869 | 0 | 7414.585 | 7414.585 | 0 | 0 | 0 | 14876.691 | 14876.691 | 0
5/11/2026 | 6:15:00 AM | 12451.335 | 12451.335 | 0 | 7421.953 | 7421.953 | 0 | 0 | 0 | 14891.594 | 14891.594 | 0
5/11/2026 | 6:30:00 AM | 12463.989 | 12463.989 | 0 | 7429.309 | 7429.309 | 0 | 0 | 0 | 14906.654 | 14906.654 | 0