## Configuration
Configuration
PEL Transfer, Version 2.8.15973
Recording status
Session name | MCC-EMNA
Report start | 5/1/2026 12:45:00 PM
Report end | 5/11/2026 6:15:00 AM
Report duration | 9 days, 17:30:00 (h:min:s)
Recording start | 5/1/2026 12:33:13 PM
Recording end | 5/11/2026 6:03:13 AM
Recording duration | 9 days, 17:30:00 (h:min:s)
1 s trend | No
200 ms trend | No
1 s harmonics | No
Aggregated harmonics | No
Instrument ID
PEL model | PEL113
PEL serial number | 108841AAH
PEL name | PEL113-108841AAH
PEL location | St Josephs
Firmware DSP version | 1.96
Firmware microprocessor version | 1.14
Hardware version
Measurement configuration and status
Aggregation period | 15 min
Electrical hook-up | 3-phase 4-wire Y
Nominal frequency | Auto
Primary nominal voltage | - - -
Secondary nominal voltage | - - -
Current sensor I1 | MA193/MA194/A193/A196
Current sensor I2 | MA193/MA194/A193/A196
Current sensor I3 | MA193/MA194/A193/A196
Line flexible sensor range | 400 A
Line flexible sensor wraps | 1

## Event Log
Event Log
Date | Time | Event
5/1/2026 | 12:33:14 PM | Start of recording

## Total Energies and Costs
Total Energies and Costs
Name | Value | Cost | Cost per kWh, kvarh or kVAh
Ep+ Total (Wh) | 20.803 MWh
Ep- Total (Wh) | 0 kWh
Ep Total (Wh) | 20.803 MWh
Eq/q1 Total (varh) | 4.966 Mvarh
Eq/q2 Total (varh) | 0 kvarh
Eq/q3 Total (varh) | 0 kvarh
Eq/q4 Total (varh) | 0 kvarh
Eq Total (varh) | 4.966 Mvarh
Es+ Total (VAh) | 23.172 MVAh
Es- Total (VAh) | 0 kVAh
Es Total (VAh) | 23.172 MVAh
Positive-sequence active energy Ep⁺ | 11.921 kWh
Unbalance active energy Epu | 20.733 MWh
Harmonic active energy EpH | 58.337 kWh
Reactive energy Net/Total Eq | 4.966 Mvarh
Distortion energy Net/Total Ed | 7.895 Mvarh
MAX 15 min Summary I1 | 281.1343 A |  |  | 5/7/2026 | 3:45:00 AM
MAX 15 min Summary I2 | 269.052 A |  |  | 5/9/2026 | 8:15:00 PM
MAX 15 min Summary I3 | 260.5414 A |  |  | 5/9/2026 | 8:15:00 PM
MAX 15 min Summary IN | 9.4842 A |  |  | 5/9/2026 | 8:15:00 PM
MAX 15 min Summary PFT+ | 0.948 |  |  | 5/3/2026 | 7:00:00 AM
MAX 15 min Summary PFT- |  |  |  | - - - | - - -
MAX 15 min Summary PT | 208.439 kW |  |  | 5/7/2026 | 3:45:00 AM
MAX 15 min Summary QT | 77.088 kvar |  |  | 5/7/2026 | 3:45:00 AM
MAX 15 min Summary ST | 227.162 kVA |  |  | 5/7/2026 | 3:45:00 AM

## Summary
Summary
Date | Time | V1 (15 min) | V2 (15 min) | V3 (15 min) | U12 (15 min) | U23 (15 min) | U31 (15 min) | I1 (15 min) | I2 (15 min) | I3 (15 min) | IN (15 min) | V1ᴄꜰ (15 min) | V2ᴄꜰ (15 min) | V3ᴄꜰ (15 min) | I1ᴄꜰ (15 min) | I2ᴄꜰ (15 min) | I3ᴄꜰ (15 min) | u₂ (15 min) | F (Hz) (15 min) | P1 (15 min) | P2 (15 min) | P3 (15 min) | PT (15 min) | P1- (15 min) | P2- (15 min) | P3- (15 min) | PT- (15 min) | P1+ (15 min) | P2+ (15 min) | P3+ (15 min) | PT+ (15 min) | Q1 (15 min) | Q2 (15 min) | Q3 (15 min) | QT (15 min) | Q1- (15 min) | Q2- (15 min) | Q3- (15 min) | QT- (15 min) | Q1+ (15 min) | Q2+ (15 min) | Q3+ (15 min) | QT+ (15 min) | S1 (15 min) | S2 (15 min) | S3 (15 min) | ST (15 min) | PF1- (15 min) | PF2- (15 min) | PF3- (15 min) | PFT- (15 min) | PF1+ (15 min) | PF2+ (15 min) | PF3+ (15 min) | PFT+ (15 min) | Cos φ1- (15 min) | Cos φ2- (15 min) | Cos φ3- (15 min) | Cos φT- (15 min) | Cos φ1+ (15 min) | Cos φ2+ (15 min) | Cos φ3+ (15 min) | Cos φT+ (15 min) | Tan Φ- (15 min) | Tan Φ+ (15 min) | V1ᴛʜᴅ (15 min) | V2ᴛʜᴅ (15 min) | V3ᴛʜᴅ (15 min) | U12ᴛʜᴅ (15 min) | U23ᴛʜᴅ (15 min) | U31ᴛʜᴅ (15 min) | I1ᴛʜᴅ (15 min) | I2ᴛʜᴅ (15 min) | I3ᴛʜᴅ (15 min) | INᴛʜᴅ (15 min) | S1- (15 min) | S2- (15 min) | S3- (15 min) | ST- (15 min) | S1+ (15 min) | S2+ (15 min) | S3+ (15 min) | ST+ (15 min) | i₂ (15 min) | N1 (15 min) | N2 (15 min) | N3 (15 min) | NT (15 min) | D1 (15 min) | D2 (15 min) | D3 (15 min) | DT (15 min) | Pᵳ1 (15 min) | Pᵳ2 (15 min) | Pᵳ3 (15 min) | PᵳT (15 min) | Pᵳ1+ (15 min) | Pᵳ2+ (15 min) | Pᵳ3+ (15 min) | PᵳT+ (15 min) | Pᵳ1- (15 min) | Pᵳ2- (15 min) | Pᵳ3- (15 min) | PᵳT- (15 min)
|  | V | V | V | V | V | V | A | A | A | A | [6 empty] | % | Hz | W | W | W | W | W | W | W | W | W | W | W | W | var | var | var | var | var | var | var | var | var | var | var | var | VA | VA | VA | VA | [18 empty] | % | % | % | % | % | % | % | % | % | % | VA | VA | VA | VA | VA | VA | VA | VA | % | var | var | var | var | var | var | var | var | W | W | W | W | W | W | W | W | W | W | W | W
5/1/2026 | 1:00:00 PM | 281.87 | 278.56 | 278.88 | 487.62 | 480.63 | 485.45 | 81.3451 | 70.5064 | 75.3748 | 2.0733 | 1.433 | 1.433 | 1.431 | 2.053 | 2.026 | 2.095 | Over-range | 60 | 20450 | 17112 | 17628 | 55191 | - - - | - - - | - - - | - - - | 20450 | 17112 | 17628 | 55191 | 2102 | 1360 | 4378 | 7840 | - - - | - - - | - - - | - - - | 2102 | 1360 | 4378 | 7840 | 22863 | 19592 | 20967 | 63422 | # # # | # # # | # # # | # # # | 0.895 | 0.873 | 0.841 | 0.87 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.987 | - - - | 0.142 | 1.68 | 1.66 | 1.74 | 1.58 | 1.69 | 1.72 | 49.05 | 55.2 | 57.93 | 0 | - - - | - - - | - - - | - - - | 22863 | 19592 | 20967 | 63422 | Over-range | 10213 | 9536 | 11346 | 31227 | 9994 | 9438 | 10468 | 30227 | 20389 | 17089 | 17577 | 55056 | 20389 | 17089 | 17577 | 55056 | - - - | - - - | - - - | - - -
5/1/2026 | 1:15:00 PM | 282.02 | 278.85 | 279.24 | 487.92 | 481.28 | 485.88 | 82.9431 | 72.2391 | 77.4264 | 2.0912 | 1.434 | 1.433 | 1.432 | 2.054 | 2.019 | 2.082 | Over-range | 60.01 | 20866 | 17540 | 18211 | 56617 | - - - | - - - | - - - | - - - | 20866 | 17540 | 18211 | 56617 | 2103 | 1526 | 4451 | 8080 | - - - | - - - | - - - | - - - | 2103 | 1526 | 4451 | 8080 | 23347 | 20109 | 21586 | 65042 | # # # | # # # | # # # | # # # | 0.894 | 0.872 | 0.844 | 0.871 | # # # | # # # | # # # | - - - | 0.995 | 0.996 | 0.971 | 0.988 | - - - | 0.143 | 1.7 | 1.67 | 1.76 | 1.6 | 1.7 | 1.74 | 49.37 | 55.5 | 57.36 | 0 | - - - | - - - | - - - | - - - | 23347 | 20109 | 21586 | 65042 | Over-range | 10467 | 9834 | 11583 | 32002 | 10253 | 9714 | 10694 | 30965 | 20810 | 17488 | 18171 | 56469 | 20810 | 17488 | 18171 | 56469 | - - - | - - - | - - - | - - -
5/1/2026 | 1:30:00 PM | 281.96 | 278.75 | 279.08 | 487.83 | 481.02 | 485.67 | 83.7652 | 72.8115 | 77.8833 | 2.1507 | 1.434 | 1.433 | 1.432 | 2.051 | 2.026 | 2.088 | Over-range | 60 | 21067 | 17675 | 18283 | 57025 | - - - | - - - | - - - | - - - | 21067 | 17675 | 18283 | 57025 | 2140 | 1489 | 4511 | 8140 | - - - | - - - | - - - | - - - | 2140 | 1489 | 4511 | 8140 | 23568 | 20258 | 21695 | 65522 | # # # | # # # | # # # | # # # | 0.894 | 0.873 | 0.843 | 0.87 | # # # | # # # | # # # | - - - | 0.995 | 0.996 | 0.971 | 0.987 | - - - | 0.143 | 1.72 | 1.68 | 1.77 | 1.61 | 1.71 | 1.76 | 49.31 | 55.42 | 57.49 | 0 | - - - | - - - | - - - | - - - | 23568 | 20258 | 21695 | 65522 | Over-range | 10560 | 9894 | 11676 | 32255 | 10341 | 9782 | 10769 | 31210 | 21000 | 17642 | 18239 | 56882 | 21000 | 17642 | 18239 | 56882 | - - - | - - - | - - - | - - -
5/1/2026 | 1:45:00 PM | 281.91 | 278.72 | 279.09 | 487.73 | 481.03 | 485.65 | 82.762 | 72.1073 | 77.3026 | 2.1373 | 1.433 | 1.433 | 1.431 | 2.046 | 2.007 | 2.071 | Over-range | 60.01 | 20850 | 17521 | 18214 | 56586 | - - - | - - - | - - - | - - - | 20850 | 17521 | 18214 | 56586 | 2047 | 1526 | 4433 | 8007 | - - - | - - - | - - - | - - - | 2047 | 1526 | 4433 | 8007 | 23270 | 20051 | 21526 | 64846 | # # # | # # # | # # # | # # # | 0.896 | 0.874 | 0.846 | 0.873 | # # # | # # # | # # # | - - - | 0.995 | 0.996 | 0.971 | 0.988 | - - - | 0.141 | 1.71 | 1.68 | 1.76 | 1.61 | 1.71 | 1.74 | 48.72 | 54.99 | 56.68 | 0 | - - - | - - - | - - - | - - - | 23270 | 20051 | 21526 | 64846 | Over-range | 10323 | 9744 | 11465 | 31653 | 10118 | 9624 | 10573 | 30623 | 20788 | 17485 | 18168 | 56441 | 20788 | 17485 | 18168 | 56441 | - - - | - - - | - - - | - - -
5/1/2026 | 2:00:00 PM | 281.91 | 278.68 | 279.01 | 487.74 | 480.9 | 485.58 | 84.9494 | 73.7134 | 79.0583 | 2.2003 | 1.433 | 1.434 | 1.431 | 2.055 | 2.025 | 2.09 | Over-range | 60 | 21357 | 17884 | 18544 | 57785 | - - - | - - - | - - - | - - - | 21357 | 17884 | 18544 | 57785 | 2145 | 1539 | 4602 | 8286 | - - - | - - - | - - - | - - - | 2145 | 1539 | 4602 | 8286 | 23909 | 20512 | 22027 | 66447 | # # # | # # # | # # # | # # # | 0.893 | 0.872 | 0.842 | 0.87 | # # # | # # # | # # # | - - - | 0.995 | 0.996 | 0.97 | 0.987 | - - - | 0.143 | 1.72 | 1.68 | 1.77 | 1.62 | 1.72 | 1.75 | 49.5 | 55.58 | 57.66 | 0 | - - - | - - - | - - - | - - - | 23909 | 20512 | 22027 | 66447 | Over-range | 10740 | 10043 | 11882 | 32791 | 10523 | 9924 | 10954 | 31727 | 21302 | 17851 | 18488 | 57641 | 21302 | 17851 | 18488 | 57641 | - - - | - - - | - - - | - - -
5/1/2026 | 2:15:00 PM | 282.18 | 279.07 | 279.38 | 488.28 | 481.61 | 486.09 | 82.9767 | 72.5034 | 77.4827 | 2.1179 | 1.433 | 1.433 | 1.431 | 2.037 | 2 | 2.061 | Over-range | 60.01 | 20969 | 17683 | 18337 | 56989 | - - - | - - - | - - - | - - - | 20969 | 17683 | 18337 | 56989 | 2069 | 1530 | 4408 | 8008 | - - - | - - - | - - - | - - - | 2069 | 1530 | 4408 | 8008 | 23353 | 20183 | 21597 | 65134 | # # # | # # # | # # # | # # # | 0.898 | 0.876 | 0.849 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.996 | 0.972 | 0.988 | - - - | 0.141 | 1.74 | 1.69 | 1.77 | 1.63 | 1.72 | 1.76 | 48.17 | 54.39 | 56.03 | 0 | - - - | - - - | - - - | - - - | 23353 | 20183 | 21597 | 65134 | Over-range | 10271 | 9727 | 11406 | 31523 | 10060 | 9606 | 10519 | 30489 | 20907 | 17641 | 18301 | 56849 | 20907 | 17641 | 18301 | 56849 | - - - | - - - | - - - | - - -
5/1/2026 | 2:30:00 PM | 282 | 278.79 | 279.14 | 487.9 | 481.12 | 485.77 | 85.9909 | 74.7256 | 80.2549 | 2.2168 | 1.433 | 1.434 | 1.432 | 2.05 | 2.016 | 2.08 | Over-range | 60 | 21664 | 18161 | 18902 | 58727 | - - - | - - - | - - - | - - - | 21664 | 18161 | 18902 | 58727 | 2129 | 1594 | 4640 | 8363 | - - - | - - - | - - - | - - - | 2129 | 1594 | 4640 | 8363 | 24213 | 20805 | 22374 | 67391 | # # # | # # # | # # # | # # # | 0.895 | 0.873 | 0.845 | 0.871 | # # # | # # # | # # # | - - - | 0.995 | 0.996 | 0.971 | 0.988 | - - - | 0.142 | 1.72 | 1.7 | 1.77 | 1.62 | 1.72 | 1.76 | 49.14 | 55.29 | 56.96 | 0 | - - - | - - - | - - - | - - - | 24213 | 20805 | 22374 | 67391 | Over-range | 10809 | 10147 | 11967 | 33047 | 10597 | 10021 | 11031 | 31971 | 21609 | 18113 | 18865 | 58587 | 21609 | 18113 | 18865 | 58587 | - - - | - - - | - - - | - - -
5/1/2026 | 2:45:00 PM | 282.05 | 278.88 | 279.12 | 488.06 | 481.17 | 485.74 | 84.5063 | 73.5002 | 78.4758 | 2.2064 | 1.432 | 1.433 | 1.431 | 2.037 | 2.012 | 2.074 | Over-range | 60 | 21330 | 17905 | 18497 | 57731 | - - - | - - - | - - - | - - - | 21330 | 17905 | 18497 | 57731 | 2119 | 1476 | 4530 | 8125 | - - - | - - - | - - - | - - - | 2119 | 1476 | 4530 | 8125 | 23776 | 20452 | 21857 | 66085 | # # # | # # # | # # # | # # # | 0.897 | 0.875 | 0.846 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.141 | 1.68 | 1.67 | 1.74 | 1.6 | 1.69 | 1.72 | 48.36 | 54.58 | 56.58 | 0 | - - - | - - - | - - - | - - - | 23776 | 20452 | 21857 | 66085 | Over-range | 10496 | 9882 | 11639 | 32145 | 10280 | 9771 | 10721 | 31102 | 21266 | 17883 | 18451 | 57600 | 21266 | 17883 | 18451 | 57600 | - - - | - - - | - - - | - - -
5/1/2026 | 3:00:00 PM | 281.99 | 278.95 | 279.18 | 488.03 | 481.36 | 485.71 | 85.7607 | 75.0498 | 79.7821 | 2.1477 | 1.433 | 1.433 | 1.431 | 2.035 | 2.016 | 2.07 | Over-range | 60.01 | 21613 | 18283 | 18843 | 58739 | - - - | - - - | - - - | - - - | 21613 | 18283 | 18843 | 58739 | 2208 | 1549 | 4521 | 8277 | - - - | - - - | - - - | - - - | 2208 | 1549 | 4521 | 8277 | 24143 | 20903 | 22243 | 67288 | # # # | # # # | # # # | # # # | 0.895 | 0.875 | 0.847 | 0.873 | # # # | # # # | # # # | - - - | 0.995 | 0.996 | 0.972 | 0.988 | - - - | 0.141 | 1.71 | 1.66 | 1.73 | 1.6 | 1.68 | 1.73 | 48.85 | 54.79 | 56.57 | 0 | - - - | - - - | - - - | - - - | 24143 | 20903 | 22243 | 67288 | Over-range | 10751 | 10129 | 11815 | 32811 | 10522 | 10010 | 10916 | 31750 | 21549 | 18249 | 18809 | 58607 | 21549 | 18249 | 18809 | 58607 | - - - | - - - | - - - | - - -
5/1/2026 | 3:15:00 PM | 282.2 | 279.17 | 279.28 | 488.48 | 481.61 | 485.94 | 86.2925 | 75.2748 | 79.7916 | 2.2399 | 1.433 | 1.433 | 1.432 | 2.035 | 2.025 | 2.083 | Over-range | 60.01 | 21772 | 18363 | 18807 | 58942 | - - - | - - - | - - - | - - - | 21772 | 18363 | 18807 | 58942 | 2262 | 1471 | 4593 | 8326 | - - - | - - - | - - - | - - - | 2262 | 1471 | 4593 | 8326 | 24312 | 20982 | 22253 | 67546 | # # # | # # # | # # # | # # # | 0.896 | 0.875 | 0.845 | 0.873 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.141 | 1.69 | 1.65 | 1.71 | 1.59 | 1.66 | 1.71 | 48.73 | 54.74 | 56.94 | 0 | - - - | - - - | - - - | - - - | 24312 | 20982 | 22253 | 67546 | Over-range | 10811 | 10147 | 11891 | 32977 | 10571 | 10040 | 10968 | 31908 | 21708 | 18338 | 18764 | 58810 | 21708 | 18338 | 18764 | 58810 | - - - | - - - | - - - | - - -
5/1/2026 | 3:30:00 PM | 282.16 | 279.09 | 279.2 | 488.4 | 481.43 | 485.83 | 84.7441 | 73.7998 | 78.403 | 2.1881 | 1.433 | 1.433 | 1.431 | 2.031 | 2.011 | 2.073 | Over-range | 60.01 | 21426 | 18023 | 18505 | 57954 | - - - | - - - | - - - | - - - | 21426 | 18023 | 18505 | 57954 | 2162 | 1420 | 4501 | 8083 | - - - | - - - | - - - | - - - | 2162 | 1420 | 4501 | 8083 | 23850 | 20548 | 21841 | 66239 | # # # | # # # | # # # | # # # | 0.898 | 0.877 | 0.847 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.14 | 1.67 | 1.63 | 1.71 | 1.57 | 1.65 | 1.7 | 47.93 | 54.18 | 56.36 | 0 | - - - | - - - | - - - | - - - | 23850 | 20548 | 21841 | 66239 | Over-range | 10465 | 9864 | 11596 | 32057 | 10239 | 9761 | 10687 | 31021 | 21376 | 17995 | 18451 | 57821 | 21376 | 17995 | 18451 | 57821 | - - - | - - - | - - - | - - -
5/1/2026 | 3:45:00 PM | 282.11 | 279.01 | 279.19 | 488.26 | 481.36 | 485.82 | 87.0455 | 75.8529 | 80.7277 | 2.2438 | 1.434 | 1.434 | 1.432 | 2.035 | 2.016 | 2.076 | Over-range | 60.01 | 21987 | 18517 | 19061 | 59566 | - - - | - - - | - - - | - - - | 21987 | 18517 | 19061 | 59566 | 2220 | 1515 | 4628 | 8363 | - - - | - - - | - - - | - - - | 2220 | 1515 | 4628 | 8363 | 24518 | 21134 | 22505 | 68157 | # # # | # # # | # # # | # # # | 0.897 | 0.876 | 0.847 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.14 | 1.69 | 1.64 | 1.73 | 1.58 | 1.67 | 1.72 | 48.49 | 54.42 | 56.53 | 0 | - - - | - - - | - - - | - - - | 24518 | 21134 | 22505 | 68157 | Over-range | 10843 | 10182 | 11961 | 33114 | 10613 | 10069 | 11029 | 32040 | 21922 | 18487 | 19017 | 59427 | 21922 | 18487 | 19017 | 59427 | - - - | - - - | - - - | - - -
5/1/2026 | 4:00:00 PM | 282.17 | 279.07 | 279.22 | 488.38 | 481.43 | 485.88 | 86.5234 | 75.4579 | 80.1562 | 2.2434 | 1.433 | 1.433 | 1.432 | 2.032 | 2.015 | 2.074 | Over-range | 59.99 | 21869 | 18432 | 18942 | 59243 | - - - | - - - | - - - | - - - | 21869 | 18432 | 18942 | 59243 | 2220 | 1493 | 4589 | 8302 | - - - | - - - | - - - | - - - | 2220 | 1493 | 4589 | 8302 | 24368 | 21021 | 22346 | 67735 | # # # | # # # | # # # | # # # | 0.898 | 0.877 | 0.848 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.14 | 1.68 | 1.65 | 1.71 | 1.58 | 1.66 | 1.7 | 48.26 | 54.31 | 56.34 | 0 | - - - | - - - | - - - | - - - | 24368 | 21021 | 22346 | 67735 | Over-range | 10742 | 10104 | 11851 | 32824 | 10510 | 9993 | 10926 | 31757 | 21816 | 18394 | 18895 | 59106 | 21816 | 18394 | 18895 | 59106 | - - - | - - - | - - - | - - -
5/1/2026 | 4:15:00 PM | 282.36 | 279.24 | 279.38 | 488.71 | 481.69 | 486.2 | 85.6127 | 74.483 | 79.3242 | 2.1958 | 1.433 | 1.433 | 1.431 | 2.032 | 2.008 | 2.072 | Over-range | 60.01 | 21681 | 18217 | 18768 | 58666 | - - - | - - - | - - - | - - - | 21681 | 18217 | 18768 | 58666 | 2155 | 1448 | 4551 | 8154 | - - - | - - - | - - - | - - - | 2155 | 1448 | 4551 | 8154 | 24116 | 20752 | 22118 | 66987 | # # # | # # # | # # # | # # # | 0.899 | 0.878 | 0.849 | 0.876 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.139 | 1.66 | 1.65 | 1.7 | 1.57 | 1.65 | 1.69 | 47.81 | 54.07 | 56.06 | 0 | - - - | - - - | - - - | - - - | 24116 | 20752 | 22118 | 66987 | Over-range | 10552 | 9938 | 11698 | 32319 | 10329 | 9831 | 10777 | 31274 | 21632 | 18174 | 18723 | 58529 | 21632 | 18174 | 18723 | 58529 | - - - | - - - | - - - | - - -
5/1/2026 | 4:30:00 PM | 282.41 | 279.47 | 279.56 | 488.92 | 482.14 | 486.32 | 86.7203 | 75.9419 | 80.1458 | 2.2228 | 1.435 | 1.435 | 1.433 | 2.028 | 2.02 | 2.073 | Over-range | 59.99 | 21937 | 18601 | 18983 | 59521 | - - - | - - - | - - - | - - - | 21937 | 18601 | 18983 | 59521 | 2300 | 1475 | 4549 | 8323 | - - - | - - - | - - - | - - - | 2300 | 1475 | 4549 | 8323 | 24454 | 21194 | 22377 | 68026 | # # # | # # # | # # # | # # # | 0.897 | 0.878 | 0.848 | 0.875 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.972 | 0.988 | - - - | 0.14 | 1.7 | 1.66 | 1.72 | 1.6 | 1.67 | 1.72 | 48.32 | 54.1 | 56.35 | 0 | - - - | - - - | - - - | - - - | 24454 | 21194 | 22377 | 68026 | Over-range | 10801 | 10156 | 11845 | 32924 | 10553 | 10048 | 10937 | 31855 | 21874 | 18574 | 18934 | 59381 | 21874 | 18574 | 18934 | 59381 | - - - | - - - | - - - | - - -
5/1/2026 | 4:45:00 PM | 282.59 | 279.64 | 279.76 | 489.22 | 482.47 | 486.65 | 85.2939 | 74.8398 | 79.0787 | 2.1807 | 1.434 | 1.434 | 1.432 | 2.02 | 2.001 | 2.057 | Over-range | 60.02 | 21628 | 18365 | 18793 | 58786 | - - - | - - - | - - - | - - - | 21628 | 18365 | 18793 | 58786 | 2216 | 1479 | 4441 | 8136 | - - - | - - - | - - - | - - - | 2216 | 1479 | 4441 | 8136 | 24042 | 20880 | 22072 | 66994 | # # # | # # # | # # # | # # # | 0.9 | 0.88 | 0.851 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.988 | - - - | 0.138 | 1.68 | 1.64 | 1.71 | 1.58 | 1.65 | 1.7 | 47.55 | 53.51 | 55.58 | 0 | - - - | - - - | - - - | - - - | 24042 | 20880 | 22072 | 66994 | Over-range | 10488 | 9929 | 11569 | 32109 | 10251 | 9818 | 10683 | 31061 | 21579 | 18331 | 18739 | 58648 | 21579 | 18331 | 18739 | 58648 | - - - | - - - | - - - | - - -
5/1/2026 | 5:00:00 PM | 282.41 | 279.34 | 279.42 | 488.86 | 481.83 | 486.23 | 87.5831 | 76.2352 | 80.8868 | 2.2577 | 1.434 | 1.434 | 1.432 | 2.031 | 2.02 | 2.082 | Over-range | 60.01 | 22162 | 18657 | 19111 | 59930 | - - - | - - - | - - - | - - - | 22162 | 18657 | 19111 | 59930 | 2276 | 1450 | 4656 | 8382 | - - - | - - - | - - - | - - - | 2276 | 1450 | 4656 | 8382 | 24698 | 21267 | 22572 | 68537 | # # # | # # # | # # # | # # # | 0.897 | 0.877 | 0.847 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.14 | 1.67 | 1.63 | 1.69 | 1.57 | 1.64 | 1.69 | 48.29 | 54.26 | 56.54 | 0 | - - - | - - - | - - - | - - - | 24698 | 21267 | 22572 | 68537 | Over-range | 10894 | 10205 | 12006 | 33238 | 10653 | 10101 | 11067 | 32164 | 22102 | 18611 | 19076 | 59788 | 22102 | 18611 | 19076 | 59788 | - - - | - - - | - - - | - - -
5/1/2026 | 5:15:00 PM | 282.75 | 279.83 | 279.85 | 489.58 | 482.69 | 486.84 | 86.2199 | 75.6783 | 79.6437 | 2.2479 | 1.434 | 1.433 | 1.433 | 2.02 | 2.013 | 2.066 | Over-range | 60.03 | 21873 | 18586 | 18927 | 59386 | - - - | - - - | - - - | - - - | 21873 | 18586 | 18927 | 59386 | 2291 | 1461 | 4499 | 8252 | - - - | - - - | - - - | - - - | 2291 | 1461 | 4499 | 8252 | 24332 | 21139 | 22251 | 67721 | # # # | # # # | # # # | # # # | 0.899 | 0.879 | 0.851 | 0.877 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.973 | 0.988 | - - - | 0.139 | 1.63 | 1.6 | 1.66 | 1.54 | 1.6 | 1.65 | 47.76 | 53.73 | 55.82 | 0 | - - - | - - - | - - - | - - - | 24332 | 21139 | 22251 | 67721 | Over-range | 10650 | 10068 | 11693 | 32534 | 10400 | 9961 | 10793 | 31470 | 21820 | 18542 | 18874 | 59237 | 21820 | 18542 | 18874 | 59237 | - - - | - - - | - - - | - - -
5/1/2026 | 5:30:00 PM | 282.52 | 279.61 | 279.7 | 489.14 | 482.41 | 486.53 | 85.3702 | 75.2144 | 79.217 | 2.1692 | 1.434 | 1.433 | 1.433 | 2.016 | 2.001 | 2.05 | Over-range | 60.01 | 21652 | 18466 | 18881 | 58999 | - - - | - - - | - - - | - - - | 21652 | 18466 | 18881 | 58999 | 2231 | 1511 | 4400 | 8143 | - - - | - - - | - - - | - - - | 2231 | 1511 | 4400 | 8143 | 24063 | 20987 | 22115 | 67164 | # # # | # # # | # # # | # # # | 0.9 | 0.88 | 0.854 | 0.878 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.974 | 0.988 | - - - | 0.138 | 1.61 | 1.58 | 1.64 | 1.52 | 1.58 | 1.63 | 47.54 | 53.49 | 55.18 | 0 | - - - | - - - | - - - | - - - | 24063 | 20987 | 22115 | 67164 | Over-range | 10488 | 9969 | 11509 | 32079 | 10248 | 9853 | 10635 | 31028 | 21594 | 18417 | 18836 | 58847 | 21594 | 18417 | 18836 | 58847 | - - - | - - - | - - - | - - -
5/1/2026 | 5:45:00 PM | 282.48 | 279.61 | 279.57 | 489.16 | 482.27 | 486.34 | 87.7004 | 77.1984 | 80.9068 | 2.2957 | 1.434 | 1.433 | 1.433 | 2.013 | 2.015 | 2.064 | Over-range | 60.01 | 22236 | 18971 | 19246 | 60453 | - - - | - - - | - - - | - - - | 22236 | 18971 | 19246 | 60453 | 2370 | 1491 | 4539 | 8400 | - - - | - - - | - - - | - - - | 2370 | 1491 | 4539 | 8400 | 24737 | 21556 | 22591 | 68885 | # # # | # # # | # # # | # # # | 0.899 | 0.88 | 0.852 | 0.878 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.973 | 0.988 | - - - | 0.139 | 1.61 | 1.58 | 1.63 | 1.52 | 1.58 | 1.62 | 47.82 | 53.56 | 55.65 | 0 | - - - | - - - | - - - | - - - | 24737 | 21556 | 22591 | 68885 | Over-range | 10834 | 10233 | 11827 | 33013 | 10571 | 10124 | 10922 | 31926 | 22172 | 18933 | 19185 | 60290 | 22172 | 18933 | 19185 | 60290 | - - - | - - - | - - - | - - -
5/1/2026 | 6:00:00 PM | 282.65 | 279.78 | 279.83 | 489.41 | 482.67 | 486.72 | 84.8702 | 74.7184 | 78.6802 | 2.2523 | 1.433 | 1.431 | 1.431 | 2.017 | 1.997 | 2.053 | Over-range | 60.01 | 21596 | 18402 | 18805 | 58804 | - - - | - - - | - - - | - - - | 21596 | 18402 | 18805 | 58804 | 2176 | 1471 | 4383 | 8031 | - - - | - - - | - - - | - - - | 2176 | 1471 | 4383 | 8031 | 23931 | 20860 | 21974 | 66766 | # # # | # # # | # # # | # # # | 0.902 | 0.882 | 0.856 | 0.881 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.974 | 0.989 | - - - | 0.137 | 1.49 | 1.47 | 1.48 | 1.42 | 1.45 | 1.48 | 46.95 | 52.96 | 54.72 | 0 | - - - | - - - | - - - | - - - | 23931 | 20860 | 21974 | 66766 | Over-range | 10300 | 9820 | 11361 | 31599 | 10067 | 9708 | 10481 | 30561 | 21522 | 18361 | 18745 | 58629 | 21522 | 18361 | 18745 | 58629 | - - - | - - - | - - - | - - -
5/1/2026 | 6:15:00 PM | 283.51 | 280.72 | 280.78 | 490.94 | 484.35 | 488.26 | 86.9424 | 76.0748 | 80.6161 | 2.2837 | 1.433 | 1.43 | 1.429 | 2.041 | 2.022 | 2.081 | Over-range | 60.03 | 22114 | 18700 | 19199 | 60013 | - - - | - - - | - - - | - - - | 22114 | 18700 | 19199 | 60013 | 2247 | 1526 | 4631 | 8403 | - - - | - - - | - - - | - - - | 2247 | 1526 | 4631 | 8403 | 24612 | 21327 | 22605 | 68544 | # # # | # # # | # # # | # # # | 0.899 | 0.877 | 0.849 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.14 | 1.44 | 1.41 | 1.4 | 1.38 | 1.37 | 1.4 | 48.24 | 54.57 | 56.29 | 0 | - - - | - - - | - - - | - - - | 24612 | 21327 | 22605 | 68544 | Over-range | 10795 | 10251 | 11929 | 33102 | 10558 | 10136 | 10994 | 32018 | 22033 | 18637 | 19130 | 59800 | 22033 | 18637 | 19130 | 59800 | - - - | - - - | - - - | - - -
5/1/2026 | 6:30:00 PM | 283.43 | 280.62 | 280.55 | 490.88 | 484.03 | 487.98 | 85.5165 | 74.6189 | 78.8666 | 2.2648 | 1.432 | 1.429 | 1.429 | 2.034 | 2.02 | 2.083 | Over-range | 60 | 21782 | 18358 | 18758 | 58898 | - - - | - - - | - - - | - - - | 21782 | 18358 | 18758 | 58898 | 2216 | 1386 | 4564 | 8166 | - - - | - - - | - - - | - - - | 2216 | 1386 | 4564 | 8166 | 24182 | 20897 | 22085 | 67164 | # # # | # # # | # # # | # # # | 0.901 | 0.878 | 0.849 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.139 | 1.43 | 1.42 | 1.42 | 1.39 | 1.39 | 1.4 | 47.54 | 54.11 | 56.1 | 0 | - - - | - - - | - - - | - - - | 24182 | 20897 | 22085 | 67164 | Over-range | 10492 | 9979 | 11649 | 32258 | 10255 | 9882 | 10717 | 31207 | 21693 | 18311 | 18690 | 58694 | 21693 | 18311 | 18690 | 58694 | - - - | - - - | - - - | - - -
5/1/2026 | 6:45:00 PM | 283.46 | 280.56 | 280.58 | 490.82 | 483.96 | 488.07 | 86.892 | 75.3622 | 80.3797 | 2.2226 | 1.433 | 1.43 | 1.429 | 2.046 | 2.026 | 2.093 | Over-range | 60 | 22094 | 18482 | 19048 | 59623 | - - - | - - - | - - - | - - - | 22094 | 18482 | 19048 | 59623 | 2219 | 1446 | 4727 | 8392 | - - - | - - - | - - - | - - - | 2219 | 1446 | 4727 | 8392 | 24585 | 21108 | 22517 | 68210 | # # # | # # # | # # # | # # # | 0.899 | 0.876 | 0.846 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.988 | - - - | 0.141 | 1.45 | 1.45 | 1.43 | 1.4 | 1.41 | 1.42 | 48.24 | 54.97 | 56.85 | 0 | - - - | - - - | - - - | - - - | 24585 | 21108 | 22517 | 68210 | Over-range | 10775 | 10194 | 12003 | 33116 | 10544 | 10090 | 11033 | 32035 | 22011 | 18418 | 18974 | 59402 | 22011 | 18418 | 18974 | 59402 | - - - | - - - | - - - | - - -
5/1/2026 | 7:00:00 PM | 283.55 | 280.66 | 280.59 | 491.03 | 484.04 | 488.13 | 87.9763 | 76.2185 | 81.0366 | 2.2484 | 1.432 | 1.429 | 1.428 | 2.048 | 2.036 | 2.106 | Over-range | 60 | 22373 | 18693 | 19157 | 60222 | - - - | - - - | - - - | - - - | 22373 | 18693 | 19157 | 60222 | 2309 | 1410 | 4808 | 8528 | - - - | - - - | - - - | - - - | 2309 | 1410 | 4808 | 8528 | 24906 | 21359 | 22708 | 68973 | # # # | # # # | # # # | # # # | 0.898 | 0.875 | 0.844 | 0.873 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.987 | - - - | 0.142 | 1.43 | 1.42 | 1.41 | 1.39 | 1.38 | 1.4 | 48.36 | 55.16 | 57.45 | 0 | - - - | - - - | - - - | - - - | 24906 | 21359 | 22708 | 68973 | Over-range | 10937 | 10331 | 12190 | 33612 | 10690 | 10235 | 11201 | 32512 | 22281 | 18640 | 19065 | 59987 | 22281 | 18640 | 19065 | 59987 | - - - | - - - | - - - | - - -
5/1/2026 | 7:15:00 PM | 283.54 | 280.74 | 280.7 | 491.05 | 484.27 | 488.2 | 86.089 | 74.9562 | 79.6759 | 2.2091 | 1.431 | 1.428 | 1.427 | 2.044 | 2.018 | 2.089 | Over-range | 60 | 21912 | 18399 | 18897 | 59208 | - - - | - - - | - - - | - - - | 21912 | 18399 | 18897 | 59208 | 2229 | 1450 | 4656 | 8336 | - - - | - - - | - - - | - - - | 2229 | 1450 | 4656 | 8336 | 24339 | 20987 | 22310 | 67636 | # # # | # # # | # # # | # # # | 0.9 | 0.877 | 0.847 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.141 | 1.41 | 1.38 | 1.37 | 1.36 | 1.34 | 1.36 | 47.8 | 54.65 | 56.68 | 0 | - - - | - - - | - - - | - - - | 24339 | 20987 | 22310 | 67636 | Over-range | 10586 | 10092 | 11853 | 32678 | 10348 | 9987 | 10900 | 31597 | 21816 | 18338 | 18820 | 58974 | 21816 | 18338 | 18820 | 58974 | - - - | - - - | - - - | - - -
5/1/2026 | 7:30:00 PM | 283.76 | 281.01 | 280.96 | 491.47 | 484.75 | 488.58 | 88.2955 | 76.812 | 81.322 | 2.2989 | 1.432 | 1.429 | 1.428 | 2.048 | 2.042 | 2.107 | Over-range | 60 | 22433 | 18848 | 19245 | 60526 | - - - | - - - | - - - | - - - | 22433 | 18848 | 19245 | 60526 | 2374 | 1463 | 4803 | 8640 | - - - | - - - | - - - | - - - | 2374 | 1463 | 4803 | 8640 | 25012 | 21554 | 22817 | 69383 | # # # | # # # | # # # | # # # | 0.897 | 0.875 | 0.843 | 0.872 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.97 | 0.987 | - - - | 0.143 | 1.42 | 1.39 | 1.36 | 1.36 | 1.34 | 1.36 | 48.74 | 55.37 | 57.58 | 0 | - - - | - - - | - - - | - - - | 25012 | 21554 | 22817 | 69383 | Over-range | 11056 | 10453 | 12253 | 33909 | 10798 | 10350 | 11272 | 32790 | 22334 | 18788 | 19158 | 60280 | 22334 | 18788 | 19158 | 60280 | - - - | - - - | - - - | - - -
5/1/2026 | 7:45:00 PM | 283.76 | 280.97 | 280.9 | 491.45 | 484.64 | 488.54 | 86.5992 | 75.2779 | 79.7172 | 2.2767 | 1.432 | 1.429 | 1.428 | 2.04 | 2.027 | 2.096 | Over-range | 60 | 22058 | 18508 | 18902 | 59467 | - - - | - - - | - - - | - - - | 22058 | 18508 | 18902 | 59467 | 2288 | 1402 | 4697 | 8387 | - - - | - - - | - - - | - - - | 2288 | 1402 | 4697 | 8387 | 24512 | 21104 | 22347 | 67964 | # # # | # # # | # # # | # # # | 0.9 | 0.877 | 0.846 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.987 | - - - | 0.141 | 1.41 | 1.4 | 1.37 | 1.37 | 1.35 | 1.36 | 47.85 | 54.64 | 56.95 | 0 | - - - | - - - | - - - | - - - | 24512 | 21104 | 22347 | 67964 | Over-range | 10680 | 10138 | 11915 | 32886 | 10432 | 10040 | 10950 | 31798 | 21971 | 18452 | 18806 | 59228 | 21971 | 18452 | 18806 | 59228 | - - - | - - - | - - - | - - -
5/1/2026 | 8:00:00 PM | 283.84 | 281.07 | 281.01 | 491.6 | 484.83 | 488.71 | 88.7232 | 77.1352 | 81.7262 | 2.3081 | 1.432 | 1.429 | 1.428 | 2.051 | 2.043 | 2.11 | Over-range | 60 | 22542 | 18917 | 19319 | 60778 | - - - | - - - | - - - | - - - | 22542 | 18917 | 19319 | 60778 | 2393 | 1469 | 4843 | 8705 | - - - | - - - | - - - | - - - | 2393 | 1469 | 4843 | 8705 | 25146 | 21651 | 22936 | 69733 | # # # | # # # | # # # | # # # | 0.896 | 0.874 | 0.842 | 0.872 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.97 | 0.987 | - - - | 0.143 | 1.42 | 1.38 | 1.36 | 1.36 | 1.34 | 1.36 | 48.87 | 55.58 | 57.84 | 0 | - - - | - - - | - - - | - - - | 25146 | 21651 | 22936 | 69733 | Over-range | 11136 | 10529 | 12358 | 34174 | 10876 | 10426 | 11369 | 33046 | 22448 | 18846 | 19233 | 60527 | 22448 | 18846 | 19233 | 60527 | - - - | - - - | - - - | - - -
5/1/2026 | 8:15:00 PM | 283.94 | 281.17 | 281.03 | 491.82 | 484.92 | 488.8 | 87.9128 | 76.22 | 80.6186 | 2.3144 | 1.432 | 1.429 | 1.428 | 2.047 | 2.045 | 2.114 | Over-range | 60 | 22372 | 18721 | 19057 | 60150 | - - - | - - - | - - - | - - - | 22372 | 18721 | 19057 | 60150 | 2372 | 1365 | 4813 | 8549 | - - - | - - - | - - - | - - - | 2372 | 1365 | 4813 | 8549 | 24912 | 21392 | 22618 | 68922 | # # # | # # # | # # # | # # # | 0.898 | 0.875 | 0.843 | 0.873 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.969 | 0.987 | - - - | 0.142 | 1.4 | 1.39 | 1.36 | 1.36 | 1.34 | 1.36 | 48.35 | 55.22 | 57.64 | 0 | - - - | - - - | - - - | - - - | 24912 | 21392 | 22618 | 68922 | Over-range | 10949 | 10346 | 12177 | 33630 | 10688 | 10256 | 11185 | 32525 | 22274 | 18650 | 18983 | 59907 | 22274 | 18650 | 18983 | 59907 | - - - | - - - | - - - | - - -
5/1/2026 | 8:30:00 PM | 283.76 | 280.97 | 280.87 | 491.48 | 484.61 | 488.52 | 87.4572 | 75.9002 | 80.3924 | 2.3002 | 1.433 | 1.43 | 1.428 | 2.041 | 2.031 | 2.102 | Over-range | 60 | 22281 | 18654 | 19041 | 59976 | - - - | - - - | - - - | - - - | 22281 | 18654 | 19041 | 59976 | 2319 | 1388 | 4768 | 8475 | - - - | - - - | - - - | - - - | 2319 | 1388 | 4768 | 8475 | 24761 | 21283 | 22540 | 68584 | # # # | # # # | # # # | # # # | 0.9 | 0.876 | 0.845 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.987 | - - - | 0.141 | 1.43 | 1.4 | 1.38 | 1.37 | 1.36 | 1.38 | 47.88 | 54.87 | 57.1 | 0 | - - - | - - - | - - - | - - - | 24761 | 21283 | 22540 | 68584 | Over-range | 10791 | 10243 | 12055 | 33247 | 10539 | 10148 | 11071 | 32149 | 22189 | 18579 | 18963 | 59731 | 22189 | 18579 | 18963 | 59731 | - - - | - - - | - - - | - - -
5/1/2026 | 8:45:00 PM | 283.54 | 280.85 | 280.63 | 491.23 | 484.32 | 488.05 | 89.0084 | 77.4759 | 81.273 | 2.3525 | 1.433 | 1.43 | 1.428 | 2.035 | 2.047 | 2.11 | Over-range | 60 | 22622 | 19031 | 19194 | 60848 | - - - | - - - | - - - | - - - | 22622 | 19031 | 19194 | 60848 | 2492 | 1354 | 4820 | 8666 | - - - | - - - | - - - | - - - | 2492 | 1354 | 4820 | 8666 | 25197 | 21727 | 22777 | 69702 | # # # | # # # | # # # | # # # | 0.898 | 0.876 | 0.843 | 0.873 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.97 | 0.987 | - - - | 0.142 | 1.43 | 1.42 | 1.37 | 1.38 | 1.36 | 1.38 | 48.36 | 55.1 | 57.72 | 0 | - - - | - - - | - - - | - - - | 25197 | 21727 | 22777 | 69702 | Over-range | 11089 | 10480 | 12259 | 33985 | 10805 | 10392 | 11272 | 32862 | 22518 | 18959 | 19120 | 60598 | 22518 | 18959 | 19120 | 60598 | - - - | - - - | - - - | - - -
5/1/2026 | 9:00:00 PM | 284.06 | 281.28 | 281.13 | 492.03 | 485.09 | 488.98 | 86.9852 | 75.4145 | 79.7776 | 2.2837 | 1.433 | 1.43 | 1.428 | 2.038 | 2.025 | 2.1 | Over-range | 59.99 | 22220 | 18584 | 18927 | 59730 | - - - | - - - | - - - | - - - | 22220 | 18584 | 18927 | 59730 | 2299 | 1329 | 4740 | 8368 | - - - | - - - | - - - | - - - | 2299 | 1329 | 4740 | 8368 | 24644 | 21164 | 22382 | 68190 | # # # | # # # | # # # | # # # | 0.902 | 0.878 | 0.846 | 0.876 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.987 | - - - | 0.14 | 1.44 | 1.43 | 1.39 | 1.39 | 1.38 | 1.4 | 47.35 | 54.42 | 56.89 | 0 | - - - | - - - | - - - | - - - | 24644 | 21164 | 22382 | 68190 | Over-range | 10648 | 10122 | 11940 | 32875 | 10397 | 10034 | 10958 | 31793 | 22123 | 18526 | 18841 | 59490 | 22123 | 18526 | 18841 | 59490 | - - - | - - - | - - - | - - -
5/1/2026 | 9:15:00 PM | 284.1 | 281.29 | 281.25 | 492.03 | 485.22 | 489.15 | 89.0524 | 77.3038 | 81.9462 | 2.3409 | 1.433 | 1.43 | 1.428 | 2.047 | 2.037 | 2.106 | Over-range | 60 | 22695 | 19011 | 19424 | 61130 | - - - | - - - | - - - | - - - | 22695 | 19011 | 19424 | 61130 | 2370 | 1445 | 4870 | 8685 | - - - | - - - | - - - | - - - | 2370 | 1445 | 4870 | 8685 | 25261 | 21714 | 23017 | 69991 | # # # | # # # | # # # | # # # | 0.898 | 0.875 | 0.844 | 0.873 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.987 | - - - | 0.142 | 1.46 | 1.44 | 1.4 | 1.41 | 1.39 | 1.41 | 48.33 | 55.15 | 57.41 | 0 | - - - | - - - | - - - | - - - | 25261 | 21714 | 23017 | 69991 | Over-range | 11085 | 10489 | 12344 | 34074 | 10828 | 10389 | 11343 | 32949 | 22601 | 18938 | 19336 | 60875 | 22601 | 18938 | 19336 | 60875 | - - - | - - - | - - - | - - -
5/1/2026 | 9:30:00 PM | 284.48 | 281.8 | 281.71 | 492.8 | 486.11 | 489.83 | 88.1954 | 77.0342 | 81.1061 | 2.3103 | 1.433 | 1.43 | 1.428 | 2.035 | 2.027 | 2.094 | Over-range | 59.99 | 22543 | 19021 | 19327 | 60891 | - - - | - - - | - - - | - - - | 22543 | 19021 | 19327 | 60891 | 2393 | 1433 | 4747 | 8573 | - - - | - - - | - - - | - - - | 2393 | 1433 | 4747 | 8573 | 25042 | 21669 | 22812 | 69523 | # # # | # # # | # # # | # # # | 0.9 | 0.878 | 0.847 | 0.876 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.971 | 0.988 | - - - | 0.141 | 1.47 | 1.45 | 1.42 | 1.42 | 1.4 | 1.42 | 47.75 | 54.51 | 56.76 | 0 | - - - | - - - | - - - | - - - | 25042 | 21669 | 22812 | 69523 | Over-range | 10896 | 10377 | 12114 | 33538 | 10630 | 10278 | 11145 | 32423 | 22452 | 18951 | 19240 | 60643 | 22452 | 18951 | 19240 | 60643 | - - - | - - - | - - - | - - -
5/1/2026 | 9:45:00 PM | 284.75 | 282.08 | 281.96 | 493.28 | 486.56 | 490.28 | 88.6057 | 77.3491 | 81.5025 | 2.326 | 1.433 | 1.43 | 1.428 | 2.035 | 2.025 | 2.093 | Over-range | 60.01 | 22690 | 19136 | 19458 | 61284 | - - - | - - - | - - - | - - - | 22690 | 19136 | 19458 | 61284 | 2385 | 1431 | 4774 | 8590 | - - - | - - - | - - - | - - - | 2385 | 1431 | 4774 | 8590 | 25184 | 21782 | 22946 | 69913 | # # # | # # # | # # # | # # # | 0.901 | 0.878 | 0.848 | 0.877 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.971 | 0.988 | - - - | 0.14 | 1.48 | 1.45 | 1.43 | 1.43 | 1.4 | 1.43 | 47.57 | 54.28 | 56.56 | 0 | - - - | - - - | - - - | - - - | 25184 | 21782 | 22946 | 69913 | Over-range | 10920 | 10402 | 12156 | 33630 | 10656 | 10303 | 11179 | 32515 | 22590 | 19074 | 19370 | 61034 | 22590 | 19074 | 19370 | 61034 | - - - | - - - | - - - | - - -
5/1/2026 | 10:00:00 PM | 285.05 | 282.34 | 282.19 | 493.79 | 486.96 | 490.72 | 89.7076 | 78.0986 | 82.1467 | 2.3539 | 1.434 | 1.43 | 1.429 | 2.035 | 2.039 | 2.106 | Over-range | 60.01 | 22980 | 19322 | 19580 | 61882 | - - - | - - - | - - - | - - - | 22980 | 19322 | 19580 | 61882 | 2461 | 1392 | 4873 | 8726 | - - - | - - - | - - - | - - - | 2461 | 1392 | 4873 | 8726 | 25534 | 22021 | 23153 | 70708 | # # # | # # # | # # # | # # # | 0.9 | 0.877 | 0.846 | 0.875 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.97 | 0.987 | - - - | 0.141 | 1.5 | 1.45 | 1.44 | 1.44 | 1.42 | 1.45 | 47.8 | 54.65 | 57.02 | 0 | - - - | - - - | - - - | - - - | 25534 | 22021 | 23153 | 70708 | Over-range | 11123 | 10561 | 12352 | 34195 | 10847 | 10469 | 11350 | 33063 | 22887 | 19260 | 19484 | 61630 | 22887 | 19260 | 19484 | 61630 | - - - | - - - | - - - | - - -
5/1/2026 | 10:15:00 PM | 285.04 | 282.21 | 282.16 | 493.66 | 486.78 | 490.75 | 87.6662 | 76.0592 | 80.7142 | 2.2844 | 1.433 | 1.43 | 1.428 | 2.04 | 2.018 | 2.094 | Over-range | 60 | 22511 | 18820 | 19278 | 60610 | - - - | - - - | - - - | - - - | 22511 | 18820 | 19278 | 60610 | 2274 | 1381 | 4797 | 8451 | - - - | - - - | - - - | - - - | 2274 | 1381 | 4797 | 8451 | 24927 | 21419 | 22731 | 69077 | # # # | # # # | # # # | # # # | 0.903 | 0.879 | 0.848 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.988 | - - - | 0.139 | 1.48 | 1.47 | 1.44 | 1.43 | 1.41 | 1.44 | 47.02 | 54.23 | 56.3 | 0 | - - - | - - - | - - - | - - - | 24927 | 21419 | 22731 | 69077 | Over-range | 10694 | 10221 | 12036 | 33117 | 10449 | 10127 | 11039 | 32020 | 22398 | 18754 | 19210 | 60362 | 22398 | 18754 | 19210 | 60362 | - - - | - - - | - - - | - - -
5/1/2026 | 10:30:00 PM | 284.45 | 281.65 | 281.5 | 492.7 | 485.72 | 489.63 | 90.2213 | 78.2247 | 82.5718 | 2.3321 | 1.434 | 1.43 | 1.428 | 2.039 | 2.041 | 2.112 | Over-range | 60.01 | 23075 | 19298 | 19613 | 61986 | - - - | - - - | - - - | - - - | 23075 | 19298 | 19613 | 61986 | 2445 | 1358 | 4933 | 8736 | - - - | - - - | - - - | - - - | 2445 | 1358 | 4933 | 8736 | 25626 | 22002 | 23215 | 70842 | # # # | # # # | # # # | # # # | 0.901 | 0.877 | 0.845 | 0.875 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.97 | 0.987 | - - - | 0.141 | 1.51 | 1.46 | 1.45 | 1.44 | 1.42 | 1.46 | 47.7 | 54.8 | 57.11 | 0 | - - - | - - - | - - - | - - - | 25626 | 22002 | 23215 | 70842 | Over-range | 11137 | 10565 | 12416 | 34285 | 10865 | 10478 | 11394 | 33154 | 22985 | 19225 | 19522 | 61732 | 22985 | 19225 | 19522 | 61732 | - - - | - - - | - - - | - - -
5/1/2026 | 10:45:00 PM | 284.44 | 281.52 | 281.45 | 492.56 | 485.51 | 489.64 | 89.1003 | 76.9122 | 81.9658 | 2.2634 | 1.434 | 1.43 | 1.428 | 2.041 | 2.023 | 2.101 | Over-range | 60 | 22846 | 18981 | 19513 | 61340 | - - - | - - - | - - - | - - - | 22846 | 18981 | 19513 | 61340 | 2272 | 1361 | 4912 | 8545 | - - - | - - - | - - - | - - - | 2272 | 1361 | 4912 | 8545 | 25292 | 21613 | 23031 | 69936 | # # # | # # # | # # # | # # # | 0.903 | 0.878 | 0.847 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.969 | 0.987 | - - - | 0.139 | 1.51 | 1.45 | 1.46 | 1.44 | 1.43 | 1.46 | 47.04 | 54.41 | 56.36 | 0 | - - - | - - - | - - - | - - - | 25292 | 21613 | 23031 | 69936 | Over-range | 10840 | 10333 | 12227 | 33572 | 10599 | 10243 | 11196 | 32466 | 22741 | 18913 | 19438 | 61093 | 22741 | 18913 | 19438 | 61093 | - - - | - - - | - - - | - - -
5/1/2026 | 11:00:00 PM | 284.83 | 281.87 | 281.8 | 493.22 | 486.09 | 490.3 | 90.2899 | 77.7519 | 83.0753 | 2.2629 | 1.434 | 1.43 | 1.428 | 2.041 | 2.022 | 2.103 | Over-range | 60 | 23201 | 19234 | 19807 | 62243 | - - - | - - - | - - - | - - - | 23201 | 19234 | 19807 | 62243 | 2280 | 1363 | 4989 | 8632 | - - - | - - - | - - - | - - - | 2280 | 1363 | 4989 | 8632 | 25668 | 21879 | 23371 | 70918 | # # # | # # # | # # # | # # # | 0.904 | 0.879 | 0.848 | 0.878 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.969 | 0.987 | - - - | 0.139 | 1.52 | 1.48 | 1.47 | 1.46 | 1.44 | 1.47 | 46.87 | 54.18 | 56.33 | 0 | - - - | - - - | - - - | - - - | 25668 | 21879 | 23371 | 70918 | Over-range | 10968 | 10425 | 12399 | 33971 | 10729 | 10336 | 11351 | 32856 | 23109 | 19165 | 19713 | 61988 | 23109 | 19165 | 19713 | 61988 | - - - | - - - | - - - | - - -
5/1/2026 | 11:15:00 PM | 284.89 | 281.94 | 281.79 | 493.37 | 486.13 | 490.32 | 91.5884 | 78.8189 | 83.7893 | 2.3034 | 1.435 | 1.431 | 1.429 | 2.037 | 2.034 | 2.112 | Over-range | 59.99 | 23528 | 19500 | 19942 | 62970 | - - - | - - - | - - - | - - - | 23528 | 19500 | 19942 | 62970 | 2398 | 1316 | 5076 | 8789 | - - - | - - - | - - - | - - - | 2398 | 1316 | 5076 | 8789 | 26056 | 22193 | 23584 | 71832 | # # # | # # # | # # # | # # # | 0.903 | 0.879 | 0.846 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.969 | 0.987 | - - - | 0.14 | 1.55 | 1.51 | 1.5 | 1.48 | 1.48 | 1.51 | 47.07 | 54.4 | 56.74 | 0 | - - - | - - - | - - - | - - - | 26056 | 22193 | 23584 | 71832 | Over-range | 11186 | 10595 | 12585 | 34551 | 10926 | 10512 | 11516 | 33414 | 23434 | 19433 | 19849 | 62716 | 23434 | 19433 | 19849 | 62716 | - - - | - - - | - - - | - - -
5/1/2026 | 11:30:00 PM | 285.26 | 282.27 | 282.15 | 493.99 | 486.72 | 490.98 | 89.4789 | 77.0028 | 82.1653 | 2.2266 | 1.434 | 1.43 | 1.428 | 2.033 | 2.013 | 2.096 | Over-range | 60 | 23090 | 19118 | 19669 | 61876 | - - - | - - - | - - - | - - - | 23090 | 19118 | 19669 | 61876 | 2241 | 1299 | 4939 | 8480 | - - - | - - - | - - - | - - - | 2241 | 1299 | 4939 | 8480 | 25470 | 21694 | 23143 | 70306 | # # # | # # # | # # # | # # # | 0.907 | 0.881 | 0.85 | 0.88 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.97 | 0.988 | - - - | 0.137 | 1.53 | 1.5 | 1.49 | 1.47 | 1.47 | 1.49 | 46.1 | 53.62 | 55.69 | 0 | - - - | - - - | - - - | - - - | 25470 | 21694 | 23143 | 70306 | Over-range | 10739 | 10251 | 12189 | 33363 | 10502 | 10168 | 11143 | 32267 | 22993 | 19058 | 19582 | 61632 | 22993 | 19058 | 19582 | 61632 | - - - | - - - | - - - | - - -
5/1/2026 | 11:45:00 PM | 285.68 | 282.75 | 282.53 | 494.81 | 487.46 | 491.61 | 92.7015 | 79.8024 | 84.466 | 2.2887 | 1.435 | 1.431 | 1.43 | 2.029 | 2.037 | 2.113 | Over-range | 60 | 23905 | 19829 | 20181 | 63916 | - - - | - - - | - - - | - - - | 23905 | 19829 | 20181 | 63916 | 2488 | 1271 | 5130 | 8889 | - - - | - - - | - - - | - - - | 2488 | 1271 | 5130 | 8889 | 26450 | 22538 | 23840 | 72827 | # # # | # # # | # # # | # # # | 0.904 | 0.88 | 0.847 | 0.878 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.969 | 0.987 | - - - | 0.139 | 1.57 | 1.53 | 1.54 | 1.51 | 1.5 | 1.54 | 46.8 | 54.12 | 56.5 | 0 | - - - | - - - | - - - | - - - | 26450 | 22538 | 23840 | 72827 | Over-range | 11313 | 10710 | 12688 | 34899 | 11036 | 10634 | 11604 | 33748 | 23809 | 19757 | 20096 | 63662 | 23809 | 19757 | 20096 | 63662 | - - - | - - - | - - - | - - -
5/2/2026 | 12:00:00 AM | 285.67 | 282.83 | 282.66 | 494.81 | 487.71 | 491.71 | 91.113 | 79.2331 | 83.4494 | 2.3289 | 1.434 | 1.43 | 1.428 | 2.014 | 2.006 | 2.081 | Over-range | 60 | 23560 | 19768 | 20103 | 63431 | - - - | - - - | - - - | - - - | 23560 | 19768 | 20103 | 63431 | 2398 | 1333 | 4900 | 8631 | - - - | - - - | - - - | - - - | 2398 | 1333 | 4900 | 8631 | 25963 | 22358 | 23540 | 71860 | # # # | # # # | # # # | # # # | 0.908 | 0.884 | 0.854 | 0.883 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.971 | 0.988 | - - - | 0.136 | 1.56 | 1.52 | 1.51 | 1.49 | 1.48 | 1.52 | 45.67 | 52.8 | 54.88 | 0 | - - - | - - - | - - - | - - - | 25963 | 22358 | 23540 | 71860 | Over-range | 10896 | 10441 | 12241 | 33750 | 10629 | 10356 | 11217 | 32628 | 23461 | 19699 | 20034 | 63195 | 23461 | 19699 | 20034 | 63195 | - - - | - - - | - - - | - - -
5/2/2026 | 12:15:00 AM | 285.9 | 282.95 | 282.75 | 495.15 | 487.81 | 492 | 93.7406 | 80.4969 | 85.6585 | 2.4274 | 1.433 | 1.429 | 1.427 | 2.039 | 2.037 | 2.118 | Over-range | 60.01 | 24182 | 20008 | 20475 | 64665 | - - - | - - - | - - - | - - - | 24182 | 20008 | 20475 | 64665 | 2407 | 1321 | 5216 | 8943 | - - - | - - - | - - - | - - - | 2407 | 1321 | 5216 | 8943 | 26762 | 22747 | 24192 | 73701 | # # # | # # # | # # # | # # # | 0.904 | 0.88 | 0.846 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.969 | 0.987 | - - - | 0.138 | 1.55 | 1.52 | 1.5 | 1.49 | 1.48 | 1.51 | 46.93 | 54.1 | 56.45 | 0 | - - - | - - - | - - - | - - - | 26762 | 22747 | 24192 | 73701 | Over-range | 11456 | 10819 | 12879 | 35343 | 11200 | 10737 | 11775 | 34192 | 24080 | 19940 | 20397 | 64417 | 24080 | 19940 | 20397 | 64417 | - - - | - - - | - - - | - - -
5/2/2026 | 12:30:00 AM | 286.09 | 283.05 | 282.93 | 495.4 | 488.03 | 492.38 | 90.6036 | 77.2251 | 82.8007 | 2.3575 | 1.432 | 1.428 | 1.426 | 2.058 | 2.046 | 2.136 | Over-range | 59.99 | 23337 | 19122 | 19680 | 62139 | - - - | - - - | - - - | - - - | 23337 | 19122 | 19680 | 62139 | 2274 | 1247 | 5153 | 8674 | - - - | - - - | - - - | - - - | 2274 | 1247 | 5153 | 8674 | 25869 | 21819 | 23389 | 71076 | # # # | # # # | # # # | # # # | 0.902 | 0.876 | 0.841 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.967 | 0.987 | - - - | 0.14 | 1.56 | 1.53 | 1.52 | 1.49 | 1.5 | 1.52 | 47.38 | 54.96 | 57.42 | 0 | - - - | - - - | - - - | - - - | 25869 | 21819 | 23389 | 71076 | Over-range | 11151 | 10504 | 12632 | 34486 | 10916 | 10430 | 11532 | 33377 | 23234 | 19069 | 19592 | 61896 | 23234 | 19069 | 19592 | 61896 | - - - | - - - | - - - | - - -
5/2/2026 | 12:45:00 AM | 286.33 | 283.25 | 283.18 | 495.75 | 488.42 | 492.83 | 89.3547 | 76.036 | 81.9773 | 2.291 | 1.432 | 1.428 | 1.426 | 2.061 | 2.036 | 2.13 | Over-range | 60 | 23051 | 18838 | 19510 | 61399 | - - - | - - - | - - - | - - - | 23051 | 18838 | 19510 | 61399 | 2180 | 1262 | 5107 | 8548 | - - - | - - - | - - - | - - - | 2180 | 1262 | 5107 | 8548 | 25526 | 21495 | 23167 | 70188 | # # # | # # # | # # # | # # # | 0.903 | 0.876 | 0.842 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.967 | 0.987 | - - - | 0.139 | 1.56 | 1.54 | 1.53 | 1.51 | 1.51 | 1.53 | 47.18 | 54.9 | 57.27 | 0 | - - - | - - - | - - - | - - - | 25526 | 21495 | 23167 | 70188 | Over-range | 10953 | 10348 | 12488 | 33989 | 10733 | 10271 | 11396 | 32896 | 22946 | 18796 | 19409 | 61150 | 22946 | 18796 | 19409 | 61150 | - - - | - - - | - - - | - - -
5/2/2026 | 1:00:00 AM | 286.57 | 283.57 | 283.42 | 496.27 | 488.93 | 493.2 | 91.0126 | 77.6514 | 83.0915 | 2.3576 | 1.433 | 1.429 | 1.427 | 2.058 | 2.051 | 2.138 | Over-range | 60.01 | 23463 | 19242 | 19756 | 62462 | - - - | - - - | - - - | - - - | 23463 | 19242 | 19756 | 62462 | 2345 | 1254 | 5199 | 8798 | - - - | - - - | - - - | - - - | 2345 | 1254 | 5199 | 8798 | 26037 | 21987 | 23519 | 71543 | # # # | # # # | # # # | # # # | 0.901 | 0.875 | 0.84 | 0.873 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.967 | 0.987 | - - - | 0.141 | 1.58 | 1.55 | 1.54 | 1.51 | 1.52 | 1.54 | 47.68 | 55.38 | 57.77 | 0 | - - - | - - - | - - - | - - - | 26037 | 21987 | 23519 | 71543 | Over-range | 11280 | 10636 | 12756 | 34871 | 11033 | 10561 | 11648 | 33743 | 23355 | 19171 | 19678 | 62205 | 23355 | 19171 | 19678 | 62205 | - - - | - - - | - - - | - - -
5/2/2026 | 1:15:00 AM | 286.85 | 283.87 | 283.77 | 496.73 | 489.52 | 493.74 | 88.5868 | 75.6688 | 81.3254 | 2.2575 | 1.432 | 1.428 | 1.426 | 2.055 | 2.027 | 2.119 | Over-range | 59.99 | 22925 | 18808 | 19450 | 61183 | - - - | - - - | - - - | - - - | 22925 | 18808 | 19450 | 61183 | 2179 | 1267 | 5030 | 8476 | - - - | - - - | - - - | - - - | 2179 | 1267 | 5030 | 8476 | 25347 | 21434 | 23032 | 69813 | # # # | # # # | # # # | # # # | 0.904 | 0.877 | 0.845 | 0.876 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.968 | 0.987 | - - - | 0.139 | 1.59 | 1.55 | 1.55 | 1.52 | 1.52 | 1.55 | 46.74 | 54.63 | 56.76 | 0 | - - - | - - - | - - - | - - - | 25347 | 21434 | 23032 | 69813 | Over-range | 10800 | 10275 | 12328 | 33600 | 10578 | 10196 | 11255 | 32514 | 22837 | 18743 | 19357 | 60938 | 22837 | 18743 | 19357 | 60938 | - - - | - - - | - - - | - - -
5/2/2026 | 1:30:00 AM | 284.84 | 281.92 | 281.74 | 493.32 | 486.09 | 490.22 | 92.0946 | 78.5083 | 84.0809 | 2.338 | 1.432 | 1.428 | 1.426 | 2.057 | 2.055 | 2.139 | Over-range | 60.01 | 23595 | 19338 | 19885 | 62818 | - - - | - - - | - - - | - - - | 23595 | 19338 | 19885 | 62818 | 2342 | 1261 | 5236 | 8839 | - - - | - - - | - - - | - - - | 2342 | 1261 | 5236 | 8839 | 26192 | 22104 | 23661 | 71958 | # # # | # # # | # # # | # # # | 0.901 | 0.875 | 0.84 | 0.873 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.967 | 0.987 | - - - | 0.141 | 1.58 | 1.55 | 1.56 | 1.52 | 1.52 | 1.55 | 47.76 | 55.43 | 57.7 | 0 | - - - | - - - | - - - | - - - | 26192 | 22104 | 23661 | 71958 | Over-range | 11363 | 10704 | 12819 | 35082 | 11118 | 10629 | 11700 | 33950 | 23486 | 19278 | 19795 | 62559 | 23486 | 19278 | 19795 | 62559 | - - - | - - - | - - - | - - -
5/2/2026 | 1:45:00 AM | 284.99 | 282.11 | 281.95 | 493.6 | 486.45 | 490.52 | 88.7386 | 75.9448 | 81.2646 | 2.2565 | 1.432 | 1.427 | 1.426 | 2.046 | 2.027 | 2.116 | Over-range | 60.02 | 22832 | 18775 | 19335 | 60942 | - - - | - - - | - - - | - - - | 22832 | 18775 | 19335 | 60942 | 2201 | 1224 | 4988 | 8412 | - - - | - - - | - - - | - - - | 2201 | 1224 | 4988 | 8412 | 25226 | 21377 | 22866 | 69469 | # # # | # # # | # # # | # # # | 0.905 | 0.878 | 0.846 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.968 | 0.987 | - - - | 0.138 | 1.59 | 1.54 | 1.56 | 1.53 | 1.53 | 1.56 | 46.52 | 54.43 | 56.5 | 0 | - - - | - - - | - - - | - - - | 25226 | 21377 | 22866 | 69469 | Over-range | 10715 | 10218 | 12201 | 33328 | 10486 | 10144 | 11134 | 32248 | 22735 | 18726 | 19240 | 60701 | 22735 | 18726 | 19240 | 60701 | - - - | - - - | - - - | - - -
5/2/2026 | 2:00:00 AM | 284.9 | 281.93 | 281.85 | 493.34 | 486.18 | 490.41 | 90.6749 | 77.1898 | 83.2478 | 2.2323 | 1.433 | 1.428 | 1.426 | 2.06 | 2.04 | 2.129 | Over-range | 60 | 23280 | 19034 | 19749 | 62063 | - - - | - - - | - - - | - - - | 23280 | 19034 | 19749 | 62063 | 2216 | 1286 | 5159 | 8661 | - - - | - - - | - - - | - - - | 2216 | 1286 | 5159 | 8661 | 25787 | 21729 | 23428 | 70944 | # # # | # # # | # # # | # # # | 0.903 | 0.876 | 0.843 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.967 | 0.987 | - - - | 0.14 | 1.61 | 1.56 | 1.57 | 1.54 | 1.54 | 1.58 | 47.28 | 55.11 | 57.1 | 0 | - - - | - - - | - - - | - - - | 25787 | 21729 | 23428 | 70944 | Over-range | 11083 | 10478 | 12600 | 34355 | 10858 | 10398 | 11495 | 33245 | 23186 | 18969 | 19651 | 61806 | 23186 | 18969 | 19651 | 61806 | - - - | - - - | - - - | - - -
5/2/2026 | 2:15:00 AM | 284.68 | 281.72 | 281.7 | 492.94 | 485.89 | 490.09 | 89.8331 | 76.6872 | 82.758 | 2.2233 | 1.433 | 1.428 | 1.426 | 2.054 | 2.024 | 2.112 | Over-range | 60 | 23076 | 18919 | 19695 | 61691 | - - - | - - - | - - - | - - - | 23076 | 18919 | 19695 | 61691 | 2142 | 1328 | 5075 | 8545 | - - - | - - - | - - - | - - - | 2142 | 1328 | 5075 | 8545 | 25515 | 21563 | 23270 | 70349 | # # # | # # # | # # # | # # # | 0.904 | 0.877 | 0.846 | 0.877 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.968 | 0.987 | - - - | 0.139 | 1.61 | 1.56 | 1.58 | 1.54 | 1.55 | 1.58 | 46.83 | 54.64 | 56.28 | 0 | - - - | - - - | - - - | - - - | 25515 | 21563 | 23270 | 70349 | Over-range | 10874 | 10342 | 12386 | 33790 | 10661 | 10256 | 11299 | 32692 | 22974 | 18861 | 19609 | 61444 | 22974 | 18861 | 19609 | 61444 | - - - | - - - | - - - | - - -
5/2/2026 | 2:30:00 AM | 284.57 | 281.65 | 281.63 | 492.77 | 485.8 | 489.93 | 90.3385 | 77.31 | 83.2312 | 2.2298 | 1.433 | 1.428 | 1.427 | 2.053 | 2.026 | 2.112 | Over-range | 60.01 | 23192 | 19070 | 19815 | 62076 | - - - | - - - | - - - | - - - | 23192 | 19070 | 19815 | 62076 | 2185 | 1347 | 5077 | 8609 | - - - | - - - | - - - | - - - | 2185 | 1347 | 5077 | 8609 | 25657 | 21738 | 23404 | 70799 | # # # | # # # | # # # | # # # | 0.904 | 0.877 | 0.847 | 0.877 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.968 | 0.987 | - - - | 0.139 | 1.6 | 1.57 | 1.57 | 1.54 | 1.54 | 1.58 | 46.92 | 54.72 | 56.34 | 0 | - - - | - - - | - - - | - - - | 25657 | 21738 | 23404 | 70799 | Over-range | 10964 | 10432 | 12449 | 34028 | 10743 | 10344 | 11367 | 32921 | 23100 | 19002 | 19720 | 61823 | 23100 | 19002 | 19720 | 61823 | - - - | - - - | - - - | - - -
5/2/2026 | 2:45:00 AM | 284.95 | 282.05 | 281.97 | 493.47 | 486.44 | 490.53 | 89.7331 | 76.7792 | 82.4129 | 2.2221 | 1.433 | 1.428 | 1.426 | 2.052 | 2.034 | 2.119 | Over-range | 60.01 | 23091 | 18985 | 19651 | 61728 | - - - | - - - | - - - | - - - | 23091 | 18985 | 19651 | 61728 | 2193 | 1278 | 5036 | 8507 | - - - | - - - | - - - | - - - | 2193 | 1278 | 5036 | 8507 | 25526 | 21622 | 23205 | 70353 | # # # | # # # | # # # | # # # | 0.905 | 0.878 | 0.847 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.968 | 0.987 | - - - | 0.138 | 1.62 | 1.56 | 1.58 | 1.54 | 1.54 | 1.58 | 46.75 | 54.58 | 56.31 | 0 | - - - | - - - | - - - | - - - | 25526 | 21622 | 23205 | 70353 | Over-range | 10873 | 10346 | 12337 | 33741 | 10649 | 10267 | 11262 | 32651 | 23005 | 18919 | 19553 | 61477 | 23005 | 18919 | 19553 | 61477 | - - - | - - - | - - - | - - -
5/2/2026 | 3:00:00 AM | 284.98 | 282.02 | 282 | 493.45 | 486.41 | 490.62 | 86.6222 | 74.1973 | 79.9106 | 2.2135 | 1.432 | 1.427 | 1.425 | 2.047 | 2.006 | 2.099 | Over-range | 60.01 | 22371 | 18386 | 19151 | 59907 | - - - | - - - | - - - | - - - | 22371 | 18386 | 19151 | 59907 | 1988 | 1250 | 4837 | 8074 | - - - | - - - | - - - | - - - | 1988 | 1250 | 4837 | 8074 | 24619 | 20876 | 22488 | 67984 | # # # | # # # | # # # | # # # | 0.909 | 0.881 | 0.852 | 0.881 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.969 | 0.988 | - - - | 0.135 | 1.6 | 1.55 | 1.55 | 1.52 | 1.53 | 1.56 | 45.6 | 53.74 | 55.06 | 0 | - - - | - - - | - - - | - - - | 24619 | 20876 | 22488 | 67984 | Over-range | 10265 | 9885 | 11781 | 32117 | 10071 | 9805 | 10742 | 31085 | 22265 | 18328 | 19082 | 59675 | 22265 | 18328 | 19082 | 59675 | - - - | - - - | - - - | - - -
5/2/2026 | 3:15:00 AM | 285.1 | 282.33 | 282.21 | 493.83 | 486.94 | 490.83 | 89.397 | 76.9587 | 81.8709 | 2.3421 | 1.433 | 1.428 | 1.426 | 2.048 | 2.04 | 2.118 | Over-range | 60.01 | 22991 | 19051 | 19548 | 61590 | - - - | - - - | - - - | - - - | 22991 | 19051 | 19548 | 61590 | 2256 | 1287 | 4967 | 8510 | - - - | - - - | - - - | - - - | 2256 | 1287 | 4967 | 8510 | 25447 | 21697 | 23074 | 70217 | # # # | # # # | # # # | # # # | 0.904 | 0.878 | 0.847 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.969 | 0.987 | - - - | 0.138 | 1.6 | 1.55 | 1.56 | 1.53 | 1.53 | 1.57 | 46.94 | 54.52 | 56.28 | 0 | - - - | - - - | - - - | - - - | 25447 | 21697 | 23074 | 70217 | Over-range | 10896 | 10380 | 12253 | 33704 | 10659 | 10299 | 11201 | 32612 | 22907 | 18989 | 19453 | 61349 | 22907 | 18989 | 19453 | 61349 | - - - | - - - | - - - | - - -
5/2/2026 | 3:30:00 AM | 285.11 | 282.18 | 282.04 | 493.76 | 486.58 | 490.72 | 86.5511 | 74.0914 | 79.3562 | 2.2211 | 1.431 | 1.426 | 1.425 | 2.044 | 2.019 | 2.108 | Over-range | 60 | 22357 | 18373 | 18987 | 59717 | - - - | - - - | - - - | - - - | 22357 | 18373 | 18987 | 59717 | 2058 | 1175 | 4823 | 8056 | - - - | - - - | - - - | - - - | 2058 | 1175 | 4823 | 8056 | 24610 | 20858 | 22334 | 67803 | # # # | # # # | # # # | # # # | 0.908 | 0.881 | 0.85 | 0.881 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.969 | 0.988 | - - - | 0.135 | 1.59 | 1.55 | 1.54 | 1.52 | 1.52 | 1.55 | 45.57 | 53.78 | 55.41 | 0 | - - - | - - - | - - - | - - - | 24610 | 20858 | 22334 | 67803 | Over-range | 10275 | 9870 | 11754 | 32091 | 10067 | 9800 | 10719 | 31063 | 22293 | 18298 | 18898 | 59489 | 22293 | 18298 | 18898 | 59489 | - - - | - - - | - - - | - - -
5/2/2026 | 3:45:00 AM | 285.09 | 282.21 | 282.07 | 493.75 | 486.65 | 490.71 | 89.227 | 76.4064 | 81.5493 | 2.315 | 1.432 | 1.427 | 1.426 | 2.052 | 2.046 | 2.127 | Over-range | 60.01 | 22952 | 18895 | 19428 | 61275 | - - - | - - - | - - - | - - - | 22952 | 18895 | 19428 | 61275 | 2220 | 1211 | 5000 | 8431 | - - - | - - - | - - - | - - - | 2220 | 1211 | 5000 | 8431 | 25391 | 21529 | 22969 | 69889 | # # # | # # # | # # # | # # # | 0.904 | 0.878 | 0.846 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.968 | 0.987 | - - - | 0.138 | 1.6 | 1.55 | 1.57 | 1.53 | 1.54 | 1.57 | 46.88 | 54.67 | 56.44 | 0 | - - - | - - - | - - - | - - - | 25391 | 21529 | 22969 | 69889 | Over-range | 10851 | 10315 | 12247 | 33598 | 10621 | 10243 | 11180 | 32523 | 22855 | 18822 | 19355 | 61032 | 22855 | 18822 | 19355 | 61032 | - - - | - - - | - - - | - - -
5/2/2026 | 4:00:00 AM | 285.38 | 282.48 | 282.34 | 494.26 | 487.11 | 491.22 | 87.1513 | 74.5521 | 79.7779 | 2.2222 | 1.432 | 1.427 | 1.424 | 2.053 | 2.034 | 2.123 | Over-range | 60 | 22474 | 18466 | 19033 | 59973 | - - - | - - - | - - - | - - - | 22474 | 18466 | 19033 | 59973 | 2127 | 1161 | 4885 | 8173 | - - - | - - - | - - - | - - - | 2127 | 1161 | 4885 | 8173 | 24811 | 21015 | 22480 | 68306 | # # # | # # # | # # # | # # # | 0.906 | 0.879 | 0.847 | 0.878 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.968 | 0.987 | - - - | 0.136 | 1.58 | 1.55 | 1.55 | 1.52 | 1.52 | 1.55 | 46.35 | 54.36 | 56.25 | 0 | - - - | - - - | - - - | - - - | 24811 | 21015 | 22480 | 68306 | Over-range | 10500 | 10029 | 11955 | 32675 | 10282 | 9961 | 10911 | 31636 | 22378 | 18405 | 18955 | 59738 | 22378 | 18405 | 18955 | 59738 | - - - | - - - | - - - | - - -
5/2/2026 | 4:15:00 AM | 285.46 | 282.56 | 282.43 | 494.38 | 487.25 | 491.35 | 86.3281 | 73.854 | 79.1339 | 2.1953 | 1.432 | 1.427 | 1.424 | 2.052 | 2.027 | 2.116 | Over-range | 60 | 22290 | 18315 | 18912 | 59517 | - - - | - - - | - - - | - - - | 22290 | 18315 | 18912 | 59517 | 2082 | 1161 | 4824 | 8067 | - - - | - - - | - - - | - - - | 2082 | 1161 | 4824 | 8067 | 24577 | 20821 | 22301 | 67699 | # # # | # # # | # # # | # # # | 0.907 | 0.88 | 0.848 | 0.879 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.969 | 0.988 | - - - | 0.136 | 1.6 | 1.56 | 1.56 | 1.53 | 1.53 | 1.57 | 45.99 | 54.1 | 55.94 | 0 | - - - | - - - | - - - | - - - | 24577 | 20821 | 22301 | 67699 | Over-range | 10339 | 9899 | 11812 | 32241 | 10127 | 9830 | 10782 | 31215 | 22219 | 18238 | 18827 | 59283 | 22219 | 18238 | 18827 | 59283 | - - - | - - - | - - - | - - -
5/2/2026 | 4:30:00 AM | 285.39 | 282.54 | 282.4 | 494.29 | 487.24 | 491.26 | 88.6355 | 75.9042 | 81.0274 | 2.2721 | 1.432 | 1.427 | 1.425 | 2.057 | 2.051 | 2.131 | Over-range | 60.01 | 22798 | 18772 | 19292 | 60862 | - - - | - - - | - - - | - - - | 22798 | 18772 | 19292 | 60862 | 2221 | 1204 | 4974 | 8399 | - - - | - - - | - - - | - - - | 2221 | 1204 | 4974 | 8399 | 25248 | 21411 | 22847 | 69507 | # # # | # # # | # # # | # # # | 0.903 | 0.877 | 0.844 | 0.876 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.968 | 0.987 | - - - | 0.138 | 1.59 | 1.55 | 1.55 | 1.52 | 1.52 | 1.55 | 47.13 | 54.9 | 56.84 | 0 | - - - | - - - | - - - | - - - | 25248 | 21411 | 22847 | 69507 | Over-range | 10840 | 10295 | 12233 | 33553 | 10610 | 10225 | 11177 | 32485 | 22703 | 18712 | 19209 | 60624 | 22703 | 18712 | 19209 | 60624 | - - - | - - - | - - - | - - -
5/2/2026 | 4:45:00 AM | 285.23 | 282.38 | 282.2 | 494.03 | 486.91 | 490.95 | 83.5803 | 71.8052 | 76.3184 | 2.1551 | 1.431 | 1.427 | 1.425 | 2.042 | 2.022 | 2.112 | Over-range | 60.01 | 21583 | 17814 | 18233 | 57630 | - - - | - - - | - - - | - - - | 21583 | 17814 | 18233 | 57630 | 2077 | 1077 | 4622 | 7775 | - - - | - - - | - - - | - - - | 2077 | 1077 | 4622 | 7775 | 23772 | 20226 | 21489 | 65487 | # # # | # # # | # # # | # # # | 0.908 | 0.881 | 0.849 | 0.88 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.969 | 0.988 | - - - | 0.135 | 1.59 | 1.56 | 1.58 | 1.53 | 1.54 | 1.57 | 45.62 | 53.73 | 55.91 | 0 | - - - | - - - | - - - | - - - | 23772 | 20226 | 21489 | 65487 | Over-range | 9951 | 9573 | 11365 | 31078 | 9731 | 9512 | 10383 | 30090 | 21504 | 17768 | 18139 | 57412 | 21504 | 17768 | 18139 | 57412 | - - - | - - - | - - - | - - -
5/2/2026 | 5:00:00 AM | 285.39 | 282.51 | 282.42 | 494.25 | 487.22 | 491.3 | 84.985 | 72.9784 | 77.6604 | 2.1759 | 1.432 | 1.428 | 1.425 | 2.054 | 2.042 | 2.125 | Over-range | 60.01 | 21864 | 18053 | 18492 | 58409 | - - - | - - - | - - - | - - - | 21864 | 18053 | 18492 | 58409 | 2157 | 1145 | 4726 | 8027 | - - - | - - - | - - - | - - - | 2157 | 1145 | 4726 | 8027 | 24186 | 20568 | 21881 | 66636 | # # # | # # # | # # # | # # # | 0.904 | 0.878 | 0.845 | 0.876 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.969 | 0.987 | - - - | 0.137 | 1.61 | 1.58 | 1.59 | 1.55 | 1.56 | 1.59 | 46.73 | 54.58 | 56.75 | 0 | - - - | - - - | - - - | - - - | 24186 | 20568 | 21881 | 66636 | Over-range | 10328 | 9850 | 11691 | 32050 | 10100 | 9783 | 10693 | 31029 | 21775 | 18003 | 18398 | 58176 | 21775 | 18003 | 18398 | 58176 | - - - | - - - | - - - | - - -
5/2/2026 | 5:15:00 AM | 285.53 | 282.72 | 282.6 | 494.55 | 487.6 | 491.55 | 85.132 | 73.4353 | 77.5146 | 2.2087 | 1.433 | 1.428 | 1.426 | 2.054 | 2.059 | 2.134 | Over-range | 60.01 | 21853 | 18160 | 18430 | 58444 | - - - | - - - | - - - | - - - | 21853 | 18160 | 18430 | 58444 | 2269 | 1134 | 4694 | 8097 | - - - | - - - | - - - | - - - | 2269 | 1134 | 4694 | 8097 | 24255 | 20721 | 21867 | 66843 | # # # | # # # | # # # | # # # | 0.901 | 0.876 | 0.843 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.969 | 0.987 | - - - | 0.139 | 1.67 | 1.61 | 1.63 | 1.58 | 1.6 | 1.64 | 47.49 | 54.93 | 57.36 | 0 | - - - | - - - | - - - | - - - | 24255 | 20721 | 21867 | 66843 | Over-range | 10513 | 9974 | 11762 | 32421 | 10265 | 9910 | 10784 | 31393 | 21757 | 18117 | 18355 | 58229 | 21757 | 18117 | 18355 | 58229 | - - - | - - - | - - - | - - -
5/2/2026 | 5:30:00 AM | 285.36 | 282.59 | 282.44 | 494.3 | 487.36 | 491.23 | 81.0363 | 70.1629 | 73.7841 | 2.1165 | 1.431 | 1.427 | 1.426 | 2.04 | 2.031 | 2.112 | Over-range | 60.01 | 20872 | 17410 | 17608 | 55891 | - - - | - - - | - - - | - - - | 20872 | 17410 | 17608 | 55891 | 2144 | 1041 | 4383 | 7568 | - - - | - - - | - - - | - - - | 2144 | 1041 | 4383 | 7568 | 23051 | 19773 | 20784 | 63608 | # # # | # # # | # # # | # # # | 0.906 | 0.88 | 0.847 | 0.879 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.97 | 0.988 | - - - | 0.135 | 1.65 | 1.61 | 1.64 | 1.58 | 1.6 | 1.64 | 46.03 | 53.8 | 56.38 | 0 | - - - | - - - | - - - | - - - | 23051 | 19773 | 20784 | 63608 | Over-range | 9768 | 9367 | 11035 | 30343 | 9529 | 9309 | 10127 | 29384 | 20816 | 17346 | 17535 | 55697 | 20816 | 17346 | 17535 | 55697 | - - - | - - - | - - - | - - -
5/2/2026 | 5:45:00 AM | 285.31 | 282.47 | 282.33 | 494.16 | 487.12 | 491.12 | 79.9616 | 69.2071 | 72.5831 | 2.1299 | 1.43 | 1.426 | 1.424 | 2.048 | 2.041 | 2.128 | Over-range | 60 | 20547 | 17151 | 17243 | 54941 | - - - | - - - | - - - | - - - | 20547 | 17151 | 17243 | 54941 | 2175 | 998 | 4323 | 7495 | - - - | - - - | - - - | - - - | 2175 | 998 | 4323 | 7495 | 22741 | 19494 | 20440 | 62676 | # # # | # # # | # # # | # # # | 0.904 | 0.88 | 0.844 | 0.877 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.97 | 0.988 | - - - | 0.136 | 1.62 | 1.56 | 1.6 | 1.53 | 1.56 | 1.59 | 46.56 | 53.99 | 57.28 | 0 | - - - | - - - | - - - | - - - | 22741 | 19494 | 20440 | 62676 | Over-range | 9729 | 9260 | 10968 | 30133 | 9482 | 9206 | 10080 | 29185 | 20484 | 17094 | 17166 | 54744 | 20484 | 17094 | 17166 | 54744 | - - - | - - - | - - - | - - -
5/2/2026 | 6:00:00 AM | 284.92 | 282.05 | 281.92 | 493.46 | 486.39 | 490.44 | 80.9922 | 69.994 | 73.2014 | 2.1254 | 1.43 | 1.427 | 1.425 | 2.055 | 2.067 | 2.148 | Over-range | 60 | 20701 | 17275 | 17266 | 55242 | - - - | - - - | - - - | - - - | 20701 | 17275 | 17266 | 55242 | 2289 | 959 | 4381 | 7630 | - - - | - - - | - - - | - - - | 2289 | 959 | 4381 | 7630 | 23003 | 19686 | 20578 | 63267 | # # # | # # # | # # # | # # # | 0.9 | 0.878 | 0.839 | 0.873 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.969 | 0.987 | - - - | 0.138 | 1.61 | 1.57 | 1.6 | 1.53 | 1.57 | 1.59 | 47.54 | 54.65 | 58.35 | 0 | - - - | - - - | - - - | - - - | 23003 | 19686 | 20578 | 63267 | Over-range | 10019 | 9434 | 11190 | 30819 | 9754 | 9385 | 10297 | 29859 | 20622 | 17213 | 17208 | 55043 | 20622 | 17213 | 17208 | 55043 | - - - | - - - | - - - | - - -
5/2/2026 | 6:15:00 AM | 284.77 | 281.98 | 281.81 | 493.27 | 486.28 | 490.19 | 77.07 | 67.0351 | 69.9107 | 2.0424 | 1.43 | 1.427 | 1.425 | 2.042 | 2.034 | 2.121 | Over-range | 59.99 | 19782 | 16619 | 16594 | 52995 | - - - | - - - | - - - | - - - | 19782 | 16619 | 16594 | 52995 | 2147 | 948 | 4095 | 7190 | - - - | - - - | - - - | - - - | 2147 | 948 | 4095 | 7190 | 21879 | 18850 | 19651 | 60380 | # # # | # # # | # # # | # # # | 0.904 | 0.882 | 0.844 | 0.878 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.971 | 0.988 | - - - | 0.136 | 1.6 | 1.56 | 1.58 | 1.53 | 1.55 | 1.59 | 46.31 | 53.49 | 57.3 | 0 | - - - | - - - | - - - | - - - | 21879 | 18850 | 19651 | 60380 | Over-range | 9335 | 8891 | 10520 | 28915 | 9085 | 8840 | 9690 | 28007 | 19718 | 16578 | 16514 | 52810 | 19718 | 16578 | 16514 | 52810 | - - - | - - - | - - - | - - -
5/2/2026 | 6:30:00 AM | 284.65 | 281.88 | 281.71 | 493.08 | 486.1 | 489.99 | 78.1114 | 67.9657 | 70.7119 | 2.0819 | 1.43 | 1.427 | 1.425 | 2.045 | 2.047 | 2.129 | Over-range | 60 | 19984 | 16809 | 16732 | 53524 | - - - | - - - | - - - | - - - | 19984 | 16809 | 16732 | 53524 | 2224 | 950 | 4150 | 7324 | - - - | - - - | - - - | - - - | 2224 | 950 | 4150 | 7324 | 22156 | 19098 | 19860 | 61114 | # # # | # # # | # # # | # # # | 0.902 | 0.88 | 0.843 | 0.876 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.97 | 0.988 | - - - | 0.137 | 1.58 | 1.53 | 1.55 | 1.5 | 1.52 | 1.55 | 46.88 | 53.94 | 57.68 | 0 | - - - | - - - | - - - | - - - | 22156 | 19098 | 19860 | 61114 | Over-range | 9553 | 9061 | 10692 | 29472 | 9291 | 9011 | 9853 | 28548 | 19905 | 16754 | 16678 | 53337 | 19905 | 16754 | 16678 | 53337 | - - - | - - - | - - - | - - -
5/2/2026 | 6:45:00 AM | 284.48 | 281.77 | 281.59 | 492.81 | 485.94 | 489.71 | 78.1239 | 68.2005 | 70.7948 | 2.0796 | 1.43 | 1.427 | 1.425 | 2.038 | 2.044 | 2.119 | Over-range | 60.01 | 19981 | 16867 | 16793 | 53642 | - - - | - - - | - - - | - - - | 19981 | 16867 | 16793 | 53642 | 2212 | 989 | 4113 | 7313 | - - - | - - - | - - - | - - - | 2212 | 989 | 4113 | 7313 | 22149 | 19158 | 19878 | 61185 | # # # | # # # | # # # | # # # | 0.902 | 0.88 | 0.845 | 0.877 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.971 | 0.988 | - - - | 0.136 | 1.59 | 1.56 | 1.56 | 1.51 | 1.54 | 1.57 | 46.77 | 53.78 | 57.25 | 0 | - - - | - - - | - - - | - - - | 22149 | 19158 | 19878 | 61185 | Over-range | 9543 | 9079 | 10628 | 29406 | 9283 | 9025 | 9800 | 28482 | 19918 | 16826 | 16713 | 53457 | 19918 | 16826 | 16713 | 53457 | - - - | - - - | - - - | - - -
5/2/2026 | 7:00:00 AM | 284.43 | 281.7 | 281.54 | 492.7 | 485.84 | 489.65 | 77.6249 | 67.8093 | 70.4769 | 2.0644 | 1.431 | 1.427 | 1.426 | 2.034 | 2.039 | 2.11 | Over-range | 60.01 | 19872 | 16781 | 16755 | 53409 | - - - | - - - | - - - | - - - | 19872 | 16781 | 16755 | 53409 | 2165 | 1009 | 4070 | 7244 | - - - | - - - | - - - | - - - | 2165 | 1009 | 4070 | 7244 | 22004 | 19044 | 19784 | 60832 | # # # | # # # | # # # | # # # | 0.903 | 0.881 | 0.847 | 0.878 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.971 | 0.988 | - - - | 0.136 | 1.61 | 1.58 | 1.61 | 1.54 | 1.57 | 1.61 | 46.48 | 53.52 | 56.74 | 0 | - - - | - - - | - - - | - - - | 22004 | 19044 | 19784 | 60832 | Over-range | 9435 | 8998 | 10514 | 29098 | 9183 | 8941 | 9694 | 28182 | 19825 | 16732 | 16681 | 53238 | 19825 | 16732 | 16681 | 53238 | - - - | - - - | - - - | - - -
5/2/2026 | 7:15:00 AM | 284.28 | 281.6 | 281.35 | 492.53 | 485.59 | 489.32 | 77.4092 | 67.9012 | 70.0788 | 2.0614 | 1.431 | 1.428 | 1.426 | 2.024 | 2.043 | 2.107 | Over-range | 60 | 19792 | 16800 | 16658 | 53250 | - - - | - - - | - - - | - - - | 19792 | 16800 | 16658 | 53250 | 2222 | 964 | 4011 | 7197 | - - - | - - - | - - - | - - - | 2222 | 964 | 4011 | 7197 | 21931 | 19060 | 19660 | 60651 | # # # | # # # | # # # | # # # | 0.903 | 0.881 | 0.847 | 0.878 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.972 | 0.988 | - - - | 0.135 | 1.66 | 1.59 | 1.66 | 1.57 | 1.61 | 1.65 | 46.61 | 53.45 | 56.59 | 0 | - - - | - - - | - - - | - - - | 21931 | 19060 | 19660 | 60651 | Over-range | 9435 | 8998 | 10435 | 29014 | 9169 | 8946 | 9634 | 28107 | 19721 | 16747 | 16623 | 53091 | 19721 | 16747 | 16623 | 53091 | - - - | - - - | - - - | - - -
5/2/2026 | 7:30:00 AM | 284.2 | 281.48 | 281.21 | 492.37 | 485.33 | 489.13 | 77.4901 | 67.8368 | 70.0497 | 2.0661 | 1.431 | 1.428 | 1.427 | 2.023 | 2.043 | 2.109 | Over-range | 60.01 | 19820 | 16784 | 16642 | 53247 | - - - | - - - | - - - | - - - | 19820 | 16784 | 16642 | 53247 | 2213 | 939 | 4036 | 7187 | - - - | - - - | - - - | - - - | 2213 | 939 | 4036 | 7187 | 21950 | 19038 | 19643 | 60631 | # # # | # # # | # # # | # # # | 0.903 | 0.882 | 0.847 | 0.878 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.972 | 0.988 | - - - | 0.135 | 1.67 | 1.63 | 1.67 | 1.58 | 1.63 | 1.67 | 46.46 | 53.38 | 56.54 | 0 | - - - | - - - | - - - | - - - | 21950 | 19038 | 19643 | 60631 | Over-range | 9419 | 8979 | 10429 | 28976 | 9156 | 8930 | 9616 | 28070 | 19737 | 16747 | 16608 | 53092 | 19737 | 16747 | 16608 | 53092 | - - - | - - - | - - - | - - -
5/2/2026 | 7:45:00 AM | 284.12 | 281.37 | 281.17 | 492.18 | 485.21 | 489.06 | 75.5746 | 66.3418 | 68.6973 | 2.0046 | 1.43 | 1.428 | 1.426 | 2.022 | 2.026 | 2.093 | Over-range | 60 | 19365 | 16441 | 16388 | 52194 | - - - | - - - | - - - | - - - | 19365 | 16441 | 16388 | 52194 | 2104 | 979 | 3897 | 6980 | - - - | - - - | - - - | - - - | 2104 | 979 | 3897 | 6980 | 21403 | 18612 | 19266 | 59281 | # # # | # # # | # # # | # # # | 0.905 | 0.883 | 0.851 | 0.88 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.973 | 0.989 | - - - | 0.134 | 1.69 | 1.65 | 1.71 | 1.61 | 1.66 | 1.7 | 46 | 52.87 | 55.81 | 0 | - - - | - - - | - - - | - - - | 21403 | 18612 | 19266 | 59281 | Over-range | 9102 | 8718 | 10122 | 28083 | 8855 | 8663 | 9342 | 27202 | 19294 | 16392 | 16357 | 52044 | 19294 | 16392 | 16357 | 52044 | - - - | - - - | - - - | - - -
5/2/2026 | 8:00:00 AM | 283.88 | 281.17 | 280.92 | 491.81 | 484.83 | 488.61 | 74.4899 | 65.5215 | 67.3525 | 1.9804 | 1.43 | 1.428 | 1.426 | 2.018 | 2.036 | 2.1 | Over-range | 60.01 | 19044 | 16230 | 16020 | 51294 | - - - | - - - | - - - | - - - | 19044 | 16230 | 16020 | 51294 | 2140 | 910 | 3803 | 6854 | - - - | - - - | - - - | - - - | 2140 | 910 | 3803 | 6854 | 21077 | 18369 | 18869 | 58314 | # # # | # # # | # # # | # # # | 0.904 | 0.884 | 0.849 | 0.88 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.973 | 0.989 | - - - | 0.134 | 1.7 | 1.68 | 1.74 | 1.62 | 1.68 | 1.73 | 46.23 | 52.72 | 56.36 | 0 | - - - | - - - | - - - | - - - | 21077 | 18369 | 18869 | 58314 | Over-range | 9020 | 8598 | 9963 | 27719 | 8762 | 8550 | 9208 | 26858 | 18964 | 16228 | 15964 | 51156 | 18964 | 16228 | 15964 | 51156 | - - - | - - - | - - - | - - -
5/2/2026 | 8:15:00 AM | 283.34 | 280.6 | 280.44 | 490.81 | 483.91 | 487.76 | 73.7194 | 65.0636 | 67.0095 | 1.9607 | 1.43 | 1.429 | 1.427 | 2.015 | 2.021 | 2.083 | Over-range | 60 | 18830 | 16098 | 15967 | 50894 | - - - | - - - | - - - | - - - | 18830 | 16098 | 15967 | 50894 | 2084 | 957 | 3719 | 6760 | - - - | - - - | - - - | - - - | 2084 | 957 | 3719 | 6760 | 20824 | 18206 | 18745 | 57776 | # # # | # # # | # # # | # # # | 0.904 | 0.884 | 0.852 | 0.881 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.974 | 0.989 | - - - | 0.133 | 1.72 | 1.66 | 1.76 | 1.63 | 1.69 | 1.74 | 46.11 | 52.58 | 55.67 | 0 | - - - | - - - | - - - | - - - | 20824 | 18206 | 18745 | 57776 | Over-range | 8884 | 8500 | 9815 | 27328 | 8636 | 8446 | 9083 | 26478 | 18758 | 16058 | 15950 | 50767 | 18758 | 16058 | 15950 | 50767 | - - - | - - - | - - - | - - -
5/2/2026 | 8:30:00 AM | 282.88 | 279.97 | 279.82 | 489.9 | 482.74 | 486.89 | 76.2593 | 66.7487 | 68.9737 | 2.0247 | 1.43 | 1.429 | 1.427 | 2.026 | 2.046 | 2.111 | Over-range | 60.01 | 19358 | 16410 | 16267 | 52034 | - - - | - - - | - - - | - - - | 19358 | 16410 | 16267 | 52034 | 2167 | 949 | 3911 | 7028 | - - - | - - - | - - - | - - - | 2167 | 949 | 3911 | 7028 | 21495 | 18627 | 19240 | 59362 | # # # | # # # | # # # | # # # | 0.901 | 0.881 | 0.845 | 0.877 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.972 | 0.988 | - - - | 0.135 | 1.69 | 1.65 | 1.75 | 1.61 | 1.68 | 1.72 | 47.05 | 53.42 | 57.11 | 0 | - - - | - - - | - - - | - - - | 21495 | 18627 | 19240 | 59362 | Over-range | 9331 | 8808 | 10269 | 28548 | 9076 | 8757 | 9495 | 27669 | 19309 | 16392 | 16196 | 51896 | 19309 | 16392 | 16196 | 51896 | - - - | - - - | - - - | - - -
5/2/2026 | 8:45:00 AM | 282.63 | 279.71 | 279.61 | 489.44 | 482.34 | 486.49 | 76.08 | 66.6618 | 68.9332 | 2.0125 | 1.43 | 1.43 | 1.427 | 2.025 | 2.044 | 2.105 | Over-range | 60.01 | 19292 | 16369 | 16260 | 51921 | - - - | - - - | - - - | - - - | 19292 | 16369 | 16260 | 51921 | 2155 | 976 | 3900 | 7030 | - - - | - - - | - - - | - - - | 2155 | 976 | 3900 | 7030 | 21426 | 18585 | 19216 | 59228 | # # # | # # # | # # # | # # # | 0.9 | 0.881 | 0.846 | 0.877 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.972 | 0.988 | - - - | 0.135 | 1.7 | 1.69 | 1.74 | 1.62 | 1.69 | 1.73 | 47.08 | 53.47 | 56.96 | 0 | - - - | - - - | - - - | - - - | 21426 | 18585 | 19216 | 59228 | Over-range | 9309 | 8796 | 10234 | 28474 | 9056 | 8741 | 9462 | 27593 | 19234 | 16347 | 16200 | 51781 | 19234 | 16347 | 16200 | 51781 | - - - | - - - | - - - | - - -
5/2/2026 | 9:00:00 AM | 282.67 | 279.78 | 279.67 | 489.52 | 482.48 | 486.58 | 75.8617 | 66.5965 | 68.7967 | 1.9965 | 1.431 | 1.43 | 1.428 | 2.023 | 2.042 | 2.1 | Over-range | 60 | 19235 | 16356 | 16244 | 51835 | - - - | - - - | - - - | - - - | 19235 | 16356 | 16244 | 51835 | 2159 | 989 | 3887 | 7035 | - - - | - - - | - - - | - - - | 2159 | 989 | 3887 | 7035 | 21368 | 18572 | 19187 | 59128 | # # # | # # # | # # # | # # # | 0.9 | 0.881 | 0.847 | 0.877 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.972 | 0.988 | - - - | 0.136 | 1.72 | 1.68 | 1.76 | 1.63 | 1.7 | 1.74 | 47.22 | 53.5 | 56.82 | 0 | - - - | - - - | - - - | - - - | 21368 | 18572 | 19187 | 59128 | Over-range | 9295 | 8794 | 10204 | 28425 | 9040 | 8738 | 9435 | 27540 | 19145 | 16342 | 16206 | 51692 | 19145 | 16342 | 16206 | 51692 | - - - | - - - | - - - | - - -
5/2/2026 | 9:15:00 AM | 282.38 | 279.46 | 279.27 | 489.05 | 481.81 | 485.96 | 73.21 | 64.2214 | 66.0069 | 1.9171 | 1.429 | 1.428 | 1.426 | 2.018 | 2.04 | 2.105 | Over-range | 60 | 18592 | 15814 | 15565 | 49972 | - - - | - - - | - - - | - - - | 18592 | 15814 | 15565 | 49972 | 2125 | 865 | 3690 | 6680 | - - - | - - - | - - - | - - - | 2125 | 865 | 3690 | 6680 | 20608 | 17898 | 18388 | 56894 | # # # | # # # | # # # | # # # | 0.902 | 0.884 | 0.847 | 0.878 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.973 | 0.988 | - - - | 0.134 | 1.66 | 1.63 | 1.7 | 1.57 | 1.65 | 1.67 | 46.51 | 52.8 | 56.98 | 0 | - - - | - - - | - - - | - - - | 20608 | 17898 | 18388 | 56894 | Over-range | 8879 | 8375 | 9782 | 27176 | 8621 | 8330 | 9060 | 26342 | 18562 | 15783 | 15498 | 49843 | 18562 | 15783 | 15498 | 49843 | - - - | - - - | - - - | - - -
5/2/2026 | 9:30:00 AM | 282.16 | 279.08 | 278.99 | 488.51 | 481.17 | 485.61 | 71.8971 | 62.9155 | 65.0454 | 1.8708 | 1.429 | 1.429 | 1.426 | 2.022 | 2.027 | 2.1 | Over-range | 59.99 | 18294 | 15503 | 15347 | 49144 | - - - | - - - | - - - | - - - | 18294 | 15503 | 15347 | 49144 | 2035 | 836 | 3639 | 6510 | - - - | - - - | - - - | - - - | 2035 | 836 | 3639 | 6510 | 20233 | 17516 | 18108 | 55858 | # # # | # # # | # # # | # # # | 0.904 | 0.885 | 0.848 | 0.88 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.973 | 0.989 | - - - | 0.133 | 1.66 | 1.64 | 1.7 | 1.57 | 1.66 | 1.68 | 46.14 | 52.42 | 56.67 | 0 | - - - | - - - | - - - | - - - | 20233 | 17516 | 18108 | 55858 | Over-range | 8636 | 8150 | 9607 | 26537 | 8393 | 8107 | 8891 | 25726 | 18229 | 15466 | 15325 | 49020 | 18229 | 15466 | 15325 | 49020 | - - - | - - - | - - - | - - -
5/2/2026 | 9:45:00 AM | 281.82 | 278.66 | 278.53 | 487.9 | 480.35 | 484.93 | 75.0462 | 65.4031 | 67.3764 | 1.9655 | 1.429 | 1.429 | 1.426 | 2.032 | 2.062 | 2.133 | Over-range | 60.01 | 18916 | 15992 | 15694 | 50602 | - - - | - - - | - - - | - - - | 18916 | 15992 | 15694 | 50602 | 2236 | 814 | 3833 | 6883 | - - - | - - - | - - - | - - - | 2236 | 814 | 3833 | 6883 | 21069 | 18164 | 18703 | 57935 | # # # | # # # | # # # | # # # | 0.898 | 0.88 | 0.839 | 0.873 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.971 | 0.988 | - - - | 0.136 | 1.61 | 1.59 | 1.65 | 1.52 | 1.62 | 1.63 | 47.75 | 53.73 | 58.57 | 0 | - - - | - - - | - - - | - - - | 21069 | 18164 | 18703 | 57935 | Over-range | 9267 | 8607 | 10168 | 28193 | 8993 | 8568 | 9418 | 27340 | 18843 | 15953 | 15668 | 50464 | 18843 | 15953 | 15668 | 50464 | - - - | - - - | - - - | - - -
5/2/2026 | 10:00:00 AM | 281.97 | 278.95 | 278.77 | 488.27 | 480.88 | 485.22 | 74.7314 | 65.373 | 66.7433 | 1.9712 | 1.429 | 1.43 | 1.427 | 2.028 | 2.071 | 2.137 | Over-range | 60 | 18806 | 15990 | 15529 | 50325 | - - - | - - - | - - - | - - - | 18806 | 15990 | 15529 | 50325 | 2331 | 792 | 3778 | 6901 | - - - | - - - | - - - | - - - | 2331 | 792 | 3778 | 6901 | 20991 | 18172 | 18548 | 57710 | # # # | # # # | # # # | # # # | 0.896 | 0.88 | 0.837 | 0.872 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.971 | 0.988 | - - - | 0.137 | 1.63 | 1.61 | 1.68 | 1.55 | 1.64 | 1.66 | 48.03 | 53.89 | 59.14 | 0 | - - - | - - - | - - - | - - - | 20991 | 18172 | 18548 | 57710 | Over-range | 9312 | 8627 | 10135 | 28223 | 9015 | 8591 | 9404 | 27366 | 18761 | 15938 | 15487 | 50186 | 18761 | 15938 | 15487 | 50186 | - - - | - - - | - - - | - - -
5/2/2026 | 10:15:00 AM | 281.75 | 278.64 | 278.6 | 487.76 | 480.45 | 484.94 | 74.5333 | 64.7757 | 67.0151 | 1.9336 | 1.429 | 1.429 | 1.427 | 2.043 | 2.066 | 2.14 | Over-range | 60 | 18748 | 15822 | 15565 | 50135 | - - - | - - - | - - - | - - - | 18748 | 15822 | 15565 | 50135 | 2226 | 829 | 3832 | 6888 | - - - | - - - | - - - | - - - | 2226 | 829 | 3832 | 6888 | 20920 | 17990 | 18605 | 57515 | # # # | # # # | # # # | # # # | 0.896 | 0.879 | 0.837 | 0.872 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.971 | 0.988 | - - - | 0.137 | 1.6 | 1.6 | 1.67 | 1.53 | 1.63 | 1.64 | 48.12 | 54 | 59.2 | 0 | - - - | - - - | - - - | - - - | 20920 | 17990 | 18605 | 57515 | Over-range | 9271 | 8555 | 10187 | 28164 | 8999 | 8515 | 9438 | 27309 | 18709 | 15768 | 15518 | 49996 | 18709 | 15768 | 15518 | 49996 | - - - | - - - | - - - | - - -
5/2/2026 | 10:30:00 AM | 281.57 | 278.47 | 278.4 | 487.46 | 480.13 | 484.6 | 73.9684 | 64.462 | 66.3713 | 1.9726 | 1.429 | 1.428 | 1.426 | 2.041 | 2.066 | 2.14 | Over-range | 60.01 | 18588 | 15744 | 15399 | 49731 | - - - | - - - | - - - | - - - | 18588 | 15744 | 15399 | 49731 | 2255 | 814 | 3776 | 6845 | - - - | - - - | - - - | - - - | 2255 | 814 | 3776 | 6845 | 20745 | 17890 | 18417 | 57052 | # # # | # # # | # # # | # # # | 0.896 | 0.88 | 0.836 | 0.872 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.971 | 0.988 | - - - | 0.138 | 1.59 | 1.57 | 1.63 | 1.51 | 1.6 | 1.6 | 48.13 | 53.93 | 59.34 | 0 | - - - | - - - | - - - | - - - | 20745 | 17890 | 18417 | 57052 | Over-range | 9201 | 8490 | 10096 | 27939 | 8920 | 8450 | 9363 | 27087 | 18549 | 15676 | 15360 | 49585 | 18549 | 15676 | 15360 | 49585 | - - - | - - - | - - - | - - -
5/2/2026 | 10:45:00 AM | 281.16 | 277.98 | 278 | 486.66 | 479.34 | 483.96 | 73.2602 | 63.701 | 66.1497 | 1.8553 | 1.429 | 1.428 | 1.426 | 2.041 | 2.052 | 2.128 | Over-range | 60.01 | 18436 | 15552 | 15385 | 49373 | - - - | - - - | - - - | - - - | 18436 | 15552 | 15385 | 49373 | 2135 | 847 | 3741 | 6723 | - - - | - - - | - - - | - - - | 2135 | 847 | 3741 | 6723 | 20524 | 17653 | 18330 | 56508 | # # # | # # # | # # # | # # # | 0.898 | 0.881 | 0.839 | 0.874 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.971 | 0.988 | - - - | 0.136 | 1.57 | 1.59 | 1.65 | 1.51 | 1.61 | 1.61 | 47.62 | 53.58 | 58.64 | 0 | - - - | - - - | - - - | - - - | 20524 | 17653 | 18330 | 56508 | Over-range | 9010 | 8347 | 9959 | 27464 | 8753 | 8304 | 9229 | 26628 | 18406 | 15497 | 15330 | 49234 | 18406 | 15497 | 15330 | 49234 | - - - | - - - | - - - | - - -
5/2/2026 | 11:00:00 AM | 281.13 | 277.92 | 277.95 | 486.58 | 479.22 | 483.89 | 73.9883 | 64.18 | 66.8469 | 1.893 | 1.429 | 1.429 | 1.426 | 2.047 | 2.056 | 2.134 | Over-range | 60 | 18587 | 15648 | 15505 | 49740 | - - - | - - - | - - - | - - - | 18587 | 15648 | 15505 | 49740 | 2154 | 858 | 3813 | 6825 | - - - | - - - | - - - | - - - | 2154 | 858 | 3813 | 6825 | 20721 | 17780 | 18518 | 57019 | # # # | # # # | # # # | # # # | 0.897 | 0.88 | 0.837 | 0.872 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.971 | 0.988 | - - - | 0.137 | 1.59 | 1.6 | 1.65 | 1.52 | 1.62 | 1.62 | 47.99 | 53.89 | 58.99 | 0 | - - - | - - - | - - - | - - - | 20721 | 17780 | 18518 | 57019 | Over-range | 9147 | 8436 | 10119 | 27854 | 8889 | 8392 | 9373 | 27005 | 18538 | 15589 | 15470 | 49597 | 18538 | 15589 | 15470 | 49597 | - - - | - - - | - - - | - - -
5/2/2026 | 11:15:00 AM | 280.71 | 277.53 | 277.52 | 485.89 | 478.52 | 483.14 | 74.9757 | 65.0481 | 67.5329 | 1.9409 | 1.429 | 1.429 | 1.426 | 2.043 | 2.061 | 2.137 | Over-range | 60.01 | 18796 | 15828 | 15627 | 50251 | - - - | - - - | - - - | - - - | 18796 | 15828 | 15627 | 50251 | 2191 | 846 | 3869 | 6906 | - - - | - - - | - - - | - - - | 2191 | 846 | 3869 | 6906 | 20966 | 17993 | 18681 | 57641 | # # # | # # # | # # # | # # # | 0.897 | 0.88 | 0.837 | 0.872 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.97 | 0.988 | - - - | 0.137 | 1.58 | 1.57 | 1.63 | 1.5 | 1.6 | 1.6 | 48.16 | 53.86 | 59.23 | 0 | - - - | - - - | - - - | - - - | 20966 | 17993 | 18681 | 57641 | Over-range | 9278 | 8552 | 10231 | 28215 | 9016 | 8510 | 9471 | 27357 | 18724 | 15816 | 15565 | 50106 | 18724 | 15816 | 15565 | 50106 | - - - | - - - | - - - | - - -
5/2/2026 | 11:30:00 AM | 280.19 | 277 | 276.99 | 484.98 | 477.6 | 482.23 | 75.5528 | 65.63 | 68.1465 | 1.9309 | 1.429 | 1.429 | 1.427 | 2.042 | 2.061 | 2.133 | Over-range | 60 | 18883 | 15915 | 15745 | 50544 | - - - | - - - | - - - | - - - | 18883 | 15915 | 15745 | 50544 | 2199 | 882 | 3885 | 6967 | - - - | - - - | - - - | - - - | 2199 | 882 | 3885 | 6967 | 21085 | 18115 | 18815 | 58015 | # # # | # # # | # # # | # # # | 0.896 | 0.879 | 0.837 | 0.871 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.971 | 0.988 | - - - | 0.138 | 1.57 | 1.57 | 1.64 | 1.5 | 1.59 | 1.6 | 48.43 | 54.11 | 59.13 | 0 | - - - | - - - | - - - | - - - | 21085 | 18115 | 18815 | 58015 | Over-range | 9368 | 8646 | 10294 | 28456 | 9106 | 8600 | 9532 | 27590 | 18807 | 15896 | 15696 | 50400 | 18807 | 15896 | 15696 | 50400 | - - - | - - - | - - - | - - -
5/2/2026 | 11:45:00 AM | 280.2 | 277.14 | 277.1 | 485.09 | 477.88 | 482.29 | 78.966 | 68.7105 | 71.1297 | 2.065 | 1.43 | 1.43 | 1.428 | 2.047 | 2.081 | 2.144 | Over-range | 60.01 | 19646 | 16607 | 16360 | 52613 | - - - | - - - | - - - | - - - | 19646 | 16607 | 16360 | 52613 | 2395 | 976 | 4096 | 7467 | - - - | - - - | - - - | - - - | 2395 | 976 | 4096 | 7467 | 22060 | 18991 | 19660 | 60711 | # # # | # # # | # # # | # # # | 0.891 | 0.875 | 0.832 | 0.867 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.97 | 0.987 | - - - | 0.142 | 1.55 | 1.56 | 1.6 | 1.48 | 1.57 | 1.57 | 49.73 | 55.34 | 60.3 | 0 | - - - | - - - | - - - | - - - | 22060 | 18991 | 19660 | 60711 | Over-range | 10022 | 9206 | 10897 | 30272 | 9732 | 9154 | 10098 | 29336 | 19577 | 16565 | 16308 | 52450 | 19577 | 16565 | 16308 | 52450 | - - - | - - - | - - - | - - -
5/2/2026 | 12:00:00 PM | 280.51 | 277.33 | 277.33 | 485.54 | 478.18 | 482.81 | 80.0861 | 69.3565 | 72.2245 | 2.0799 | 1.429 | 1.429 | 1.427 | 2.052 | 2.082 | 2.149 | Over-range | 60.01 | 19933 | 16755 | 16581 | 53269 | - - - | - - - | - - - | - - - | 19933 | 16755 | 16581 | 53269 | 2401 | 992 | 4204 | 7597 | - - - | - - - | - - - | - - - | 2401 | 992 | 4204 | 7597 | 22391 | 19179 | 19972 | 61542 | # # # | # # # | # # # | # # # | 0.89 | 0.874 | 0.83 | 0.866 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.969 | 0.987 | - - - | 0.143 | 1.55 | 1.57 | 1.63 | 1.49 | 1.59 | 1.58 | 49.9 | 55.56 | 60.59 | 0 | - - - | - - - | - - - | - - - | 22391 | 19179 | 19972 | 61542 | Over-range | 10191 | 9327 | 11128 | 30801 | 9904 | 9274 | 10303 | 29849 | 19869 | 16700 | 16539 | 53109 | 19869 | 16700 | 16539 | 53109 | - - - | - - - | - - - | - - -
5/2/2026 | 12:15:00 PM | 282.06 | 278.78 | 278.81 | 488.16 | 480.68 | 485.45 | 82.6072 | 71.0381 | 74.572 | 2.1212 | 1.431 | 1.43 | 1.429 | 2.063 | 2.092 | 2.164 | Over-range | 59.98 | 20674 | 17232 | 17165 | 55072 | - - - | - - - | - - - | - - - | 20674 | 17232 | 17165 | 55072 | 2454 | 1027 | 4461 | 7943 | - - - | - - - | - - - | - - - | 2454 | 1027 | 4461 | 7943 | 23252 | 19769 | 20753 | 63774 | # # # | # # # | # # # | # # # | 0.889 | 0.872 | 0.827 | 0.864 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.968 | 0.987 | - - - | 0.144 | 1.5 | 1.53 | 1.56 | 1.44 | 1.53 | 1.52 | 50.36 | 56.14 | 61.26 | 0 | - - - | - - - | - - - | - - - | 23252 | 19769 | 20753 | 63774 | Over-range | 10635 | 9684 | 11661 | 32147 | 10348 | 9630 | 10773 | 31151 | 20596 | 17191 | 17106 | 54893 | 20596 | 17191 | 17106 | 54893 | - - - | - - - | - - - | - - -
5/2/2026 | 12:30:00 PM | 281.96 | 278.71 | 278.7 | 488.02 | 480.52 | 485.26 | 81.3184 | 70.032 | 73.4172 | 2.1087 | 1.43 | 1.43 | 1.427 | 2.057 | 2.08 | 2.154 | Over-range | 59.99 | 20385 | 17012 | 16936 | 54332 | - - - | - - - | - - - | - - - | 20385 | 17012 | 16936 | 54332 | 2387 | 992 | 4365 | 7744 | - - - | - - - | - - - | - - - | 2387 | 992 | 4365 | 7744 | 22862 | 19468 | 20410 | 62741 | # # # | # # # | # # # | # # # | 0.892 | 0.874 | 0.83 | 0.866 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.968 | 0.987 | - - - | 0.142 | 1.48 | 1.5 | 1.54 | 1.42 | 1.51 | 1.5 | 49.65 | 55.51 | 60.55 | 0 | - - - | - - - | - - - | - - - | 22862 | 19468 | 20410 | 62741 | Over-range | 10340 | 9462 | 11385 | 31355 | 10061 | 9409 | 10515 | 30383 | 20294 | 16975 | 16890 | 54159 | 20294 | 16975 | 16890 | 54159 | - - - | - - - | - - - | - - -
5/2/2026 | 12:45:00 PM | 281.87 | 278.53 | 278.6 | 487.76 | 480.24 | 485.14 | 84.3402 | 72.1329 | 76.6374 | 2.1214 | 1.431 | 1.43 | 1.429 | 2.069 | 2.083 | 2.159 | Over-range | 59.99 | 21119 | 17473 | 17659 | 56251 | - - - | - - - | - - - | - - - | 21119 | 17473 | 17659 | 56251 | 2363 | 1104 | 4617 | 8083 | - - - | - - - | - - - | - - - | 2363 | 1104 | 4617 | 8083 | 23729 | 20058 | 21320 | 65108 | # # # | # # # | # # # | # # # | 0.89 | 0.871 | 0.828 | 0.864 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.967 | 0.987 | - - - | 0.144 | 1.51 | 1.51 | 1.57 | 1.44 | 1.53 | 1.53 | 50.3 | 56.25 | 60.81 | 0 | - - - | - - - | - - - | - - - | 23729 | 20058 | 21320 | 65108 | Over-range | 10812 | 9848 | 11941 | 32771 | 10550 | 9786 | 11012 | 31758 | 21045 | 17434 | 17596 | 56075 | 21045 | 17434 | 17596 | 56075 | - - - | - - - | - - - | - - -
5/2/2026 | 1:00:00 PM | 282.03 | 278.74 | 278.79 | 488.08 | 480.62 | 485.44 | 82.411 | 70.6898 | 74.9031 | 2.1043 | 1.431 | 1.429 | 1.428 | 2.066 | 2.072 | 2.152 | Over-range | 59.99 | 20687 | 17165 | 17300 | 55153 | - - - | - - - | - - - | - - - | 20687 | 17165 | 17300 | 55153 | 2323 | 1071 | 4487 | 7881 | - - - | - - - | - - - | - - - | 2323 | 1071 | 4487 | 7881 | 23185 | 19660 | 20837 | 63682 | # # # | # # # | # # # | # # # | 0.892 | 0.873 | 0.83 | 0.866 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.968 | 0.987 | - - - | 0.143 | 1.43 | 1.46 | 1.5 | 1.38 | 1.46 | 1.45 | 49.68 | 55.72 | 60.42 | 0 | - - - | - - - | - - - | - - - | 23185 | 19660 | 20837 | 63682 | Over-range | 10460 | 9580 | 11609 | 31820 | 10198 | 9520 | 10707 | 30828 | 20607 | 17120 | 17241 | 54968 | 20607 | 17120 | 17241 | 54968 | - - - | - - - | - - - | - - -
5/2/2026 | 1:15:00 PM | 282.01 | 278.76 | 278.87 | 488.04 | 480.73 | 485.49 | 85.2281 | 73.0871 | 78.1246 | 2.1385 | 1.432 | 1.43 | 1.429 | 2.071 | 2.066 | 2.143 | Over-range | 59.99 | 21412 | 17725 | 18112 | 57249 | - - - | - - - | - - - | - - - | 21412 | 17725 | 18112 | 57249 | 2303 | 1238 | 4694 | 8235 | - - - | - - - | - - - | - - - | 2303 | 1238 | 4694 | 8235 | 23991 | 20341 | 21751 | 66083 | # # # | # # # | # # # | # # # | 0.892 | 0.871 | 0.833 | 0.866 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.968 | 0.987 | - - - | 0.144 | 1.43 | 1.44 | 1.46 | 1.37 | 1.43 | 1.42 | 49.84 | 56.23 | 59.87 | 0 | - - - | - - - | - - - | - - - | 23991 | 20341 | 21751 | 66083 | Over-range | 10816 | 9976 | 12040 | 32996 | 10567 | 9899 | 11087 | 31952 | 21331 | 17664 | 18043 | 57038 | 21331 | 17664 | 18043 | 57038 | - - - | - - - | - - - | - - -
5/2/2026 | 1:30:00 PM | 282.13 | 278.76 | 278.89 | 488.17 | 480.7 | 485.64 | 85.9647 | 73.3191 | 78.8588 | 2.1386 | 1.432 | 1.431 | 1.43 | 2.076 | 2.065 | 2.149 | Over-range | 59.99 | 21616 | 17780 | 18257 | 57653 | - - - | - - - | - - - | - - - | 21616 | 17780 | 18257 | 57653 | 2282 | 1229 | 4795 | 8306 | - - - | - - - | - - - | - - - | 2282 | 1229 | 4795 | 8306 | 24211 | 20409 | 21958 | 66578 | # # # | # # # | # # # | # # # | 0.893 | 0.871 | 0.832 | 0.866 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.967 | 0.987 | - - - | 0.144 | 1.44 | 1.47 | 1.47 | 1.39 | 1.45 | 1.44 | 49.81 | 56.3 | 60.06 | 0 | - - - | - - - | - - - | - - - | 24211 | 20409 | 21958 | 66578 | Over-range | 10901 | 10017 | 12196 | 33288 | 10659 | 9941 | 11214 | 32235 | 21527 | 17721 | 18190 | 57438 | 21527 | 17721 | 18190 | 57438 | - - - | - - - | - - - | - - -
5/2/2026 | 1:45:00 PM | 282.21 | 278.86 | 278.92 | 488.35 | 480.8 | 485.71 | 84.466 | 72.0391 | 77.3633 | 2.1143 | 1.431 | 1.43 | 1.428 | 2.07 | 2.055 | 2.142 | Over-range | 59.99 | 21286 | 17506 | 17943 | 56735 | - - - | - - - | - - - | - - - | 21286 | 17506 | 17943 | 56735 | 2222 | 1171 | 4690 | 8084 | - - - | - - - | - - - | - - - | 2222 | 1171 | 4690 | 8084 | 23771 | 20041 | 21528 | 65339 | # # # | # # # | # # # | # # # | 0.896 | 0.874 | 0.834 | 0.868 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.967 | 0.987 | - - - | 0.142 | 1.43 | 1.45 | 1.45 | 1.39 | 1.43 | 1.42 | 49.06 | 55.66 | 59.54 | 0 | - - - | - - - | - - - | - - - | 23771 | 20041 | 21528 | 65339 | Over-range | 10571 | 9752 | 11889 | 32391 | 10335 | 9681 | 10925 | 31366 | 21198 | 17455 | 17863 | 56516 | 21198 | 17455 | 17863 | 56516 | - - - | - - - | - - - | - - -
5/2/2026 | 2:00:00 PM | 282.01 | 278.65 | 278.8 | 487.96 | 480.53 | 485.47 | 87.3968 | 74.3045 | 80.5086 | 2.0998 | 1.432 | 1.429 | 1.428 | 2.084 | 2.064 | 2.151 | Over-range | 59.99 | 21979 | 17992 | 18639 | 58610 | - - - | - - - | - - - | - - - | 21979 | 17992 | 18639 | 58610 | 2246 | 1289 | 4915 | 8450 | - - - | - - - | - - - | - - - | 2246 | 1289 | 4915 | 8450 | 24606 | 20675 | 22413 | 67694 | # # # | # # # | # # # | # # # | 0.893 | 0.87 | 0.832 | 0.866 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.967 | 0.986 | - - - | 0.144 | 1.4 | 1.42 | 1.41 | 1.36 | 1.39 | 1.37 | 49.89 | 56.61 | 60.06 | 0 | - - - | - - - | - - - | - - - | 24606 | 20675 | 22413 | 67694 | Over-range | 11058 | 10182 | 12444 | 33862 | 10827 | 10100 | 11432 | 32791 | 21884 | 17927 | 18555 | 58366 | 21884 | 17927 | 18555 | 58366 | - - - | - - - | - - - | - - -
5/2/2026 | 2:15:00 PM | 282.17 | 278.76 | 278.96 | 488.17 | 480.76 | 485.78 | 86.3348 | 73.3563 | 79.8826 | 2.0536 | 1.432 | 1.429 | 1.427 | 2.08 | 2.04 | 2.135 | Over-range | 59.99 | 21794 | 17806 | 18579 | 58179 | - - - | - - - | - - - | - - - | 21794 | 17806 | 18579 | 58179 | 2124 | 1305 | 4850 | 8278 | - - - | - - - | - - - | - - - | 2124 | 1305 | 4850 | 8278 | 24303 | 20408 | 22239 | 66951 | # # # | # # # | # # # | # # # | 0.897 | 0.873 | 0.835 | 0.869 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.967 | 0.987 | - - - | 0.142 | 1.39 | 1.41 | 1.39 | 1.35 | 1.38 | 1.36 | 48.92 | 55.98 | 59.1 | 0 | - - - | - - - | - - - | - - - | 24303 | 20408 | 22239 | 66951 | Over-range | 10745 | 9968 | 12216 | 33110 | 10533 | 9882 | 11212 | 32059 | 21712 | 17729 | 18499 | 57940 | 21712 | 17729 | 18499 | 57940 | - - - | - - - | - - - | - - -
5/2/2026 | 2:30:00 PM | 282.16 | 278.71 | 278.97 | 488.1 | 480.71 | 485.8 | 87.652 | 74.3933 | 81.1181 | 2.1666 | 1.432 | 1.43 | 1.427 | 2.087 | 2.05 | 2.144 | Over-range | 59.98 | 22083 | 18036 | 18825 | 58944 | - - - | - - - | - - - | - - - | 22083 | 18036 | 18825 | 58944 | 2160 | 1350 | 4958 | 8468 | - - - | - - - | - - - | - - - | 2160 | 1350 | 4958 | 8468 | 24684 | 20700 | 22591 | 67976 | # # # | # # # | # # # | # # # | 0.895 | 0.871 | 0.833 | 0.867 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.967 | 0.987 | - - - | 0.144 | 1.37 | 1.41 | 1.37 | 1.33 | 1.37 | 1.34 | 49.6 | 56.27 | 59.59 | 0 | - - - | - - - | - - - | - - - | 24684 | 20700 | 22591 | 67976 | Over-range | 11024 | 10156 | 12485 | 33845 | 10810 | 10066 | 11458 | 32769 | 21976 | 17977 | 18743 | 58696 | 21976 | 17977 | 18743 | 58696 | - - - | - - - | - - - | - - -
5/2/2026 | 2:45:00 PM | 281.89 | 278.43 | 278.72 | 487.6 | 480.26 | 485.37 | 88.1886 | 74.9022 | 81.8751 | 2.1527 | 1.431 | 1.429 | 1.428 | 2.086 | 2.045 | 2.136 | Over-range | 59.98 | 22202 | 18135 | 19023 | 59360 | - - - | - - - | - - - | - - - | 22202 | 18135 | 19023 | 59360 | 2117 | 1416 | 4973 | 8506 | - - - | - - - | - - - | - - - | 2117 | 1416 | 4973 | 8506 | 24817 | 20825 | 22785 | 68427 | # # # | # # # | # # # | # # # | 0.895 | 0.871 | 0.835 | 0.868 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.967 | 0.987 | - - - | 0.143 | 1.35 | 1.39 | 1.37 | 1.32 | 1.37 | 1.33 | 49.61 | 56.34 | 59.27 | 0 | - - - | - - - | - - - | - - - | 24817 | 20825 | 22785 | 68427 | Over-range | 11083 | 10235 | 12538 | 34029 | 10878 | 10136 | 11510 | 32948 | 22116 | 18072 | 18934 | 59122 | 22116 | 18072 | 18934 | 59122 | - - - | - - - | - - - | - - -
5/2/2026 | 3:00:00 PM | 282.21 | 278.83 | 279.06 | 488.25 | 480.92 | 485.9 | 86.8158 | 74.0017 | 80.7397 | 2.1728 | 1.431 | 1.429 | 1.427 | 2.073 | 2.02 | 2.116 | Over-range | 59.98 | 21967 | 17993 | 18878 | 58837 | - - - | - - - | - - - | - - - | 21967 | 17993 | 18878 | 58837 | 2031 | 1403 | 4862 | 8297 | - - - | - - - | - - - | - - - | 2031 | 1403 | 4862 | 8297 | 24437 | 20587 | 22480 | 67504 | # # # | # # # | # # # | # # # | 0.899 | 0.874 | 0.84 | 0.872 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.968 | 0.987 | - - - | 0.141 | 1.36 | 1.4 | 1.36 | 1.33 | 1.36 | 1.33 | 48.36 | 55.41 | 58.06 | 0 | - - - | - - - | - - - | - - - | 24437 | 20587 | 22480 | 67504 | Over-range | 10694 | 10001 | 12199 | 33070 | 10499 | 9902 | 11188 | 32012 | 21884 | 17931 | 18794 | 58609 | 21884 | 17931 | 18794 | 58609 | - - - | - - - | - - - | - - -
5/2/2026 | 3:15:00 PM | 281.96 | 278.5 | 278.72 | 487.76 | 480.3 | 485.41 | 89.5469 | 75.9324 | 83.1267 | 2.2306 | 1.431 | 1.429 | 1.427 | 2.082 | 2.038 | 2.132 | Over-range | 60 | 22597 | 18408 | 19353 | 60358 | - - - | - - - | - - - | - - - | 22597 | 18408 | 19353 | 60358 | 2093 | 1424 | 5072 | 8589 | - - - | - - - | - - - | - - - | 2093 | 1424 | 5072 | 8589 | 25205 | 21115 | 23137 | 69457 | # # # | # # # | # # # | # # # | 0.897 | 0.872 | 0.837 | 0.869 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.967 | 0.987 | - - - | 0.142 | 1.36 | 1.39 | 1.37 | 1.32 | 1.36 | 1.33 | 49.12 | 56.06 | 58.75 | 0 | - - - | - - - | - - - | - - - | 25205 | 21115 | 23137 | 69457 | Over-range | 11159 | 10342 | 12675 | 34357 | 10961 | 10243 | 11616 | 33266 | 22510 | 18337 | 19274 | 60121 | 22510 | 18337 | 19274 | 60121 | - - - | - - - | - - - | - - -
5/2/2026 | 3:30:00 PM | 281.93 | 278.51 | 278.65 | 487.78 | 480.24 | 485.29 | 89.8491 | 76.1025 | 83.2842 | 2.1942 | 1.431 | 1.429 | 1.427 | 2.077 | 2.039 | 2.131 | Over-range | 59.99 | 22701 | 18465 | 19400 | 60565 | - - - | - - - | - - - | - - - | 22701 | 18465 | 19400 | 60565 | 2099 | 1376 | 5092 | 8566 | - - - | - - - | - - - | - - - | 2099 | 1376 | 5092 | 8566 | 25290 | 21165 | 23173 | 69627 | # # # | # # # | # # # | # # # | 0.898 | 0.872 | 0.837 | 0.87 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.967 | 0.987 | - - - | 0.141 | 1.37 | 1.4 | 1.38 | 1.33 | 1.37 | 1.34 | 48.8 | 55.88 | 58.54 | 0 | - - - | - - - | - - - | - - - | 25290 | 21165 | 23173 | 69627 | Over-range | 11141 | 10341 | 12670 | 34338 | 10942 | 10249 | 11602 | 33252 | 22610 | 18408 | 19319 | 60337 | 22610 | 18408 | 19319 | 60337 | - - - | - - - | - - - | - - -
5/2/2026 | 3:45:00 PM | 282.02 | 278.67 | 278.82 | 487.96 | 480.59 | 485.5 | 88.368 | 75.248 | 82.3697 | 2.1731 | 1.431 | 1.428 | 1.426 | 2.066 | 2.011 | 2.104 | Over-range | 59.98 | 22403 | 18300 | 19329 | 60032 | - - - | - - - | - - - | - - - | 22403 | 18300 | 19329 | 60032 | 1974 | 1439 | 4957 | 8370 | - - - | - - - | - - - | - - - | 1974 | 1439 | 4957 | 8370 | 24859 | 20924 | 22918 | 68701 | # # # | # # # | # # # | # # # | 0.901 | 0.875 | 0.843 | 0.874 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.968 | 0.987 | - - - | 0.139 | 1.36 | 1.4 | 1.36 | 1.33 | 1.35 | 1.33 | 47.77 | 55.21 | 57.12 | 0 | - - - | - - - | - - - | - - - | 24859 | 20924 | 22918 | 68701 | Over-range | 10763 | 10141 | 12307 | 33387 | 10580 | 10038 | 11265 | 32321 | 22326 | 18238 | 19242 | 59806 | 22326 | 18238 | 19242 | 59806 | - - - | - - - | - - - | - - -
5/2/2026 | 4:00:00 PM | 281.87 | 278.44 | 278.63 | 487.64 | 480.17 | 485.24 | 91.0146 | 76.9489 | 84.7881 | 2.1888 | 1.431 | 1.428 | 1.427 | 2.081 | 2.03 | 2.126 | Over-range | 59.98 | 23005 | 18657 | 19796 | 61458 | - - - | - - - | - - - | - - - | 23005 | 18657 | 19796 | 61458 | 2014 | 1467 | 5180 | 8660 | - - - | - - - | - - - | - - - | 2014 | 1467 | 5180 | 8660 | 25615 | 21398 | 23591 | 70605 | # # # | # # # | # # # | # # # | 0.898 | 0.872 | 0.839 | 0.871 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.967 | 0.987 | - - - | 0.141 | 1.38 | 1.39 | 1.36 | 1.33 | 1.35 | 1.34 | 48.76 | 55.98 | 58.03 | 0 | - - - | - - - | - - - | - - - | 25615 | 21398 | 23591 | 70605 | Over-range | 11259 | 10475 | 12830 | 34744 | 11077 | 10372 | 11738 | 33647 | 22920 | 18596 | 19711 | 61228 | 22920 | 18596 | 19711 | 61228 | - - - | - - - | - - - | - - -
5/2/2026 | 4:15:00 PM | 281.91 | 278.48 | 278.61 | 487.74 | 480.17 | 485.25 | 89.4746 | 75.7166 | 83.1594 | 2.2125 | 1.431 | 1.429 | 1.427 | 2.071 | 2.021 | 2.118 | Over-range | 59.99 | 22670 | 18402 | 19451 | 60522 | - - - | - - - | - - - | - - - | 22670 | 18402 | 19451 | 60522 | 1977 | 1389 | 5072 | 8439 | - - - | - - - | - - - | - - - | 1977 | 1389 | 5072 | 8439 | 25170 | 21048 | 23127 | 69345 | # # # | # # # | # # # | # # # | 0.901 | 0.874 | 0.841 | 0.873 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.967 | 0.987 | - - - | 0.139 | 1.37 | 1.4 | 1.37 | 1.33 | 1.36 | 1.34 | 47.98 | 55.33 | 57.51 | 0 | - - - | - - - | - - - | - - - | 25170 | 21048 | 23127 | 69345 | Over-range | 10925 | 10214 | 12505 | 33831 | 10744 | 10119 | 11430 | 32761 | 22578 | 18345 | 19376 | 60300 | 22578 | 18345 | 19376 | 60300 | - - - | - - - | - - - | - - -
5/2/2026 | 4:30:00 PM | 281.85 | 278.43 | 278.6 | 487.62 | 480.15 | 485.18 | 90.8316 | 76.97 | 84.5522 | 2.2585 | 1.431 | 1.429 | 1.427 | 2.079 | 2.029 | 2.123 | Over-range | 59.97 | 22951 | 18662 | 19737 | 61350 | - - - | - - - | - - - | - - - | 22951 | 18662 | 19737 | 61350 | 2033 | 1472 | 5161 | 8666 | - - - | - - - | - - - | - - - | 2033 | 1472 | 5161 | 8666 | 25555 | 21398 | 23520 | 70473 | # # # | # # # | # # # | # # # | 0.898 | 0.872 | 0.839 | 0.871 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.967 | 0.987 | - - - | 0.141 | 1.37 | 1.39 | 1.35 | 1.33 | 1.35 | 1.32 | 48.73 | 55.88 | 58.02 | 0 | - - - | - - - | - - - | - - - | 25555 | 21398 | 23520 | 70473 | Over-range | 11231 | 10466 | 12787 | 34664 | 11045 | 10362 | 11699 | 33563 | 22850 | 18608 | 19655 | 61112 | 22850 | 18608 | 19655 | 61112 | - - - | - - - | - - - | - - -
5/2/2026 | 4:45:00 PM | 281.68 | 278.31 | 278.45 | 487.37 | 479.92 | 484.89 | 90.9707 | 77.1001 | 84.5656 | 2.2371 | 1.43 | 1.428 | 1.427 | 2.077 | 2.034 | 2.125 | Over-range | 59.99 | 22970 | 18687 | 19735 | 61392 | - - - | - - - | - - - | - - - | 22970 | 18687 | 19735 | 61392 | 2044 | 1458 | 5152 | 8654 | - - - | - - - | - - - | - - - | 2044 | 1458 | 5152 | 8654 | 25585 | 21430 | 23516 | 70532 | # # # | # # # | # # # | # # # | 0.898 | 0.872 | 0.839 | 0.87 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.967 | 0.987 | - - - | 0.141 | 1.38 | 1.4 | 1.36 | 1.34 | 1.36 | 1.33 | 48.81 | 55.92 | 58.01 | 0 | - - - | - - - | - - - | - - - | 25585 | 21430 | 23516 | 70532 | Over-range | 11262 | 10487 | 12783 | 34709 | 11075 | 10385 | 11699 | 33613 | 22871 | 18637 | 19656 | 61164 | 22871 | 18637 | 19656 | 61164 | - - - | - - - | - - - | - - -
5/2/2026 | 5:00:00 PM | 281.77 | 278.32 | 278.43 | 487.49 | 479.86 | 484.96 | 88.3876 | 74.637 | 82.0988 | 2.1769 | 1.43 | 1.428 | 1.426 | 2.071 | 2.017 | 2.117 | Over-range | 59.99 | 22413 | 18148 | 19203 | 59764 | - - - | - - - | - - - | - - - | 22413 | 18148 | 19203 | 59764 | 1919 | 1328 | 5009 | 8256 | - - - | - - - | - - - | - - - | 1919 | 1328 | 5009 | 8256 | 24842 | 20730 | 22809 | 68382 | # # # | # # # | # # # | # # # | 0.902 | 0.875 | 0.842 | 0.874 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.967 | 0.987 | - - - | 0.138 | 1.37 | 1.4 | 1.36 | 1.34 | 1.36 | 1.34 | 47.54 | 55.05 | 57.24 | 0 | - - - | - - - | - - - | - - - | 24842 | 20730 | 22809 | 68382 | Over-range | 10705 | 10016 | 12302 | 33213 | 10532 | 9927 | 11236 | 32171 | 22340 | 18089 | 19121 | 59550 | 22340 | 18089 | 19121 | 59550 | - - - | - - - | - - - | - - -
5/2/2026 | 5:15:00 PM | 282.06 | 278.69 | 278.87 | 488.01 | 480.64 | 485.59 | 90.1109 | 76.2578 | 84.0151 | 2.1632 | 1.432 | 1.429 | 1.427 | 2.076 | 2.023 | 2.117 | Over-range | 60 | 22830 | 18532 | 19681 | 61043 | - - - | - - - | - - - | - - - | 22830 | 18532 | 19681 | 61043 | 1971 | 1447 | 5119 | 8537 | - - - | - - - | - - - | - - - | 1971 | 1447 | 5119 | 8537 | 25375 | 21225 | 23396 | 69996 | # # # | # # # | # # # | # # # | 0.9 | 0.873 | 0.841 | 0.872 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.968 | 0.987 | - - - | 0.14 | 1.4 | 1.42 | 1.38 | 1.37 | 1.38 | 1.36 | 48.32 | 55.65 | 57.52 | 0 | - - - | - - - | - - - | - - - | 25375 | 21225 | 23396 | 69996 | Over-range | 11070 | 10345 | 12646 | 34239 | 10893 | 10243 | 11563 | 33158 | 22737 | 18471 | 19607 | 60815 | 22737 | 18471 | 19607 | 60815 | - - - | - - - | - - - | - - -
5/2/2026 | 5:30:00 PM | 281.86 | 278.61 | 278.7 | 487.78 | 480.47 | 485.22 | 89.791 | 76.3949 | 83.3795 | 2.1708 | 1.431 | 1.429 | 1.427 | 2.068 | 2.03 | 2.116 | Over-range | 59.97 | 22718 | 18566 | 19530 | 60813 | - - - | - - - | - - - | - - - | 22718 | 18566 | 19530 | 60813 | 2061 | 1417 | 5037 | 8514 | - - - | - - - | - - - | - - - | 2061 | 1417 | 5037 | 8514 | 25263 | 21252 | 23202 | 69717 | # # # | # # # | # # # | # # # | 0.899 | 0.874 | 0.842 | 0.872 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.968 | 0.987 | - - - | 0.14 | 1.39 | 1.42 | 1.38 | 1.36 | 1.37 | 1.35 | 48.35 | 55.53 | 57.5 | 0 | - - - | - - - | - - - | - - - | 25263 | 21252 | 23202 | 69717 | Over-range | 11045 | 10340 | 12523 | 34080 | 10850 | 10242 | 11466 | 33000 | 22629 | 18510 | 19452 | 60591 | 22629 | 18510 | 19452 | 60591 | - - - | - - - | - - - | - - -
5/2/2026 | 5:45:00 PM | 282.2 | 278.8 | 278.95 | 488.25 | 480.78 | 485.78 | 87.7254 | 74.3367 | 81.6905 | 2.1053 | 1.431 | 1.428 | 1.426 | 2.072 | 2.013 | 2.112 | Over-range | 60 | 22263 | 18100 | 19159 | 59522 | - - - | - - - | - - - | - - - | 22263 | 18100 | 19159 | 59522 | 1936 | 1367 | 4949 | 8252 | - - - | - - - | - - - | - - - | 1936 | 1367 | 4949 | 8252 | 24693 | 20681 | 22740 | 68114 | # # # | # # # | # # # | # # # | 0.902 | 0.875 | 0.843 | 0.874 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.968 | 0.987 | - - - | 0.139 | 1.39 | 1.41 | 1.37 | 1.35 | 1.37 | 1.34 | 47.73 | 55.12 | 57.19 | 0 | - - - | - - - | - - - | - - - | 24693 | 20681 | 22740 | 68114 | Over-range | 10671 | 10002 | 12242 | 33097 | 10493 | 9908 | 11197 | 32051 | 22170 | 18034 | 19092 | 59296 | 22170 | 18034 | 19092 | 59296 | - - - | - - - | - - - | - - -
5/2/2026 | 6:00:00 PM | 281.83 | 278.43 | 278.55 | 487.62 | 480.11 | 485.11 | 89.8683 | 75.8954 | 83.2451 | 2.1041 | 1.431 | 1.429 | 1.427 | 2.074 | 2.037 | 2.129 | Over-range | 59.98 | 22737 | 18431 | 19438 | 60606 | - - - | - - - | - - - | - - - | 22737 | 18431 | 19438 | 60606 | 2038 | 1339 | 5093 | 8470 | - - - | - - - | - - - | - - - | 2038 | 1339 | 5093 | 8470 | 25286 | 21104 | 23157 | 69548 | # # # | # # # | # # # | # # # | 0.899 | 0.873 | 0.839 | 0.871 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.967 | 0.987 | - - - | 0.14 | 1.39 | 1.41 | 1.38 | 1.35 | 1.38 | 1.35 | 48.39 | 55.67 | 57.89 | 0 | - - - | - - - | - - - | - - - | 25286 | 21104 | 23157 | 69548 | Over-range | 11057 | 10279 | 12581 | 34101 | 10868 | 10191 | 11504 | 33033 | 22646 | 18376 | 19361 | 60383 | 22646 | 18376 | 19361 | 60383 | - - - | - - - | - - - | - - -
5/2/2026 | 6:15:00 PM | 282.1 | 278.8 | 278.87 | 488.17 | 480.75 | 485.58 | 87.0569 | 73.8657 | 80.6385 | 2.0652 | 1.431 | 1.428 | 1.427 | 2.066 | 2.021 | 2.116 | Over-range | 59.99 | 22092 | 18004 | 18905 | 59001 | - - - | - - - | - - - | - - - | 22092 | 18004 | 18905 | 59001 | 1997 | 1288 | 4880 | 8165 | - - - | - - - | - - - | - - - | 1997 | 1288 | 4880 | 8165 | 24500 | 20553 | 22443 | 67496 | # # # | # # # | # # # | # # # | 0.902 | 0.876 | 0.842 | 0.874 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.968 | 0.987 | - - - | 0.138 | 1.4 | 1.42 | 1.39 | 1.37 | 1.38 | 1.36 | 47.57 | 54.92 | 57.26 | 0 | - - - | - - - | - - - | - - - | 24500 | 20553 | 22443 | 67496 | Over-range | 10582 | 9911 | 12091 | 32765 | 10391 | 9827 | 11062 | 31731 | 22012 | 17941 | 18836 | 58789 | 22012 | 17941 | 18836 | 58789 | - - - | - - - | - - - | - - -
5/2/2026 | 6:30:00 PM | 282.3 | 278.85 | 278.96 | 488.42 | 480.79 | 485.89 | 89.06 | 74.8584 | 82.2623 | 2.0405 | 1.431 | 1.429 | 1.427 | 2.082 | 2.045 | 2.143 | Over-range | 59.99 | 22561 | 18203 | 19171 | 59935 | - - - | - - - | - - - | - - - | 22561 | 18203 | 19171 | 59935 | 2050 | 1246 | 5089 | 8385 | - - - | - - - | - - - | - - - | 2050 | 1246 | 5089 | 8385 | 25100 | 20845 | 22914 | 68858 | # # # | # # # | # # # | # # # | 0.899 | 0.873 | 0.837 | 0.87 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.966 | 0.987 | - - - | 0.14 | 1.4 | 1.41 | 1.4 | 1.36 | 1.38 | 1.37 | 48.49 | 55.72 | 58.47 | 0 | - - - | - - - | - - - | - - - | 25100 | 20845 | 22914 | 68858 | Over-range | 10993 | 10153 | 12548 | 33889 | 10800 | 10076 | 11469 | 32835 | 22460 | 18150 | 19104 | 59713 | 22460 | 18150 | 19104 | 59713 | - - - | - - - | - - - | - - -
5/2/2026 | 6:45:00 PM | 282.57 | 279.15 | 279.17 | 488.95 | 481.22 | 486.27 | 86.3448 | 72.8124 | 79.5307 | 2.053 | 1.43 | 1.428 | 1.426 | 2.071 | 2.03 | 2.134 | Over-range | 59.99 | 21945 | 17774 | 18582 | 58301 | - - - | - - - | - - - | - - - | 21945 | 17774 | 18582 | 58301 | 2013 | 1156 | 4885 | 8054 | - - - | - - - | - - - | - - - | 2013 | 1156 | 4885 | 8054 | 24328 | 20276 | 22148 | 66752 | # # # | # # # | # # # | # # # | 0.902 | 0.877 | 0.839 | 0.873 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.967 | 0.987 | - - - | 0.138 | 1.4 | 1.42 | 1.38 | 1.36 | 1.38 | 1.36 | 47.45 | 54.83 | 57.87 | 0 | - - - | - - - | - - - | - - - | 24328 | 20276 | 22148 | 66752 | Over-range | 10490 | 9753 | 12045 | 32489 | 10295 | 9684 | 11010 | 31475 | 21857 | 17717 | 18521 | 58095 | 21857 | 17717 | 18521 | 58095 | - - - | - - - | - - - | - - -
5/2/2026 | 7:00:00 PM | 282.86 | 279.48 | 279.56 | 489.45 | 481.88 | 486.86 | 88.3892 | 74.5401 | 81.4244 | 2.049 | 1.431 | 1.428 | 1.426 | 2.08 | 2.048 | 2.146 | Over-range | 60.01 | 22421 | 18166 | 19006 | 59593 | - - - | - - - | - - - | - - - | 22421 | 18166 | 19006 | 59593 | 2106 | 1229 | 5020 | 8355 | - - - | - - - | - - - | - - - | 2106 | 1229 | 5020 | 8355 | 24949 | 20796 | 22725 | 68470 | # # # | # # # | # # # | # # # | 0.899 | 0.874 | 0.836 | 0.87 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.967 | 0.987 | - - - | 0.14 | 1.41 | 1.42 | 1.39 | 1.37 | 1.38 | 1.37 | 48.44 | 55.68 | 58.61 | 0 | - - - | - - - | - - - | - - - | 24949 | 20796 | 22725 | 68470 | Over-range | 10936 | 10120 | 12451 | 33701 | 10731 | 10044 | 11394 | 32649 | 22336 | 18103 | 18929 | 59368 | 22336 | 18103 | 18929 | 59368 | - - - | - - - | - - - | - - -
5/2/2026 | 7:15:00 PM | 283.17 | 280.07 | 279.98 | 490.23 | 482.87 | 487.35 | 86.6265 | 73.7498 | 79.5009 | 2.1268 | 1.431 | 1.428 | 1.426 | 2.063 | 2.039 | 2.131 | Over-range | 59.99 | 22034 | 18061 | 18644 | 58739 | - - - | - - - | - - - | - - - | 22034 | 18061 | 18644 | 58739 | 2163 | 1189 | 4844 | 8196 | - - - | - - - | - - - | - - - | 2163 | 1189 | 4844 | 8196 | 24466 | 20610 | 22211 | 67287 | # # # | # # # | # # # | # # # | 0.901 | 0.876 | 0.839 | 0.873 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.968 | 0.987 | - - - | 0.14 | 1.43 | 1.42 | 1.37 | 1.38 | 1.37 | 1.37 | 47.73 | 54.89 | 58.01 | 0 | - - - | - - - | - - - | - - - | 24466 | 20610 | 22211 | 67287 | Over-range | 10625 | 9924 | 12065 | 32802 | 10402 | 9852 | 11050 | 31762 | 21956 | 18009 | 18559 | 58524 | 21956 | 18009 | 18559 | 58524 | - - - | - - - | - - - | - - -
5/2/2026 | 7:30:00 PM | 283.17 | 280.09 | 279.96 | 490.27 | 482.87 | 487.33 | 86.9517 | 74.0188 | 79.5577 | 2.1157 | 1.432 | 1.429 | 1.426 | 2.064 | 2.048 | 2.138 | Over-range | 59.97 | 22098 | 18121 | 18628 | 58847 | - - - | - - - | - - - | - - - | 22098 | 18121 | 18628 | 58847 | 2221 | 1152 | 4856 | 8228 | - - - | - - - | - - - | - - - | 2221 | 1152 | 4856 | 8228 | 24568 | 20693 | 22231 | 67492 | # # # | # # # | # # # | # # # | 0.899 | 0.876 | 0.838 | 0.872 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.967 | 0.987 | - - - | 0.14 | 1.41 | 1.43 | 1.38 | 1.38 | 1.37 | 1.37 | 48.05 | 55.09 | 58.4 | 0 | - - - | - - - | - - - | - - - | 24568 | 20693 | 22231 | 67492 | Over-range | 10729 | 9987 | 12129 | 33034 | 10497 | 9920 | 11115 | 31993 | 22008 | 18066 | 18551 | 58626 | 22008 | 18066 | 18551 | 58626 | - - - | - - - | - - - | - - -
5/2/2026 | 7:45:00 PM | 283.24 | 280.2 | 280.02 | 490.44 | 483.03 | 487.42 | 87.3049 | 74.4524 | 79.7219 | 2.1083 | 1.432 | 1.429 | 1.427 | 2.062 | 2.054 | 2.142 | Over-range | 59.98 | 22166 | 18222 | 18646 | 59034 | - - - | - - - | - - - | - - - | 22166 | 18222 | 18646 | 59034 | 2295 | 1148 | 4853 | 8296 | - - - | - - - | - - - | - - - | 2295 | 1148 | 4853 | 8296 | 24670 | 20819 | 22278 | 67767 | # # # | # # # | # # # | # # # | 0.899 | 0.875 | 0.837 | 0.871 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.967 | 0.987 | - - - | 0.141 | 1.42 | 1.43 | 1.37 | 1.38 | 1.36 | 1.36 | 48.26 | 55.26 | 58.7 | 0 | - - - | - - - | - - - | - - - | 24670 | 20819 | 22278 | 67767 | Over-range | 10821 | 10065 | 12186 | 33261 | 10575 | 9999 | 11178 | 32209 | 22080 | 18164 | 18563 | 58808 | 22080 | 18164 | 18563 | 58808 | - - - | - - - | - - - | - - -
5/2/2026 | 8:00:00 PM | 283.39 | 280.45 | 280.18 | 490.81 | 483.42 | 487.63 | 85.5282 | 73.4313 | 77.5986 | 2.2829 | 1.431 | 1.428 | 1.425 | 2.052 | 2.057 | 2.141 | Over-range | 59.97 | 21731 | 18014 | 18167 | 57911 | - - - | - - - | - - - | - - - | 21731 | 18014 | 18167 | 57911 | 2331 | 1087 | 4697 | 8114 | - - - | - - - | - - - | - - - | 2331 | 1087 | 4697 | 8114 | 24171 | 20544 | 21693 | 66409 | # # # | # # # | # # # | # # # | 0.899 | 0.877 | 0.838 | 0.872 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.968 | 0.987 | - - - | 0.14 | 1.4 | 1.4 | 1.35 | 1.37 | 1.35 | 1.34 | 47.95 | 54.82 | 58.59 | 0 | - - - | - - - | - - - | - - - | 24171 | 20544 | 21693 | 66409 | Over-range | 10573 | 9873 | 11848 | 32480 | 10313 | 9813 | 10878 | 31450 | 21643 | 17955 | 18096 | 57694 | 21643 | 17955 | 18096 | 57694 | - - - | - - - | - - - | - - -
5/2/2026 | 8:15:00 PM | 283.96 | 280.98 | 280.81 | 491.73 | 484.43 | 488.7 | 86.8083 | 74.272 | 78.7952 | 2.2776 | 1.431 | 1.428 | 1.426 | 2.066 | 2.072 | 2.159 | Over-range | 59.97 | 22050 | 18221 | 18420 | 58691 | - - - | - - - | - - - | - - - | 22050 | 18221 | 18420 | 58691 | 2391 | 1116 | 4836 | 8343 | - - - | - - - | - - - | - - - | 2391 | 1116 | 4836 | 8343 | 24601 | 20833 | 22092 | 67526 | # # # | # # # | # # # | # # # | 0.896 | 0.875 | 0.834 | 0.869 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.967 | 0.987 | - - - | 0.142 | 1.43 | 1.42 | 1.38 | 1.39 | 1.37 | 1.38 | 48.84 | 55.47 | 59.47 | 0 | - - - | - - - | - - - | - - - | 24601 | 20833 | 22092 | 67526 | Over-range | 10903 | 10096 | 12192 | 33380 | 10637 | 10034 | 11192 | 32321 | 21939 | 18173 | 18347 | 58459 | 21939 | 18173 | 18347 | 58459 | - - - | - - - | - - - | - - -
5/2/2026 | 8:30:00 PM | 283.94 | 281.07 | 280.84 | 491.79 | 484.58 | 488.66 | 83.4792 | 71.8705 | 75.8703 | 2.218 | 1.431 | 1.428 | 1.425 | 2.05 | 2.046 | 2.134 | Over-range | 59.98 | 21291 | 17699 | 17839 | 56830 | - - - | - - - | - - - | - - - | 21291 | 17699 | 17839 | 56830 | 2279 | 1073 | 4566 | 7918 | - - - | - - - | - - - | - - - | 2279 | 1073 | 4566 | 7918 | 23630 | 20148 | 21253 | 65031 | # # # | # # # | # # # | # # # | 0.901 | 0.878 | 0.839 | 0.874 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.968 | 0.987 | - - - | 0.139 | 1.42 | 1.41 | 1.37 | 1.38 | 1.36 | 1.37 | 47.39 | 54.38 | 58.29 | 0 | - - - | - - - | - - - | - - - | 23630 | 20148 | 21253 | 65031 | Over-range | 10238 | 9622 | 11547 | 31593 | 9981 | 9561 | 10606 | 30585 | 21209 | 17649 | 17751 | 56610 | 21209 | 17649 | 17751 | 56610 | - - - | - - - | - - - | - - -
5/2/2026 | 8:45:00 PM | 283.81 | 280.9 | 280.7 | 491.53 | 484.29 | 488.45 | 86.9412 | 74.4269 | 78.6698 | 2.2289 | 1.432 | 1.429 | 1.426 | 2.062 | 2.079 | 2.16 | Over-range | 59.98 | 22073 | 18254 | 18379 | 58706 | - - - | - - - | - - - | - - - | 22073 | 18254 | 18379 | 58706 | 2430 | 1065 | 4814 | 8309 | - - - | - - - | - - - | - - - | 2430 | 1065 | 4814 | 8309 | 24628 | 20873 | 22048 | 67549 | # # # | # # # | # # # | # # # | 0.896 | 0.875 | 0.834 | 0.869 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.967 | 0.987 | - - - | 0.141 | 1.44 | 1.43 | 1.4 | 1.4 | 1.38 | 1.4 | 48.77 | 55.51 | 59.56 | 0 | - - - | - - - | - - - | - - - | 24628 | 20873 | 22048 | 67549 | Over-range | 10915 | 10119 | 12174 | 33397 | 10641 | 10062 | 11181 | 32347 | 21978 | 18203 | 18293 | 58475 | 21978 | 18203 | 18293 | 58475 | - - - | - - - | - - - | - - -
5/2/2026 | 9:00:00 PM | 284.03 | 281.13 | 280.89 | 491.93 | 484.66 | 488.78 | 84.0131 | 72.0714 | 75.8288 | 2.1624 | 1.431 | 1.428 | 1.426 | 2.058 | 2.071 | 2.158 | Over-range | 59.98 | 21366 | 17724 | 17723 | 56812 | - - - | - - - | - - - | - - - | 21366 | 17724 | 17723 | 56812 | 2384 | 981 | 4609 | 7974 | - - - | - - - | - - - | - - - | 2384 | 981 | 4609 | 7974 | 23796 | 20213 | 21250 | 65260 | # # # | # # # | # # # | # # # | 0.898 | 0.877 | 0.834 | 0.871 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.967 | 0.987 | - - - | 0.14 | 1.43 | 1.41 | 1.39 | 1.38 | 1.37 | 1.38 | 48.24 | 54.89 | 59.56 | 0 | - - - | - - - | - - - | - - - | 23796 | 20213 | 21250 | 65260 | Over-range | 10467 | 9714 | 11720 | 32094 | 10191 | 9664 | 10775 | 31088 | 21269 | 17685 | 17635 | 56589 | 21269 | 17685 | 17635 | 56589 | - - - | - - - | - - - | - - -
5/2/2026 | 9:15:00 PM | 284.23 | 281.41 | 281.17 | 492.33 | 485.2 | 489.18 | 82.6787 | 71.1855 | 74.6159 | 2.1324 | 1.431 | 1.428 | 1.425 | 2.058 | 2.069 | 2.156 | Over-range | 59.99 | 21027 | 17521 | 17450 | 55998 | - - - | - - - | - - - | - - - | 21027 | 17521 | 17450 | 55998 | 2398 | 972 | 4498 | 7869 | - - - | - - - | - - - | - - - | 2398 | 972 | 4498 | 7869 | 23428 | 19978 | 20924 | 64331 | # # # | # # # | # # # | # # # | 0.898 | 0.877 | 0.834 | 0.871 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.968 | 0.987 | - - - | 0.141 | 1.45 | 1.42 | 1.4 | 1.4 | 1.38 | 1.4 | 48.25 | 54.85 | 59.67 | 0 | - - - | - - - | - - - | - - - | 23428 | 19978 | 20924 | 64331 | Over-range | 10320 | 9593 | 11542 | 31645 | 10038 | 9543 | 10629 | 30651 | 20939 | 17464 | 17369 | 55772 | 20939 | 17464 | 17369 | 55772 | - - - | - - - | - - - | - - -
5/2/2026 | 9:30:00 PM | 284.37 | 281.59 | 281.35 | 492.58 | 485.53 | 489.44 | 85 | 73.2477 | 76.433 | 2.1965 | 1.432 | 1.428 | 1.426 | 2.062 | 2.093 | 2.172 | Over-range | 59.99 | 21543 | 17989 | 17813 | 57345 | - - - | - - - | - - - | - - - | 21543 | 17989 | 17813 | 57345 | 2565 | 996 | 4642 | 8204 | - - - | - - - | - - - | - - - | 2565 | 996 | 4642 | 8204 | 24122 | 20589 | 21467 | 66178 | # # # | # # # | # # # | # # # | 0.893 | 0.874 | 0.83 | 0.867 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.967 | 0.987 | - - - | 0.143 | 1.46 | 1.43 | 1.42 | 1.41 | 1.39 | 1.41 | 49.46 | 55.79 | 60.66 | 0 | - - - | - - - | - - - | - - - | 24122 | 20589 | 21467 | 66178 | Over-range | 10845 | 10012 | 11976 | 33017 | 10537 | 9962 | 11039 | 31982 | 21438 | 17932 | 17745 | 57115 | 21438 | 17932 | 17745 | 57115 | - - - | - - - | - - - | - - -
5/2/2026 | 9:45:00 PM | 284.98 | 282.2 | 281.83 | 493.72 | 486.42 | 490.35 | 81.0551 | 69.7565 | 72.333 | 2.0812 | 1.431 | 1.428 | 1.425 | 2.051 | 2.078 | 2.172 | Over-range | 59.99 | 20676 | 17250 | 16892 | 54818 | - - - | - - - | - - - | - - - | 20676 | 17250 | 16892 | 54818 | 2498 | 792 | 4387 | 7677 | - - - | - - - | - - - | - - - | 2498 | 792 | 4387 | 7677 | 23027 | 19630 | 20331 | 62988 | # # # | # # # | # # # | # # # | 0.898 | 0.879 | 0.831 | 0.87 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.968 | 0.987 | - - - | 0.14 | 1.46 | 1.44 | 1.41 | 1.41 | 1.39 | 1.42 | 47.95 | 54.48 | 60.43 | 0 | - - - | - - - | - - - | - - - | 23027 | 19630 | 20331 | 62988 | Over-range | 10126 | 9364 | 11308 | 31005 | 9813 | 9330 | 10423 | 30039 | 20592 | 17194 | 16815 | 54600 | 20592 | 17194 | 16815 | 54600 | - - - | - - - | - - - | - - -
5/2/2026 | 10:00:00 PM | 285.07 | 282.33 | 282.09 | 493.84 | 486.83 | 490.68 | 79.663 | 68.798 | 71.5417 | 2.0259 | 1.431 | 1.428 | 1.426 | 2.055 | 2.068 | 2.161 | Over-range | 60 | 20308 | 17017 | 16740 | 54065 | - - - | - - - | - - - | - - - | 20308 | 17017 | 16740 | 54065 | 2433 | 867 | 4282 | 7582 | - - - | - - - | - - - | - - - | 2433 | 867 | 4282 | 7582 | 22634 | 19369 | 20117 | 62120 | # # # | # # # | # # # | # # # | 0.897 | 0.879 | 0.832 | 0.87 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.968 | 0.987 | - - - | 0.14 | 1.47 | 1.45 | 1.43 | 1.42 | 1.41 | 1.43 | 48.12 | 54.43 | 60.32 | 0 | - - - | - - - | - - - | - - - | 22634 | 19369 | 20117 | 62120 | Over-range | 9984 | 9244 | 11152 | 30572 | 9683 | 9203 | 10297 | 29617 | 20234 | 16967 | 16650 | 53851 | 20234 | 16967 | 16650 | 53851 | - - - | - - - | - - - | - - -
5/2/2026 | 10:15:00 PM | 285.26 | 282.6 | 282.37 | 494.2 | 487.36 | 491.06 | 79.5484 | 69.0219 | 71.25 | 2.0715 | 1.432 | 1.428 | 1.426 | 2.056 | 2.08 | 2.166 | Over-range | 59.98 | 20241 | 17064 | 16675 | 53980 | - - - | - - - | - - - | - - - | 20241 | 17064 | 16675 | 53980 | 2507 | 870 | 4247 | 7624 | - - - | - - - | - - - | - - - | 2507 | 870 | 4247 | 7624 | 22615 | 19447 | 20061 | 62123 | # # # | # # # | # # # | # # # | 0.895 | 0.877 | 0.831 | 0.869 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.969 | 0.987 | - - - | 0.141 | 1.48 | 1.46 | 1.45 | 1.43 | 1.42 | 1.45 | 48.65 | 54.75 | 60.59 | 0 | - - - | - - - | - - - | - - - | 22615 | 19447 | 20061 | 62123 | Over-range | 10074 | 9322 | 11147 | 30725 | 9757 | 9281 | 10307 | 29764 | 20145 | 17007 | 16607 | 53759 | 20145 | 17007 | 16607 | 53759 | - - - | - - - | - - - | - - -
5/2/2026 | 10:30:00 PM | 285.07 | 282.35 | 282.15 | 493.82 | 486.92 | 490.74 | 81.7157 | 70.425 | 73.0896 | 2.0898 | 1.433 | 1.428 | 1.426 | 2.072 | 2.108 | 2.193 | Over-range | 59.98 | 20714 | 17348 | 16994 | 55057 | - - - | - - - | - - - | - - - | 20714 | 17348 | 16994 | 55057 | 2584 | 872 | 4426 | 7882 | - - - | - - - | - - - | - - - | 2584 | 872 | 4426 | 7882 | 23239 | 19843 | 20576 | 63658 | # # # | # # # | # # # | # # # | 0.891 | 0.874 | 0.826 | 0.865 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.967 | 0.986 | - - - | 0.143 | 1.49 | 1.45 | 1.45 | 1.42 | 1.42 | 1.45 | 49.74 | 55.74 | 61.78 | 0 | - - - | - - - | - - - | - - - | 23239 | 19843 | 20576 | 63658 | Over-range | 10526 | 9629 | 11596 | 31940 | 10204 | 9589 | 10718 | 30952 | 20641 | 17279 | 16908 | 54828 | 20641 | 17279 | 16908 | 54828 | - - - | - - - | - - - | - - -
5/2/2026 | 10:45:00 PM | 285.39 | 282.71 | 282.42 | 494.44 | 487.47 | 491.2 | 76.602 | 66.277 | 67.8728 | 2.0069 | 1.432 | 1.429 | 1.426 | 2.053 | 2.087 | 2.185 | Over-range | 60 | 19540 | 16443 | 15846 | 51829 | - - - | - - - | - - - | - - - | 19540 | 16443 | 15846 | 51829 | 2494 | 653 | 4070 | 7217 | - - - | - - - | - - - | - - - | 2494 | 653 | 4070 | 7217 | 21786 | 18679 | 19113 | 59578 | # # # | # # # | # # # | # # # | 0.897 | 0.88 | 0.829 | 0.87 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.968 | 0.987 | - - - | 0.139 | 1.5 | 1.47 | 1.49 | 1.45 | 1.45 | 1.48 | 48 | 54.04 | 61.08 | 0 | - - - | - - - | - - - | - - - | 21786 | 18679 | 19113 | 59578 | Over-range | 9622 | 8856 | 10681 | 29360 | 9293 | 8832 | 9875 | 28459 | 19448 | 16397 | 15778 | 51623 | 19448 | 16397 | 15778 | 51623 | - - - | - - - | - - - | - - -
5/2/2026 | 11:00:00 PM | 285.75 | 283.19 | 282.91 | 495.13 | 488.37 | 491.91 | 75.1964 | 65.5884 | 66.7636 | 2.003 | 1.432 | 1.428 | 1.425 | 2.048 | 2.079 | 2.173 | Over-range | 59.99 | 19211 | 16321 | 15657 | 51189 | - - - | - - - | - - - | - - - | 19211 | 16321 | 15657 | 51189 | 2499 | 682 | 3923 | 7104 | - - - | - - - | - - - | - - - | 2499 | 682 | 3923 | 7104 | 21412 | 18516 | 18827 | 58755 | # # # | # # # | # # # | # # # | 0.897 | 0.881 | 0.832 | 0.871 | # # # | # # # | # # # | - - - | 0.991 | 0.999 | 0.97 | 0.987 | - - - | 0.139 | 1.51 | 1.46 | 1.46 | 1.44 | 1.43 | 1.47 | 47.86 | 53.75 | 60.65 | 0 | - - - | - - - | - - - | - - - | 21412 | 18516 | 18827 | 58755 | Over-range | 9445 | 8738 | 10451 | 28822 | 9109 | 8711 | 9687 | 27933 | 19119 | 16260 | 15605 | 50985 | 19119 | 16260 | 15605 | 50985 | - - - | - - - | - - - | - - -
5/2/2026 | 11:15:00 PM | 285.74 | 283.01 | 282.77 | 494.99 | 488.01 | 491.84 | 74.1803 | 64.2752 | 65.6848 | 1.9606 | 1.431 | 1.428 | 1.425 | 2.056 | 2.082 | 2.19 | Over-range | 59.98 | 18957 | 16004 | 15337 | 50298 | - - - | - - - | - - - | - - - | 18957 | 16004 | 15337 | 50298 | 2457 | 604 | 3905 | 6966 | - - - | - - - | - - - | - - - | 2457 | 604 | 3905 | 6966 | 21124 | 18135 | 18513 | 57772 | # # # | # # # | # # # | # # # | 0.897 | 0.882 | 0.829 | 0.871 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.969 | 0.987 | - - - | 0.139 | 1.5 | 1.46 | 1.47 | 1.44 | 1.43 | 1.47 | 47.83 | 53.45 | 61.4 | 0 | - - - | - - - | - - - | - - - | 21124 | 18135 | 18513 | 57772 | Over-range | 9308 | 8524 | 10364 | 28401 | 8978 | 8503 | 9600 | 27534 | 18868 | 15968 | 15260 | 50096 | 18868 | 15968 | 15260 | 50096 | - - - | - - - | - - - | - - -
5/2/2026 | 11:30:00 PM | 286.05 | 283.33 | 283.11 | 495.54 | 488.6 | 492.41 | 73.4706 | 63.774 | 64.8555 | 1.9446 | 1.432 | 1.429 | 1.425 | 2.053 | 2.084 | 2.191 | Over-range | 59.99 | 18789 | 15905 | 15158 | 49852 | - - - | - - - | - - - | - - - | 18789 | 15905 | 15158 | 49852 | 2493 | 575 | 3854 | 6922 | - - - | - - - | - - - | - - - | 2493 | 575 | 3854 | 6922 | 20945 | 18015 | 18304 | 57265 | # # # | # # # | # # # | # # # | 0.897 | 0.883 | 0.828 | 0.871 | # # # | # # # | # # # | - - - | 0.991 | 0.999 | 0.969 | 0.987 | - - - | 0.139 | 1.52 | 1.48 | 1.49 | 1.46 | 1.46 | 1.49 | 47.88 | 53.4 | 61.48 | 0 | - - - | - - - | - - - | - - - | 20945 | 18015 | 18304 | 57265 | Over-range | 9246 | 8456 | 10258 | 28162 | 8903 | 8436 | 9506 | 27298 | 18690 | 15866 | 15095 | 49651 | 18690 | 15866 | 15095 | 49651 | - - - | - - - | - - - | - - -
5/2/2026 | 11:45:00 PM | 286.52 | 283.86 | 283.68 | 496.36 | 489.59 | 493.29 | 74.3283 | 64.5815 | 65.7936 | 1.9445 | 1.433 | 1.429 | 1.426 | 2.058 | 2.089 | 2.19 | Over-range | 59.98 | 18989 | 16100 | 15386 | 50475 | - - - | - - - | - - - | - - - | 18989 | 16100 | 15386 | 50475 | 2525 | 633 | 3903 | 7061 | - - - | - - - | - - - | - - - | 2525 | 633 | 3903 | 7061 | 21211 | 18271 | 18596 | 58077 | # # # | # # # | # # # | # # # | 0.895 | 0.881 | 0.827 | 0.869 | # # # | # # # | # # # | - - - | 0.991 | 0.999 | 0.969 | 0.987 | - - - | 0.14 | 1.54 | 1.49 | 1.51 | 1.47 | 1.47 | 1.5 | 48.34 | 53.82 | 61.68 | 0 | - - - | - - - | - - - | - - - | 21211 | 18271 | 18596 | 58077 | Over-range | 9439 | 8631 | 10439 | 28706 | 9095 | 8608 | 9681 | 27824 | 18896 | 16055 | 15320 | 50270 | 18896 | 16055 | 15320 | 50270 | - - - | - - - | - - - | - - -
5/3/2026 | 12:00:00 AM | 286.78 | 284.17 | 283.88 | 496.9 | 490.03 | 493.64 | 74.4922 | 64.7707 | 65.2745 | 1.9608 | 1.433 | 1.429 | 1.426 | 2.053 | 2.109 | 2.208 | Over-range | 59.99 | 18992 | 16145 | 15189 | 50326 | - - - | - - - | - - - | - - - | 18992 | 16145 | 15189 | 50326 | 2657 | 537 | 3878 | 7073 | - - - | - - - | - - - | - - - | 2657 | 537 | 3878 | 7073 | 21272 | 18338 | 18455 | 58065 | # # # | # # # | # # # | # # # | 0.893 | 0.88 | 0.823 | 0.867 | # # # | # # # | # # # | - - - | 0.99 | 0.999 | 0.969 | 0.986 | - - - | 0.141 | 1.53 | 1.52 | 1.51 | 1.48 | 1.48 | 1.51 | 48.75 | 54.04 | 62.86 | 0 | - - - | - - - | - - - | - - - | 21272 | 18338 | 18455 | 58065 | Over-range | 9572 | 8689 | 10479 | 28945 | 9196 | 8672 | 9734 | 28067 | 18908 | 16103 | 15108 | 50119 | 18908 | 16103 | 15108 | 50119 | - - - | - - - | - - - | - - -
5/3/2026 | 12:15:00 AM | 287.04 | 284.39 | 284.19 | 497.29 | 490.49 | 494.17 | 74.0282 | 64.3395 | 64.9767 | 1.9536 | 1.433 | 1.429 | 1.426 | 2.062 | 2.112 | 2.215 | Over-range | 59.98 | 18867 | 16043 | 15104 | 50014 | - - - | - - - | - - - | - - - | 18867 | 16043 | 15104 | 50014 | 2661 | 549 | 3859 | 7069 | - - - | - - - | - - - | - - - | 2661 | 549 | 3859 | 7069 | 21164 | 18232 | 18394 | 57790 | # # # | # # # | # # # | # # # | 0.891 | 0.88 | 0.821 | 0.865 | # # # | # # # | # # # | - - - | 0.99 | 0.999 | 0.969 | 0.986 | - - - | 0.141 | 1.55 | 1.51 | 1.51 | 1.48 | 1.48 | 1.51 | 49.11 | 54.23 | 63.29 | 0 | - - - | - - - | - - - | - - - | 21164 | 18232 | 18394 | 57790 | Over-range | 9579 | 8654 | 10494 | 28934 | 9202 | 8636 | 9759 | 28057 | 18794 | 15979 | 15032 | 49805 | 18794 | 15979 | 15032 | 49805 | - - - | - - - | - - - | - - -
5/3/2026 | 12:30:00 AM | 286.35 | 283.78 | 283.51 | 496.17 | 489.4 | 492.96 | 73.7625 | 64.2524 | 64.3486 | 1.9444 | 1.432 | 1.428 | 1.425 | 2.057 | 2.123 | 2.222 | Over-range | 59.98 | 18732 | 15981 | 14905 | 49618 | - - - | - - - | - - - | - - - | 18732 | 15981 | 14905 | 49618 | 2715 | 478 | 3810 | 7004 | - - - | - - - | - - - | - - - | 2715 | 478 | 3810 | 7004 | 21035 | 18165 | 18173 | 57373 | # # # | # # # | # # # | # # # | 0.89 | 0.88 | 0.82 | 0.865 | # # # | # # # | # # # | - - - | 0.989 | 1 | 0.969 | 0.986 | - - - | 0.141 | 1.56 | 1.5 | 1.49 | 1.47 | 1.48 | 1.5 | 49.35 | 54.3 | 63.46 | 0 | - - - | - - - | - - - | - - - | 21035 | 18165 | 18173 | 57373 | Over-range | 9561 | 8628 | 10394 | 28788 | 9167 | 8615 | 9671 | 27923 | 18628 | 15923 | 14863 | 49414 | 18628 | 15923 | 14863 | 49414 | - - - | - - - | - - - | - - -
5/3/2026 | 12:45:00 AM | 285.14 | 282.65 | 282.47 | 494.06 | 487.6 | 491.02 | 69.9079 | 61.2047 | 61.6414 | 1.8705 | 1.431 | 1.427 | 1.424 | 2.052 | 2.085 | 2.188 | Over-range | 59.99 | 17822 | 15259 | 14395 | 47476 | - - - | - - - | - - - | - - - | 17822 | 15259 | 14395 | 47476 | 2436 | 534 | 3555 | 6525 | - - - | - - - | - - - | - - - | 2436 | 534 | 3555 | 6525 | 19879 | 17258 | 17366 | 54503 | # # # | # # # | # # # | # # # | 0.897 | 0.884 | 0.829 | 0.871 | # # # | # # # | # # # | - - - | 0.991 | 0.999 | 0.971 | 0.987 | - - - | 0.137 | 1.54 | 1.5 | 1.5 | 1.47 | 1.48 | 1.51 | 47.82 | 53.06 | 61.66 | 0 | - - - | - - - | - - - | - - - | 19879 | 17258 | 17366 | 54503 | Over-range | 8797 | 8058 | 9711 | 26754 | 8453 | 8040 | 9037 | 25946 | 17748 | 15222 | 14322 | 47291 | 17748 | 15222 | 14322 | 47291 | - - - | - - - | - - - | - - -
5/3/2026 | 1:00:00 AM | 285.59 | 283.12 | 282.94 | 494.85 | 488.43 | 491.79 | 69.8692 | 61.26 | 61.415 | 1.8581 | 1.432 | 1.428 | 1.425 | 2.055 | 2.095 | 2.197 | Over-range | 59.99 | 17777 | 15274 | 14292 | 47343 | - - - | - - - | - - - | - - - | 17777 | 15274 | 14292 | 47343 | 2534 | 505 | 3549 | 6588 | - - - | - - - | - - - | - - - | 2534 | 505 | 3549 | 6588 | 19887 | 17293 | 17319 | 54499 | # # # | # # # | # # # | # # # | 0.894 | 0.883 | 0.825 | 0.869 | # # # | # # # | # # # | - - - | 0.99 | 0.999 | 0.97 | 0.987 | - - - | 0.139 | 1.53 | 1.49 | 1.5 | 1.47 | 1.46 | 1.51 | 48.48 | 53.33 | 62.63 | 0 | - - - | - - - | - - - | - - - | 19887 | 17293 | 17319 | 54499 | Over-range | 8906 | 8104 | 9780 | 26982 | 8537 | 8088 | 9114 | 26165 | 17668 | 15234 | 14246 | 47148 | 17668 | 15234 | 14246 | 47148 | - - - | - - - | - - - | - - -
5/3/2026 | 1:15:00 AM | 285.48 | 282.99 | 282.8 | 494.65 | 488.18 | 491.59 | 72.3291 | 63.2468 | 63.3278 | 1.8905 | 1.433 | 1.429 | 1.426 | 2.057 | 2.117 | 2.211 | Over-range | 59.97 | 18304 | 15687 | 14652 | 48644 | - - - | - - - | - - - | - - - | 18304 | 15687 | 14652 | 48644 | 2659 | 521 | 3700 | 6880 | - - - | - - - | - - - | - - - | 2659 | 521 | 3700 | 6880 | 20562 | 17832 | 17839 | 56233 | # # # | # # # | # # # | # # # | 0.89 | 0.88 | 0.821 | 0.865 | # # # | # # # | # # # | - - - | 0.99 | 0.999 | 0.969 | 0.986 | - - - | 0.141 | 1.59 | 1.52 | 1.54 | 1.5 | 1.5 | 1.55 | 49.35 | 54.25 | 63.39 | 0 | - - - | - - - | - - - | - - - | 20562 | 17832 | 17839 | 56233 | Over-range | 9354 | 8471 | 10171 | 28189 | 8968 | 8455 | 9474 | 27336 | 18201 | 15644 | 14590 | 48435 | 18201 | 15644 | 14590 | 48435 | - - - | - - - | - - - | - - -
5/3/2026 | 1:30:00 AM | 285.54 | 282.86 | 282.68 | 494.65 | 487.86 | 491.6 | 72.6336 | 62.8594 | 63.3264 | 1.8381 | 1.434 | 1.429 | 1.427 | 2.066 | 2.125 | 2.23 | Over-range | 59.99 | 18401 | 15586 | 14603 | 48589 | - - - | - - - | - - - | - - - | 18401 | 15586 | 14603 | 48589 | 2622 | 445 | 3793 | 6860 | - - - | - - - | - - - | - - - | 2622 | 445 | 3793 | 6860 | 20650 | 17715 | 17838 | 56203 | # # # | # # # | # # # | # # # | 0.891 | 0.88 | 0.819 | 0.865 | # # # | # # # | # # # | - - - | 0.99 | 1 | 0.967 | 0.986 | - - - | 0.141 | 1.59 | 1.54 | 1.54 | 1.51 | 1.52 | 1.55 | 49.2 | 54.25 | 63.8 | 0 | - - - | - - - | - - - | - - - | 20650 | 17715 | 17838 | 56203 | Over-range | 9360 | 8414 | 10237 | 28223 | 8985 | 8402 | 9509 | 27376 | 18298 | 15564 | 14514 | 48376 | 18298 | 15564 | 14514 | 48376 | - - - | - - - | - - - | - - -
5/3/2026 | 1:45:00 AM | 285.91 | 283.17 | 282.96 | 495.28 | 488.32 | 492.16 | 69.5896 | 60.2704 | 60.5452 | 1.8445 | 1.432 | 1.428 | 1.425 | 2.062 | 2.109 | 2.23 | Over-range | 59.99 | 17743 | 15046 | 14003 | 46792 | - - - | - - - | - - - | - - - | 17743 | 15046 | 14003 | 46792 | 2534 | 360 | 3602 | 6495 | - - - | - - - | - - - | - - - | 2534 | 360 | 3602 | 6495 | 19835 | 17021 | 17084 | 53941 | # # # | # # # | # # # | # # # | 0.895 | 0.884 | 0.82 | 0.868 | # # # | # # # | # # # | - - - | 0.99 | 1 | 0.968 | 0.986 | - - - | 0.139 | 1.55 | 1.52 | 1.54 | 1.49 | 1.5 | 1.53 | 48.26 | 53.17 | 63.73 | 0 | - - - | - - - | - - - | - - - | 19835 | 17021 | 17084 | 53941 | Over-range | 8858 | 7953 | 9784 | 26818 | 8487 | 7945 | 9096 | 26019 | 17666 | 15004 | 13919 | 46590 | 17666 | 15004 | 13919 | 46590 | - - - | - - - | - - - | - - -
5/3/2026 | 2:00:00 AM | 285.96 | 283.3 | 283.15 | 495.38 | 488.66 | 492.36 | 69.0585 | 60.1359 | 60.4185 | 1.8288 | 1.433 | 1.428 | 1.425 | 2.06 | 2.099 | 2.212 | Over-range | 60 | 17606 | 15021 | 14036 | 46663 | - - - | - - - | - - - | - - - | 17606 | 15021 | 14036 | 46663 | 2511 | 427 | 3535 | 6473 | - - - | - - - | - - - | - - - | 2511 | 427 | 3535 | 6473 | 19684 | 16990 | 17058 | 53732 | # # # | # # # | # # # | # # # | 0.894 | 0.884 | 0.823 | 0.868 | # # # | # # # | # # # | - - - | 0.99 | 1 | 0.969 | 0.987 | - - - | 0.139 | 1.54 | 1.53 | 1.52 | 1.49 | 1.49 | 1.52 | 48.31 | 53.17 | 63.06 | 0 | - - - | - - - | - - - | - - - | 19684 | 16990 | 17058 | 53732 | Over-range | 8795 | 7934 | 9690 | 26625 | 8428 | 7922 | 9022 | 25826 | 17522 | 14955 | 13991 | 46468 | 17522 | 14955 | 13991 | 46468 | - - - | - - - | - - - | - - -
5/3/2026 | 2:15:00 AM | 286.16 | 283.51 | 283.29 | 495.76 | 488.95 | 492.63 | 71.5852 | 62.1297 | 62.0832 | 1.8481 | 1.433 | 1.428 | 1.426 | 2.067 | 2.143 | 2.244 | Over-range | 59.99 | 18094 | 15425 | 14263 | 47782 | - - - | - - - | - - - | - - - | 18094 | 15425 | 14263 | 47782 | 2712 | 398 | 3695 | 6805 | - - - | - - - | - - - | - - - | 2712 | 398 | 3695 | 6805 | 20393 | 17546 | 17518 | 55457 | # # # | # # # | # # # | # # # | 0.887 | 0.879 | 0.814 | 0.862 | # # # | # # # | # # # | - - - | 0.989 | 1 | 0.968 | 0.986 | - - - | 0.142 | 1.55 | 1.53 | 1.52 | 1.49 | 1.5 | 1.53 | 50.05 | 54.48 | 64.97 | 0 | - - - | - - - | - - - | - - - | 20393 | 17546 | 17518 | 55457 | Over-range | 9397 | 8354 | 10165 | 28127 | 8997 | 8345 | 9470 | 27291 | 17990 | 15383 | 14201 | 47573 | 17990 | 15383 | 14201 | 47573 | - - - | - - - | - - - | - - -
5/3/2026 | 2:30:00 AM | 286.46 | 283.78 | 283.63 | 496.22 | 489.49 | 493.21 | 70.9678 | 61.5849 | 61.8059 | 1.8375 | 1.433 | 1.428 | 1.426 | 2.074 | 2.14 | 2.243 | Over-range | 59.98 | 17958 | 15311 | 14225 | 47494 | - - - | - - - | - - - | - - - | 17958 | 15311 | 14225 | 47494 | 2646 | 433 | 3669 | 6748 | - - - | - - - | - - - | - - - | 2646 | 433 | 3669 | 6748 | 20244 | 17414 | 17460 | 55118 | # # # | # # # | # # # | # # # | 0.887 | 0.879 | 0.815 | 0.862 | # # # | # # # | # # # | - - - | 0.989 | 1 | 0.968 | 0.986 | - - - | 0.142 | 1.56 | 1.53 | 1.56 | 1.51 | 1.52 | 1.55 | 50.19 | 54.3 | 64.95 | 0 | - - - | - - - | - - - | - - - | 20244 | 17414 | 17460 | 55118 | Over-range | 9333 | 8287 | 10119 | 27946 | 8950 | 8275 | 9431 | 27119 | 17855 | 15291 | 14146 | 47291 | 17855 | 15291 | 14146 | 47291 | - - - | - - - | - - - | - - -
5/3/2026 | 2:45:00 AM | 286.66 | 284.08 | 283.89 | 496.66 | 490.01 | 493.57 | 67.3896 | 58.9435 | 58.7711 | 1.8083 | 1.432 | 1.427 | 1.425 | 2.069 | 2.129 | 2.226 | Over-range | 59.99 | 17111 | 14734 | 13639 | 45483 | - - - | - - - | - - - | - - - | 17111 | 14734 | 13639 | 45483 | 2516 | 454 | 3413 | 6383 | - - - | - - - | - - - | - - - | 2516 | 454 | 3413 | 6383 | 19250 | 16693 | 16633 | 52576 | # # # | # # # | # # # | # # # | 0.889 | 0.883 | 0.82 | 0.865 | # # # | # # # | # # # | - - - | 0.989 | 1 | 0.97 | 0.987 | - - - | 0.14 | 1.55 | 1.51 | 1.52 | 1.48 | 1.49 | 1.51 | 49.75 | 53.42 | 63.96 | 0 | - - - | - - - | - - - | - - - | 19250 | 16693 | 16633 | 52576 | Over-range | 8809 | 7840 | 9516 | 26353 | 8442 | 7827 | 8883 | 25568 | 16998 | 14727 | 13561 | 45286 | 16998 | 14727 | 13561 | 45286 | - - - | - - - | - - - | - - -
5/3/2026 | 3:00:00 AM | 286.71 | 284.06 | 283.95 | 496.66 | 490.03 | 493.7 | 70.1456 | 61.047 | 61.261 | 1.8493 | 1.433 | 1.427 | 1.426 | 2.084 | 2.155 | 2.247 | Over-range | 59.98 | 17691 | 15161 | 14100 | 46952 | - - - | - - - | - - - | - - - | 17691 | 15161 | 14100 | 46952 | 2626 | 503 | 3607 | 6736 | - - - | - - - | - - - | - - - | 2626 | 503 | 3607 | 6736 | 20022 | 17273 | 17323 | 54619 | # # # | # # # | # # # | # # # | 0.884 | 0.878 | 0.814 | 0.86 | # # # | # # # | # # # | - - - | 0.989 | 0.999 | 0.968 | 0.986 | - - - | 0.143 | 1.54 | 1.49 | 1.52 | 1.47 | 1.48 | 1.52 | 51.16 | 54.76 | 65.19 | 0 | - - - | - - - | - - - | - - - | 20022 | 17273 | 17323 | 54619 | Over-range | 9366 | 8270 | 10058 | 27883 | 8990 | 8255 | 9389 | 27057 | 17582 | 15137 | 14029 | 46749 | 17582 | 15137 | 14029 | 46749 | - - - | - - - | - - - | - - -
5/3/2026 | 3:15:00 AM | 286.68 | 284.11 | 283.94 | 496.68 | 490.09 | 493.62 | 65.0617 | 56.9478 | 56.9516 | 1.7678 | 1.432 | 1.427 | 1.424 | 2.067 | 2.11 | 2.213 | Over-range | 59.97 | 16604 | 14304 | 13288 | 44196 | - - - | - - - | - - - | - - - | 16604 | 14304 | 13288 | 44196 | 2410 | 438 | 3258 | 6106 | - - - | - - - | - - - | - - - | 2410 | 438 | 3258 | 6106 | 18603 | 16144 | 16131 | 50878 | # # # | # # # | # # # | # # # | 0.893 | 0.886 | 0.824 | 0.869 | # # # | # # # | # # # | - - - | 0.99 | 1 | 0.971 | 0.987 | - - - | 0.138 | 1.56 | 1.49 | 1.53 | 1.49 | 1.49 | 1.52 | 48.82 | 52.71 | 63.05 | 0 | - - - | - - - | - - - | - - - | 18603 | 16144 | 16131 | 50878 | Over-range | 8383 | 7481 | 9142 | 25193 | 8029 | 7468 | 8542 | 24441 | 16543 | 14229 | 13248 | 44019 | 16543 | 14229 | 13248 | 44019 | - - - | - - - | - - - | - - -
5/3/2026 | 3:30:00 AM | 286.73 | 284.27 | 284.1 | 496.84 | 490.44 | 493.79 | 68.4054 | 60.0725 | 59.6378 | 1.8412 | 1.432 | 1.427 | 1.425 | 2.07 | 2.148 | 2.228 | Over-range | 59.98 | 17273 | 14954 | 13814 | 46042 | - - - | - - - | - - - | - - - | 17273 | 14954 | 13814 | 46042 | 2607 | 522 | 3418 | 6546 | - - - | - - - | - - - | - - - | 2607 | 522 | 3418 | 6546 | 19519 | 17004 | 16875 | 53398 | # # # | # # # | # # # | # # # | 0.885 | 0.879 | 0.819 | 0.862 | # # # | # # # | # # # | - - - | 0.989 | 0.999 | 0.97 | 0.987 | - - - | 0.142 | 1.54 | 1.52 | 1.54 | 1.49 | 1.49 | 1.53 | 50.54 | 54.27 | 64.36 | 0 | - - - | - - - | - - - | - - - | 19519 | 17004 | 16875 | 53398 | Over-range | 9079 | 8085 | 9685 | 27022 | 8697 | 8068 | 9062 | 26217 | 17215 | 14898 | 13735 | 45848 | 17215 | 14898 | 13735 | 45848 | - - - | - - - | - - - | - - -
5/3/2026 | 3:45:00 AM | 286.88 | 284.34 | 284.2 | 497.03 | 490.54 | 494.04 | 67.8945 | 59.3394 | 59.3219 | 1.7848 | 1.433 | 1.428 | 1.426 | 2.079 | 2.149 | 2.233 | Over-range | 59.97 | 17142 | 14776 | 13722 | 45639 | - - - | - - - | - - - | - - - | 17142 | 14776 | 13722 | 45639 | 2567 | 515 | 3435 | 6517 | - - - | - - - | - - - | - - - | 2567 | 515 | 3435 | 6517 | 19382 | 16803 | 16788 | 52973 | # # # | # # # | # # # | # # # | 0.884 | 0.879 | 0.817 | 0.862 | # # # | # # # | # # # | - - - | 0.989 | 0.999 | 0.97 | 0.986 | - - - | 0.143 | 1.57 | 1.54 | 1.55 | 1.51 | 1.51 | 1.55 | 50.84 | 54.38 | 64.49 | 0 | - - - | - - - | - - - | - - - | 19382 | 16803 | 16788 | 52973 | Over-range | 9035 | 7993 | 9665 | 26868 | 8663 | 7976 | 9034 | 26066 | 17050 | 14716 | 13672 | 45438 | 17050 | 14716 | 13672 | 45438 | - - - | - - - | - - - | - - -
5/3/2026 | 4:00:00 AM | 286.99 | 284.47 | 284.31 | 497.24 | 490.75 | 494.21 | 63.9906 | 56.283 | 56.1137 | 1.7531 | 1.431 | 1.426 | 1.424 | 2.073 | 2.126 | 2.215 | Over-range | 59.98 | 16289 | 14125 | 13115 | 43529 | - - - | - - - | - - - | - - - | 16289 | 14125 | 13115 | 43529 | 2386 | 484 | 3185 | 6055 | - - - | - - - | - - - | - - - | 2386 | 484 | 3185 | 6055 | 18311 | 15968 | 15911 | 50190 | # # # | # # # | # # # | # # # | 0.89 | 0.885 | 0.824 | 0.867 | # # # | # # # | # # # | - - - | 0.989 | 0.999 | 0.972 | 0.987 | - - - | 0.139 | 1.56 | 1.51 | 1.51 | 1.48 | 1.48 | 1.53 | 49.64 | 53 | 63.03 | 0 | - - - | - - - | - - - | - - - | 18311 | 15968 | 15911 | 50190 | Over-range | 8357 | 7442 | 9006 | 24971 | 8010 | 7426 | 8423 | 24226 | 16185 | 14068 | 13094 | 43347 | 16185 | 14068 | 13094 | 43347 | - - - | - - - | - - - | - - -
5/3/2026 | 4:15:00 AM | 286.91 | 284.48 | 284.36 | 497.14 | 490.87 | 494.17 | 65.6648 | 57.8278 | 57.6852 | 1.7606 | 1.432 | 1.427 | 1.425 | 2.076 | 2.136 | 2.217 | Over-range | 59.99 | 16622 | 14449 | 13430 | 44501 | - - - | - - - | - - - | - - - | 16622 | 14449 | 13430 | 44501 | 2473 | 549 | 3260 | 6282 | - - - | - - - | - - - | - - - | 2473 | 549 | 3260 | 6282 | 18758 | 16393 | 16336 | 51487 | # # # | # # # | # # # | # # # | 0.886 | 0.881 | 0.822 | 0.864 | # # # | # # # | # # # | - - - | 0.989 | 0.999 | 0.972 | 0.987 | - - - | 0.141 | 1.57 | 1.5 | 1.53 | 1.49 | 1.49 | 1.53 | 50.43 | 53.82 | 63.52 | 0 | - - - | - - - | - - - | - - - | 18758 | 16393 | 16336 | 51487 | Over-range | 8685 | 7735 | 9295 | 25874 | 8325 | 7716 | 8704 | 25099 | 16534 | 14382 | 13397 | 44313 | 16534 | 14382 | 13397 | 44313 | - - - | - - - | - - - | - - -
5/3/2026 | 4:30:00 AM | 286.86 | 284.33 | 284.14 | 497.04 | 490.47 | 493.94 | 66.6536 | 58.4191 | 58.1793 | 1.7858 | 1.432 | 1.427 | 1.425 | 2.079 | 2.155 | 2.235 | Over-range | 59.99 | 16824 | 14550 | 13471 | 44845 | - - - | - - - | - - - | - - - | 16824 | 14550 | 13471 | 44845 | 2508 | 511 | 3349 | 6368 | - - - | - - - | - - - | - - - | 2508 | 511 | 3349 | 6368 | 19029 | 16538 | 16461 | 52028 | # # # | # # # | # # # | # # # | 0.884 | 0.88 | 0.818 | 0.862 | # # # | # # # | # # # | - - - | 0.989 | 0.999 | 0.97 | 0.987 | - - - | 0.142 | 1.55 | 1.5 | 1.51 | 1.48 | 1.48 | 1.52 | 50.93 | 54.14 | 64.39 | 0 | - - - | - - - | - - - | - - - | 19029 | 16538 | 16461 | 52028 | Over-range | 8880 | 7854 | 9453 | 26355 | 8518 | 7838 | 8840 | 25574 | 16724 | 14529 | 13400 | 44653 | 16724 | 14529 | 13400 | 44653 | - - - | - - - | - - - | - - -
5/3/2026 | 4:45:00 AM | 287.04 | 284.43 | 284.23 | 497.31 | 490.59 | 494.19 | 67.3653 | 58.6727 | 58.7682 | 1.7604 | 1.433 | 1.427 | 1.425 | 2.089 | 2.163 | 2.249 | Over-range | 59.99 | 16998 | 14608 | 13560 | 45165 | - - - | - - - | - - - | - - - | 16998 | 14608 | 13560 | 45165 | 2530 | 497 | 3411 | 6439 | - - - | - - - | - - - | - - - | 2530 | 497 | 3411 | 6439 | 19245 | 16621 | 16629 | 52494 | # # # | # # # | # # # | # # # | 0.883 | 0.879 | 0.815 | 0.86 | # # # | # # # | # # # | - - - | 0.989 | 0.999 | 0.969 | 0.986 | - - - | 0.143 | 1.57 | 1.51 | 1.53 | 1.5 | 1.49 | 1.53 | 51.17 | 54.5 | 65.04 | 0 | - - - | - - - | - - - | - - - | 19245 | 16621 | 16629 | 52494 | Over-range | 9014 | 7920 | 9620 | 26730 | 8651 | 7904 | 8994 | 25943 | 16936 | 14555 | 13474 | 44966 | 16936 | 14555 | 13474 | 44966 | - - - | - - - | - - - | - - -
5/3/2026 | 5:00:00 AM | 286.84 | 284.39 | 284.11 | 497.09 | 490.51 | 493.85 | 66.5313 | 58.4277 | 58.0481 | 1.7618 | 1.432 | 1.427 | 1.425 | 2.083 | 2.169 | 2.238 | Over-range | 59.98 | 16735 | 14526 | 13423 | 44684 | - - - | - - - | - - - | - - - | 16735 | 14526 | 13423 | 44684 | 2551 | 547 | 3312 | 6410 | - - - | - - - | - - - | - - - | 2551 | 547 | 3312 | 6410 | 18997 | 16547 | 16424 | 51968 | # # # | # # # | # # # | # # # | 0.881 | 0.878 | 0.817 | 0.86 | # # # | # # # | # # # | - - - | 0.988 | 0.999 | 0.971 | 0.986 | - - - | 0.143 | 1.56 | 1.51 | 1.51 | 1.49 | 1.48 | 1.52 | 51.68 | 54.79 | 64.74 | 0 | - - - | - - - | - - - | - - - | 18997 | 16547 | 16424 | 51968 | Over-range | 8977 | 7916 | 9459 | 26509 | 8607 | 7897 | 8860 | 25722 | 16658 | 14462 | 13365 | 44485 | 16658 | 14462 | 13365 | 44485 | - - - | - - - | - - - | - - -
5/3/2026 | 5:15:00 AM | 286.81 | 284.26 | 284.09 | 496.92 | 490.37 | 493.88 | 63.6813 | 55.8808 | 55.9838 | 1.7175 | 1.431 | 1.426 | 1.424 | 2.092 | 2.146 | 2.228 | Over-range | 60 | 16092 | 13956 | 13016 | 43064 | - - - | - - - | - - - | - - - | 16092 | 13956 | 13016 | 43064 | 2345 | 545 | 3177 | 6067 | - - - | - - - | - - - | - - - | 2345 | 545 | 3177 | 6067 | 18189 | 15827 | 15850 | 49866 | # # # | # # # | # # # | # # # | 0.885 | 0.882 | 0.821 | 0.864 | # # # | # # # | # # # | - - - | 0.989 | 0.999 | 0.971 | 0.987 | - - - | 0.141 | 1.53 | 1.5 | 1.51 | 1.48 | 1.47 | 1.51 | 51.01 | 53.63 | 63.83 | 0 | - - - | - - - | - - - | - - - | 18189 | 15827 | 15850 | 49866 | Over-range | 8470 | 7459 | 9038 | 25121 | 8138 | 7439 | 8462 | 24377 | 15977 | 13921 | 12976 | 42875 | 15977 | 13921 | 12976 | 42875 | - - - | - - - | - - - | - - -
5/3/2026 | 5:30:00 AM | 286.76 | 284.31 | 284.06 | 496.94 | 490.42 | 493.75 | 62.4546 | 55.1118 | 54.782 | 1.7176 | 1.431 | 1.426 | 1.424 | 2.08 | 2.143 | 2.217 | Over-range | 60 | 15810 | 13800 | 12789 | 42400 | - - - | - - - | - - - | - - - | 15810 | 13800 | 12789 | 42400 | 2336 | 525 | 3062 | 5922 | - - - | - - - | - - - | - - - | 2336 | 525 | 3062 | 5922 | 17847 | 15622 | 15516 | 48986 | # # # | # # # | # # # | # # # | 0.886 | 0.883 | 0.824 | 0.866 | # # # | # # # | # # # | - - - | 0.989 | 0.999 | 0.972 | 0.987 | - - - | 0.14 | 1.53 | 1.5 | 1.5 | 1.47 | 1.46 | 1.51 | 50.63 | 53.28 | 63.21 | 0 | - - - | - - - | - - - | - - - | 17847 | 15622 | 15516 | 48986 | Over-range | 8273 | 7316 | 8781 | 24516 | 7937 | 7297 | 8229 | 23790 | 15704 | 13754 | 12763 | 42221 | 15704 | 13754 | 12763 | 42221 | - - - | - - - | - - - | - - -
5/3/2026 | 5:45:00 AM | 286.59 | 284.09 | 283.9 | 496.58 | 490.08 | 493.5 | 65.6962 | 57.7487 | 57.566 | 1.7518 | 1.432 | 1.427 | 1.425 | 2.092 | 2.168 | 2.235 | Over-range | 60 | 16474 | 14327 | 13312 | 44113 | - - - | - - - | - - - | - - - | 16474 | 14327 | 13312 | 44113 | 2464 | 609 | 3259 | 6332 | - - - | - - - | - - - | - - - | 2464 | 609 | 3259 | 6332 | 18728 | 16329 | 16274 | 51332 | # # # | # # # | # # # | # # # | 0.88 | 0.877 | 0.818 | 0.859 | # # # | # # # | # # # | - - - | 0.989 | 0.999 | 0.971 | 0.987 | - - - | 0.143 | 1.52 | 1.47 | 1.51 | 1.46 | 1.46 | 1.5 | 52.14 | 54.76 | 64.71 | 0 | - - - | - - - | - - - | - - - | 18728 | 16329 | 16274 | 51332 | Over-range | 8897 | 7827 | 9354 | 26224 | 8549 | 7802 | 8768 | 25448 | 16394 | 14297 | 13225 | 43916 | 16394 | 14297 | 13225 | 43916 | - - - | - - - | - - - | - - -
5/3/2026 | 6:00:00 AM | 286.55 | 284.05 | 283.82 | 496.53 | 489.96 | 493.38 | 64.9031 | 57.0162 | 56.7924 | 1.7224 | 1.432 | 1.427 | 1.425 | 2.085 | 2.164 | 2.232 | Over-range | 60.01 | 16311 | 14175 | 13149 | 43634 | - - - | - - - | - - - | - - - | 16311 | 14175 | 13149 | 43634 | 2433 | 571 | 3203 | 6207 | - - - | - - - | - - - | - - - | 2433 | 571 | 3203 | 6207 | 18506 | 16125 | 16050 | 50681 | # # # | # # # | # # # | # # # | 0.881 | 0.879 | 0.819 | 0.861 | # # # | # # # | # # # | - - - | 0.989 | 0.999 | 0.971 | 0.987 | - - - | 0.142 | 1.55 | 1.49 | 1.54 | 1.49 | 1.48 | 1.52 | 51.61 | 54.34 | 64.41 | 0 | - - - | - - - | - - - | - - - | 18506 | 16125 | 16050 | 50681 | Over-range | 8732 | 7678 | 9198 | 25756 | 8386 | 7657 | 8622 | 24997 | 16254 | 14133 | 13059 | 43446 | 16254 | 14133 | 13059 | 43446 | - - - | - - - | - - - | - - -
5/3/2026 | 6:15:00 AM | 286.23 | 283.64 | 283.44 | 495.91 | 489.23 | 492.82 | 59.6866 | 52.6734 | 52.6966 | 1.6732 | 1.431 | 1.426 | 1.424 | 2.086 | 2.129 | 2.208 | Over-range | 60 | 15156 | 13231 | 12356 | 40743 | - - - | - - - | - - - | - - - | 15156 | 13231 | 12356 | 40743 | 2172 | 555 | 2889 | 5616 | - - - | - - - | - - - | - - - | 2172 | 555 | 2889 | 5616 | 17062 | 14923 | 14920 | 46905 | # # # | # # # | # # # | # # # | 0.888 | 0.887 | 0.828 | 0.869 | # # # | # # # | # # # | - - - | 0.99 | 0.999 | 0.974 | 0.988 | - - - | 0.138 | 1.53 | 1.48 | 1.47 | 1.46 | 1.45 | 1.49 | 50.15 | 52.63 | 62.51 | 0 | - - - | - - - | - - - | - - - | 17062 | 14923 | 14920 | 46905 | Over-range | 7834 | 6899 | 8362 | 23234 | 7526 | 6876 | 7847 | 22545 | 15100 | 13151 | 12323 | 40573 | 15100 | 13151 | 12323 | 40573 | - - - | - - - | - - - | - - -
5/3/2026 | 6:30:00 AM | 286.02 | 283.48 | 283.23 | 495.6 | 488.93 | 492.42 | 64.9493 | 57.0087 | 56.9123 | 1.7088 | 1.432 | 1.427 | 1.425 | 2.09 | 2.174 | 2.236 | Over-range | 60 | 16235 | 14112 | 13121 | 43468 | - - - | - - - | - - - | - - - | 16235 | 14112 | 13121 | 43468 | 2437 | 584 | 3215 | 6237 | - - - | - - - | - - - | - - - | 2437 | 584 | 3215 | 6237 | 18478 | 16087 | 16045 | 50610 | # # # | # # # | # # # | # # # | 0.879 | 0.877 | 0.818 | 0.859 | # # # | # # # | # # # | - - - | 0.989 | 0.999 | 0.971 | 0.987 | - - - | 0.143 | 1.52 | 1.45 | 1.47 | 1.45 | 1.43 | 1.48 | 52.51 | 54.88 | 64.57 | 0 | - - - | - - - | - - - | - - - | 18478 | 16087 | 16045 | 50610 | Over-range | 8814 | 7714 | 9227 | 25896 | 8470 | 7692 | 8649 | 25134 | 16131 | 14062 | 13080 | 43273 | 16131 | 14062 | 13080 | 43273 | - - - | - - - | - - - | - - -
5/3/2026 | 6:45:00 AM | 289.37 | 286.41 | 286.16 | 501.18 | 493.76 | 497.96 | 32.4291 | 29.5813 | 28.8364 | 0.8524 | 1.433 | 1.426 | 1.421 | 1.996 | 2.075 | 1.92 | Over-range | 60.01 | 7630 | 7158 | 6652 | 21439 | - - - | - - - | - - - | - - - | 7630 | 7158 | 6652 | 21439 | 799 | 232 | 849 | 1879 | - - - | - - - | - - - | - - - | 799 | 232 | 849 | 1879 | 8294 | 7664 | 7362 | 23319 | # # # | # # # | # # # | # # # | 0.92 | 0.934 | 0.904 | 0.919 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.988 | 0.994 | - - - | 0.088 | 1.63 | 1.57 | 1.55 | 1.57 | 1.52 | 1.59 | 38.8 | 33.75 | 38.4 | 0 | - - - | - - - | - - - | - - - | 8294 | 7664 | 7362 | 23319 | Over-range | 3211 | 2639 | 2986 | 8884 | 3109 | 2628 | 2853 | 8679 | 7600 | 7172 | 6597 | 21368 | 7600 | 7172 | 6597 | 21368 | - - - | - - - | - - - | - - -
5/3/2026 | 7:00:00 AM | 289.94 | 286.93 | 286.69 | 502.13 | 494.64 | 498.93 | 21.7236 | 20.9415 | 19.8097 | 0.4728 | 1.432 | 1.425 | 1.42 | 1.988 | 2.06 | 1.865 | Over-range | 60.02 | 5904 | 5766 | 5386 | 17055 | - - - | - - - | - - - | - - - | 5904 | 5766 | 5386 | 17055 | 480 | 185 | 389 | 1054 | - - - | - - - | - - - | - - - | 480 | 185 | 389 | 1054 | 6298 | 6009 | 5679 | 17987 | # # # | # # # | # # # | # # # | 0.937 | 0.96 | 0.948 | 0.948 | # # # | # # # | # # # | - - - | 0.997 | 0.999 | 0.997 | 0.998 | - - - | 0.062 | 1.68 | 1.58 | 1.57 | 1.59 | 1.53 | 1.62 | 37.16 | 30.05 | 33.58 | 0 | - - - | - - - | - - - | - - - | 6298 | 6009 | 5679 | 17987 | Over-range | 2194 | 1692 | 1802 | 5712 | 2141 | 1682 | 1760 | 5614 | 5881 | 5783 | 5337 | 17001 | 5881 | 5783 | 5337 | 17001 | - - - | - - - | - - - | - - -
5/3/2026 | 7:15:00 AM | 289.29 | 286.26 | 285.99 | 501.02 | 493.43 | 497.77 | 23.0814 | 22.0157 | 21.0526 | 0.5032 | 1.432 | 1.426 | 1.421 | 1.994 | 2.054 | 1.874 | Over-range | 60.01 | 6218 | 6009 | 5652 | 17879 | - - - | - - - | - - - | - - - | 6218 | 6009 | 5652 | 17879 | 551 | 200 | 510 | 1261 | - - - | - - - | - - - | - - - | 551 | 200 | 510 | 1261 | 6670 | 6298 | 6013 | 18981 | # # # | # # # | # # # | # # # | 0.932 | 0.954 | 0.94 | 0.942 | # # # | # # # | # # # | - - - | 0.996 | 1 | 0.996 | 0.997 | - - - | 0.07 | 1.68 | 1.57 | 1.58 | 1.59 | 1.54 | 1.61 | 38.97 | 31.98 | 35.76 | 0 | - - - | - - - | - - - | - - - | 6670 | 6298 | 6013 | 18981 | Over-range | 2414 | 1885 | 2048 | 6370 | 2350 | 1874 | 1984 | 6244 | 6152 | 6021 | 5642 | 17815 | 6152 | 6021 | 5642 | 17815 | - - - | - - - | - - - | - - -
5/3/2026 | 7:30:00 AM | 289.16 | 286.07 | 285.85 | 500.73 | 493.13 | 497.56 | 25.1067 | 23.6159 | 23.0375 | 0.5517 | 1.433 | 1.426 | 1.421 | 2.016 | 2.023 | 1.895 | Over-range | 60.03 | 6730 | 6406 | 6117 | 19254 | - - - | - - - | - - - | - - - | 6730 | 6406 | 6117 | 19254 | 611 | 305 | 657 | 1573 | - - - | - - - | - - - | - - - | 611 | 305 | 657 | 1573 | 7260 | 6756 | 6585 | 20601 | # # # | # # # | # # # | # # # | 0.927 | 0.948 | 0.929 | 0.935 | # # # | # # # | # # # | - - - | 0.996 | 0.999 | 0.994 | 0.996 | - - - | 0.082 | 1.71 | 1.61 | 1.62 | 1.63 | 1.58 | 1.66 | 40.4 | 34.04 | 39.17 | 0 | - - - | - - - | - - - | - - - | 7260 | 6756 | 6585 | 20601 | Over-range | 2721 | 2144 | 2438 | 7327 | 2652 | 2123 | 2348 | 7156 | 6695 | 6404 | 6082 | 19181 | 6695 | 6404 | 6082 | 19181 | - - - | - - - | - - - | - - -
5/3/2026 | 7:45:00 AM | 288.99 | 285.92 | 285.74 | 500.42 | 492.91 | 497.33 | 25.5287 | 23.9574 | 23.5237 | 0.5607 | 1.433 | 1.426 | 1.421 | 2.024 | 2.011 | 1.897 | Over-range | 60.02 | 6834 | 6487 | 6229 | 19551 | - - - | - - - | - - - | - - - | 6834 | 6487 | 6229 | 19551 | 618 | 311 | 711 | 1640 | - - - | - - - | - - - | - - - | 618 | 311 | 711 | 1640 | 7378 | 6850 | 6722 | 20949 | # # # | # # # | # # # | # # # | 0.926 | 0.947 | 0.927 | 0.933 | # # # | # # # | # # # | - - - | 0.996 | 0.999 | 0.994 | 0.996 | - - - | 0.084 | 1.73 | 1.61 | 1.64 | 1.64 | 1.59 | 1.67 | 40.89 | 34.41 | 39.57 | 0 | - - - | - - - | - - - | - - - | 7378 | 6850 | 6722 | 20949 | Over-range | 2778 | 2199 | 2526 | 7525 | 2708 | 2177 | 2424 | 7345 | 6761 | 6498 | 6216 | 19475 | 6761 | 6498 | 6216 | 19475 | - - - | - - - | - - - | - - -
5/3/2026 | 8:00:00 AM | 288.95 | 285.89 | 285.87 | 500.27 | 493.05 | 497.44 | 25.7977 | 24.1574 | 23.9637 | 0.5649 | 1.432 | 1.426 | 1.421 | 2.033 | 1.989 | 1.899 | Over-range | 60.03 | 6903 | 6536 | 6336 | 19775 | - - - | - - - | - - - | - - - | 6903 | 6536 | 6336 | 19775 | 592 | 362 | 723 | 1678 | - - - | - - - | - - - | - - - | 592 | 362 | 723 | 1678 | 7454 | 6906 | 6850 | 21211 | # # # | # # # | # # # | # # # | 0.926 | 0.946 | 0.925 | 0.932 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.993 | 0.996 | - - - | 0.085 | 1.72 | 1.62 | 1.66 | 1.64 | 1.6 | 1.69 | 40.88 | 34.56 | 40.26 | 0 | - - - | - - - | - - - | - - - | 7454 | 6906 | 6850 | 21211 | Over-range | 2812 | 2231 | 2604 | 7670 | 2749 | 2201 | 2502 | 7485 | 6857 | 6542 | 6299 | 19699 | 6857 | 6542 | 6299 | 19699 | - - - | - - - | - - - | - - -
5/3/2026 | 8:15:00 AM | 288.62 | 285.52 | 285.52 | 499.65 | 492.41 | 496.87 | 26.4582 | 24.722 | 24.5797 | 0.5799 | 1.432 | 1.426 | 1.421 | 2.034 | 1.983 | 1.896 | Over-range | 60.01 | 7062 | 6664 | 6469 | 20196 | - - - | - - - | - - - | - - - | 7062 | 6664 | 6469 | 20196 | 615 | 399 | 755 | 1769 | - - - | - - - | - - - | - - - | 615 | 399 | 755 | 1769 | 7636 | 7058 | 7018 | 21712 | # # # | # # # | # # # | # # # | 0.925 | 0.944 | 0.922 | 0.93 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.993 | 0.996 | - - - | 0.088 | 1.74 | 1.62 | 1.66 | 1.64 | 1.61 | 1.69 | 41.17 | 35.27 | 41.14 | 0 | - - - | - - - | - - - | - - - | 7636 | 7058 | 7018 | 21712 | Over-range | 2904 | 2324 | 2719 | 7969 | 2838 | 2290 | 2612 | 7770 | 7044 | 6663 | 6408 | 20116 | 7044 | 6663 | 6408 | 20116 | - - - | - - - | - - - | - - -
5/3/2026 | 8:30:00 AM | 288.35 | 285.11 | 285.21 | 499.06 | 491.75 | 496.45 | 27.1595 | 25.1463 | 25.2717 | 0.5915 | 1.433 | 1.427 | 1.422 | 2.044 | 1.974 | 1.91 | Over-range | 60.01 | 7225 | 6753 | 6608 | 20587 | - - - | - - - | - - - | - - - | 7225 | 6753 | 6608 | 20587 | 637 | 422 | 805 | 1865 | - - - | - - - | - - - | - - - | 637 | 422 | 805 | 1865 | 7831 | 7169 | 7208 | 22208 | # # # | # # # | # # # | # # # | 0.923 | 0.942 | 0.917 | 0.927 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.993 | 0.996 | - - - | 0.091 | 1.72 | 1.63 | 1.65 | 1.63 | 1.6 | 1.68 | 41.7 | 36.21 | 42.45 | 0 | - - - | - - - | - - - | - - - | 7831 | 7169 | 7208 | 22208 | Over-range | 3020 | 2406 | 2877 | 8329 | 2952 | 2369 | 2762 | 8117 | 7225 | 6721 | 6558 | 20504 | 7225 | 6721 | 6558 | 20504 | - - - | - - - | - - - | - - -
5/3/2026 | 8:45:00 AM | 288.26 | 284.89 | 285.02 | 498.81 | 491.32 | 496.25 | 28.345 | 25.9623 | 26.2991 | 0.6139 | 1.433 | 1.427 | 1.423 | 2.053 | 1.975 | 1.92 | Over-range | 60.02 | 7511 | 6939 | 6819 | 21270 | - - - | - - - | - - - | - - - | 7511 | 6939 | 6819 | 21270 | 686 | 430 | 910 | 2026 | - - - | - - - | - - - | - - - | 686 | 430 | 910 | 2026 | 8169 | 7396 | 7495 | 23060 | # # # | # # # | # # # | # # # | 0.92 | 0.938 | 0.91 | 0.922 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.991 | 0.995 | - - - | 0.095 | 1.7 | 1.58 | 1.59 | 1.6 | 1.56 | 1.64 | 42.83 | 37.54 | 44.03 | 0 | - - - | - - - | - - - | - - - | 8169 | 7396 | 7495 | 23060 | Over-range | 3212 | 2558 | 3109 | 8908 | 3138 | 2522 | 2973 | 8674 | 7500 | 6895 | 6781 | 21176 | 7500 | 6895 | 6781 | 21176 | - - - | - - - | - - - | - - -
5/3/2026 | 9:00:00 AM | 286.92 | 283.46 | 283.68 | 496.37 | 488.9 | 493.99 | 62.252 | 55.0892 | 56.3237 | 1.6587 | 1.432 | 1.426 | 1.423 | 2.02 | 1.935 | 1.953 | Over-range | 60.01 | 13270 | 11627 | 11514 | 36412 | - - - | - - - | - - - | - - - | 13270 | 11627 | 11514 | 36412 | 1285 | 566 | 2156 | 4007 | - - - | - - - | - - - | - - - | 1285 | 566 | 2156 | 4007 | 14314 | 12590 | 12926 | 39830 | # # # | # # # | # # # | # # # | 0.927 | 0.924 | 0.891 | 0.914 | # # # | # # # | # # # | - - - | 0.995 | 0.999 | 0.982 | 0.992 | - - - | 0.11 | 1.63 | 1.55 | 1.58 | 1.55 | 1.54 | 1.59 | 42.38 | 40.49 | 47.14 | 0 | - - - | - - - | - - - | - - - | 14314 | 12590 | 12926 | 39830 | Over-range | 5339 | 4815 | 5868 | 16128 | 5178 | 4777 | 5446 | 15619 | 13236 | 11551 | 11484 | 36271 | 13236 | 11551 | 11484 | 36271 | - - - | - - - | - - - | - - -
5/3/2026 | 9:15:00 AM | 283.79 | 280.92 | 280.97 | 491.36 | 484.64 | 488.73 | 145.9992 | 130.8573 | 130.9854 | 4.9745 | 1.433 | 1.43 | 1.429 | 1.789 | 1.781 | 1.897 | Over-range | 60.01 | 38924 | 33936 | 32919 | 105779 | - - - | - - - | - - - | - - - | 38924 | 33936 | 32919 | 105779 | 4128 | 1456 | 6922 | 12505 | - - - | - - - | - - - | - - - | 4128 | 1456 | 6922 | 12505 | 41370 | 36702 | 36755 | 114827 | # # # | # # # | # # # | # # # | 0.941 | 0.925 | 0.896 | 0.921 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.978 | 0.991 | - - - | 0.118 | 1.67 | 1.66 | 1.68 | 1.6 | 1.66 | 1.67 | 34.72 | 41.12 | 44.5 | 0 | - - - | - - - | - - - | - - - | 41370 | 36702 | 36755 | 114827 | Over-range | 14004 | 13975 | 16340 | 44660 | 13382 | 13897 | 14801 | 42873 | 38829 | 33886 | 32830 | 105544 | 38829 | 33886 | 32830 | 105544 | - - - | - - - | - - - | - - -
5/3/2026 | 9:30:00 AM | 283.73 | 280.65 | 280.82 | 491.07 | 484.19 | 488.63 | 138.3993 | 122.4686 | 124.453 | 4.1671 | 1.432 | 1.43 | 1.428 | 1.812 | 1.797 | 1.922 | Over-range | 60 | 36855 | 31597 | 31098 | 99550 | - - - | - - - | - - - | - - - | 36855 | 31597 | 31098 | 99550 | 3686 | 1209 | 6719 | 11614 | - - - | - - - | - - - | - - - | 3686 | 1209 | 6719 | 11614 | 39178 | 34275 | 34862 | 108314 | # # # | # # # | # # # | # # # | 0.941 | 0.922 | 0.892 | 0.919 | # # # | # # # | # # # | - - - | 0.995 | 0.999 | 0.977 | 0.991 | - - - | 0.117 | 1.62 | 1.63 | 1.62 | 1.56 | 1.61 | 1.61 | 34.99 | 42.06 | 45.32 | 0 | - - - | - - - | - - - | - - - | 39178 | 34275 | 34862 | 108314 | Over-range | 13277 | 13277 | 15744 | 42661 | 12755 | 13218 | 14238 | 41049 | 36773 | 31549 | 31002 | 99323 | 36773 | 31549 | 31002 | 99323 | - - - | - - - | - - - | - - -
5/3/2026 | 9:45:00 AM | 283.84 | 280.81 | 280.93 | 491.32 | 484.44 | 488.81 | 105.8863 | 93.175 | 96.974 | 2.85 | 1.433 | 1.429 | 1.428 | 1.915 | 1.879 | 1.972 | Over-range | 60.01 | 27603 | 23526 | 23815 | 74944 | - - - | - - - | - - - | - - - | 27603 | 23526 | 23815 | 74944 | 2591 | 1380 | 5241 | 9213 | - - - | - - - | - - - | - - - | 2591 | 1380 | 5241 | 9213 | 29757 | 25927 | 27052 | 82736 | # # # | # # # | # # # | # # # | 0.928 | 0.907 | 0.88 | 0.906 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.976 | 0.99 | - - - | 0.123 | 1.56 | 1.54 | 1.56 | 1.5 | 1.53 | 1.55 | 39.66 | 46.22 | 48.5 | 0 | - - - | - - - | - - - | - - - | 29757 | 25927 | 27052 | 82736 | Over-range | 11099 | 10894 | 12820 | 35029 | 10785 | 10796 | 11699 | 33796 | 27532 | 23473 | 23720 | 74725 | 27532 | 23473 | 23720 | 74725 | - - - | - - - | - - - | - - -
5/3/2026 | 10:00:00 AM | 283.91 | 280.74 | 280.95 | 491.31 | 484.34 | 488.94 | 89.3807 | 77.7894 | 83.8381 | 2.087 | 1.433 | 1.429 | 1.426 | 1.987 | 1.916 | 2.005 | Over-range | 60.03 | 23302 | 19558 | 20582 | 63443 | - - - | - - - | - - - | - - - | 23302 | 19558 | 20582 | 63443 | 1823 | 1462 | 4579 | 7865 | - - - | - - - | - - - | - - - | 1823 | 1462 | 4579 | 7865 | 25308 | 21791 | 23500 | 70599 | # # # | # # # | # # # | # # # | 0.921 | 0.898 | 0.876 | 0.899 | # # # | # # # | # # # | - - - | 0.997 | 0.997 | 0.976 | 0.99 | - - - | 0.124 | 1.51 | 1.5 | 1.49 | 1.46 | 1.46 | 1.49 | 42.07 | 48.85 | 49.81 | 0 | - - - | - - - | - - - | - - - | 25308 | 21791 | 23500 | 70599 | Over-range | 9859 | 9602 | 11329 | 30940 | 9689 | 9490 | 10362 | 29924 | 23235 | 19512 | 20484 | 63231 | 23235 | 19512 | 20484 | 63231 | - - - | - - - | - - - | - - -
5/3/2026 | 10:15:00 AM | 283.28 | 279.99 | 280.36 | 490.07 | 483.15 | 487.97 | 84.6194 | 72.7752 | 79.6848 | 2.0107 | 1.431 | 1.428 | 1.425 | 2.031 | 1.944 | 2.039 | Over-range | 60 | 21888 | 18068 | 19315 | 59271 | - - - | - - - | - - - | - - - | 21888 | 18068 | 19315 | 59271 | 1629 | 1425 | 4545 | 7599 | - - - | - - - | - - - | - - - | 1629 | 1425 | 4545 | 7599 | 23917 | 20342 | 22300 | 66558 | # # # | # # # | # # # | # # # | 0.915 | 0.888 | 0.866 | 0.89 | # # # | # # # | # # # | - - - | 0.997 | 0.997 | 0.973 | 0.989 | - - - | 0.128 | 1.49 | 1.47 | 1.47 | 1.43 | 1.44 | 1.46 | 43.9 | 51.48 | 51.81 | 0 | - - - | - - - | - - - | - - - | 23917 | 20342 | 22300 | 66558 | Over-range | 9621 | 9338 | 11128 | 30241 | 9482 | 9228 | 10157 | 29270 | 21815 | 17987 | 19253 | 59056 | 21815 | 17987 | 19253 | 59056 | - - - | - - - | - - - | - - -
5/3/2026 | 10:30:00 AM | 283.01 | 279.58 | 280.01 | 489.47 | 482.44 | 487.49 | 79.9265 | 68.2081 | 75.4153 | 1.9309 | 1.431 | 1.428 | 1.425 | 2.053 | 1.947 | 2.054 | Over-range | 60.01 | 20619 | 16831 | 18137 | 55586 | - - - | - - - | - - - | - - - | 20619 | 16831 | 18137 | 55586 | 1479 | 1341 | 4412 | 7232 | - - - | - - - | - - - | - - - | 1479 | 1341 | 4412 | 7232 | 22565 | 19037 | 21076 | 62678 | # # # | # # # | # # # | # # # | 0.914 | 0.884 | 0.861 | 0.887 | # # # | # # # | # # # | - - - | 0.997 | 0.997 | 0.971 | 0.989 | - - - | 0.13 | 1.46 | 1.46 | 1.45 | 1.41 | 1.43 | 1.44 | 44.43 | 52.63 | 53.02 | 0 | - - - | - - - | - - - | - - - | 22565 | 19037 | 21076 | 62678 | Over-range | 9151 | 8889 | 10723 | 28928 | 9031 | 8787 | 9773 | 28009 | 20528 | 16752 | 18092 | 55372 | 20528 | 16752 | 18092 | 55372 | - - - | - - - | - - - | - - -
5/3/2026 | 10:45:00 AM | 283.08 | 279.74 | 280.18 | 489.64 | 482.77 | 487.68 | 78.9391 | 67.4798 | 74.1545 | 1.9029 | 1.432 | 1.428 | 1.425 | 2.065 | 1.969 | 2.075 | Over-range | 60.01 | 20274 | 16607 | 17717 | 54598 | - - - | - - - | - - - | - - - | 20274 | 16607 | 17717 | 54598 | 1609 | 1303 | 4349 | 7261 | - - - | - - - | - - - | - - - | 1609 | 1303 | 4349 | 7261 | 22277 | 18831 | 20724 | 61833 | # # # | # # # | # # # | # # # | 0.91 | 0.882 | 0.855 | 0.883 | # # # | # # # | # # # | - - - | 0.997 | 0.997 | 0.971 | 0.988 | - - - | 0.133 | 1.48 | 1.46 | 1.45 | 1.42 | 1.43 | 1.45 | 45.4 | 53.36 | 54.55 | 0 | - - - | - - - | - - - | - - - | 22277 | 18831 | 20724 | 61833 | Over-range | 9219 | 8874 | 10743 | 28999 | 9077 | 8777 | 9823 | 28075 | 20211 | 16521 | 17640 | 54373 | 20211 | 16521 | 17640 | 54373 | - - - | - - - | - - - | - - -
5/3/2026 | 11:00:00 AM | 282.9 | 279.51 | 279.98 | 489.29 | 482.38 | 487.37 | 79.2884 | 67.5825 | 74.3467 | 1.9025 | 1.432 | 1.429 | 1.426 | 2.073 | 1.98 | 2.088 | Over-range | 60.01 | 20295 | 16588 | 17672 | 54555 | - - - | - - - | - - - | - - - | 20295 | 16588 | 17672 | 54555 | 1653 | 1295 | 4398 | 7346 | - - - | - - - | - - - | - - - | 1653 | 1295 | 4398 | 7346 | 22357 | 18841 | 20759 | 61957 | # # # | # # # | # # # | # # # | 0.908 | 0.88 | 0.851 | 0.88 | # # # | # # # | # # # | - - - | 0.997 | 0.997 | 0.97 | 0.988 | - - - | 0.135 | 1.5 | 1.47 | 1.48 | 1.43 | 1.45 | 1.47 | 46.06 | 53.74 | 55.41 | 0 | - - - | - - - | - - - | - - - | 22357 | 18841 | 20759 | 61957 | Over-range | 9366 | 8930 | 10884 | 29345 | 9219 | 8835 | 9955 | 28410 | 20228 | 16514 | 17585 | 54327 | 20228 | 16514 | 17585 | 54327 | - - - | - - - | - - - | - - -
5/3/2026 | 11:15:00 AM | 282.58 | 279.18 | 279.66 | 488.71 | 481.81 | 486.83 | 80.305 | 68.3731 | 75.2556 | 1.9435 | 1.432 | 1.429 | 1.426 | 2.076 | 1.99 | 2.095 | Over-range | 60 | 20483 | 16734 | 17815 | 55032 | - - - | - - - | - - - | - - - | 20483 | 16734 | 17815 | 55032 | 1692 | 1308 | 4477 | 7477 | - - - | - - - | - - - | - - - | 1692 | 1308 | 4477 | 7477 | 22614 | 19038 | 20984 | 62636 | # # # | # # # | # # # | # # # | 0.906 | 0.879 | 0.849 | 0.879 | # # # | # # # | # # # | - - - | 0.997 | 0.997 | 0.97 | 0.988 | - - - | 0.136 | 1.49 | 1.46 | 1.46 | 1.42 | 1.44 | 1.46 | 46.65 | 54.06 | 55.9 | 0 | - - - | - - - | - - - | - - - | 22614 | 19038 | 20984 | 62636 | Over-range | 9571 | 9073 | 11079 | 29888 | 9420 | 8978 | 10135 | 28937 | 20375 | 16685 | 17740 | 54800 | 20375 | 16685 | 17740 | 54800 | - - - | - - - | - - - | - - -
5/3/2026 | 11:30:00 AM | 282.68 | 279.4 | 279.86 | 488.97 | 482.24 | 487.04 | 82.4153 | 70.4248 | 77.2843 | 1.9431 | 1.434 | 1.43 | 1.428 | 2.076 | 1.998 | 2.094 | Over-range | 60.02 | 20967 | 17201 | 18280 | 56448 | - - - | - - - | - - - | - - - | 20967 | 17201 | 18280 | 56448 | 1813 | 1407 | 4599 | 7819 | - - - | - - - | - - - | - - - | 1813 | 1407 | 4599 | 7819 | 23223 | 19627 | 21572 | 64421 | # # # | # # # | # # # | # # # | 0.903 | 0.876 | 0.847 | 0.876 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.969 | 0.988 | - - - | 0.139 | 1.51 | 1.46 | 1.48 | 1.44 | 1.45 | 1.47 | 47.46 | 54.76 | 56.32 | 0 | - - - | - - - | - - - | - - - | 23223 | 19627 | 21572 | 64421 | Over-range | 9971 | 9448 | 11445 | 31020 | 9804 | 9342 | 10480 | 30018 | 20853 | 17144 | 18206 | 56203 | 20853 | 17144 | 18206 | 56203 | - - - | - - - | - - - | - - -
5/3/2026 | 11:45:00 AM | 282.56 | 279.16 | 279.67 | 488.67 | 481.82 | 486.83 | 82.5475 | 70.1785 | 77.6091 | 1.9635 | 1.433 | 1.429 | 1.427 | 2.084 | 1.994 | 2.099 | Over-range | 60.02 | 21005 | 17121 | 18328 | 56453 | - - - | - - - | - - - | - - - | 21005 | 17121 | 18328 | 56453 | 1731 | 1417 | 4653 | 7800 | - - - | - - - | - - - | - - - | 1731 | 1417 | 4653 | 7800 | 23254 | 19543 | 21649 | 64446 | # # # | # # # | # # # | # # # | 0.903 | 0.876 | 0.847 | 0.876 | # # # | # # # | # # # | - - - | 0.997 | 0.997 | 0.969 | 0.987 | - - - | 0.138 | 1.49 | 1.47 | 1.48 | 1.43 | 1.45 | 1.47 | 47.41 | 54.83 | 56.48 | 0 | - - - | - - - | - - - | - - - | 23254 | 19543 | 21649 | 64446 | Over-range | 9965 | 9418 | 11515 | 31062 | 9813 | 9310 | 10533 | 30066 | 20898 | 17061 | 18250 | 56210 | 20898 | 17061 | 18250 | 56210 | - - - | - - - | - - - | - - -
5/3/2026 | 12:00:00 PM | 282.25 | 278.84 | 279.33 | 488.14 | 481.24 | 486.27 | 84.2551 | 71.5236 | 78.9678 | 2.0753 | 1.434 | 1.43 | 1.428 | 2.086 | 2.007 | 2.109 | Over-range | 60.01 | 21381 | 17415 | 18566 | 57362 | - - - | - - - | - - - | - - - | 21381 | 17415 | 18566 | 57362 | 1825 | 1432 | 4775 | 8032 | - - - | - - - | - - - | - - - | 1825 | 1432 | 4775 | 8032 | 23715 | 19899 | 22007 | 65621 | # # # | # # # | # # # | # # # | 0.902 | 0.875 | 0.844 | 0.874 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.968 | 0.987 | - - - | 0.14 | 1.51 | 1.48 | 1.49 | 1.44 | 1.46 | 1.49 | 47.84 | 55.17 | 57.12 | 0 | - - - | - - - | - - - | - - - | 23715 | 19899 | 22007 | 65621 | Over-range | 10249 | 9624 | 11809 | 31852 | 10085 | 9517 | 10801 | 30823 | 21305 | 17332 | 18472 | 57109 | 21305 | 17332 | 18472 | 57109 | - - - | - - - | - - - | - - -
5/3/2026 | 12:15:00 PM | 282.27 | 278.9 | 279.39 | 488.18 | 481.36 | 486.32 | 84.6771 | 72.0358 | 79.502 | 2.0118 | 1.434 | 1.431 | 1.429 | 2.086 | 2.007 | 2.106 | Over-range | 60 | 21473 | 17527 | 18706 | 57706 | - - - | - - - | - - - | - - - | 21473 | 17527 | 18706 | 57706 | 1855 | 1476 | 4791 | 8122 | - - - | - - - | - - - | - - - | 1855 | 1476 | 4791 | 8122 | 23842 | 20048 | 22166 | 66056 | # # # | # # # | # # # | # # # | 0.901 | 0.874 | 0.844 | 0.874 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.968 | 0.987 | - - - | 0.141 | 1.53 | 1.49 | 1.5 | 1.45 | 1.47 | 1.5 | 48.16 | 55.35 | 57.14 | 0 | - - - | - - - | - - - | - - - | 23842 | 20048 | 22166 | 66056 | Over-range | 10352 | 9729 | 11885 | 32129 | 10184 | 9616 | 10877 | 31085 | 21372 | 17460 | 18616 | 57448 | 21372 | 17460 | 18616 | 57448 | - - - | - - - | - - - | - - -
5/3/2026 | 12:30:00 PM | 282.14 | 278.84 | 279.28 | 488.03 | 481.25 | 486.08 | 82.8923 | 70.708 | 77.8449 | 1.9897 | 1.433 | 1.43 | 1.428 | 2.078 | 1.995 | 2.095 | Over-range | 60.01 | 21060 | 17240 | 18359 | 56658 | - - - | - - - | - - - | - - - | 21060 | 17240 | 18359 | 56658 | 1799 | 1426 | 4640 | 7865 | - - - | - - - | - - - | - - - | 1799 | 1426 | 4640 | 7865 | 23317 | 19669 | 21683 | 64669 | # # # | # # # | # # # | # # # | 0.903 | 0.876 | 0.847 | 0.876 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.969 | 0.987 | - - - | 0.139 | 1.51 | 1.46 | 1.48 | 1.44 | 1.44 | 1.48 | 47.35 | 54.77 | 56.52 | 0 | - - - | - - - | - - - | - - - | 23317 | 19669 | 21683 | 64669 | Over-range | 9996 | 9464 | 11530 | 31153 | 9833 | 9356 | 10555 | 30144 | 20978 | 17170 | 18259 | 56407 | 20978 | 17170 | 18259 | 56407 | - - - | - - - | - - - | - - -
5/3/2026 | 12:45:00 PM | 282.03 | 278.7 | 279.16 | 487.82 | 481.01 | 485.9 | 85.2616 | 72.3695 | 80.2119 | 1.9656 | 1.434 | 1.43 | 1.429 | 2.088 | 2.006 | 2.107 | Over-range | 60.01 | 21610 | 17594 | 18851 | 58055 | - - - | - - - | - - - | - - - | 21610 | 17594 | 18851 | 58055 | 1837 | 1489 | 4843 | 8169 | - - - | - - - | - - - | - - - | 1837 | 1489 | 4843 | 8169 | 23993 | 20133 | 22347 | 66473 | # # # | # # # | # # # | # # # | 0.901 | 0.874 | 0.844 | 0.873 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.968 | 0.987 | - - - | 0.141 | 1.53 | 1.48 | 1.5 | 1.45 | 1.46 | 1.5 | 48.19 | 55.47 | 57.24 | 0 | - - - | - - - | - - - | - - - | 23993 | 20133 | 22347 | 66473 | Over-range | 10419 | 9784 | 11997 | 32365 | 10256 | 9670 | 10976 | 31317 | 21508 | 17534 | 18751 | 57794 | 21508 | 17534 | 18751 | 57794 | - - - | - - - | - - - | - - -
5/3/2026 | 1:00:00 PM | 281.86 | 278.55 | 279.01 | 487.53 | 480.76 | 485.62 | 83.1555 | 70.8392 | 78.2654 | 1.9724 | 1.434 | 1.43 | 1.428 | 2.077 | 1.989 | 2.089 | Over-range | 60.01 | 21125 | 17255 | 18467 | 56848 | - - - | - - - | - - - | - - - | 21125 | 17255 | 18467 | 56848 | 1750 | 1450 | 4675 | 7875 | - - - | - - - | - - - | - - - | 1750 | 1450 | 4675 | 7875 | 23371 | 19688 | 21784 | 64843 | # # # | # # # | # # # | # # # | 0.904 | 0.876 | 0.848 | 0.877 | # # # | # # # | # # # | - - - | 0.997 | 0.996 | 0.969 | 0.987 | - - - | 0.139 | 1.54 | 1.49 | 1.51 | 1.46 | 1.47 | 1.51 | 47.2 | 54.72 | 56.21 | 0 | - - - | - - - | - - - | - - - | 23371 | 19688 | 21784 | 64843 | Over-range | 9983 | 9478 | 11545 | 31169 | 9828 | 9366 | 10556 | 30158 | 21025 | 17205 | 18373 | 56603 | 21025 | 17205 | 18373 | 56603 | - - - | - - - | - - - | - - -
5/3/2026 | 1:15:00 PM | 281.87 | 278.64 | 279.1 | 487.58 | 480.97 | 485.68 | 86.0508 | 73.3257 | 80.994 | 1.9817 | 1.435 | 1.431 | 1.429 | 2.084 | 2.008 | 2.101 | Over-range | 60.01 | 21798 | 17815 | 19064 | 58676 | - - - | - - - | - - - | - - - | 21798 | 17815 | 19064 | 58676 | 1884 | 1536 | 4870 | 8290 | - - - | - - - | - - - | - - - | 1884 | 1536 | 4870 | 8290 | 24212 | 20403 | 22571 | 67185 | # # # | # # # | # # # | # # # | 0.9 | 0.873 | 0.845 | 0.873 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.969 | 0.987 | - - - | 0.141 | 1.55 | 1.49 | 1.52 | 1.47 | 1.47 | 1.53 | 48.29 | 55.66 | 57.01 | 0 | - - - | - - - | - - - | - - - | 24212 | 20403 | 22571 | 67185 | Over-range | 10531 | 9942 | 12078 | 32710 | 10361 | 9822 | 11052 | 31642 | 21693 | 17742 | 18975 | 58411 | 21693 | 17742 | 18975 | 58411 | - - - | - - - | - - - | - - -
5/3/2026 | 1:30:00 PM | 281.83 | 278.59 | 279.03 | 487.53 | 480.85 | 485.58 | 85.2444 | 72.6413 | 80.3464 | 1.9962 | 1.434 | 1.43 | 1.428 | 2.082 | 1.997 | 2.094 | Over-range | 60.01 | 21606 | 17660 | 18929 | 58195 | - - - | - - - | - - - | - - - | 21606 | 17660 | 18929 | 58195 | 1823 | 1536 | 4810 | 8169 | - - - | - - - | - - - | - - - | 1823 | 1536 | 4810 | 8169 | 23965 | 20195 | 22372 | 66531 | # # # | # # # | # # # | # # # | 0.902 | 0.875 | 0.846 | 0.875 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.969 | 0.987 | - - - | 0.14 | 1.54 | 1.49 | 1.5 | 1.46 | 1.46 | 1.5 | 47.89 | 55.27 | 56.64 | 0 | - - - | - - - | - - - | - - - | 23965 | 20195 | 22372 | 66531 | Over-range | 10358 | 9793 | 11918 | 32228 | 10196 | 9671 | 10904 | 31175 | 21519 | 17583 | 18838 | 57940 | 21519 | 17583 | 18838 | 57940 | - - - | - - - | - - - | - - -
5/3/2026 | 1:45:00 PM | 281.41 | 278.18 | 278.63 | 486.79 | 480.16 | 484.88 | 85.3485 | 72.8294 | 80.6057 | 1.9806 | 1.434 | 1.43 | 1.428 | 2.079 | 1.993 | 2.087 | Over-range | 60.01 | 21616 | 17684 | 19001 | 58301 | - - - | - - - | - - - | - - - | 21616 | 17684 | 19001 | 58301 | 1800 | 1560 | 4802 | 8162 | - - - | - - - | - - - | - - - | 1800 | 1560 | 4802 | 8162 | 23957 | 20217 | 22409 | 66584 | # # # | # # # | # # # | # # # | 0.902 | 0.875 | 0.848 | 0.876 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.969 | 0.987 | - - - | 0.14 | 1.54 | 1.49 | 1.51 | 1.46 | 1.47 | 1.51 | 47.75 | 55.16 | 56.22 | 0 | - - - | - - - | - - - | - - - | 23957 | 20217 | 22409 | 66584 | Over-range | 10321 | 9796 | 11874 | 32146 | 10162 | 9671 | 10860 | 31092 | 21517 | 17615 | 18906 | 58038 | 21517 | 17615 | 18906 | 58038 | - - - | - - - | - - - | - - -
5/3/2026 | 2:00:00 PM | 281.41 | 278.24 | 278.76 | 486.78 | 480.36 | 484.99 | 86.8635 | 74.2518 | 82.4436 | 1.9199 | 1.436 | 1.432 | 1.43 | 2.083 | 1.99 | 2.082 | Over-range | 60 | 21982 | 18014 | 19469 | 59466 | - - - | - - - | - - - | - - - | 21982 | 18014 | 19469 | 59466 | 1821 | 1688 | 4889 | 8397 | - - - | - - - | - - - | - - - | 1821 | 1688 | 4889 | 8397 | 24400 | 20628 | 22948 | 67976 | # # # | # # # | # # # | # # # | 0.901 | 0.873 | 0.848 | 0.875 | # # # | # # # | # # # | - - - | 0.997 | 0.996 | 0.97 | 0.987 | - - - | 0.141 | 1.56 | 1.51 | 1.52 | 1.48 | 1.48 | 1.53 | 48.22 | 55.5 | 56.25 | 0 | - - - | - - - | - - - | - - - | 24400 | 20628 | 22948 | 67976 | Over-range | 10583 | 10048 | 12141 | 32919 | 10424 | 9905 | 11114 | 31830 | 21868 | 17944 | 19382 | 59194 | 21868 | 17944 | 19382 | 59194 | - - - | - - - | - - - | - - -
5/3/2026 | 2:15:00 PM | 281.7 | 278.54 | 278.94 | 487.36 | 480.76 | 485.36 | 85.5997 | 73.18 | 80.8345 | 1.9956 | 1.435 | 1.431 | 1.429 | 2.074 | 1.984 | 2.08 | Over-range | 60.01 | 21723 | 17806 | 19096 | 58625 | - - - | - - - | - - - | - - - | 21723 | 17806 | 19096 | 58625 | 1815 | 1574 | 4800 | 8189 | - - - | - - - | - - - | - - - | 1815 | 1574 | 4800 | 8189 | 24048 | 20337 | 22494 | 66879 | # # # | # # # | # # # | # # # | 0.903 | 0.875 | 0.849 | 0.877 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.97 | 0.987 | - - - | 0.14 | 1.55 | 1.49 | 1.49 | 1.47 | 1.46 | 1.5 | 47.42 | 54.96 | 55.97 | 0 | - - - | - - - | - - - | - - - | 24048 | 20337 | 22494 | 66879 | Over-range | 10304 | 9821 | 11881 | 32165 | 10143 | 9694 | 10868 | 31105 | 21625 | 17722 | 19011 | 58359 | 21625 | 17722 | 19011 | 58359 | - - - | - - - | - - - | - - -
5/3/2026 | 2:30:00 PM | 281.78 | 278.63 | 279.08 | 487.47 | 480.98 | 485.57 | 88.4495 | 75.5299 | 83.6636 | 2.0641 | 1.435 | 1.431 | 1.429 | 2.083 | 1.997 | 2.091 | Over-range | 60 | 22402 | 18351 | 19733 | 60486 | - - - | - - - | - - - | - - - | 22402 | 18351 | 19733 | 60486 | 1887 | 1676 | 5006 | 8569 | - - - | - - - | - - - | - - - | 1887 | 1676 | 5006 | 8569 | 24886 | 21019 | 23318 | 69223 | # # # | # # # | # # # | # # # | 0.9 | 0.873 | 0.846 | 0.874 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.969 | 0.987 | - - - | 0.142 | 1.55 | 1.5 | 1.51 | 1.48 | 1.47 | 1.52 | 48.38 | 55.59 | 56.69 | 0 | - - - | - - - | - - - | - - - | 24886 | 21019 | 23318 | 69223 | Over-range | 10831 | 10247 | 12419 | 33652 | 10665 | 10108 | 11366 | 32543 | 22296 | 18282 | 19636 | 60215 | 22296 | 18282 | 19636 | 60215 | - - - | - - - | - - - | - - -
5/3/2026 | 2:45:00 PM | 281.45 | 278.38 | 278.82 | 486.95 | 480.58 | 485.02 | 86.0332 | 74.0371 | 81.4488 | 1.9968 | 1.435 | 1.431 | 1.429 | 2.066 | 1.977 | 2.067 | Over-range | 60.01 | 21816 | 18015 | 19293 | 59124 | - - - | - - - | - - - | - - - | 21816 | 18015 | 19293 | 59124 | 1845 | 1641 | 4762 | 8248 | - - - | - - - | - - - | - - - | 1845 | 1641 | 4762 | 8248 | 24150 | 20565 | 22658 | 67374 | # # # | # # # | # # # | # # # | 0.903 | 0.876 | 0.852 | 0.878 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.971 | 0.988 | - - - | 0.14 | 1.54 | 1.5 | 1.51 | 1.48 | 1.47 | 1.51 | 47.38 | 54.75 | 55.5 | 0 | - - - | - - - | - - - | - - - | 24150 | 20565 | 22658 | 67374 | Over-range | 10349 | 9915 | 11875 | 32286 | 10183 | 9778 | 10878 | 31214 | 21714 | 17940 | 19215 | 58868 | 21714 | 17940 | 19215 | 58868 | - - - | - - - | - - - | - - -
5/3/2026 | 3:00:00 PM | 281.53 | 278.48 | 278.87 | 487.13 | 480.7 | 485.12 | 88.6029 | 76.1504 | 83.7997 | 2.0741 | 1.435 | 1.431 | 1.429 | 2.073 | 1.991 | 2.081 | Over-range | 60.01 | 22440 | 18520 | 19800 | 60760 | - - - | - - - | - - - | - - - | 22440 | 18520 | 19800 | 60760 | 1949 | 1702 | 4943 | 8594 | - - - | - - - | - - - | - - - | 1949 | 1702 | 4943 | 8594 | 24906 | 21178 | 23337 | 69421 | # # # | # # # | # # # | # # # | 0.901 | 0.875 | 0.848 | 0.875 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.97 | 0.987 | - - - | 0.141 | 1.55 | 1.49 | 1.51 | 1.48 | 1.46 | 1.52 | 48.1 | 55.21 | 56.29 | 0 | - - - | - - - | - - - | - - - | 24906 | 21178 | 23337 | 69421 | Over-range | 10798 | 10270 | 12349 | 33566 | 10620 | 10128 | 11316 | 32447 | 22336 | 18441 | 19711 | 60489 | 22336 | 18441 | 19711 | 60489 | - - - | - - - | - - - | - - -
5/3/2026 | 3:15:00 PM | 281.18 | 277.99 | 278.47 | 486.39 | 479.89 | 484.54 | 87.0224 | 74.7719 | 82.7724 | 2.0855 | 1.434 | 1.43 | 1.428 | 2.067 | 1.965 | 2.061 | Over-range | 60.01 | 22074 | 18184 | 19614 | 59872 | - - - | - - - | - - - | - - - | 22074 | 18184 | 19614 | 59872 | 1770 | 1715 | 4837 | 8321 | - - - | - - - | - - - | - - - | 1770 | 1715 | 4837 | 8321 | 24408 | 20744 | 23001 | 68152 | # # # | # # # | # # # | # # # | 0.904 | 0.877 | 0.853 | 0.878 | # # # | # # # | # # # | - - - | 0.997 | 0.996 | 0.971 | 0.988 | - - - | 0.139 | 1.54 | 1.48 | 1.49 | 1.46 | 1.46 | 1.5 | 47.14 | 54.53 | 55.13 | 0 | - - - | - - - | - - - | - - - | 24408 | 20744 | 23001 | 68152 | Over-range | 10405 | 9978 | 12006 | 32538 | 10253 | 9829 | 10989 | 31456 | 21977 | 18110 | 19532 | 59619 | 21977 | 18110 | 19532 | 59619 | - - - | - - - | - - - | - - -
5/3/2026 | 3:30:00 PM | 281.05 | 278.03 | 278.45 | 486.3 | 479.98 | 484.35 | 89.7172 | 77.7609 | 85.1119 | 2.0835 | 1.435 | 1.431 | 1.43 | 2.056 | 1.976 | 2.058 | Over-range | 60 | 22738 | 18963 | 20221 | 61922 | - - - | - - - | - - - | - - - | 22738 | 18963 | 20221 | 61922 | 1981 | 1787 | 4871 | 8640 | - - - | - - - | - - - | - - - | 1981 | 1787 | 4871 | 8640 | 25174 | 21590 | 23665 | 70430 | # # # | # # # | # # # | # # # | 0.903 | 0.878 | 0.855 | 0.879 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.972 | 0.988 | - - - | 0.14 | 1.54 | 1.49 | 1.51 | 1.47 | 1.46 | 1.51 | 47.41 | 54.07 | 55.07 | 0 | - - - | - - - | - - - | - - - | 25174 | 21590 | 23665 | 70430 | Over-range | 10798 | 10319 | 12289 | 33542 | 10614 | 10163 | 11282 | 32411 | 22640 | 18892 | 20120 | 61653 | 22640 | 18892 | 20120 | 61653 | - - - | - - - | - - - | - - -
5/3/2026 | 3:45:00 PM | 280.97 | 277.89 | 278.37 | 486.09 | 479.77 | 484.23 | 90.3828 | 78.2742 | 86.031 | 2.1052 | 1.436 | 1.432 | 1.43 | 2.058 | 1.967 | 2.054 | Over-range | 60.01 | 22915 | 19090 | 20454 | 62459 | - - - | - - - | - - - | - - - | 22915 | 19090 | 20454 | 62459 | 1946 | 1838 | 4920 | 8704 | - - - | - - - | - - - | - - - | 1946 | 1838 | 4920 | 8704 | 25355 | 21723 | 23913 | 70991 | # # # | # # # | # # # | # # # | 0.904 | 0.879 | 0.855 | 0.88 | # # # | # # # | # # # | - - - | 0.996 | 0.995 | 0.972 | 0.988 | - - - | 0.139 | 1.55 | 1.5 | 1.51 | 1.48 | 1.46 | 1.51 | 47.34 | 53.89 | 54.86 | 0 | - - - | - - - | - - - | - - - | 25355 | 21723 | 23913 | 70991 | Over-range | 10846 | 10363 | 12384 | 33730 | 10669 | 10199 | 11365 | 32588 | 22806 | 19020 | 20363 | 62189 | 22806 | 19020 | 20363 | 62189 | - - - | - - - | - - - | - - -
5/3/2026 | 4:00:00 PM | 280.92 | 277.85 | 278.24 | 486.06 | 479.6 | 484.06 | 89.3837 | 77.4913 | 84.7751 | 2.1714 | 1.435 | 1.431 | 1.429 | 2.043 | 1.955 | 2.044 | Over-range | 60 | 22728 | 18963 | 20207 | 61898 | - - - | - - - | - - - | - - - | 22728 | 18963 | 20207 | 61898 | 1914 | 1742 | 4819 | 8475 | - - - | - - - | - - - | - - - | 1914 | 1742 | 4819 | 8475 | 25049 | 21486 | 23538 | 70073 | # # # | # # # | # # # | # # # | 0.907 | 0.882 | 0.859 | 0.883 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.972 | 0.988 | - - - | 0.137 | 1.55 | 1.49 | 1.51 | 1.48 | 1.47 | 1.52 | 46.21 | 52.9 | 54 | 0 | - - - | - - - | - - - | - - - | 25049 | 21486 | 23538 | 70073 | Over-range | 10521 | 10101 | 12065 | 32830 | 10345 | 9949 | 11061 | 31718 | 22637 | 18892 | 20113 | 61642 | 22637 | 18892 | 20113 | 61642 | - - - | - - - | - - - | - - -
5/3/2026 | 4:15:00 PM | 280.76 | 277.72 | 278.1 | 485.8 | 479.39 | 483.79 | 91.9293 | 79.7747 | 87.2878 | 2.1687 | 1.435 | 1.431 | 1.43 | 2.048 | 1.964 | 2.049 | Over-range | 60 | 23327 | 19499 | 20778 | 63604 | - - - | - - - | - - - | - - - | 23327 | 19499 | 20778 | 63604 | 2011 | 1829 | 4954 | 8795 | - - - | - - - | - - - | - - - | 2011 | 1829 | 4954 | 8795 | 25773 | 22128 | 24244 | 72145 | # # # | # # # | # # # | # # # | 0.905 | 0.881 | 0.857 | 0.882 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.972 | 0.988 | - - - | 0.138 | 1.54 | 1.48 | 1.5 | 1.47 | 1.46 | 1.5 | 46.89 | 53.27 | 54.47 | 0 | - - - | - - - | - - - | - - - | 25773 | 22128 | 24244 | 72145 | Over-range | 10952 | 10459 | 12487 | 34038 | 10766 | 10298 | 11462 | 32882 | 23225 | 19424 | 20686 | 63335 | 23225 | 19424 | 20686 | 63335 | - - - | - - - | - - - | - - -
5/3/2026 | 4:30:00 PM | 280.69 | 277.59 | 278.03 | 485.6 | 479.19 | 483.7 | 90.3575 | 78.3354 | 86.0066 | 2.1082 | 1.435 | 1.431 | 1.43 | 2.044 | 1.948 | 2.038 | Over-range | 59.99 | 22966 | 19155 | 20517 | 62638 | - - - | - - - | - - - | - - - | 22966 | 19155 | 20517 | 62638 | 1889 | 1810 | 4857 | 8556 | - - - | - - - | - - - | - - - | 1889 | 1810 | 4857 | 8556 | 25310 | 21708 | 23871 | 70889 | # # # | # # # | # # # | # # # | 0.907 | 0.882 | 0.86 | 0.884 | # # # | # # # | # # # | - - - | 0.997 | 0.996 | 0.973 | 0.988 | - - - | 0.137 | 1.53 | 1.49 | 1.5 | 1.47 | 1.46 | 1.51 | 46.22 | 52.88 | 53.81 | 0 | - - - | - - - | - - - | - - - | 25310 | 21708 | 23871 | 70889 | Over-range | 10628 | 10211 | 12194 | 33174 | 10458 | 10049 | 11185 | 32052 | 22871 | 19086 | 20426 | 62383 | 22871 | 19086 | 20426 | 62383 | - - - | - - - | - - - | - - -
5/3/2026 | 4:45:00 PM | 280.45 | 277.38 | 277.69 | 485.29 | 478.7 | 483.16 | 92.0514 | 79.6777 | 87.0582 | 2.2094 | 1.435 | 1.431 | 1.43 | 2.039 | 1.961 | 2.05 | Over-range | 59.99 | 23383 | 19507 | 20715 | 63604 | - - - | - - - | - - - | - - - | 23383 | 19507 | 20715 | 63604 | 2009 | 1730 | 4949 | 8688 | - - - | - - - | - - - | - - - | 2009 | 1730 | 4949 | 8688 | 25773 | 22071 | 24140 | 71985 | # # # | # # # | # # # | # # # | 0.907 | 0.884 | 0.858 | 0.884 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.972 | 0.988 | - - - | 0.137 | 1.56 | 1.51 | 1.52 | 1.49 | 1.48 | 1.53 | 46.2 | 52.59 | 54.07 | 0 | - - - | - - - | - - - | - - - | 25773 | 22071 | 24140 | 71985 | Over-range | 10831 | 10322 | 12389 | 33691 | 10643 | 10176 | 11357 | 32551 | 23280 | 19436 | 20633 | 63350 | 23280 | 19436 | 20633 | 63350 | - - - | - - - | - - - | - - -
5/3/2026 | 5:00:00 PM | 280.34 | 277.16 | 277.56 | 484.97 | 478.36 | 483.01 | 93.4615 | 80.7476 | 88.6493 | 2.1651 | 1.435 | 1.431 | 1.43 | 2.044 | 1.958 | 2.048 | Over-range | 60 | 23718 | 19738 | 21093 | 64549 | - - - | - - - | - - - | - - - | 23718 | 19738 | 21093 | 64549 | 1981 | 1817 | 5031 | 8828 | - - - | - - - | - - - | - - - | 1981 | 1817 | 5031 | 8828 | 26161 | 22352 | 24575 | 73088 | # # # | # # # | # # # | # # # | 0.907 | 0.883 | 0.858 | 0.883 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.972 | 0.988 | - - - | 0.137 | 1.54 | 1.5 | 1.5 | 1.47 | 1.47 | 1.51 | 46.45 | 52.77 | 54.05 | 0 | - - - | - - - | - - - | - - - | 26161 | 22352 | 24575 | 73088 | Over-range | 11032 | 10488 | 12605 | 34271 | 10852 | 10329 | 11558 | 33114 | 23621 | 19669 | 21006 | 64296 | 23621 | 19669 | 21006 | 64296 | - - - | - - - | - - - | - - -
5/3/2026 | 5:15:00 PM | 280.29 | 277.32 | 277.69 | 485.02 | 478.72 | 483 | 91.1332 | 79.593 | 86.5932 | 2.1609 | 1.434 | 1.43 | 1.429 | 2.027 | 1.941 | 2.024 | Over-range | 60 | 23163 | 19522 | 20723 | 63408 | - - - | - - - | - - - | - - - | 23163 | 19522 | 20723 | 63408 | 1968 | 1821 | 4770 | 8558 | - - - | - - - | - - - | - - - | 1968 | 1821 | 4770 | 8558 | 25489 | 22033 | 24002 | 71524 | # # # | # # # | # # # | # # # | 0.909 | 0.886 | 0.863 | 0.886 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.974 | 0.989 | - - - | 0.135 | 1.53 | 1.47 | 1.48 | 1.46 | 1.44 | 1.49 | 45.73 | 51.87 | 53.01 | 0 | - - - | - - - | - - - | - - - | 25489 | 22033 | 24002 | 71524 | Over-range | 10629 | 10212 | 12102 | 33074 | 10445 | 10049 | 11122 | 31948 | 23076 | 19454 | 20633 | 63164 | 23076 | 19454 | 20633 | 63164 | - - - | - - - | - - - | - - -
5/3/2026 | 5:30:00 PM | 280.02 | 277.02 | 277.43 | 484.52 | 478.22 | 482.57 | 93.5843 | 81.45 | 88.9111 | 2.2081 | 1.435 | 1.431 | 1.43 | 2.035 | 1.953 | 2.038 | Over-range | 60 | 23731 | 19934 | 21203 | 64869 | - - - | - - - | - - - | - - - | 23731 | 19934 | 21203 | 64869 | 2032 | 1853 | 4948 | 8833 | - - - | - - - | - - - | - - - | 2032 | 1853 | 4948 | 8833 | 26172 | 22540 | 24636 | 73348 | # # # | # # # | # # # | # # # | 0.907 | 0.884 | 0.861 | 0.884 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.974 | 0.989 | - - - | 0.136 | 1.54 | 1.49 | 1.5 | 1.47 | 1.46 | 1.51 | 46.31 | 52.33 | 53.64 | 0 | - - - | - - - | - - - | - - - | 26172 | 22540 | 24636 | 73348 | Over-range | 11029 | 10517 | 12540 | 34220 | 10840 | 10352 | 11523 | 33061 | 23645 | 19863 | 21117 | 64625 | 23645 | 19863 | 21117 | 64625 | - - - | - - - | - - - | - - -
5/3/2026 | 5:45:00 PM | 280.13 | 277.24 | 277.61 | 484.79 | 478.63 | 482.78 | 91.8081 | 80.5876 | 87.2821 | 2.2148 | 1.434 | 1.431 | 1.429 | 2.019 | 1.933 | 2.015 | Over-range | 60 | 23340 | 19802 | 20944 | 64085 | - - - | - - - | - - - | - - - | 23340 | 19802 | 20944 | 64085 | 2006 | 1862 | 4731 | 8598 | - - - | - - - | - - - | - - - | 2006 | 1862 | 4731 | 8598 | 25664 | 22303 | 24188 | 72155 | # # # | # # # | # # # | # # # | 0.909 | 0.888 | 0.866 | 0.888 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.975 | 0.989 | - - - | 0.134 | 1.53 | 1.48 | 1.49 | 1.46 | 1.45 | 1.5 | 45.44 | 51.32 | 52.49 | 0 | - - - | - - - | - - - | - - - | 25664 | 22303 | 24188 | 72155 | Over-range | 10661 | 10258 | 12090 | 33133 | 10470 | 10087 | 11126 | 31998 | 23258 | 19724 | 20863 | 63846 | 23258 | 19724 | 20863 | 63846 | - - - | - - - | - - - | - - -
5/3/2026 | 6:00:00 PM | 279.83 | 276.97 | 277.32 | 484.31 | 478.16 | 482.26 | 94.1466 | 82.6693 | 89.2805 | 2.2585 | 1.434 | 1.43 | 1.43 | 2.023 | 1.952 | 2.026 | Over-range | 60 | 23846 | 20256 | 21334 | 65437 | - - - | - - - | - - - | - - - | 23846 | 20256 | 21334 | 65437 | 2145 | 1899 | 4864 | 8909 | - - - | - - - | - - - | - - - | 2145 | 1899 | 4864 | 8909 | 26306 | 22870 | 24727 | 73903 | # # # | # # # | # # # | # # # | 0.907 | 0.886 | 0.863 | 0.885 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.975 | 0.989 | - - - | 0.136 | 1.53 | 1.49 | 1.51 | 1.47 | 1.46 | 1.5 | 46.26 | 51.9 | 53.28 | 0 | - - - | - - - | - - - | - - - | 26306 | 22870 | 24727 | 73903 | Over-range | 11100 | 10614 | 12494 | 34330 | 10890 | 10442 | 11508 | 33154 | 23759 | 20182 | 21256 | 65197 | 23759 | 20182 | 21256 | 65197 | - - - | - - - | - - - | - - -
5/3/2026 | 6:15:00 PM | 280.06 | 276.84 | 277.22 | 484.47 | 477.75 | 482.48 | 94.5336 | 81.5253 | 89.4217 | 2.2755 | 1.433 | 1.43 | 1.428 | 2.041 | 1.96 | 2.051 | Over-range | 60 | 23976 | 19925 | 21255 | 65155 | - - - | - - - | - - - | - - - | 23976 | 19925 | 21255 | 65155 | 1971 | 1778 | 5079 | 8827 | - - - | - - - | - - - | - - - | 1971 | 1778 | 5079 | 8827 | 26435 | 22540 | 24757 | 73733 | # # # | # # # | # # # | # # # | 0.907 | 0.884 | 0.859 | 0.884 | # # # | # # # | # # # | - - - | 0.997 | 0.996 | 0.972 | 0.988 | - - - | 0.136 | 1.5 | 1.49 | 1.49 | 1.45 | 1.46 | 1.47 | 46.27 | 52.44 | 53.88 | 0 | - - - | - - - | - - - | - - - | 26435 | 22540 | 24757 | 73733 | Over-range | 11126 | 10536 | 12689 | 34499 | 10950 | 10385 | 11628 | 33351 | 23885 | 19871 | 21169 | 64925 | 23885 | 19871 | 21169 | 64925 | - - - | - - - | - - - | - - -
5/3/2026 | 6:30:00 PM | 280.27 | 277.09 | 277.38 | 484.91 | 478.11 | 482.76 | 92.5997 | 80.1061 | 87.415 | 2.2595 | 1.433 | 1.43 | 1.428 | 2.028 | 1.949 | 2.04 | Over-range | 60 | 23550 | 19634 | 20837 | 64021 | - - - | - - - | - - - | - - - | 23550 | 19634 | 20837 | 64021 | 1942 | 1710 | 4924 | 8576 | - - - | - - - | - - - | - - - | 1942 | 1710 | 4924 | 8576 | 25896 | 22158 | 24202 | 72256 | # # # | # # # | # # # | # # # | 0.909 | 0.886 | 0.861 | 0.886 | # # # | # # # | # # # | - - - | 0.997 | 0.996 | 0.973 | 0.989 | - - - | 0.134 | 1.49 | 1.47 | 1.46 | 1.44 | 1.44 | 1.46 | 45.51 | 51.88 | 53.28 | 0 | - - - | - - - | - - - | - - - | 25896 | 22158 | 24202 | 72256 | Over-range | 10758 | 10265 | 12302 | 33476 | 10581 | 10122 | 11274 | 32358 | 23454 | 19576 | 20760 | 63789 | 23454 | 19576 | 20760 | 63789 | - - - | - - - | - - - | - - -
5/3/2026 | 6:45:00 PM | 280.14 | 276.97 | 277.3 | 484.67 | 477.96 | 482.6 | 94.5515 | 81.8741 | 89.3607 | 2.2385 | 1.433 | 1.43 | 1.429 | 2.035 | 1.962 | 2.048 | Over-range | 59.99 | 23975 | 20020 | 21256 | 65251 | - - - | - - - | - - - | - - - | 23975 | 20020 | 21256 | 65251 | 2042 | 1789 | 5030 | 8861 | - - - | - - - | - - - | - - - | 2042 | 1789 | 5030 | 8861 | 26448 | 22650 | 24749 | 73846 | # # # | # # # | # # # | # # # | 0.907 | 0.884 | 0.859 | 0.884 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.973 | 0.989 | - - - | 0.136 | 1.47 | 1.47 | 1.47 | 1.43 | 1.44 | 1.45 | 46.37 | 52.5 | 53.93 | 0 | - - - | - - - | - - - | - - - | 26448 | 22650 | 24749 | 73846 | Over-range | 11158 | 10591 | 12670 | 34563 | 10970 | 10438 | 11629 | 33408 | 23883 | 19953 | 21176 | 65011 | 23883 | 19953 | 21176 | 65011 | - - - | - - - | - - - | - - -
5/3/2026 | 7:00:00 PM | 280.58 | 277.45 | 277.67 | 485.52 | 478.69 | 483.26 | 94.3104 | 81.4037 | 88.6619 | 2.3093 | 1.433 | 1.43 | 1.428 | 2.038 | 1.974 | 2.061 | Over-range | 60 | 23956 | 19938 | 21072 | 64966 | - - - | - - - | - - - | - - - | 23956 | 19938 | 21072 | 64966 | 2062 | 1694 | 5069 | 8824 | - - - | - - - | - - - | - - - | 2062 | 1694 | 5069 | 8824 | 26424 | 22559 | 24588 | 73570 | # # # | # # # | # # # | # # # | 0.907 | 0.884 | 0.857 | 0.883 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.972 | 0.988 | - - - | 0.136 | 1.48 | 1.47 | 1.45 | 1.43 | 1.43 | 1.44 | 46.31 | 52.58 | 54.26 | 0 | - - - | - - - | - - - | - - - | 26424 | 22559 | 24588 | 73570 | Over-range | 11141 | 10550 | 12666 | 34510 | 10949 | 10413 | 11607 | 33363 | 23865 | 19883 | 20982 | 64730 | 23865 | 19883 | 20982 | 64730 | - - - | - - - | - - - | - - -
5/3/2026 | 7:15:00 PM | 280.52 | 277.51 | 277.61 | 485.55 | 478.72 | 483.07 | 92.2659 | 79.9964 | 86.4809 | 2.3229 | 1.433 | 1.43 | 1.428 | 2.022 | 1.961 | 2.046 | Over-range | 60 | 23476 | 19652 | 20606 | 63735 | - - - | - - - | - - - | - - - | 23476 | 19652 | 20606 | 63735 | 2053 | 1618 | 4882 | 8553 | - - - | - - - | - - - | - - - | 2053 | 1618 | 4882 | 8553 | 25822 | 22158 | 23963 | 71943 | # # # | # # # | # # # | # # # | 0.909 | 0.887 | 0.86 | 0.886 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.134 | 1.46 | 1.45 | 1.44 | 1.42 | 1.41 | 1.43 | 45.46 | 51.73 | 53.54 | 0 | - - - | - - - | - - - | - - - | 25822 | 22158 | 23963 | 71943 | Over-range | 10743 | 10232 | 12223 | 33352 | 10545 | 10103 | 11206 | 32236 | 23394 | 19587 | 20529 | 63510 | 23394 | 19587 | 20529 | 63510 | - - - | - - - | - - - | - - -
5/3/2026 | 7:30:00 PM | 280.6 | 277.58 | 277.67 | 485.69 | 478.83 | 483.2 | 93.8535 | 81.2882 | 87.7113 | 2.2975 | 1.433 | 1.43 | 1.429 | 2.029 | 1.981 | 2.061 | Over-range | 59.99 | 23833 | 19942 | 20848 | 64622 | - - - | - - - | - - - | - - - | 23833 | 19942 | 20848 | 64622 | 2160 | 1626 | 4982 | 8768 | - - - | - - - | - - - | - - - | 2160 | 1626 | 4982 | 8768 | 26297 | 22536 | 24325 | 73158 | # # # | # # # | # # # | # # # | 0.906 | 0.885 | 0.857 | 0.883 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.972 | 0.988 | - - - | 0.136 | 1.48 | 1.47 | 1.46 | 1.43 | 1.44 | 1.45 | 46.29 | 52.33 | 54.3 | 0 | - - - | - - - | - - - | - - - | 26297 | 22536 | 24325 | 73158 | Over-range | 11108 | 10495 | 12530 | 34282 | 10895 | 10368 | 11497 | 33142 | 23741 | 19889 | 20768 | 64397 | 23741 | 19889 | 20768 | 64397 | - - - | - - - | - - - | - - -
5/3/2026 | 7:45:00 PM | 280.99 | 278.08 | 278.14 | 486.45 | 479.72 | 483.9 | 92.6109 | 80.7235 | 86.559 | 2.3264 | 1.433 | 1.43 | 1.429 | 2.023 | 1.977 | 2.053 | Over-range | 60 | 23544 | 19834 | 20633 | 64011 | - - - | - - - | - - - | - - - | 23544 | 19834 | 20633 | 64011 | 2186 | 1658 | 4865 | 8709 | - - - | - - - | - - - | - - - | 2186 | 1658 | 4865 | 8709 | 25971 | 22409 | 24036 | 72417 | # # # | # # # | # # # | # # # | 0.907 | 0.885 | 0.858 | 0.884 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.973 | 0.988 | - - - | 0.136 | 1.46 | 1.47 | 1.44 | 1.42 | 1.42 | 1.42 | 46.15 | 52.25 | 54.11 | 0 | - - - | - - - | - - - | - - - | 25971 | 22409 | 24036 | 72417 | Over-range | 10955 | 10427 | 12324 | 33849 | 10735 | 10294 | 11323 | 32710 | 23465 | 19773 | 20539 | 63778 | 23465 | 19773 | 20539 | 63778 | - - - | - - - | - - - | - - -
5/3/2026 | 8:00:00 PM | 281.08 | 278.2 | 278.31 | 486.59 | 479.99 | 484.13 | 92.1842 | 80.3827 | 86.2573 | 2.3572 | 1.433 | 1.43 | 1.428 | 2.024 | 1.975 | 2.051 | Over-range | 60.01 | 23433 | 19754 | 20580 | 63767 | - - - | - - - | - - - | - - - | 23433 | 19754 | 20580 | 63767 | 2147 | 1674 | 4842 | 8663 | - - - | - - - | - - - | - - - | 2147 | 1674 | 4842 | 8663 | 25855 | 22321 | 23965 | 72141 | # # # | # # # | # # # | # # # | 0.906 | 0.885 | 0.859 | 0.884 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.973 | 0.989 | - - - | 0.136 | 1.49 | 1.46 | 1.44 | 1.43 | 1.43 | 1.44 | 46.22 | 52.22 | 53.95 | 0 | - - - | - - - | - - - | - - - | 25855 | 22321 | 23965 | 72141 | Over-range | 10915 | 10390 | 12273 | 33717 | 10702 | 10253 | 11277 | 32585 | 23341 | 19700 | 20500 | 63541 | 23341 | 19700 | 20500 | 63541 | - - - | - - - | - - - | - - -
5/3/2026 | 8:15:00 PM | 281.34 | 278.46 | 278.39 | 487.14 | 480.24 | 484.38 | 93.2616 | 80.9038 | 86.3275 | 2.3893 | 1.433 | 1.43 | 1.428 | 2.025 | 2.002 | 2.077 | Over-range | 59.99 | 23706 | 19892 | 20507 | 64106 | - - - | - - - | - - - | - - - | 23706 | 19892 | 20507 | 64106 | 2285 | 1522 | 4946 | 8753 | - - - | - - - | - - - | - - - | 2285 | 1522 | 4946 | 8753 | 26197 | 22497 | 24003 | 72697 | # # # | # # # | # # # | # # # | 0.905 | 0.884 | 0.854 | 0.882 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.137 | 1.47 | 1.47 | 1.43 | 1.43 | 1.42 | 1.43 | 46.55 | 52.62 | 54.91 | 0 | - - - | - - - | - - - | - - - | 26197 | 22497 | 24003 | 72697 | Over-range | 11139 | 10505 | 12468 | 34266 | 10902 | 10394 | 11445 | 33129 | 23614 | 19830 | 20433 | 63876 | 23614 | 19830 | 20433 | 63876 | - - - | - - - | - - - | - - -
5/3/2026 | 8:30:00 PM | 281.42 | 278.45 | 278.43 | 487.19 | 480.23 | 484.52 | 91.6314 | 79.3237 | 85.1202 | 2.3153 | 1.433 | 1.429 | 1.427 | 2.028 | 1.992 | 2.071 | Over-range | 59.99 | 23323 | 19494 | 20239 | 63056 | - - - | - - - | - - - | - - - | 23323 | 19494 | 20239 | 63056 | 2164 | 1514 | 4883 | 8561 | - - - | - - - | - - - | - - - | 2164 | 1514 | 4883 | 8561 | 25731 | 22047 | 23661 | 71439 | # # # | # # # | # # # | # # # | 0.906 | 0.884 | 0.855 | 0.883 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.972 | 0.988 | - - - | 0.136 | 1.46 | 1.46 | 1.43 | 1.42 | 1.41 | 1.42 | 46.19 | 52.58 | 54.62 | 0 | - - - | - - - | - - - | - - - | 25731 | 22047 | 23661 | 71439 | Over-range | 10858 | 10295 | 12248 | 33557 | 10640 | 10182 | 11232 | 32446 | 23239 | 19428 | 20152 | 62820 | 23239 | 19428 | 20152 | 62820 | - - - | - - - | - - - | - - -
5/3/2026 | 8:45:00 PM | 281.13 | 278.06 | 278 | 486.67 | 479.46 | 483.92 | 93.3836 | 80.1695 | 86.1437 | 2.2864 | 1.432 | 1.43 | 1.427 | 2.035 | 2.017 | 2.096 | Over-range | 59.99 | 23710 | 19648 | 20353 | 63712 | - - - | - - - | - - - | - - - | 23710 | 19648 | 20353 | 63712 | 2245 | 1408 | 5045 | 8698 | - - - | - - - | - - - | - - - | 2245 | 1408 | 5045 | 8698 | 26215 | 22264 | 23920 | 72399 | # # # | # # # | # # # | # # # | 0.904 | 0.882 | 0.851 | 0.88 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.988 | - - - | 0.137 | 1.46 | 1.46 | 1.45 | 1.42 | 1.43 | 1.43 | 46.77 | 53.21 | 55.52 | 0 | - - - | - - - | - - - | - - - | 26215 | 22264 | 23920 | 72399 | Over-range | 11176 | 10469 | 12561 | 34373 | 10948 | 10373 | 11503 | 33255 | 23625 | 19578 | 20274 | 63477 | 23625 | 19578 | 20274 | 63477 | - - - | - - - | - - - | - - -
5/3/2026 | 9:00:00 PM | 281.41 | 278.47 | 278.29 | 487.29 | 480.09 | 484.33 | 89.8685 | 77.4917 | 82.7801 | 2.1804 | 1.432 | 1.429 | 1.427 | 2.023 | 2.001 | 2.082 | Over-range | 60.01 | 22913 | 19066 | 19645 | 61624 | - - - | - - - | - - - | - - - | 22913 | 19066 | 19645 | 61624 | 2167 | 1298 | 4789 | 8255 | - - - | - - - | - - - | - - - | 2167 | 1298 | 4789 | 8255 | 25230 | 21534 | 22991 | 69755 | # # # | # # # | # # # | # # # | 0.908 | 0.885 | 0.855 | 0.883 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.971 | 0.988 | - - - | 0.134 | 1.46 | 1.44 | 1.43 | 1.42 | 1.4 | 1.42 | 45.67 | 52.41 | 54.75 | 0 | - - - | - - - | - - - | - - - | 25230 | 21534 | 22991 | 69755 | Over-range | 10549 | 10006 | 11938 | 32663 | 10324 | 9921 | 10935 | 31603 | 22817 | 19013 | 19561 | 61391 | 22817 | 19013 | 19561 | 61391 | - - - | - - - | - - - | - - -
5/3/2026 | 9:15:00 PM | 281.41 | 278.56 | 278.45 | 487.3 | 480.38 | 484.47 | 91.8118 | 79.426 | 84.6892 | 2.2013 | 1.433 | 1.43 | 1.428 | 2.031 | 2.017 | 2.089 | Over-range | 60.01 | 23318 | 19505 | 20071 | 62894 | - - - | - - - | - - - | - - - | 23318 | 19505 | 20071 | 62894 | 2288 | 1405 | 4877 | 8570 | - - - | - - - | - - - | - - - | 2288 | 1405 | 4877 | 8570 | 25790 | 22091 | 23545 | 71426 | # # # | # # # | # # # | # # # | 0.904 | 0.883 | 0.852 | 0.88 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.136 | 1.49 | 1.47 | 1.45 | 1.44 | 1.43 | 1.45 | 46.8 | 53.07 | 55.42 | 0 | - - - | - - - | - - - | - - - | 25790 | 22091 | 23545 | 71426 | Over-range | 11009 | 10370 | 12305 | 33839 | 10768 | 10274 | 11297 | 32735 | 23216 | 19455 | 19981 | 62652 | 23216 | 19455 | 19981 | 62652 | - - - | - - - | - - - | - - -
5/3/2026 | 9:30:00 PM | 281.89 | 279.01 | 278.85 | 488.15 | 481.08 | 485.23 | 89.9899 | 77.68 | 82.7832 | 2.1792 | 1.433 | 1.43 | 1.428 | 2.026 | 2.008 | 2.087 | Over-range | 60.02 | 22947 | 19126 | 19660 | 61734 | - - - | - - - | - - - | - - - | 22947 | 19126 | 19660 | 61734 | 2224 | 1307 | 4807 | 8338 | - - - | - - - | - - - | - - - | 2224 | 1307 | 4807 | 8338 | 25307 | 21627 | 23040 | 69973 | # # # | # # # | # # # | # # # | 0.907 | 0.884 | 0.853 | 0.882 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.971 | 0.988 | - - - | 0.135 | 1.5 | 1.48 | 1.46 | 1.45 | 1.43 | 1.46 | 46.03 | 52.7 | 55.05 | 0 | - - - | - - - | - - - | - - - | 25307 | 21627 | 23040 | 69973 | Over-range | 10658 | 10091 | 12007 | 32923 | 10423 | 10006 | 11002 | 31850 | 22839 | 19074 | 19587 | 61499 | 22839 | 19074 | 19587 | 61499 | - - - | - - - | - - - | - - -
5/3/2026 | 9:45:00 PM | 282.4 | 279.4 | 279.26 | 488.96 | 481.72 | 486.06 | 91.4004 | 78.2196 | 84.0367 | 2.2088 | 1.433 | 1.43 | 1.427 | 2.046 | 2.029 | 2.112 | Over-range | 60.02 | 23288 | 19209 | 19866 | 62363 | - - - | - - - | - - - | - - - | 23288 | 19209 | 19866 | 62363 | 2227 | 1312 | 5009 | 8548 | - - - | - - - | - - - | - - - | 2227 | 1312 | 5009 | 8548 | 25764 | 21819 | 23435 | 71018 | # # # | # # # | # # # | # # # | 0.904 | 0.88 | 0.848 | 0.878 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.969 | 0.988 | - - - | 0.137 | 1.48 | 1.47 | 1.45 | 1.44 | 1.43 | 1.44 | 46.92 | 53.88 | 56.24 | 0 | - - - | - - - | - - - | - - - | 25764 | 21819 | 23435 | 71018 | Over-range | 11009 | 10344 | 12424 | 33956 | 10781 | 10260 | 11370 | 32862 | 23200 | 19136 | 19775 | 62110 | 23200 | 19136 | 19775 | 62110 | - - - | - - - | - - - | - - -
5/3/2026 | 10:00:00 PM | 282.63 | 279.63 | 279.47 | 489.36 | 482.11 | 486.43 | 89.8159 | 76.7228 | 82.3205 | 2.1746 | 1.432 | 1.43 | 1.427 | 2.047 | 2.035 | 2.119 | Over-range | 60.02 | 22897 | 18836 | 19430 | 61163 | - - - | - - - | - - - | - - - | 22897 | 18836 | 19430 | 61163 | 2218 | 1222 | 4956 | 8395 | - - - | - - - | - - - | - - - | 2218 | 1222 | 4956 | 8395 | 25330 | 21415 | 22966 | 69711 | # # # | # # # | # # # | # # # | 0.904 | 0.88 | 0.846 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.969 | 0.987 | - - - | 0.137 | 1.5 | 1.48 | 1.47 | 1.45 | 1.44 | 1.46 | 46.89 | 54.14 | 56.52 | 0 | - - - | - - - | - - - | - - - | 25330 | 21415 | 22966 | 69711 | Over-range | 10822 | 10184 | 12238 | 33429 | 10592 | 10111 | 11190 | 32358 | 22803 | 18766 | 19352 | 60920 | 22803 | 18766 | 19352 | 60920 | - - - | - - - | - - - | - - -
5/3/2026 | 10:15:00 PM | 283.08 | 279.88 | 279.77 | 490.01 | 482.47 | 487.16 | 87.8653 | 74.2692 | 80.6777 | 2.0936 | 1.433 | 1.43 | 1.427 | 2.054 | 2.019 | 2.119 | Over-range | 60 | 22508 | 18267 | 19064 | 59840 | - - - | - - - | - - - | - - - | 22508 | 18267 | 19064 | 59840 | 2009 | 1150 | 4953 | 8112 | - - - | - - - | - - - | - - - | 2009 | 1150 | 4953 | 8112 | 24803 | 20738 | 22523 | 68064 | # # # | # # # | # # # | # # # | 0.908 | 0.881 | 0.846 | 0.879 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.968 | 0.987 | - - - | 0.136 | 1.55 | 1.52 | 1.5 | 1.49 | 1.48 | 1.5 | 46.03 | 53.73 | 56.16 | 0 | - - - | - - - | - - - | - - - | 24803 | 20738 | 22523 | 68064 | Over-range | 10408 | 9814 | 11986 | 32414 | 10211 | 9745 | 10915 | 31382 | 22401 | 18229 | 18967 | 59597 | 22401 | 18229 | 18967 | 59597 | - - - | - - - | - - - | - - -
5/3/2026 | 10:30:00 PM | 283.37 | 280.2 | 280.05 | 490.55 | 483 | 487.62 | 90.3427 | 76.3303 | 82.4181 | 2.1492 | 1.433 | 1.431 | 1.427 | 2.06 | 2.052 | 2.144 | Over-range | 60.02 | 23068 | 18739 | 19369 | 61175 | - - - | - - - | - - - | - - - | 23068 | 18739 | 19369 | 61175 | 2234 | 1131 | 5130 | 8495 | - - - | - - - | - - - | - - - | 2234 | 1131 | 5130 | 8495 | 25552 | 21355 | 23046 | 69953 | # # # | # # # | # # # | # # # | 0.903 | 0.877 | 0.84 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.966 | 0.987 | - - - | 0.139 | 1.55 | 1.52 | 1.52 | 1.49 | 1.5 | 1.52 | 47.28 | 54.76 | 57.53 | 0 | - - - | - - - | - - - | - - - | 25552 | 21355 | 23046 | 69953 | Over-range | 10981 | 10237 | 12482 | 33908 | 10751 | 10174 | 11379 | 32826 | 22959 | 18683 | 19284 | 60926 | 22959 | 18683 | 19284 | 60926 | - - - | - - - | - - - | - - -
5/3/2026 | 10:45:00 PM | 283.67 | 280.55 | 280.34 | 491.13 | 483.55 | 488.1 | 86.5021 | 73.4521 | 78.883 | 2.1471 | 1.432 | 1.429 | 1.426 | 2.052 | 2.032 | 2.131 | Over-range | 60.02 | 22173 | 18097 | 18605 | 58875 | - - - | - - - | - - - | - - - | 22173 | 18097 | 18605 | 58875 | 2139 | 1063 | 4853 | 8055 | - - - | - - - | - - - | - - - | 2139 | 1063 | 4853 | 8055 | 24471 | 20558 | 22064 | 67093 | # # # | # # # | # # # | # # # | 0.906 | 0.88 | 0.843 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.967 | 0.987 | - - - | 0.137 | 1.53 | 1.51 | 1.49 | 1.47 | 1.47 | 1.49 | 46.26 | 53.98 | 56.97 | 0 | - - - | - - - | - - - | - - - | 24471 | 20558 | 22064 | 67093 | Over-range | 10340 | 9750 | 11852 | 32152 | 10116 | 9691 | 10814 | 31127 | 22080 | 18039 | 18514 | 58633 | 22080 | 18039 | 18514 | 58633 | - - - | - - - | - - - | - - -
5/3/2026 | 11:00:00 PM | 283.98 | 280.69 | 280.5 | 491.57 | 483.72 | 488.56 | 89.0854 | 74.9201 | 80.9586 | 2.1189 | 1.433 | 1.43 | 1.426 | 2.065 | 2.055 | 2.16 | Over-range | 60.02 | 22797 | 18423 | 18966 | 60186 | - - - | - - - | - - - | - - - | 22797 | 18423 | 18966 | 60186 | 2244 | 1011 | 5104 | 8360 | - - - | - - - | - - - | - - - | 2244 | 1011 | 5104 | 8360 | 25242 | 20990 | 22663 | 68894 | # # # | # # # | # # # | # # # | 0.903 | 0.878 | 0.837 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.965 | 0.987 | - - - | 0.139 | 1.53 | 1.52 | 1.5 | 1.47 | 1.48 | 1.5 | 47.14 | 54.78 | 58.31 | 0 | - - - | - - - | - - - | - - - | 25242 | 20990 | 22663 | 68894 | Over-range | 10827 | 10055 | 12401 | 33512 | 10591 | 10004 | 11301 | 32452 | 22678 | 18363 | 18892 | 59933 | 22678 | 18363 | 18892 | 59933 | - - - | - - - | - - - | - - -
5/3/2026 | 11:15:00 PM | 283.78 | 280.49 | 280.33 | 491.2 | 483.41 | 488.25 | 87.0611 | 73.3589 | 79.1426 | 2.0923 | 1.433 | 1.43 | 1.426 | 2.059 | 2.042 | 2.148 | Over-range | 59.99 | 22307 | 18056 | 18583 | 58946 | - - - | - - - | - - - | - - - | 22307 | 18056 | 18583 | 58946 | 2163 | 983 | 4943 | 8090 | - - - | - - - | - - - | - - - | 2163 | 983 | 4943 | 8090 | 24637 | 20529 | 22134 | 67300 | # # # | # # # | # # # | # # # | 0.905 | 0.88 | 0.84 | 0.876 | # # # | # # # | # # # | - - - | 0.995 | 0.999 | 0.966 | 0.987 | - - - | 0.137 | 1.58 | 1.54 | 1.54 | 1.5 | 1.52 | 1.55 | 46.43 | 54.27 | 57.66 | 0 | - - - | - - - | - - - | - - - | 24637 | 20529 | 22134 | 67300 | Over-range | 10444 | 9763 | 12019 | 32453 | 10218 | 9713 | 10955 | 31428 | 22214 | 17982 | 18510 | 58705 | 22214 | 17982 | 18510 | 58705 | - - - | - - - | - - - | - - -
5/3/2026 | 11:30:00 PM | 283.92 | 280.7 | 280.63 | 491.43 | 483.93 | 488.64 | 87.3172 | 73.8882 | 79.6561 | 2.0842 | 1.433 | 1.429 | 1.426 | 2.063 | 2.047 | 2.145 | Over-range | 60.02 | 22345 | 18173 | 18738 | 59256 | - - - | - - - | - - - | - - - | 22345 | 18173 | 18738 | 59256 | 2181 | 1070 | 4945 | 8195 | - - - | - - - | - - - | - - - | 2181 | 1070 | 4945 | 8195 | 24733 | 20701 | 22309 | 67743 | # # # | # # # | # # # | # # # | 0.904 | 0.878 | 0.84 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.967 | 0.987 | - - - | 0.138 | 1.56 | 1.53 | 1.56 | 1.5 | 1.52 | 1.54 | 47.03 | 54.63 | 57.75 | 0 | - - - | - - - | - - - | - - - | 24733 | 20701 | 22309 | 67743 | Over-range | 10592 | 9910 | 12102 | 32813 | 10365 | 9852 | 11045 | 31773 | 22242 | 18124 | 18647 | 59013 | 22242 | 18124 | 18647 | 59013 | - - - | - - - | - - - | - - -
5/3/2026 | 11:45:00 PM | 284.5 | 281.3 | 281.19 | 492.48 | 484.92 | 489.6 | 87.264 | 73.7852 | 79.2507 | 2.0927 | 1.433 | 1.43 | 1.427 | 2.065 | 2.057 | 2.156 | Over-range | 60.02 | 22340 | 18170 | 18605 | 59116 | - - - | - - - | - - - | - - - | 22340 | 18170 | 18605 | 59116 | 2277 | 1015 | 4961 | 8253 | - - - | - - - | - - - | - - - | 2277 | 1015 | 4961 | 8253 | 24763 | 20713 | 22237 | 67713 | # # # | # # # | # # # | # # # | 0.902 | 0.877 | 0.837 | 0.873 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.966 | 0.987 | - - - | 0.14 | 1.58 | 1.54 | 1.54 | 1.5 | 1.51 | 1.54 | 47.33 | 54.91 | 58.47 | 0 | - - - | - - - | - - - | - - - | 24763 | 20713 | 22237 | 67713 | Over-range | 10673 | 9940 | 12173 | 33003 | 10427 | 9888 | 11116 | 31954 | 22235 | 18100 | 18532 | 58867 | 22235 | 18100 | 18532 | 58867 | - - - | - - - | - - - | - - -
5/4/2026 | 12:00:00 AM | 284.76 | 281.51 | 281.52 | 492.83 | 485.4 | 490.17 | 84.3256 | 71.4861 | 76.9257 | 2.1013 | 1.432 | 1.428 | 1.425 | 2.071 | 2.045 | 2.149 | Over-range | 60.02 | 21621 | 17628 | 18113 | 57362 | - - - | - - - | - - - | - - - | 21621 | 17628 | 18113 | 57362 | 2139 | 1034 | 4773 | 7946 | - - - | - - - | - - - | - - - | 2139 | 1034 | 4773 | 7946 | 23942 | 20074 | 21603 | 65619 | # # # | # # # | # # # | # # # | 0.903 | 0.878 | 0.838 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.967 | 0.987 | - - - | 0.139 | 1.57 | 1.53 | 1.54 | 1.5 | 1.52 | 1.54 | 47.08 | 54.55 | 58.08 | 0 | - - - | - - - | - - - | - - - | 23942 | 20074 | 21603 | 65619 | Over-range | 10272 | 9598 | 11767 | 31846 | 10047 | 9542 | 10756 | 30839 | 21515 | 17569 | 18047 | 57131 | 21515 | 17569 | 18047 | 57131 | - - - | - - - | - - - | - - -
5/4/2026 | 12:15:00 AM | 284.84 | 281.51 | 281.45 | 492.95 | 485.27 | 490.18 | 84.2262 | 71.1044 | 76.4532 | 2.0261 | 1.432 | 1.429 | 1.425 | 2.073 | 2.054 | 2.164 | Over-range | 59.99 | 21600 | 17539 | 17935 | 57074 | - - - | - - - | - - - | - - - | 21600 | 17539 | 17935 | 57074 | 2193 | 937 | 4785 | 7915 | - - - | - - - | - - - | - - - | 2193 | 937 | 4785 | 7915 | 23921 | 19967 | 21464 | 65352 | # # # | # # # | # # # | # # # | 0.903 | 0.878 | 0.836 | 0.873 | # # # | # # # | # # # | - - - | 0.995 | 0.999 | 0.966 | 0.987 | - - - | 0.139 | 1.58 | 1.55 | 1.55 | 1.51 | 1.53 | 1.55 | 47.08 | 54.58 | 58.74 | 0 | - - - | - - - | - - - | - - - | 23921 | 19967 | 21464 | 65352 | Over-range | 10267 | 9539 | 11784 | 31814 | 10030 | 9493 | 10769 | 30813 | 21497 | 17480 | 17859 | 56835 | 21497 | 17480 | 17859 | 56835 | - - - | - - - | - - - | - - -
5/4/2026 | 12:30:00 AM | 284.89 | 281.53 | 281.47 | 493.03 | 485.28 | 490.25 | 81.0684 | 68.4757 | 73.2882 | 2.0087 | 1.432 | 1.428 | 1.425 | 2.074 | 2.053 | 2.17 | Over-range | 60.01 | 20811 | 16919 | 17181 | 54911 | - - - | - - - | - - - | - - - | 20811 | 16919 | 17181 | 54911 | 2138 | 827 | 4560 | 7525 | - - - | - - - | - - - | - - - | 2138 | 827 | 4560 | 7525 | 23013 | 19220 | 20564 | 62797 | # # # | # # # | # # # | # # # | 0.904 | 0.88 | 0.836 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.999 | 0.966 | 0.987 | - - - | 0.137 | 1.57 | 1.53 | 1.55 | 1.5 | 1.53 | 1.54 | 46.6 | 54.1 | 58.81 | 0 | - - - | - - - | - - - | - - - | 23013 | 19220 | 20564 | 62797 | Over-range | 9811 | 9113 | 11293 | 30444 | 9575 | 9075 | 10331 | 29499 | 20736 | 16848 | 17099 | 54682 | 20736 | 16848 | 17099 | 54682 | - - - | - - - | - - - | - - -
5/4/2026 | 12:45:00 AM | 285.11 | 281.88 | 281.75 | 493.52 | 485.88 | 490.62 | 79.2782 | 67.2774 | 71.4188 | 1.9734 | 1.432 | 1.429 | 1.425 | 2.065 | 2.053 | 2.167 | Over-range | 60 | 20397 | 16676 | 16790 | 53863 | - - - | - - - | - - - | - - - | 20397 | 16676 | 16790 | 53863 | 2148 | 758 | 4411 | 7316 | - - - | - - - | - - - | - - - | 2148 | 758 | 4411 | 7316 | 22527 | 18911 | 20061 | 61499 | # # # | # # # | # # # | # # # | 0.906 | 0.882 | 0.837 | 0.876 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.967 | 0.987 | - - - | 0.136 | 1.57 | 1.56 | 1.57 | 1.52 | 1.54 | 1.56 | 46.2 | 53.66 | 58.61 | 0 | - - - | - - - | - - - | - - - | 22527 | 18911 | 20061 | 61499 | Over-range | 9549 | 8913 | 10974 | 29659 | 9304 | 8881 | 10048 | 28743 | 20309 | 16626 | 16709 | 53644 | 20309 | 16626 | 16709 | 53644 | - - - | - - - | - - - | - - -
5/4/2026 | 1:00:00 AM | 285.21 | 281.89 | 281.78 | 493.63 | 485.88 | 490.77 | 78.9951 | 67.0131 | 70.9676 | 1.9651 | 1.432 | 1.428 | 1.424 | 2.074 | 2.064 | 2.181 | Over-range | 60.01 | 20283 | 16588 | 16611 | 53481 | - - - | - - - | - - - | - - - | 20283 | 16588 | 16611 | 53481 | 2206 | 730 | 4403 | 7340 | - - - | - - - | - - - | - - - | 2206 | 730 | 4403 | 7340 | 22456 | 18837 | 19941 | 61234 | # # # | # # # | # # # | # # # | 0.903 | 0.881 | 0.833 | 0.873 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.966 | 0.987 | - - - | 0.137 | 1.57 | 1.54 | 1.55 | 1.51 | 1.53 | 1.54 | 46.83 | 53.99 | 59.61 | 0 | - - - | - - - | - - - | - - - | 22456 | 18837 | 19941 | 61234 | Over-range | 9625 | 8922 | 11028 | 29803 | 9369 | 8892 | 10111 | 28885 | 20178 | 16559 | 16519 | 53256 | 20178 | 16559 | 16519 | 53256 | - - - | - - - | - - - | - - -
5/4/2026 | 1:15:00 AM | 285.12 | 281.67 | 281.68 | 493.33 | 485.56 | 490.68 | 79.6084 | 67.1306 | 71.8702 | 1.9567 | 1.432 | 1.429 | 1.425 | 2.084 | 2.062 | 2.184 | Over-range | 60 | 20422 | 16593 | 16793 | 53807 | - - - | - - - | - - - | - - - | 20422 | 16593 | 16793 | 53807 | 2139 | 783 | 4487 | 7409 | - - - | - - - | - - - | - - - | 2139 | 783 | 4487 | 7409 | 22618 | 18855 | 20178 | 61650 | # # # | # # # | # # # | # # # | 0.903 | 0.88 | 0.832 | 0.873 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.966 | 0.987 | - - - | 0.138 | 1.59 | 1.58 | 1.57 | 1.54 | 1.56 | 1.57 | 46.99 | 54.16 | 59.72 | 0 | - - - | - - - | - - - | - - - | 22618 | 18855 | 20178 | 61650 | Over-range | 9710 | 8949 | 11180 | 30070 | 9471 | 8915 | 10240 | 29143 | 20330 | 16554 | 16690 | 53574 | 20330 | 16554 | 16690 | 53574 | - - - | - - - | - - - | - - -
5/4/2026 | 1:30:00 AM | 284.89 | 281.42 | 281.46 | 492.91 | 485.15 | 490.29 | 79.3523 | 66.9322 | 71.5776 | 1.9436 | 1.432 | 1.428 | 1.425 | 2.084 | 2.064 | 2.184 | Over-range | 60 | 20332 | 16529 | 16712 | 53572 | - - - | - - - | - - - | - - - | 20332 | 16529 | 16712 | 53572 | 2150 | 764 | 4465 | 7379 | - - - | - - - | - - - | - - - | 2150 | 764 | 4465 | 7379 | 22523 | 18780 | 20080 | 61383 | # # # | # # # | # # # | # # # | 0.903 | 0.88 | 0.832 | 0.873 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.966 | 0.987 | - - - | 0.138 | 1.57 | 1.57 | 1.57 | 1.52 | 1.55 | 1.56 | 47.04 | 54.15 | 59.63 | 0 | - - - | - - - | - - - | - - - | 22523 | 18780 | 20080 | 61383 | Over-range | 9679 | 8909 | 11126 | 29942 | 9437 | 8876 | 10190 | 29019 | 20223 | 16478 | 16640 | 53341 | 20223 | 16478 | 16640 | 53341 | - - - | - - - | - - - | - - -
5/4/2026 | 1:45:00 AM | 285.1 | 281.7 | 281.81 | 493.28 | 485.75 | 490.78 | 77.8264 | 65.9114 | 70.189 | 1.9241 | 1.432 | 1.429 | 1.425 | 2.083 | 2.065 | 2.182 | Over-range | 60.01 | 19939 | 16298 | 16417 | 52653 | - - - | - - - | - - - | - - - | 19939 | 16298 | 16417 | 52653 | 2148 | 774 | 4337 | 7258 | - - - | - - - | - - - | - - - | 2148 | 774 | 4337 | 7258 | 22109 | 18513 | 19716 | 60339 | # # # | # # # | # # # | # # # | 0.902 | 0.88 | 0.833 | 0.873 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.966 | 0.987 | - - - | 0.138 | 1.58 | 1.59 | 1.61 | 1.54 | 1.57 | 1.58 | 47.17 | 54.04 | 59.72 | 0 | - - - | - - - | - - - | - - - | 22109 | 18513 | 19716 | 60339 | Over-range | 9540 | 8775 | 10912 | 29445 | 9295 | 8741 | 10014 | 28536 | 19852 | 16245 | 16336 | 52432 | 19852 | 16245 | 16336 | 52432 | - - - | - - - | - - - | - - -
5/4/2026 | 2:00:00 AM | 285.45 | 282.03 | 282.06 | 493.91 | 486.23 | 491.28 | 77.4541 | 65.5144 | 69.2962 | 1.9226 | 1.432 | 1.428 | 1.425 | 2.084 | 2.083 | 2.201 | Over-range | 60.01 | 19838 | 16215 | 16148 | 52202 | - - - | - - - | - - - | - - - | 19838 | 16215 | 16148 | 52202 | 2241 | 683 | 4309 | 7233 | - - - | - - - | - - - | - - - | 2241 | 683 | 4309 | 7233 | 22028 | 18421 | 19483 | 59932 | # # # | # # # | # # # | # # # | 0.901 | 0.88 | 0.829 | 0.871 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.966 | 0.987 | - - - | 0.139 | 1.58 | 1.58 | 1.58 | 1.53 | 1.56 | 1.57 | 47.4 | 54.17 | 60.62 | 0 | - - - | - - - | - - - | - - - | 22028 | 18421 | 19483 | 59932 | Over-range | 9562 | 8734 | 10895 | 29419 | 9296 | 8708 | 10006 | 28516 | 19772 | 16156 | 16047 | 51975 | 19772 | 16156 | 16047 | 51975 | - - - | - - - | - - - | - - -
5/4/2026 | 2:15:00 AM | 285.31 | 281.84 | 282.02 | 493.56 | 486.03 | 491.19 | 74.9625 | 63.5378 | 67.8193 | 1.9138 | 1.431 | 1.427 | 1.424 | 2.087 | 2.049 | 2.176 | Over-range | 60.01 | 19275 | 15766 | 15923 | 50964 | - - - | - - - | - - - | - - - | 19275 | 15766 | 15923 | 50964 | 2013 | 762 | 4177 | 6953 | - - - | - - - | - - - | - - - | 2013 | 762 | 4177 | 6953 | 21319 | 17859 | 19077 | 58256 | # # # | # # # | # # # | # # # | 0.904 | 0.883 | 0.835 | 0.875 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.967 | 0.987 | - - - | 0.136 | 1.58 | 1.58 | 1.58 | 1.53 | 1.56 | 1.56 | 46.71 | 53.34 | 59.29 | 0 | - - - | - - - | - - - | - - - | 21319 | 17859 | 19077 | 58256 | Over-range | 9096 | 8386 | 10500 | 28199 | 8870 | 8351 | 9634 | 27328 | 19163 | 15738 | 15845 | 50745 | 19163 | 15738 | 15845 | 50745 | - - - | - - - | - - - | - - -
5/4/2026 | 2:30:00 AM | 285.31 | 281.95 | 282.09 | 493.64 | 486.25 | 491.2 | 72.0056 | 61.5565 | 64.9449 | 1.8746 | 1.431 | 1.427 | 1.424 | 2.076 | 2.041 | 2.169 | Over-range | 60.01 | 18558 | 15342 | 15286 | 49185 | - - - | - - - | - - - | - - - | 18558 | 15342 | 15286 | 49185 | 2032 | 694 | 3927 | 6653 | - - - | - - - | - - - | - - - | 2032 | 694 | 3927 | 6653 | 20496 | 17325 | 18281 | 56102 | # # # | # # # | # # # | # # # | 0.905 | 0.885 | 0.836 | 0.877 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.968 | 0.987 | - - - | 0.135 | 1.61 | 1.56 | 1.59 | 1.53 | 1.57 | 1.57 | 46.34 | 52.64 | 59.24 | 0 | - - - | - - - | - - - | - - - | 20496 | 17325 | 18281 | 56102 | Over-range | 8695 | 8045 | 10024 | 26975 | 8454 | 8015 | 9223 | 26142 | 18437 | 15326 | 15217 | 48980 | 18437 | 15326 | 15217 | 48980 | - - - | - - - | - - - | - - -
5/4/2026 | 2:45:00 AM | 285.58 | 282.16 | 282.31 | 494.07 | 486.58 | 491.64 | 75.5082 | 64.0357 | 67.6932 | 1.8958 | 1.432 | 1.428 | 1.425 | 2.092 | 2.08 | 2.204 | Over-range | 60 | 19296 | 15853 | 15743 | 50892 | - - - | - - - | - - - | - - - | 19296 | 15853 | 15743 | 50892 | 2231 | 692 | 4167 | 7090 | - - - | - - - | - - - | - - - | 2231 | 692 | 4167 | 7090 | 21475 | 18007 | 19041 | 58523 | # # # | # # # | # # # | # # # | 0.899 | 0.88 | 0.827 | 0.87 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.966 | 0.987 | - - - | 0.139 | 1.6 | 1.58 | 1.58 | 1.54 | 1.57 | 1.57 | 47.94 | 54.14 | 61.25 | 0 | - - - | - - - | - - - | - - - | 21475 | 18007 | 19041 | 58523 | Over-range | 9411 | 8534 | 10702 | 28869 | 9143 | 8506 | 9857 | 27985 | 19216 | 15788 | 15660 | 50664 | 19216 | 15788 | 15660 | 50664 | - - - | - - - | - - - | - - -
5/4/2026 | 3:00:00 AM | 285.68 | 282.38 | 282.47 | 494.35 | 486.97 | 491.81 | 74.4907 | 63.4785 | 66.3235 | 1.8709 | 1.432 | 1.428 | 1.425 | 2.088 | 2.094 | 2.214 | Over-range | 60.02 | 19010 | 15731 | 15392 | 50133 | - - - | - - - | - - - | - - - | 19010 | 15731 | 15392 | 50133 | 2328 | 610 | 4065 | 7003 | - - - | - - - | - - - | - - - | 2328 | 610 | 4065 | 7003 | 21200 | 17868 | 18669 | 57738 | # # # | # # # | # # # | # # # | 0.897 | 0.88 | 0.825 | 0.868 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.966 | 0.986 | - - - | 0.14 | 1.59 | 1.57 | 1.57 | 1.53 | 1.56 | 1.57 | 48.31 | 54.1 | 61.91 | 0 | - - - | - - - | - - - | - - - | 21200 | 17868 | 18669 | 57738 | Over-range | 9372 | 8467 | 10559 | 28618 | 9078 | 8445 | 9745 | 27748 | 18905 | 15690 | 15319 | 49913 | 18905 | 15690 | 15319 | 49913 | - - - | - - - | - - - | - - -
5/4/2026 | 3:15:00 AM | 285.6 | 282.39 | 282.55 | 494.22 | 487.12 | 491.81 | 69.4394 | 59.8259 | 62.1269 | 1.8258 | 1.43 | 1.426 | 1.424 | 2.079 | 2.061 | 2.184 | Over-range | 60 | 17833 | 14931 | 14576 | 47339 | - - - | - - - | - - - | - - - | 17833 | 14931 | 14576 | 47339 | 2156 | 616 | 3685 | 6457 | - - - | - - - | - - - | - - - | 2156 | 616 | 3685 | 6457 | 19784 | 16860 | 17519 | 54164 | # # # | # # # | # # # | # # # | 0.901 | 0.886 | 0.832 | 0.874 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.969 | 0.987 | - - - | 0.136 | 1.57 | 1.56 | 1.58 | 1.51 | 1.55 | 1.56 | 47.07 | 52.7 | 60.51 | 0 | - - - | - - - | - - - | - - - | 19784 | 16860 | 17519 | 54164 | Over-range | 8560 | 7828 | 9715 | 26304 | 8284 | 7803 | 8989 | 25499 | 17741 | 14879 | 14522 | 47142 | 17741 | 14879 | 14522 | 47142 | - - - | - - - | - - - | - - -
5/4/2026 | 3:30:00 AM | 285.73 | 282.55 | 282.65 | 494.49 | 487.35 | 491.98 | 70.0048 | 60.2681 | 62.1521 | 1.8107 | 1.431 | 1.427 | 1.424 | 2.076 | 2.082 | 2.2 | Over-range | 60 | 17894 | 15007 | 14494 | 47395 | - - - | - - - | - - - | - - - | 17894 | 15007 | 14494 | 47395 | 2277 | 554 | 3681 | 6512 | - - - | - - - | - - - | - - - | 2277 | 554 | 3681 | 6512 | 19916 | 16968 | 17500 | 54384 | # # # | # # # | # # # | # # # | 0.899 | 0.884 | 0.828 | 0.872 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.969 | 0.987 | - - - | 0.137 | 1.57 | 1.55 | 1.59 | 1.51 | 1.55 | 1.56 | 47.6 | 53.03 | 61.36 | 0 | - - - | - - - | - - - | - - - | 19916 | 16968 | 17500 | 54384 | Over-range | 8733 | 7911 | 9802 | 26650 | 8431 | 7892 | 9085 | 25842 | 17829 | 14927 | 14445 | 47202 | 17829 | 14927 | 14445 | 47202 | - - - | - - - | - - - | - - -
5/4/2026 | 3:45:00 AM | 285.83 | 282.56 | 282.76 | 494.57 | 487.43 | 492.22 | 70.7025 | 60.5771 | 62.5473 | 1.8026 | 1.431 | 1.427 | 1.424 | 2.095 | 2.113 | 2.233 | Over-range | 60 | 17964 | 15033 | 14448 | 47446 | - - - | - - - | - - - | - - - | 17964 | 15033 | 14448 | 47446 | 2361 | 531 | 3736 | 6629 | - - - | - - - | - - - | - - - | 2361 | 531 | 3736 | 6629 | 20121 | 17055 | 17613 | 54789 | # # # | # # # | # # # | # # # | 0.893 | 0.881 | 0.82 | 0.866 | # # # | # # # | # # # | - - - | 0.991 | 0.999 | 0.968 | 0.987 | - - - | 0.14 | 1.57 | 1.54 | 1.58 | 1.5 | 1.55 | 1.55 | 49.04 | 53.8 | 63.3 | 0 | - - - | - - - | - - - | - - - | 20121 | 17055 | 17613 | 54789 | Over-range | 9051 | 8046 | 10069 | 27377 | 8738 | 8029 | 9350 | 26562 | 17905 | 14970 | 14370 | 47245 | 17905 | 14970 | 14370 | 47245 | - - - | - - - | - - - | - - -
5/4/2026 | 4:00:00 AM | 285.53 | 282.43 | 282.57 | 494.17 | 487.23 | 491.73 | 70.1861 | 60.6689 | 61.8943 | 1.823 | 1.43 | 1.426 | 1.424 | 2.086 | 2.12 | 2.227 | Over-range | 60 | 17781 | 15036 | 14300 | 47118 | - - - | - - - | - - - | - - - | 17781 | 15036 | 14300 | 47118 | 2437 | 545 | 3639 | 6621 | - - - | - - - | - - - | - - - | 2437 | 545 | 3639 | 6621 | 19957 | 17072 | 17423 | 54452 | # # # | # # # | # # # | # # # | 0.891 | 0.881 | 0.821 | 0.865 | # # # | # # # | # # # | - - - | 0.991 | 0.999 | 0.969 | 0.987 | - - - | 0.141 | 1.58 | 1.56 | 1.57 | 1.51 | 1.56 | 1.57 | 49.3 | 54.05 | 63.33 | 0 | - - - | - - - | - - - | - - - | 19957 | 17072 | 17423 | 54452 | Over-range | 9048 | 8077 | 9947 | 27269 | 8713 | 8059 | 9258 | 26453 | 17727 | 14967 | 14231 | 46924 | 17727 | 14967 | 14231 | 46924 | - - - | - - - | - - - | - - -
5/4/2026 | 4:15:00 AM | 285.85 | 282.7 | 282.78 | 494.73 | 487.6 | 492.18 | 69.9679 | 60.2876 | 61.2677 | 1.8174 | 1.43 | 1.427 | 1.425 | 2.084 | 2.134 | 2.242 | Over-range | 60 | 17713 | 14957 | 14101 | 46771 | - - - | - - - | - - - | - - - | 17713 | 14957 | 14101 | 46771 | 2476 | 467 | 3635 | 6578 | - - - | - - - | - - - | - - - | 2476 | 467 | 3635 | 6578 | 19914 | 16981 | 17253 | 54148 | # # # | # # # | # # # | # # # | 0.889 | 0.881 | 0.817 | 0.864 | # # # | # # # | # # # | - - - | 0.99 | 1 | 0.968 | 0.986 | - - - | 0.141 | 1.6 | 1.57 | 1.64 | 1.52 | 1.6 | 1.61 | 49.64 | 53.91 | 64.15 | 0 | - - - | - - - | - - - | - - - | 19914 | 16981 | 17253 | 54148 | Over-range | 9088 | 8033 | 9936 | 27263 | 8744 | 8019 | 9248 | 26457 | 17655 | 14927 | 14006 | 46588 | 17655 | 14927 | 14006 | 46588 | - - - | - - - | - - - | - - -
5/4/2026 | 4:30:00 AM | 285.68 | 282.59 | 282.63 | 494.49 | 487.4 | 491.87 | 69.6547 | 60.2613 | 60.8919 | 1.8471 | 1.43 | 1.427 | 1.425 | 2.078 | 2.135 | 2.237 | Over-range | 60.01 | 17610 | 14939 | 14024 | 46573 | - - - | - - - | - - - | - - - | 17610 | 14939 | 14024 | 46573 | 2506 | 458 | 3586 | 6550 | - - - | - - - | - - - | - - - | 2506 | 458 | 3586 | 6550 | 19809 | 16962 | 17141 | 53911 | # # # | # # # | # # # | # # # | 0.889 | 0.881 | 0.818 | 0.864 | # # # | # # # | # # # | - - - | 0.99 | 1 | 0.969 | 0.986 | - - - | 0.141 | 1.59 | 1.57 | 1.61 | 1.51 | 1.58 | 1.59 | 49.73 | 53.94 | 63.85 | 0 | - - - | - - - | - - - | - - - | 19809 | 16962 | 17141 | 53911 | Over-range | 9060 | 8024 | 9850 | 27132 | 8706 | 8011 | 9174 | 26329 | 17529 | 14880 | 13985 | 46393 | 17529 | 14880 | 13985 | 46393 | - - - | - - - | - - - | - - -
5/4/2026 | 4:45:00 AM | 285.33 | 282.32 | 282.44 | 493.9 | 487.08 | 491.41 | 67.8906 | 59.1117 | 59.9255 | 1.7787 | 1.43 | 1.427 | 1.425 | 2.074 | 2.111 | 2.209 | Over-range | 60 | 17200 | 14678 | 13894 | 45772 | - - - | - - - | - - - | - - - | 17200 | 14678 | 13894 | 45772 | 2364 | 547 | 3459 | 6370 | - - - | - - - | - - - | - - - | 2364 | 547 | 3459 | 6370 | 19291 | 16633 | 16857 | 52781 | # # # | # # # | # # # | # # # | 0.892 | 0.882 | 0.824 | 0.867 | # # # | # # # | # # # | - - - | 0.991 | 0.999 | 0.97 | 0.987 | - - - | 0.139 | 1.56 | 1.57 | 1.62 | 1.51 | 1.57 | 1.58 | 49.15 | 53.29 | 62.73 | 0 | - - - | - - - | - - - | - - - | 19291 | 16633 | 16857 | 52781 | Over-range | 8725 | 7815 | 9540 | 26259 | 8399 | 7796 | 8891 | 25475 | 17107 | 14668 | 13820 | 45596 | 17107 | 14668 | 13820 | 45596 | - - - | - - - | - - - | - - -
5/4/2026 | 5:00:00 AM | 285.18 | 282.12 | 282.16 | 493.65 | 486.61 | 491.03 | 67.169 | 58.4673 | 58.911 | 1.7848 | 1.43 | 1.427 | 1.425 | 2.071 | 2.122 | 2.218 | Over-range | 60 | 16988 | 14508 | 13623 | 45120 | - - - | - - - | - - - | - - - | 16988 | 14508 | 13623 | 45120 | 2379 | 486 | 3398 | 6262 | - - - | - - - | - - - | - - - | 2379 | 486 | 3398 | 6262 | 19076 | 16434 | 16558 | 52067 | # # # | # # # | # # # | # # # | 0.891 | 0.883 | 0.823 | 0.867 | # # # | # # # | # # # | - - - | 0.99 | 0.999 | 0.97 | 0.987 | - - - | 0.139 | 1.61 | 1.57 | 1.66 | 1.52 | 1.61 | 1.63 | 49.35 | 53.2 | 63.06 | 0 | - - - | - - - | - - - | - - - | 19076 | 16434 | 16558 | 52067 | Over-range | 8667 | 7712 | 9406 | 25965 | 8334 | 7697 | 8771 | 25199 | 16903 | 14498 | 13554 | 44955 | 16903 | 14498 | 13554 | 44955 | - - - | - - - | - - - | - - -
5/4/2026 | 5:15:00 AM | 285.01 | 282.08 | 282.07 | 493.45 | 486.55 | 490.75 | 66.5719 | 58.4902 | 58.6385 | 1.7816 | 1.43 | 1.428 | 1.426 | 2.053 | 2.1 | 2.184 | Over-range | 60 | 16886 | 14541 | 13675 | 45103 | - - - | - - - | - - - | - - - | 16886 | 14541 | 13675 | 45103 | 2332 | 547 | 3286 | 6165 | - - - | - - - | - - - | - - - | 2332 | 547 | 3286 | 6165 | 18905 | 16447 | 16489 | 51842 | # # # | # # # | # # # | # # # | 0.893 | 0.884 | 0.829 | 0.87 | # # # | # # # | # # # | - - - | 0.99 | 0.999 | 0.972 | 0.988 | - - - | 0.137 | 1.67 | 1.6 | 1.69 | 1.56 | 1.64 | 1.68 | 48.51 | 52.82 | 61.59 | 0 | - - - | - - - | - - - | - - - | 18905 | 16447 | 16489 | 51842 | Over-range | 8490 | 7678 | 9207 | 25538 | 8163 | 7659 | 8601 | 24783 | 16833 | 14523 | 13603 | 44959 | 16833 | 14523 | 13603 | 44959 | - - - | - - - | - - - | - - -
5/4/2026 | 5:30:00 AM | 284.73 | 281.97 | 281.9 | 493.11 | 486.4 | 490.3 | 67.3847 | 59.6513 | 59.3705 | 1.8135 | 1.431 | 1.429 | 1.428 | 2.042 | 2.108 | 2.172 | Over-range | 60 | 17011 | 14777 | 13844 | 45632 | - - - | - - - | - - - | - - - | 17011 | 14777 | 13844 | 45632 | 2402 | 606 | 3257 | 6264 | - - - | - - - | - - - | - - - | 2402 | 606 | 3257 | 6264 | 19096 | 16750 | 16662 | 52508 | # # # | # # # | # # # | # # # | 0.891 | 0.882 | 0.831 | 0.869 | # # # | # # # | # # # | - - - | 0.99 | 0.999 | 0.973 | 0.988 | - - - | 0.137 | 1.7 | 1.67 | 1.75 | 1.61 | 1.7 | 1.74 | 48.95 | 53.24 | 61.35 | 0 | - - - | - - - | - - - | - - - | 19096 | 16750 | 16662 | 52508 | Over-range | 8667 | 7879 | 9266 | 25955 | 8328 | 7855 | 8675 | 25188 | 16977 | 14744 | 13781 | 45502 | 16977 | 14744 | 13781 | 45502 | - - - | - - - | - - - | - - -
5/4/2026 | 5:45:00 AM | 284.4 | 281.59 | 281.49 | 492.51 | 485.67 | 489.66 | 67.7734 | 59.9328 | 59.4582 | 1.8285 | 1.431 | 1.429 | 1.428 | 2.045 | 2.122 | 2.186 | Over-range | 60.01 | 17035 | 14805 | 13790 | 45630 | - - - | - - - | - - - | - - - | 17035 | 14805 | 13790 | 45630 | 2464 | 572 | 3261 | 6297 | - - - | - - - | - - - | - - - | 2464 | 572 | 3261 | 6297 | 19189 | 16808 | 16671 | 52668 | # # # | # # # | # # # | # # # | 0.888 | 0.881 | 0.827 | 0.866 | # # # | # # # | # # # | - - - | 0.99 | 0.999 | 0.973 | 0.988 | - - - | 0.138 | 1.77 | 1.73 | 1.82 | 1.67 | 1.76 | 1.81 | 49.7 | 53.67 | 62.2 | 0 | - - - | - - - | - - - | - - - | 19189 | 16808 | 16671 | 52668 | Over-range | 8824 | 7949 | 9363 | 26280 | 8472 | 7928 | 8776 | 25515 | 16996 | 14754 | 13751 | 45500 | 16996 | 14754 | 13751 | 45500 | - - - | - - - | - - - | - - -
5/4/2026 | 6:00:00 AM | 283.72 | 280.96 | 280.85 | 491.37 | 484.59 | 488.5 | 67.7693 | 60.0304 | 59.5681 | 1.8138 | 1.432 | 1.429 | 1.428 | 2.043 | 2.119 | 2.178 | Over-range | 60.01 | 16985 | 14791 | 13795 | 45571 | - - - | - - - | - - - | - - - | 16985 | 14791 | 13795 | 45571 | 2448 | 587 | 3240 | 6276 | - - - | - - - | - - - | - - - | 2448 | 587 | 3240 | 6276 | 19138 | 16795 | 16662 | 52596 | # # # | # # # | # # # | # # # | 0.887 | 0.881 | 0.828 | 0.867 | # # # | # # # | # # # | - - - | 0.99 | 0.999 | 0.973 | 0.988 | - - - | 0.138 | 1.75 | 1.7 | 1.83 | 1.66 | 1.74 | 1.8 | 49.78 | 53.64 | 62 | 0 | - - - | - - - | - - - | - - - | 19138 | 16795 | 16662 | 52596 | Over-range | 8807 | 7950 | 9338 | 26235 | 8459 | 7928 | 8758 | 25473 | 16934 | 14747 | 13767 | 45447 | 16934 | 14747 | 13767 | 45447 | - - - | - - - | - - - | - - -
5/4/2026 | 6:15:00 AM | 282.59 | 279.87 | 279.73 | 489.45 | 482.7 | 486.55 | 67.5679 | 60.0561 | 59.4873 | 1.7863 | 1.432 | 1.43 | 1.429 | 2.031 | 2.11 | 2.162 | Over-range | 59.98 | 16899 | 14756 | 13789 | 45444 | - - - | - - - | - - - | - - - | 16899 | 14756 | 13789 | 45444 | 2390 | 609 | 3188 | 6187 | - - - | - - - | - - - | - - - | 2390 | 609 | 3188 | 6187 | 19010 | 16741 | 16571 | 52321 | # # # | # # # | # # # | # # # | 0.889 | 0.881 | 0.832 | 0.869 | # # # | # # # | # # # | - - - | 0.99 | 0.999 | 0.974 | 0.988 | - - - | 0.136 | 1.84 | 1.78 | 1.89 | 1.72 | 1.82 | 1.88 | 49.33 | 53.29 | 61.09 | 0 | - - - | - - - | - - - | - - - | 19010 | 16741 | 16571 | 52321 | Over-range | 8696 | 7901 | 9184 | 25909 | 8361 | 7877 | 8612 | 25159 | 16855 | 14750 | 13738 | 45342 | 16855 | 14750 | 13738 | 45342 | - - - | - - - | - - - | - - -
5/4/2026 | 6:30:00 AM | 281.91 | 279.04 | 278.92 | 488.17 | 481.19 | 485.31 | 65.086 | 57.7494 | 57.4471 | 1.7248 | 1.43 | 1.429 | 1.429 | 2.029 | 2.089 | 2.15 | Over-range | 60 | 16337 | 14216 | 13358 | 43910 | - - - | - - - | - - - | - - - | 16337 | 14216 | 13358 | 43910 | 2220 | 558 | 3064 | 5841 | - - - | - - - | - - - | - - - | 2220 | 558 | 3064 | 5841 | 18277 | 16056 | 15969 | 50302 | # # # | # # # | # # # | # # # | 0.894 | 0.885 | 0.837 | 0.873 | # # # | # # # | # # # | - - - | 0.991 | 0.999 | 0.975 | 0.988 | - - - | 0.133 | 1.82 | 1.78 | 1.9 | 1.72 | 1.82 | 1.88 | 48.21 | 52.17 | 59.99 | 0 | - - - | - - - | - - - | - - - | 18277 | 16056 | 15969 | 50302 | Over-range | 8185 | 7457 | 8746 | 24519 | 7879 | 7436 | 8192 | 23813 | 16269 | 14219 | 13325 | 43812 | 16269 | 14219 | 13325 | 43812 | - - - | - - - | - - - | - - -
5/4/2026 | 6:45:00 AM | 281.73 | 278.95 | 278.89 | 487.88 | 481.16 | 485.12 | 63.7601 | 56.783 | 56.5096 | 1.6602 | 1.431 | 1.43 | 1.429 | 2.025 | 2.076 | 2.136 | Over-range | 60 | 16035 | 14014 | 13192 | 43241 | - - - | - - - | - - - | - - - | 16035 | 14014 | 13192 | 43241 | 2162 | 587 | 2971 | 5721 | - - - | - - - | - - - | - - - | 2162 | 587 | 2971 | 5721 | 17908 | 15796 | 15720 | 49424 | # # # | # # # | # # # | # # # | 0.895 | 0.887 | 0.839 | 0.875 | # # # | # # # | # # # | - - - | 0.991 | 0.999 | 0.975 | 0.989 | - - - | 0.132 | 1.81 | 1.76 | 1.85 | 1.69 | 1.78 | 1.85 | 47.82 | 51.69 | 59.61 | 0 | - - - | - - - | - - - | - - - | 17908 | 15796 | 15720 | 49424 | Over-range | 7967 | 7284 | 8544 | 23921 | 7668 | 7260 | 8011 | 23227 | 15973 | 14039 | 13134 | 43146 | 15973 | 14039 | 13134 | 43146 | - - - | - - - | - - - | - - -
5/4/2026 | 7:00:00 AM | 282.29 | 279.49 | 279.56 | 488.76 | 482.23 | 486.22 | 66.9488 | 59.3651 | 59.7765 | 1.7555 | 1.432 | 1.431 | 1.429 | 2.044 | 2.091 | 2.151 | Over-range | 60.03 | 16747 | 14576 | 13872 | 45195 | - - - | - - - | - - - | - - - | 16747 | 14576 | 13872 | 45195 | 2245 | 701 | 3200 | 6146 | - - - | - - - | - - - | - - - | 2245 | 701 | 3200 | 6146 | 18818 | 16526 | 16636 | 51980 | # # # | # # # | # # # | # # # | 0.89 | 0.882 | 0.834 | 0.87 | # # # | # # # | # # # | - - - | 0.991 | 0.999 | 0.974 | 0.988 | - - - | 0.136 | 1.81 | 1.73 | 1.85 | 1.69 | 1.78 | 1.85 | 49.37 | 53 | 60.56 | 0 | - - - | - - - | - - - | - - - | 18818 | 16526 | 16636 | 51980 | Over-range | 8572 | 7780 | 9178 | 25656 | 8272 | 7748 | 8602 | 24908 | 16674 | 14584 | 13840 | 45097 | 16674 | 14584 | 13840 | 45097 | - - - | - - - | - - - | - - -
5/4/2026 | 7:15:00 AM | 281.81 | 279 | 279.01 | 487.96 | 481.32 | 485.32 | 67.2013 | 59.5602 | 59.7244 | 1.7764 | 1.431 | 1.431 | 1.429 | 2.037 | 2.094 | 2.152 | Over-range | 60 | 16778 | 14601 | 13832 | 45211 | - - - | - - - | - - - | - - - | 16778 | 14601 | 13832 | 45211 | 2291 | 670 | 3191 | 6152 | - - - | - - - | - - - | - - - | 2291 | 670 | 3191 | 6152 | 18851 | 16548 | 16594 | 51993 | # # # | # # # | # # # | # # # | 0.89 | 0.882 | 0.834 | 0.87 | # # # | # # # | # # # | - - - | 0.991 | 0.999 | 0.974 | 0.988 | - - - | 0.136 | 1.78 | 1.73 | 1.81 | 1.66 | 1.75 | 1.82 | 49.15 | 53.04 | 60.57 | 0 | - - - | - - - | - - - | - - - | 18851 | 16548 | 16594 | 51993 | Over-range | 8582 | 7781 | 9160 | 25651 | 8270 | 7752 | 8586 | 24902 | 16732 | 14568 | 13813 | 45113 | 16732 | 14568 | 13813 | 45113 | - - - | - - - | - - - | - - -
5/4/2026 | 7:30:00 AM | 281.66 | 278.86 | 278.95 | 487.65 | 481.16 | 485.15 | 67.1454 | 59.6414 | 60.1408 | 1.7463 | 1.431 | 1.431 | 1.429 | 2.04 | 2.081 | 2.136 | Over-range | 60.02 | 16773 | 14607 | 13983 | 45363 | - - - | - - - | - - - | - - - | 16773 | 14607 | 13983 | 45363 | 2216 | 751 | 3184 | 6150 | - - - | - - - | - - - | - - - | 2216 | 751 | 3184 | 6150 | 18827 | 16562 | 16708 | 52096 | # # # | # # # | # # # | # # # | 0.891 | 0.882 | 0.837 | 0.871 | # # # | # # # | # # # | - - - | 0.991 | 0.999 | 0.975 | 0.989 | - - - | 0.136 | 1.79 | 1.73 | 1.86 | 1.69 | 1.78 | 1.84 | 49.07 | 53.05 | 59.79 | 0 | - - - | - - - | - - - | - - - | 18827 | 16562 | 16708 | 52096 | Over-range | 8539 | 7798 | 9138 | 25593 | 8246 | 7762 | 8566 | 24843 | 16727 | 14572 | 13969 | 45269 | 16727 | 14572 | 13969 | 45269 | - - - | - - - | - - - | - - -
5/4/2026 | 7:45:00 AM | 281.7 | 278.94 | 279.04 | 487.75 | 481.34 | 485.27 | 67.3194 | 59.737 | 60.3619 | 1.7398 | 1.432 | 1.432 | 1.429 | 2.04 | 2.079 | 2.133 | Over-range | 60.02 | 16821 | 14637 | 14035 | 45493 | - - - | - - - | - - - | - - - | 16821 | 14637 | 14035 | 45493 | 2212 | 769 | 3210 | 6191 | - - - | - - - | - - - | - - - | 2212 | 769 | 3210 | 6191 | 18875 | 16597 | 16771 | 52243 | # # # | # # # | # # # | # # # | 0.891 | 0.882 | 0.837 | 0.871 | # # # | # # # | # # # | - - - | 0.991 | 0.999 | 0.975 | 0.988 | - - - | 0.136 | 1.79 | 1.72 | 1.83 | 1.68 | 1.76 | 1.82 | 49.02 | 53.08 | 59.83 | 0 | - - - | - - - | - - - | - - - | 18875 | 16597 | 16771 | 52243 | Over-range | 8551 | 7817 | 9174 | 25660 | 8259 | 7779 | 8594 | 24902 | 16780 | 14619 | 13990 | 45389 | 16780 | 14619 | 13990 | 45389 | - - - | - - - | - - - | - - -
5/4/2026 | 8:00:00 AM | 281.84 | 278.94 | 279.14 | 487.85 | 481.36 | 485.54 | 67.5366 | 59.546 | 60.9274 | 1.7185 | 1.431 | 1.432 | 1.429 | 2.054 | 2.071 | 2.137 | Over-range | 60.04 | 16902 | 14583 | 14175 | 45661 | - - - | - - - | - - - | - - - | 16902 | 14583 | 14175 | 45661 | 2124 | 800 | 3276 | 6201 | - - - | - - - | - - - | - - - | 2124 | 800 | 3276 | 6201 | 18950 | 16543 | 16937 | 52430 | # # # | # # # | # # # | # # # | 0.892 | 0.881 | 0.837 | 0.871 | # # # | # # # | # # # | - - - | 0.992 | 0.998 | 0.974 | 0.988 | - - - | 0.136 | 1.78 | 1.71 | 1.81 | 1.66 | 1.74 | 1.8 | 48.98 | 53.19 | 59.64 | 0 | - - - | - - - | - - - | - - - | 18950 | 16543 | 16937 | 52430 | Over-range | 8556 | 7803 | 9263 | 25743 | 8288 | 7761 | 8664 | 24985 | 16870 | 14544 | 14147 | 45561 | 16870 | 14544 | 14147 | 45561 | - - - | - - - | - - - | - - -
5/4/2026 | 8:15:00 AM | 281.36 | 278.36 | 278.58 | 486.95 | 480.34 | 484.67 | 68.2335 | 60.113 | 61.3698 | 1.7193 | 1.431 | 1.432 | 1.429 | 2.049 | 2.077 | 2.141 | Over-range | 60.03 | 17030 | 14675 | 14227 | 45931 | - - - | - - - | - - - | - - - | 17030 | 14675 | 14227 | 45931 | 2165 | 774 | 3317 | 6256 | - - - | - - - | - - - | - - - | 2165 | 774 | 3317 | 6256 | 19113 | 16668 | 17029 | 52810 | # # # | # # # | # # # | # # # | 0.891 | 0.88 | 0.835 | 0.87 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.974 | 0.988 | - - - | 0.136 | 1.77 | 1.71 | 1.83 | 1.65 | 1.76 | 1.81 | 49.24 | 53.49 | 59.95 | 0 | - - - | - - - | - - - | - - - | 19113 | 16668 | 17029 | 52810 | Over-range | 8668 | 7897 | 9353 | 26040 | 8393 | 7859 | 8745 | 25277 | 16972 | 14651 | 14209 | 45831 | 16972 | 14651 | 14209 | 45831 | - - - | - - - | - - - | - - -
5/4/2026 | 8:30:00 AM | 281.01 | 277.86 | 278.29 | 486.13 | 479.63 | 484.22 | 68.5531 | 60.2403 | 62.4697 | 1.6895 | 1.432 | 1.433 | 1.429 | 2.056 | 2.052 | 2.12 | Over-range | 60.03 | 17110 | 14670 | 14509 | 46289 | - - - | - - - | - - - | - - - | 17110 | 14670 | 14509 | 46289 | 2037 | 913 | 3371 | 6321 | - - - | - - - | - - - | - - - | 2037 | 913 | 3371 | 6321 | 19184 | 16679 | 17319 | 53181 | # # # | # # # | # # # | # # # | 0.892 | 0.88 | 0.838 | 0.87 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.974 | 0.988 | - - - | 0.137 | 1.78 | 1.75 | 1.86 | 1.68 | 1.79 | 1.84 | 49.21 | 53.61 | 59.5 | 0 | - - - | - - - | - - - | - - - | 19184 | 16679 | 17319 | 53181 | Over-range | 8665 | 7929 | 9451 | 26162 | 8422 | 7876 | 8830 | 25387 | 17073 | 14655 | 14458 | 46186 | 17073 | 14655 | 14458 | 46186 | - - - | - - - | - - - | - - -
5/4/2026 | 8:45:00 AM | 280.33 | 276.89 | 277.45 | 484.72 | 477.93 | 483.03 | 70.2717 | 61.0586 | 64.1384 | 1.7239 | 1.432 | 1.433 | 1.429 | 2.061 | 2.05 | 2.125 | Over-range | 60.02 | 17515 | 14805 | 14832 | 47152 | - - - | - - - | - - - | - - - | 17515 | 14805 | 14832 | 47152 | 1983 | 926 | 3544 | 6452 | - - - | - - - | - - - | - - - | 1983 | 926 | 3544 | 6452 | 19614 | 16846 | 17726 | 54187 | # # # | # # # | # # # | # # # | 0.893 | 0.879 | 0.837 | 0.87 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.972 | 0.988 | - - - | 0.137 | 1.76 | 1.76 | 1.88 | 1.67 | 1.81 | 1.83 | 49.06 | 53.89 | 59.4 | 0 | - - - | - - - | - - - | - - - | 19614 | 16846 | 17726 | 54187 | Over-range | 8818 | 8033 | 9699 | 26676 | 8592 | 7979 | 9028 | 25884 | 17491 | 14772 | 14777 | 47040 | 17491 | 14772 | 14777 | 47040 | - - - | - - - | - - - | - - -
5/4/2026 | 9:00:00 AM | 280.11 | 276.62 | 277.3 | 484.23 | 477.57 | 482.76 | 71.4186 | 61.9441 | 66.0277 | 1.6958 | 1.432 | 1.433 | 1.429 | 2.066 | 2.028 | 2.106 | Over-range | 60.01 | 17829 | 14992 | 15334 | 48154 | - - - | - - - | - - - | - - - | 17829 | 14992 | 15334 | 48154 | 1862 | 1060 | 3657 | 6578 | - - - | - - - | - - - | - - - | 1862 | 1060 | 3657 | 6578 | 19923 | 17075 | 18234 | 55232 | # # # | # # # | # # # | # # # | 0.895 | 0.878 | 0.841 | 0.872 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.988 | - - - | 0.137 | 1.77 | 1.75 | 1.85 | 1.66 | 1.8 | 1.82 | 48.79 | 54.01 | 58.26 | 0 | - - - | - - - | - - - | - - - | 19923 | 17075 | 18234 | 55232 | Over-range | 8882 | 8166 | 9861 | 27029 | 8684 | 8097 | 9158 | 26216 | 17779 | 14960 | 15304 | 48043 | 17779 | 14960 | 15304 | 48043 | - - - | - - - | - - - | - - -
5/4/2026 | 9:15:00 AM | 279.82 | 276.28 | 276.89 | 483.74 | 476.87 | 482.15 | 73.9389 | 63.672 | 67.8784 | 1.757 | 1.432 | 1.433 | 1.429 | 2.066 | 2.046 | 2.123 | Over-range | 60 | 18403 | 15364 | 15668 | 49435 | - - - | - - - | - - - | - - - | 18403 | 15364 | 15668 | 49435 | 1961 | 1022 | 3854 | 6837 | - - - | - - - | - - - | - - - | 1961 | 1022 | 3854 | 6837 | 20611 | 17537 | 18732 | 56881 | # # # | # # # | # # # | # # # | 0.893 | 0.876 | 0.837 | 0.869 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.971 | 0.988 | - - - | 0.138 | 1.71 | 1.72 | 1.82 | 1.62 | 1.76 | 1.78 | 49.3 | 54.59 | 59.1 | 0 | - - - | - - - | - - - | - - - | 20611 | 17537 | 18732 | 56881 | Over-range | 9271 | 8451 | 10259 | 28112 | 9061 | 8389 | 9507 | 27268 | 18347 | 15338 | 15634 | 49320 | 18347 | 15338 | 15634 | 49320 | - - - | - - - | - - - | - - -
5/4/2026 | 9:30:00 AM | 279.55 | 275.93 | 276.55 | 483.22 | 476.23 | 481.66 | 77.4347 | 66.1735 | 71.386 | 1.7857 | 1.434 | 1.434 | 1.431 | 2.079 | 2.056 | 2.135 | Over-range | 60.01 | 19230 | 15894 | 16420 | 51544 | - - - | - - - | - - - | - - - | 19230 | 15894 | 16420 | 51544 | 1973 | 1117 | 4142 | 7232 | - - - | - - - | - - - | - - - | 1973 | 1117 | 4142 | 7232 | 21590 | 18218 | 19689 | 59498 | # # # | # # # | # # # | # # # | 0.891 | 0.872 | 0.834 | 0.866 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.969 | 0.987 | - - - | 0.14 | 1.72 | 1.69 | 1.8 | 1.62 | 1.75 | 1.77 | 50.17 | 55.63 | 59.53 | 0 | - - - | - - - | - - - | - - - | 21590 | 18218 | 19689 | 59498 | Over-range | 9810 | 8900 | 10862 | 29707 | 9609 | 8829 | 10041 | 28813 | 19167 | 15865 | 16387 | 51419 | 19167 | 15865 | 16387 | 51419 | - - - | - - - | - - - | - - -
5/4/2026 | 9:45:00 AM | 279.87 | 276.42 | 276.97 | 483.9 | 477.1 | 482.22 | 75.292 | 65.2676 | 69.8182 | 1.7885 | 1.433 | 1.433 | 1.431 | 2.051 | 2.017 | 2.087 | Over-range | 60.01 | 18810 | 15760 | 16258 | 50828 | - - - | - - - | - - - | - - - | 18810 | 15760 | 16258 | 50828 | 1900 | 1194 | 3919 | 7014 | - - - | - - - | - - - | - - - | 1900 | 1194 | 3919 | 7014 | 20990 | 17978 | 19269 | 58238 | # # # | # # # | # # # | # # # | 0.896 | 0.877 | 0.844 | 0.873 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.138 | 1.73 | 1.72 | 1.81 | 1.64 | 1.76 | 1.78 | 48.55 | 54.33 | 57.39 | 0 | - - - | - - - | - - - | - - - | 20990 | 17978 | 19269 | 58238 | Over-range | 9304 | 8646 | 10338 | 28408 | 9108 | 8563 | 9567 | 27529 | 18757 | 15729 | 16226 | 50712 | 18757 | 15729 | 16226 | 50712 | - - - | - - - | - - - | - - -
5/4/2026 | 10:00:00 AM | 281.07 | 277.56 | 278.15 | 485.94 | 479.07 | 484.32 | 80.4123 | 69.1967 | 74.751 | 1.9317 | 1.434 | 1.434 | 1.432 | 2.069 | 2.038 | 2.107 | Over-range | 60.01 | 20105 | 16713 | 17409 | 54227 | - - - | - - - | - - - | - - - | 20105 | 16713 | 17409 | 54227 | 1991 | 1352 | 4324 | 7667 | - - - | - - - | - - - | - - - | 1991 | 1352 | 4324 | 7667 | 22555 | 19172 | 20752 | 62479 | # # # | # # # | # # # | # # # | 0.891 | 0.872 | 0.839 | 0.868 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.988 | - - - | 0.141 | 1.71 | 1.71 | 1.79 | 1.62 | 1.74 | 1.76 | 50.02 | 55.68 | 58.37 | 0 | - - - | - - - | - - - | - - - | 22555 | 19172 | 20752 | 62479 | Over-range | 10216 | 9391 | 11290 | 31019 | 10019 | 9293 | 10429 | 30056 | 20040 | 16678 | 17377 | 54095 | 20040 | 16678 | 17377 | 54095 | - - - | - - - | - - - | - - -
5/4/2026 | 10:15:00 AM | 280.62 | 276.98 | 277.59 | 485.08 | 478.02 | 483.48 | 79.9844 | 68.5701 | 74.3898 | 1.9288 | 1.433 | 1.434 | 1.431 | 2.058 | 2.018 | 2.091 | Over-range | 60.02 | 20046 | 16571 | 17353 | 53969 | - - - | - - - | - - - | - - - | 20046 | 16571 | 17353 | 53969 | 1887 | 1309 | 4306 | 7502 | - - - | - - - | - - - | - - - | 1887 | 1309 | 4306 | 7502 | 22381 | 18949 | 20598 | 61929 | # # # | # # # | # # # | # # # | 0.896 | 0.875 | 0.842 | 0.872 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.97 | 0.988 | - - - | 0.139 | 1.72 | 1.72 | 1.82 | 1.63 | 1.77 | 1.78 | 48.85 | 54.89 | 57.34 | 0 | - - - | - - - | - - - | - - - | 22381 | 18949 | 20598 | 61929 | Over-range | 9945 | 9186 | 11091 | 30352 | 9764 | 9092 | 10221 | 29410 | 19997 | 16539 | 17315 | 53851 | 19997 | 16539 | 17315 | 53851 | - - - | - - - | - - - | - - -
5/4/2026 | 10:30:00 AM | 280.51 | 276.91 | 277.47 | 484.93 | 477.85 | 483.26 | 82.1592 | 70.4603 | 76.3751 | 1.9664 | 1.433 | 1.435 | 1.432 | 2.056 | 2.026 | 2.094 | Over-range | 60.01 | 20574 | 17008 | 17814 | 55397 | - - - | - - - | - - - | - - - | 20574 | 17008 | 17814 | 55397 | 1950 | 1357 | 4428 | 7736 | - - - | - - - | - - - | - - - | 1950 | 1357 | 4428 | 7736 | 23001 | 19479 | 21154 | 63634 | # # # | # # # | # # # | # # # | 0.895 | 0.873 | 0.842 | 0.871 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.988 | - - - | 0.14 | 1.75 | 1.76 | 1.84 | 1.65 | 1.79 | 1.81 | 49.16 | 55.31 | 57.41 | 0 | - - - | - - - | - - - | - - - | 23001 | 19479 | 21154 | 63634 | Over-range | 10278 | 9492 | 11403 | 31300 | 10091 | 9394 | 10508 | 30329 | 20538 | 16970 | 17774 | 55281 | 20538 | 16970 | 17774 | 55281 | - - - | - - - | - - - | - - -
5/4/2026 | 10:45:00 AM | 280.55 | 276.82 | 277.44 | 484.89 | 477.7 | 483.32 | 83.097 | 70.8589 | 77.5989 | 1.9876 | 1.433 | 1.434 | 1.432 | 2.058 | 2.011 | 2.087 | Over-range | 60.01 | 20865 | 17113 | 18145 | 56123 | - - - | - - - | - - - | - - - | 20865 | 17113 | 18145 | 56123 | 1833 | 1395 | 4545 | 7772 | - - - | - - - | - - - | - - - | 1833 | 1395 | 4545 | 7772 | 23263 | 19579 | 21490 | 64332 | # # # | # # # | # # # | # # # | 0.897 | 0.874 | 0.844 | 0.872 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.97 | 0.988 | - - - | 0.139 | 1.73 | 1.73 | 1.85 | 1.64 | 1.78 | 1.8 | 48.66 | 54.97 | 56.68 | 0 | - - - | - - - | - - - | - - - | 23263 | 19579 | 21490 | 64332 | Over-range | 10279 | 9509 | 11509 | 31429 | 10114 | 9406 | 10573 | 30453 | 20811 | 17079 | 18121 | 56010 | 20811 | 17079 | 18121 | 56010 | - - - | - - - | - - - | - - -
5/4/2026 | 11:00:00 AM | 280.63 | 277.05 | 277.59 | 485.17 | 478.09 | 483.45 | 83.1652 | 71.3306 | 77.7234 | 2.0241 | 1.434 | 1.435 | 1.432 | 2.043 | 1.997 | 2.069 | Over-range | 60.02 | 20946 | 17294 | 18273 | 56514 | - - - | - - - | - - - | - - - | 20946 | 17294 | 18273 | 56514 | 1839 | 1411 | 4497 | 7747 | - - - | - - - | - - - | - - - | 1839 | 1411 | 4497 | 7747 | 23282 | 19721 | 21529 | 64532 | # # # | # # # | # # # | # # # | 0.9 | 0.877 | 0.849 | 0.876 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.971 | 0.988 | - - - | 0.137 | 1.78 | 1.77 | 1.87 | 1.68 | 1.81 | 1.84 | 47.83 | 54.15 | 55.66 | 0 | - - - | - - - | - - - | - - - | 23282 | 19721 | 21529 | 64532 | Over-range | 10154 | 9474 | 11378 | 31135 | 9986 | 9368 | 10451 | 30156 | 20884 | 17267 | 18245 | 56396 | 20884 | 17267 | 18245 | 56396 | - - - | - - - | - - - | - - -
5/4/2026 | 11:15:00 AM | 280.51 | 276.94 | 277.6 | 484.88 | 478.05 | 483.4 | 85.3176 | 73.535 | 80.3992 | 2.0105 | 1.435 | 1.436 | 1.434 | 2.045 | 1.985 | 2.057 | Over-range | 60.01 | 21480 | 17826 | 18973 | 58279 | - - - | - - - | - - - | - - - | 21480 | 17826 | 18973 | 58279 | 1862 | 1594 | 4576 | 8032 | - - - | - - - | - - - | - - - | 1862 | 1594 | 4576 | 8032 | 23891 | 20332 | 22287 | 66509 | # # # | # # # | # # # | # # # | 0.899 | 0.877 | 0.851 | 0.876 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.972 | 0.988 | - - - | 0.138 | 1.78 | 1.75 | 1.87 | 1.67 | 1.8 | 1.83 | 48.1 | 54.17 | 55.29 | 0 | - - - | - - - | - - - | - - - | 23891 | 20332 | 22287 | 66509 | Over-range | 10452 | 9776 | 11689 | 32036 | 10284 | 9645 | 10756 | 31012 | 21426 | 17783 | 18945 | 58154 | 21426 | 17783 | 18945 | 58154 | - - - | - - - | - - - | - - -
5/4/2026 | 11:30:00 AM | 280.2 | 276.66 | 277.25 | 484.4 | 477.51 | 482.79 | 84.8619 | 73.4287 | 79.8101 | 2.0634 | 1.434 | 1.436 | 1.433 | 2.029 | 1.97 | 2.042 | Over-range | 60.01 | 21408 | 17861 | 18890 | 58159 | - - - | - - - | - - - | - - - | 21408 | 17861 | 18890 | 58159 | 1856 | 1562 | 4477 | 7895 | - - - | - - - | - - - | - - - | 1856 | 1562 | 4477 | 7895 | 23722 | 20274 | 22083 | 66080 | # # # | # # # | # # # | # # # | 0.903 | 0.881 | 0.855 | 0.88 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.973 | 0.989 | - - - | 0.136 | 1.76 | 1.73 | 1.86 | 1.67 | 1.79 | 1.82 | 47.08 | 52.97 | 54.34 | 0 | - - - | - - - | - - - | - - - | 23722 | 20274 | 22083 | 66080 | Over-range | 10209 | 9590 | 11431 | 31350 | 10039 | 9462 | 10518 | 30340 | 21355 | 17833 | 18852 | 58040 | 21355 | 17833 | 18852 | 58040 | - - - | - - - | - - - | - - -
5/4/2026 | 11:45:00 AM | 280.05 | 276.49 | 277.09 | 484.13 | 477.21 | 482.54 | 87.2553 | 75.3845 | 82.1034 | 2.1128 | 1.434 | 1.436 | 1.433 | 2.032 | 1.976 | 2.047 | Over-range | 60 | 21985 | 18320 | 19413 | 59718 | - - - | - - - | - - - | - - - | 21985 | 18320 | 19413 | 59718 | 1908 | 1620 | 4622 | 8150 | - - - | - - - | - - - | - - - | 1908 | 1620 | 4622 | 8150 | 24395 | 20812 | 22718 | 67925 | # # # | # # # | # # # | # # # | 0.901 | 0.88 | 0.855 | 0.879 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.973 | 0.988 | - - - | 0.137 | 1.77 | 1.76 | 1.86 | 1.67 | 1.8 | 1.83 | 47.46 | 53.22 | 54.56 | 0 | - - - | - - - | - - - | - - - | 24395 | 20812 | 22718 | 67925 | Over-range | 10565 | 9874 | 11794 | 32351 | 10390 | 9739 | 10850 | 31308 | 21932 | 18279 | 19382 | 59592 | 21932 | 18279 | 19382 | 59592 | - - - | - - - | - - - | - - -
5/4/2026 | 12:00:00 PM | 279.93 | 276.49 | 277.06 | 484 | 477.23 | 482.37 | 88.7483 | 77.202 | 83.4822 | 2.2017 | 1.435 | 1.436 | 1.434 | 2.02 | 1.97 | 2.037 | Over-range | 60 | 22373 | 18815 | 19798 | 60986 | - - - | - - - | - - - | - - - | 22373 | 18815 | 19798 | 60986 | 2009 | 1682 | 4623 | 8314 | - - - | - - - | - - - | - - - | 2009 | 1682 | 4623 | 8314 | 24804 | 21316 | 23098 | 69217 | # # # | # # # | # # # | # # # | 0.902 | 0.883 | 0.857 | 0.881 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.974 | 0.989 | - - - | 0.136 | 1.77 | 1.76 | 1.85 | 1.68 | 1.8 | 1.83 | 47.19 | 52.53 | 54.11 | 0 | - - - | - - - | - - - | - - - | 24804 | 21316 | 23098 | 69217 | Over-range | 10703 | 10015 | 11893 | 32726 | 10513 | 9873 | 10958 | 31652 | 22329 | 18775 | 19758 | 60862 | 22329 | 18775 | 19758 | 60862 | - - - | - - - | - - - | - - -
5/4/2026 | 12:15:00 PM | 279.56 | 276.23 | 276.81 | 483.41 | 476.87 | 481.8 | 86.3515 | 75.8267 | 80.8228 | 2.376 | 1.432 | 1.433 | 1.431 | 2.005 | 1.96 | 2.026 | Over-range | 59.99 | 21756 | 18493 | 19221 | 59470 | - - - | - - - | - - - | - - - | 21756 | 18493 | 19221 | 59470 | 2030 | 1563 | 4369 | 7961 | - - - | - - - | - - - | - - - | 2030 | 1563 | 4369 | 7961 | 24096 | 20912 | 22338 | 67346 | # # # | # # # | # # # | # # # | 0.903 | 0.884 | 0.861 | 0.883 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.975 | 0.989 | - - - | 0.134 | 1.61 | 1.58 | 1.66 | 1.51 | 1.6 | 1.64 | 46.7 | 52.03 | 53.39 | 0 | - - - | - - - | - - - | - - - | 24096 | 20912 | 22338 | 67346 | Over-range | 10346 | 9756 | 11373 | 31578 | 10144 | 9629 | 10500 | 30557 | 21713 | 18465 | 19188 | 59366 | 21713 | 18465 | 19188 | 59366 | - - - | - - - | - - - | - - -
5/4/2026 | 12:30:00 PM | 279.6 | 276.25 | 276.86 | 483.46 | 476.92 | 481.89 | 85.7802 | 74.7195 | 79.8593 | 2.3659 | 1.433 | 1.434 | 1.433 | 2.027 | 1.985 | 2.059 | Over-range | 59.99 | 21473 | 18093 | 18808 | 58374 | - - - | - - - | - - - | - - - | 21473 | 18093 | 18808 | 58374 | 2029 | 1492 | 4425 | 7946 | - - - | - - - | - - - | - - - | 2029 | 1492 | 4425 | 7946 | 23924 | 20597 | 22059 | 66580 | # # # | # # # | # # # | # # # | 0.898 | 0.878 | 0.853 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.989 | - - - | 0.136 | 1.51 | 1.47 | 1.54 | 1.4 | 1.47 | 1.53 | 48.19 | 53.68 | 55.15 | 0 | - - - | - - - | - - - | - - - | 23924 | 20597 | 22059 | 66580 | Over-range | 10541 | 9839 | 11519 | 32004 | 10344 | 9725 | 10635 | 31002 | 21434 | 18068 | 18782 | 58284 | 21434 | 18068 | 18782 | 58284 | - - - | - - - | - - - | - - -
5/4/2026 | 12:45:00 PM | 278.91 | 275.53 | 276.14 | 482.24 | 475.66 | 480.69 | 79.3289 | 68.9338 | 73.6622 | 2.143 | 1.431 | 1.432 | 1.431 | 2.031 | 1.983 | 2.061 | Over-range | 59.98 | 19814 | 16628 | 17268 | 53710 | - - - | - - - | - - - | - - - | 19814 | 16628 | 17268 | 53710 | 1856 | 1284 | 4086 | 7225 | - - - | - - - | - - - | - - - | 1856 | 1284 | 4086 | 7225 | 22046 | 18934 | 20280 | 61260 | # # # | # # # | # # # | # # # | 0.899 | 0.878 | 0.852 | 0.877 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.135 | 1.49 | 1.45 | 1.52 | 1.38 | 1.45 | 1.5 | 47.81 | 53.76 | 55.36 | 0 | - - - | - - - | - - - | - - - | 22046 | 18934 | 20280 | 61260 | Over-range | 9658 | 9050 | 10628 | 29444 | 9478 | 8959 | 9812 | 28543 | 19775 | 16607 | 17242 | 53624 | 19775 | 16607 | 17242 | 53624 | - - - | - - - | - - - | - - -
5/4/2026 | 1:00:00 PM | 279.12 | 275.9 | 276.53 | 482.69 | 476.42 | 481.16 | 79.6265 | 69.5253 | 74.0061 | 2.0672 | 1.432 | 1.432 | 1.431 | 2.038 | 1.994 | 2.065 | Over-range | 59.98 | 19846 | 16755 | 17356 | 53956 | - - - | - - - | - - - | - - - | 19846 | 16755 | 17356 | 53956 | 1932 | 1329 | 4068 | 7329 | - - - | - - - | - - - | - - - | 1932 | 1329 | 4068 | 7329 | 22162 | 19134 | 20419 | 61715 | # # # | # # # | # # # | # # # | 0.896 | 0.876 | 0.85 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.989 | - - - | 0.136 | 1.51 | 1.47 | 1.53 | 1.41 | 1.46 | 1.52 | 48.65 | 54.44 | 55.89 | 0 | - - - | - - - | - - - | - - - | 22162 | 19134 | 20419 | 61715 | Over-range | 9854 | 9236 | 10750 | 29938 | 9663 | 9140 | 9950 | 29027 | 19805 | 16730 | 17330 | 53865 | 19805 | 16730 | 17330 | 53865 | - - - | - - - | - - - | - - -
5/4/2026 | 1:15:00 PM | 279.16 | 275.87 | 276.44 | 482.75 | 476.26 | 481.12 | 80.2881 | 69.8303 | 74.1403 | 2.2152 | 1.432 | 1.432 | 1.432 | 2.043 | 2.012 | 2.085 | Over-range | 59.98 | 19986 | 16814 | 17300 | 54100 | - - - | - - - | - - - | - - - | 19986 | 16814 | 17300 | 54100 | 1998 | 1266 | 4153 | 7417 | - - - | - - - | - - - | - - - | 1998 | 1266 | 4153 | 7417 | 22357 | 19221 | 20451 | 62030 | # # # | # # # | # # # | # # # | 0.894 | 0.875 | 0.846 | 0.872 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.137 | 1.49 | 1.45 | 1.52 | 1.39 | 1.44 | 1.5 | 49.07 | 54.78 | 56.75 | 0 | - - - | - - - | - - - | - - - | 22357 | 19221 | 20451 | 62030 | Over-range | 10012 | 9310 | 10902 | 30330 | 9811 | 9224 | 10079 | 29409 | 19946 | 16791 | 17274 | 54011 | 19946 | 16791 | 17274 | 54011 | - - - | - - - | - - - | - - -
5/4/2026 | 1:30:00 PM | 278.89 | 275.56 | 276.19 | 482.22 | 475.76 | 480.7 | 78.0082 | 67.928 | 72.3678 | 2.1328 | 1.431 | 1.432 | 1.431 | 2.039 | 1.991 | 2.068 | Over-range | 59.98 | 19439 | 16358 | 16925 | 52722 | - - - | - - - | - - - | - - - | 19439 | 16358 | 16925 | 52722 | 1867 | 1261 | 4003 | 7132 | - - - | - - - | - - - | - - - | 1867 | 1261 | 4003 | 7132 | 21678 | 18659 | 19928 | 60265 | # # # | # # # | # # # | # # # | 0.897 | 0.877 | 0.849 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.989 | - - - | 0.135 | 1.48 | 1.44 | 1.51 | 1.37 | 1.44 | 1.49 | 48.31 | 54.17 | 55.93 | 0 | - - - | - - - | - - - | - - - | 21678 | 18659 | 19928 | 60265 | Over-range | 9584 | 8971 | 10512 | 29172 | 9400 | 8882 | 9720 | 28286 | 19400 | 16338 | 16899 | 52636 | 19400 | 16338 | 16899 | 52636 | - - - | - - - | - - - | - - -
5/4/2026 | 1:45:00 PM | 278.92 | 275.61 | 276.24 | 482.28 | 475.85 | 480.77 | 81.1357 | 70.6432 | 75.0703 | 2.3878 | 1.433 | 1.433 | 1.432 | 2.048 | 2.015 | 2.088 | Over-range | 59.98 | 20136 | 16961 | 17465 | 54562 | - - - | - - - | - - - | - - - | 20136 | 16961 | 17465 | 54562 | 2018 | 1349 | 4226 | 7594 | - - - | - - - | - - - | - - - | 2018 | 1349 | 4226 | 7594 | 22581 | 19432 | 20695 | 62708 | # # # | # # # | # # # | # # # | 0.892 | 0.873 | 0.844 | 0.87 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.139 | 1.5 | 1.47 | 1.54 | 1.4 | 1.47 | 1.52 | 49.72 | 55.24 | 57.23 | 0 | - - - | - - - | - - - | - - - | 22581 | 19432 | 20695 | 62708 | Over-range | 10212 | 9480 | 11099 | 30895 | 10011 | 9383 | 10263 | 29947 | 20097 | 16938 | 17435 | 54470 | 20097 | 16938 | 17435 | 54470 | - - - | - - - | - - - | - - -
5/4/2026 | 2:00:00 PM | 278.92 | 275.64 | 276.2 | 482.34 | 475.84 | 480.71 | 78.7145 | 68.4976 | 72.9895 | 2.1201 | 1.432 | 1.433 | 1.432 | 2.03 | 1.989 | 2.061 | Over-range | 59.99 | 19643 | 16515 | 17106 | 53263 | - - - | - - - | - - - | - - - | 19643 | 16515 | 17106 | 53263 | 1871 | 1281 | 4027 | 7178 | - - - | - - - | - - - | - - - | 1871 | 1281 | 4027 | 7178 | 21879 | 18825 | 20102 | 60806 | # # # | # # # | # # # | # # # | 0.898 | 0.877 | 0.851 | 0.876 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.989 | - - - | 0.135 | 1.5 | 1.47 | 1.53 | 1.4 | 1.46 | 1.52 | 48.01 | 54 | 55.54 | 0 | - - - | - - - | - - - | - - - | 21879 | 18825 | 20102 | 60806 | Over-range | 9625 | 9030 | 10551 | 29309 | 9441 | 8938 | 9752 | 28417 | 19606 | 16492 | 17080 | 53178 | 19606 | 16492 | 17080 | 53178 | - - - | - - - | - - - | - - -
5/4/2026 | 2:15:00 PM | 278.56 | 275.12 | 275.78 | 481.57 | 474.97 | 480.11 | 82.1354 | 70.802 | 76.264 | 1.9596 | 1.433 | 1.433 | 1.433 | 2.047 | 2.011 | 2.083 | Over-range | 59.98 | 20399 | 16965 | 17763 | 55127 | - - - | - - - | - - - | - - - | 20399 | 16965 | 17763 | 55127 | 1918 | 1327 | 4269 | 7514 | - - - | - - - | - - - | - - - | 1918 | 1327 | 4269 | 7514 | 22833 | 19443 | 20998 | 63274 | # # # | # # # | # # # | # # # | 0.893 | 0.873 | 0.846 | 0.871 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.972 | 0.988 | - - - | 0.136 | 1.52 | 1.5 | 1.57 | 1.42 | 1.5 | 1.55 | 49.36 | 55.33 | 56.71 | 0 | - - - | - - - | - - - | - - - | 22833 | 19443 | 20998 | 63274 | Over-range | 10251 | 9496 | 11191 | 31043 | 10070 | 9402 | 10345 | 30120 | 20359 | 16944 | 17737 | 55039 | 20359 | 16944 | 17737 | 55039 | - - - | - - - | - - - | - - -
5/4/2026 | 2:30:00 PM | 278.84 | 275.48 | 276.12 | 482.1 | 475.61 | 480.62 | 80.805 | 70.0367 | 75.2026 | 2.0193 | 1.433 | 1.434 | 1.433 | 2.035 | 1.989 | 2.061 | Over-range | 59.98 | 20168 | 16871 | 17647 | 54686 | - - - | - - - | - - - | - - - | 20168 | 16871 | 17647 | 54686 | 1847 | 1340 | 4142 | 7329 | - - - | - - - | - - - | - - - | 1847 | 1340 | 4142 | 7329 | 22468 | 19244 | 20715 | 62427 | # # # | # # # | # # # | # # # | 0.898 | 0.877 | 0.852 | 0.876 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.134 | 1.54 | 1.5 | 1.58 | 1.44 | 1.51 | 1.56 | 48.17 | 54.16 | 55.34 | 0 | - - - | - - - | - - - | - - - | 22468 | 19244 | 20715 | 62427 | Over-range | 9893 | 9253 | 10843 | 30091 | 9719 | 9155 | 10020 | 29184 | 20134 | 16846 | 17623 | 54603 | 20134 | 16846 | 17623 | 54603 | - - - | - - - | - - - | - - -
5/4/2026 | 2:45:00 PM | 279.09 | 275.76 | 276.36 | 482.56 | 476.07 | 481.02 | 82.193 | 71.1518 | 76.6027 | 1.9366 | 1.434 | 1.434 | 1.433 | 2.032 | 1.988 | 2.059 | Over-range | 59.98 | 20546 | 17163 | 18013 | 55722 | - - - | - - - | - - - | - - - | 20546 | 17163 | 18013 | 55722 | 1893 | 1346 | 4231 | 7470 | - - - | - - - | - - - | - - - | 1893 | 1346 | 4231 | 7470 | 22882 | 19577 | 21125 | 63585 | # # # | # # # | # # # | # # # | 0.898 | 0.877 | 0.853 | 0.876 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.134 | 1.56 | 1.52 | 1.6 | 1.46 | 1.52 | 1.58 | 48.03 | 54.16 | 55.08 | 0 | - - - | - - - | - - - | - - - | 22882 | 19577 | 21125 | 63585 | Over-range | 10063 | 9414 | 11030 | 30609 | 9882 | 9317 | 10187 | 29683 | 20514 | 17138 | 17990 | 55642 | 20514 | 17138 | 17990 | 55642 | - - - | - - - | - - - | - - -
5/4/2026 | 3:00:00 PM | 279.09 | 275.73 | 276.33 | 482.56 | 476.01 | 481.01 | 83.0598 | 71.7509 | 77.3561 | 2.0284 | 1.433 | 1.434 | 1.433 | 2.036 | 1.993 | 2.066 | Over-range | 59.98 | 20755 | 17305 | 18164 | 56225 | - - - | - - - | - - - | - - - | 20755 | 17305 | 18164 | 56225 | 1908 | 1352 | 4311 | 7571 | - - - | - - - | - - - | - - - | 1908 | 1352 | 4311 | 7571 | 23129 | 19746 | 21336 | 64211 | # # # | # # # | # # # | # # # | 0.897 | 0.876 | 0.851 | 0.876 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.135 | 1.55 | 1.51 | 1.58 | 1.45 | 1.51 | 1.57 | 48.22 | 54.25 | 55.32 | 0 | - - - | - - - | - - - | - - - | 23129 | 19746 | 21336 | 64211 | Over-range | 10201 | 9506 | 11187 | 30999 | 10021 | 9409 | 10323 | 30061 | 20726 | 17283 | 18142 | 56151 | 20726 | 17283 | 18142 | 56151 | - - - | - - - | - - - | - - -
5/4/2026 | 3:15:00 PM | 279 | 275.7 | 276.25 | 482.46 | 475.92 | 480.83 | 81.8219 | 71.0166 | 76.0076 | 2.0533 | 1.433 | 1.433 | 1.433 | 2.019 | 1.976 | 2.049 | Over-range | 59.99 | 20502 | 17192 | 17921 | 55615 | - - - | - - - | - - - | - - - | 20502 | 17192 | 17921 | 55615 | 1876 | 1309 | 4158 | 7343 | - - - | - - - | - - - | - - - | 1876 | 1309 | 4158 | 7343 | 22752 | 19521 | 20939 | 63211 | # # # | # # # | # # # | # # # | 0.901 | 0.881 | 0.856 | 0.88 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.974 | 0.989 | - - - | 0.132 | 1.55 | 1.51 | 1.59 | 1.45 | 1.51 | 1.57 | 47.1 | 53.05 | 54.3 | 0 | - - - | - - - | - - - | - - - | 22752 | 19521 | 20939 | 63211 | Over-range | 9855 | 9242 | 10822 | 30024 | 9674 | 9148 | 9991 | 29112 | 20470 | 17171 | 17899 | 55540 | 20470 | 17171 | 17899 | 55540 | - - - | - - - | - - - | - - -
5/4/2026 | 3:30:00 PM | 278.61 | 275.29 | 275.86 | 481.77 | 475.23 | 480.16 | 84.6045 | 73.2971 | 78.6238 | 1.9413 | 1.433 | 1.434 | 1.433 | 2.029 | 1.996 | 2.063 | Over-range | 59.97 | 21103 | 17666 | 18463 | 57232 | - - - | - - - | - - - | - - - | 21103 | 17666 | 18463 | 57232 | 1979 | 1366 | 4308 | 7653 | - - - | - - - | - - - | - - - | 1979 | 1366 | 4308 | 7653 | 23523 | 20141 | 21654 | 65317 | # # # | # # # | # # # | # # # | 0.897 | 0.877 | 0.853 | 0.876 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.974 | 0.989 | - - - | 0.134 | 1.54 | 1.5 | 1.58 | 1.44 | 1.51 | 1.56 | 48.24 | 54.04 | 55.17 | 0 | - - - | - - - | - - - | - - - | 23523 | 20141 | 21654 | 65317 | Over-range | 10385 | 9669 | 11309 | 31464 | 10194 | 9572 | 10456 | 30519 | 21071 | 17646 | 18442 | 57159 | 21071 | 17646 | 18442 | 57159 | - - - | - - - | - - - | - - -
5/4/2026 | 3:45:00 PM | 278.79 | 275.43 | 275.95 | 482.08 | 475.39 | 480.4 | 81.9088 | 70.8057 | 76.1249 | 1.91 | 1.433 | 1.433 | 1.433 | 2.021 | 1.98 | 2.052 | Over-range | 59.99 | 20527 | 17118 | 17927 | 55572 | - - - | - - - | - - - | - - - | 20527 | 17118 | 17927 | 55572 | 1844 | 1271 | 4178 | 7293 | - - - | - - - | - - - | - - - | 1844 | 1271 | 4178 | 7293 | 22768 | 19449 | 20954 | 63172 | # # # | # # # | # # # | # # # | 0.902 | 0.88 | 0.856 | 0.88 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.974 | 0.989 | - - - | 0.131 | 1.53 | 1.49 | 1.57 | 1.43 | 1.49 | 1.55 | 47.01 | 53.25 | 54.34 | 0 | - - - | - - - | - - - | - - - | 22768 | 19449 | 20954 | 63172 | Over-range | 9839 | 9229 | 10843 | 30021 | 9665 | 9141 | 10006 | 29121 | 20493 | 17097 | 17908 | 55497 | 20493 | 17097 | 17908 | 55497 | - - - | - - - | - - - | - - -
5/4/2026 | 4:00:00 PM | 278.76 | 275.3 | 275.87 | 481.94 | 475.17 | 480.35 | 84.3854 | 72.7261 | 78.4057 | 2.2131 | 1.434 | 1.435 | 1.434 | 2.034 | 1.999 | 2.073 | Over-range | 59.98 | 21082 | 17538 | 18377 | 56997 | - - - | - - - | - - - | - - - | 21082 | 17538 | 18377 | 56997 | 1937 | 1322 | 4409 | 7668 | - - - | - - - | - - - | - - - | 1937 | 1322 | 4409 | 7668 | 23473 | 19985 | 21593 | 65050 | # # # | # # # | # # # | # # # | 0.898 | 0.878 | 0.851 | 0.876 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.972 | 0.988 | - - - | 0.135 | 1.56 | 1.52 | 1.6 | 1.45 | 1.52 | 1.59 | 48.01 | 53.98 | 55.28 | 0 | - - - | - - - | - - - | - - - | 23473 | 19985 | 21593 | 65050 | Over-range | 10312 | 9578 | 11331 | 31334 | 10129 | 9486 | 10438 | 30381 | 21049 | 17517 | 18352 | 56918 | 21049 | 17517 | 18352 | 56918 | - - - | - - - | - - - | - - -
5/4/2026 | 4:15:00 PM | 278.44 | 275.06 | 275.67 | 481.41 | 474.83 | 479.9 | 81.2147 | 70.3602 | 75.8891 | 2.189 | 1.433 | 1.434 | 1.433 | 2.032 | 1.982 | 2.057 | Over-range | 59.97 | 20285 | 16954 | 17824 | 55062 | - - - | - - - | - - - | - - - | 20285 | 16954 | 17824 | 55062 | 1825 | 1333 | 4205 | 7363 | - - - | - - - | - - - | - - - | 1825 | 1333 | 4205 | 7363 | 22548 | 19302 | 20872 | 62722 | # # # | # # # | # # # | # # # | 0.9 | 0.878 | 0.854 | 0.878 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.134 | 1.54 | 1.5 | 1.59 | 1.44 | 1.51 | 1.57 | 47.56 | 53.65 | 54.65 | 0 | - - - | - - - | - - - | - - - | 22548 | 19302 | 20872 | 62722 | Over-range | 9836 | 9223 | 10853 | 30016 | 9664 | 9125 | 10006 | 29099 | 20254 | 16934 | 17802 | 54989 | 20254 | 16934 | 17802 | 54989 | - - - | - - - | - - - | - - -
5/4/2026 | 4:30:00 PM | 278.38 | 275.04 | 275.63 | 481.35 | 474.81 | 479.79 | 83.8783 | 72.8119 | 78.2119 | 2.2949 | 1.434 | 1.434 | 1.434 | 2.034 | 1.997 | 2.067 | Over-range | 59.98 | 20910 | 17538 | 18341 | 56789 | - - - | - - - | - - - | - - - | 20910 | 17538 | 18341 | 56789 | 1968 | 1379 | 4344 | 7691 | - - - | - - - | - - - | - - - | 1968 | 1379 | 4344 | 7691 | 23309 | 19992 | 21525 | 64827 | # # # | # # # | # # # | # # # | 0.897 | 0.877 | 0.852 | 0.876 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.135 | 1.55 | 1.52 | 1.6 | 1.45 | 1.52 | 1.58 | 48.27 | 54 | 55.17 | 0 | - - - | - - - | - - - | - - - | 23309 | 19992 | 21525 | 64827 | Over-range | 10293 | 9594 | 11262 | 31252 | 10103 | 9495 | 10391 | 30290 | 20876 | 17519 | 18317 | 56712 | 20876 | 17519 | 18317 | 56712 | - - - | - - - | - - - | - - -
5/4/2026 | 4:45:00 PM | 280.51 | 277.04 | 277.66 | 484.94 | 478.23 | 483.43 | 82.4443 | 71.2283 | 76.9011 | 2.2535 | 1.434 | 1.435 | 1.433 | 2.037 | 1.985 | 2.066 | Over-range | 59.98 | 20742 | 17292 | 18161 | 56195 | - - - | - - - | - - - | - - - | 20742 | 17292 | 18161 | 56195 | 1860 | 1345 | 4323 | 7527 | - - - | - - - | - - - | - - - | 1860 | 1345 | 4323 | 7527 | 23065 | 19688 | 21303 | 64056 | # # # | # # # | # # # | # # # | 0.899 | 0.878 | 0.853 | 0.877 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.134 | 1.56 | 1.51 | 1.6 | 1.45 | 1.52 | 1.58 | 47.67 | 53.67 | 54.89 | 0 | - - - | - - - | - - - | - - - | 23065 | 19688 | 21303 | 64056 | Over-range | 10078 | 9409 | 11127 | 30725 | 9904 | 9313 | 10253 | 29788 | 20709 | 17275 | 18143 | 56127 | 20709 | 17275 | 18143 | 56127 | - - - | - - - | - - - | - - -
5/4/2026 | 5:00:00 PM | 281.45 | 278.27 | 278.78 | 486.82 | 480.4 | 485.1 | 82.1973 | 71.6773 | 76.6041 | 2.1835 | 1.434 | 1.435 | 1.434 | 2.034 | 1.998 | 2.066 | Over-range | 59.98 | 20698 | 17458 | 18162 | 56317 | - - - | - - - | - - - | - - - | 20698 | 17458 | 18162 | 56317 | 2004 | 1360 | 4239 | 7603 | - - - | - - - | - - - | - - - | 2004 | 1360 | 4239 | 7603 | 23081 | 19902 | 21313 | 64296 | # # # | # # # | # # # | # # # | 0.897 | 0.877 | 0.852 | 0.876 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.974 | 0.989 | - - - | 0.135 | 1.58 | 1.54 | 1.61 | 1.48 | 1.54 | 1.6 | 48.26 | 53.99 | 55.31 | 0 | - - - | - - - | - - - | - - - | 23081 | 19902 | 21313 | 64296 | Over-range | 10205 | 9553 | 11148 | 31005 | 10006 | 9455 | 10311 | 30058 | 20663 | 17438 | 18140 | 56241 | 20663 | 17438 | 18140 | 56241 | - - - | - - - | - - - | - - -
5/4/2026 | 5:15:00 PM | 282.01 | 279.02 | 279.46 | 487.93 | 481.73 | 486.1 | 83.3563 | 73.6848 | 77.5506 | 2.3905 | 1.434 | 1.435 | 1.434 | 2.017 | 1.985 | 2.046 | Over-range | 60 | 21074 | 18069 | 18539 | 57682 | - - - | - - - | - - - | - - - | 21074 | 18069 | 18539 | 57682 | 2080 | 1487 | 4166 | 7734 | - - - | - - - | - - - | - - - | 2080 | 1487 | 4166 | 7734 | 23460 | 20520 | 21634 | 65614 | # # # | # # # | # # # | # # # | 0.898 | 0.881 | 0.857 | 0.879 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.989 | - - - | 0.134 | 1.54 | 1.51 | 1.56 | 1.46 | 1.5 | 1.55 | 47.82 | 53.03 | 54.49 | 0 | - - - | - - - | - - - | - - - | 23460 | 20520 | 21634 | 65614 | Over-range | 10299 | 9722 | 11146 | 31257 | 10086 | 9607 | 10338 | 30285 | 21036 | 18049 | 18513 | 57598 | 21036 | 18049 | 18513 | 57598 | - - - | - - - | - - - | - - -
5/4/2026 | 5:30:00 PM | 281.73 | 278.53 | 279.01 | 487.29 | 480.8 | 485.53 | 81.5609 | 71.3818 | 75.969 | 2.4384 | 1.434 | 1.434 | 1.434 | 2.027 | 1.976 | 2.05 | Over-range | 59.98 | 20627 | 17454 | 18096 | 56177 | - - - | - - - | - - - | - - - | 20627 | 17454 | 18096 | 56177 | 1877 | 1440 | 4184 | 7501 | - - - | - - - | - - - | - - - | 1877 | 1440 | 4184 | 7501 | 22914 | 19834 | 21148 | 63895 | # # # | # # # | # # # | # # # | 0.9 | 0.88 | 0.856 | 0.879 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.974 | 0.989 | - - - | 0.134 | 1.5 | 1.47 | 1.53 | 1.42 | 1.46 | 1.51 | 47.43 | 53.15 | 54.46 | 0 | - - - | - - - | - - - | - - - | 22914 | 19834 | 21148 | 63895 | Over-range | 9968 | 9415 | 10936 | 30421 | 9789 | 9304 | 10104 | 29482 | 20590 | 17429 | 18070 | 56089 | 20590 | 17429 | 18070 | 56089 | - - - | - - - | - - - | - - -
5/4/2026 | 5:45:00 PM | 281.77 | 278.61 | 279.06 | 487.41 | 480.93 | 485.58 | 84.0002 | 73.5458 | 77.6857 | 2.5689 | 1.434 | 1.435 | 1.435 | 2.03 | 2.003 | 2.071 | Over-range | 59.97 | 21185 | 17961 | 18438 | 57584 | - - - | - - - | - - - | - - - | 21185 | 17961 | 18438 | 57584 | 2049 | 1434 | 4323 | 7806 | - - - | - - - | - - - | - - - | 2049 | 1434 | 4323 | 7806 | 23626 | 20458 | 21646 | 65730 | # # # | # # # | # # # | # # # | 0.897 | 0.878 | 0.852 | 0.876 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.974 | 0.989 | - - - | 0.136 | 1.51 | 1.48 | 1.54 | 1.42 | 1.47 | 1.52 | 48.36 | 53.81 | 55.42 | 0 | - - - | - - - | - - - | - - - | 23626 | 20458 | 21646 | 65730 | Over-range | 10452 | 9791 | 11335 | 31680 | 10249 | 9685 | 10478 | 30703 | 21148 | 17940 | 18410 | 57498 | 21148 | 17940 | 18410 | 57498 | - - - | - - - | - - - | - - -
5/4/2026 | 6:00:00 PM | 282.07 | 278.93 | 279.41 | 487.93 | 481.54 | 486.16 | 80.3835 | 70.5641 | 74.9172 | 2.3526 | 1.433 | 1.433 | 1.433 | 2.025 | 1.973 | 2.045 | Over-range | 59.99 | 20371 | 17291 | 17908 | 55571 | - - - | - - - | - - - | - - - | 20371 | 17291 | 17908 | 55571 | 1863 | 1415 | 4088 | 7366 | - - - | - - - | - - - | - - - | 1863 | 1415 | 4088 | 7366 | 22605 | 19630 | 20883 | 63118 | # # # | # # # | # # # | # # # | 0.901 | 0.881 | 0.858 | 0.88 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.975 | 0.989 | - - - | 0.133 | 1.46 | 1.43 | 1.48 | 1.38 | 1.42 | 1.46 | 47.14 | 52.94 | 54.11 | 0 | - - - | - - - | - - - | - - - | 22605 | 19630 | 20883 | 63118 | Over-range | 9788 | 9289 | 10734 | 29909 | 9608 | 9180 | 9925 | 28988 | 20332 | 17272 | 17879 | 55483 | 20332 | 17272 | 17879 | 55483 | - - - | - - - | - - - | - - -
5/4/2026 | 6:15:00 PM | 282.99 | 279.89 | 280.26 | 489.61 | 483.09 | 487.64 | 83.8715 | 73.0971 | 77.498 | 2.458 | 1.433 | 1.432 | 1.433 | 2.041 | 2.011 | 2.084 | Over-range | 60 | 21235 | 17892 | 18407 | 57534 | - - - | - - - | - - - | - - - | 21235 | 17892 | 18407 | 57534 | 2051 | 1402 | 4382 | 7835 | - - - | - - - | - - - | - - - | 2051 | 1402 | 4382 | 7835 | 23689 | 20424 | 21686 | 65799 | # # # | # # # | # # # | # # # | 0.896 | 0.876 | 0.849 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.988 | - - - | 0.136 | 1.36 | 1.33 | 1.36 | 1.29 | 1.29 | 1.34 | 48.59 | 54.48 | 56.22 | 0 | - - - | - - - | - - - | - - - | 23689 | 20424 | 21686 | 65799 | Over-range | 10491 | 9848 | 11460 | 31911 | 10288 | 9747 | 10589 | 30935 | 21183 | 17860 | 18368 | 57412 | 21183 | 17860 | 18368 | 57412 | - - - | - - - | - - - | - - -
5/4/2026 | 6:30:00 PM | 283.2 | 280.18 | 280.51 | 490.05 | 483.59 | 488 | 81.5357 | 71.3505 | 75.4079 | 2.5723 | 1.432 | 1.431 | 1.433 | 2.034 | 1.996 | 2.072 | Over-range | 59.97 | 20710 | 17521 | 17974 | 56206 | - - - | - - - | - - - | - - - | 20710 | 17521 | 17974 | 56206 | 1979 | 1361 | 4249 | 7590 | - - - | - - - | - - - | - - - | 1979 | 1361 | 4249 | 7590 | 23024 | 19940 | 21102 | 64066 | # # # | # # # | # # # | # # # | 0.9 | 0.879 | 0.852 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.989 | - - - | 0.135 | 1.34 | 1.3 | 1.32 | 1.27 | 1.26 | 1.31 | 47.67 | 53.71 | 55.47 | 0 | - - - | - - - | - - - | - - - | 23024 | 19940 | 21102 | 64066 | Over-range | 10049 | 9513 | 11049 | 30726 | 9852 | 9415 | 10199 | 29774 | 20663 | 17493 | 17930 | 56086 | 20663 | 17493 | 17930 | 56086 | - - - | - - - | - - - | - - -
5/4/2026 | 6:45:00 PM | 282.92 | 279.87 | 280.21 | 489.52 | 483.05 | 487.52 | 83.1207 | 72.4296 | 76.7816 | 2.5423 | 1.433 | 1.431 | 1.433 | 2.041 | 2.009 | 2.085 | Over-range | 59.97 | 21067 | 17742 | 18245 | 57055 | - - - | - - - | - - - | - - - | 21067 | 17742 | 18245 | 57055 | 2005 | 1364 | 4357 | 7726 | - - - | - - - | - - - | - - - | 2005 | 1364 | 4357 | 7726 | 23467 | 20231 | 21477 | 65175 | # # # | # # # | # # # | # # # | 0.898 | 0.877 | 0.85 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.135 | 1.35 | 1.3 | 1.32 | 1.27 | 1.26 | 1.32 | 48.23 | 54.24 | 55.99 | 0 | - - - | - - - | - - - | - - - | 23467 | 20231 | 21477 | 65175 | Over-range | 10328 | 9719 | 11325 | 31489 | 10131 | 9623 | 10453 | 30526 | 21014 | 17711 | 18205 | 56931 | 21014 | 17711 | 18205 | 56931 | - - - | - - - | - - - | - - -
5/4/2026 | 7:00:00 PM | 283.08 | 280.17 | 280.38 | 489.96 | 483.5 | 487.72 | 81.3853 | 71.2508 | 74.7415 | 2.5023 | 1.432 | 1.43 | 1.432 | 2.037 | 2.021 | 2.094 | Over-range | 59.98 | 20603 | 17467 | 17710 | 55780 | - - - | - - - | - - - | - - - | 20603 | 17467 | 17710 | 55780 | 2131 | 1246 | 4241 | 7618 | - - - | - - - | - - - | - - - | 2131 | 1246 | 4241 | 7618 | 22976 | 19914 | 20909 | 63800 | # # # | # # # | # # # | # # # | 0.897 | 0.877 | 0.847 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.137 | 1.27 | 1.23 | 1.23 | 1.21 | 1.17 | 1.22 | 48.38 | 54.32 | 56.72 | 0 | - - - | - - - | - - - | - - - | 22976 | 19914 | 20909 | 63800 | Over-range | 10160 | 9561 | 11110 | 30950 | 9934 | 9479 | 10269 | 29998 | 20548 | 17436 | 17661 | 55645 | 20548 | 17436 | 17661 | 55645 | - - - | - - - | - - - | - - -
5/4/2026 | 7:15:00 PM | 283.62 | 280.76 | 280.99 | 490.92 | 484.57 | 488.71 | 81.6907 | 71.393 | 75.2639 | 2.3686 | 1.433 | 1.43 | 1.432 | 2.039 | 2.015 | 2.091 | Over-range | 59.99 | 20750 | 17550 | 17904 | 56204 | - - - | - - - | - - - | - - - | 20750 | 17550 | 17904 | 56204 | 2096 | 1252 | 4269 | 7618 | - - - | - - - | - - - | - - - | 2096 | 1252 | 4269 | 7618 | 23109 | 19997 | 21102 | 64208 | # # # | # # # | # # # | # # # | 0.898 | 0.878 | 0.849 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.988 | - - - | 0.136 | 1.29 | 1.24 | 1.24 | 1.23 | 1.18 | 1.24 | 48.09 | 54.19 | 56.37 | 0 | - - - | - - - | - - - | - - - | 23109 | 19997 | 21102 | 64208 | Over-range | 10161 | 9581 | 11162 | 31025 | 9942 | 9498 | 10313 | 30075 | 20694 | 17513 | 17856 | 56063 | 20694 | 17513 | 17856 | 56063 | - - - | - - - | - - - | - - -
5/4/2026 | 7:30:00 PM | 283.83 | 281.04 | 281.2 | 491.36 | 485.02 | 489.03 | 82.4369 | 72.026 | 75.6657 | 2.3285 | 1.434 | 1.431 | 1.433 | 2.037 | 2.026 | 2.099 | Over-range | 59.97 | 20930 | 17715 | 17972 | 56617 | - - - | - - - | - - - | - - - | 20930 | 17715 | 17972 | 56617 | 2194 | 1221 | 4312 | 7727 | - - - | - - - | - - - | - - - | 2194 | 1221 | 4312 | 7727 | 23348 | 20204 | 21239 | 64791 | # # # | # # # | # # # | # # # | 0.896 | 0.877 | 0.846 | 0.874 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.972 | 0.988 | - - - | 0.137 | 1.31 | 1.25 | 1.24 | 1.24 | 1.18 | 1.24 | 48.46 | 54.46 | 56.98 | 0 | - - - | - - - | - - - | - - - | 23348 | 20204 | 21239 | 64791 | Over-range | 10337 | 9710 | 11313 | 31483 | 10101 | 9633 | 10459 | 30520 | 20872 | 17683 | 17919 | 56474 | 20872 | 17683 | 17919 | 56474 | - - - | - - - | - - - | - - -
5/4/2026 | 7:45:00 PM | 284.06 | 281.37 | 281.44 | 491.86 | 485.54 | 489.38 | 79.7392 | 69.8779 | 72.994 | 2.1804 | 1.433 | 1.43 | 1.432 | 2.026 | 2.017 | 2.09 | Over-range | 59.98 | 20302 | 17240 | 17381 | 54923 | - - - | - - - | - - - | - - - | 20302 | 17240 | 17381 | 54923 | 2165 | 1129 | 4117 | 7411 | - - - | - - - | - - - | - - - | 2165 | 1129 | 4117 | 7411 | 22582 | 19607 | 20490 | 62680 | # # # | # # # | # # # | # # # | 0.899 | 0.879 | 0.848 | 0.876 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.973 | 0.989 | - - - | 0.135 | 1.3 | 1.24 | 1.22 | 1.24 | 1.17 | 1.23 | 47.66 | 53.84 | 56.55 | 0 | - - - | - - - | - - - | - - - | 22582 | 19607 | 20490 | 62680 | Over-range | 9877 | 9335 | 10844 | 30181 | 9636 | 9267 | 10032 | 29257 | 20241 | 17203 | 17329 | 54773 | 20241 | 17203 | 17329 | 54773 | - - - | - - - | - - - | - - -
5/4/2026 | 8:00:00 PM | 284.56 | 281.91 | 281.99 | 492.75 | 486.52 | 490.28 | 82.0949 | 72.024 | 75.0443 | 2.3107 | 1.434 | 1.431 | 1.432 | 2.033 | 2.031 | 2.1 | Over-range | 59.98 | 20882 | 17766 | 17864 | 56512 | - - - | - - - | - - - | - - - | 20882 | 17766 | 17864 | 56512 | 2280 | 1206 | 4271 | 7757 | - - - | - - - | - - - | - - - | 2280 | 1206 | 4271 | 7757 | 23308 | 20263 | 21127 | 64697 | # # # | # # # | # # # | # # # | 0.896 | 0.877 | 0.846 | 0.874 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.972 | 0.988 | - - - | 0.137 | 1.32 | 1.26 | 1.24 | 1.25 | 1.18 | 1.25 | 48.54 | 54.55 | 57.24 | 0 | - - - | - - - | - - - | - - - | 23308 | 20263 | 21127 | 64697 | Over-range | 10342 | 9740 | 11272 | 31477 | 10087 | 9665 | 10432 | 30506 | 20818 | 17726 | 17807 | 56351 | 20818 | 17726 | 17807 | 56351 | - - - | - - - | - - - | - - -
5/4/2026 | 8:15:00 PM | 284.9 | 282.27 | 282.31 | 493.38 | 487.12 | 490.84 | 79.9518 | 70.2872 | 72.9536 | 2.2582 | 1.433 | 1.429 | 1.431 | 2.029 | 2.026 | 2.1 | Over-range | 59.97 | 20377 | 17380 | 17372 | 55129 | - - - | - - - | - - - | - - - | 20377 | 17380 | 17372 | 55129 | 2264 | 1135 | 4128 | 7528 | - - - | - - - | - - - | - - - | 2264 | 1135 | 4128 | 7528 | 22710 | 19787 | 20543 | 63041 | # # # | # # # | # # # | # # # | 0.897 | 0.878 | 0.846 | 0.875 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.973 | 0.988 | - - - | 0.137 | 1.29 | 1.23 | 1.22 | 1.23 | 1.16 | 1.22 | 48.1 | 54.12 | 57.3 | 0 | - - - | - - - | - - - | - - - | 22710 | 19787 | 20543 | 63041 | Over-range | 10015 | 9453 | 10958 | 30554 | 9756 | 9385 | 10151 | 29612 | 20310 | 17345 | 17315 | 54969 | 20310 | 17345 | 17315 | 54969 | - - - | - - - | - - - | - - -
5/4/2026 | 8:30:00 PM | 284.73 | 282.05 | 282.03 | 493.08 | 486.63 | 490.45 | 80.7466 | 70.7482 | 73.2145 | 2.2826 | 1.433 | 1.429 | 1.431 | 2.03 | 2.042 | 2.115 | Over-range | 59.98 | 20533 | 17462 | 17352 | 55347 | - - - | - - - | - - - | - - - | 20533 | 17462 | 17352 | 55347 | 2338 | 1062 | 4186 | 7586 | - - - | - - - | - - - | - - - | 2338 | 1062 | 4186 | 7586 | 22921 | 19901 | 20596 | 63419 | # # # | # # # | # # # | # # # | 0.896 | 0.877 | 0.843 | 0.873 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.972 | 0.988 | - - - | 0.137 | 1.28 | 1.23 | 1.21 | 1.22 | 1.16 | 1.21 | 48.45 | 54.46 | 57.95 | 0 | - - - | - - - | - - - | - - - | 22921 | 19901 | 20596 | 63419 | Over-range | 10176 | 9543 | 11089 | 30942 | 9904 | 9483 | 10268 | 29997 | 20467 | 17422 | 17295 | 55184 | 20467 | 17422 | 17295 | 55184 | - - - | - - - | - - - | - - -
5/4/2026 | 8:45:00 PM | 284.74 | 282.04 | 282 | 493.1 | 486.58 | 490.44 | 81.717 | 71.5208 | 73.7087 | 2.2751 | 1.433 | 1.43 | 1.431 | 2.03 | 2.057 | 2.128 | Over-range | 59.98 | 20740 | 17628 | 17404 | 55772 | - - - | - - - | - - - | - - - | 20740 | 17628 | 17404 | 55772 | 2451 | 1020 | 4248 | 7719 | - - - | - - - | - - - | - - - | 2451 | 1020 | 4248 | 7719 | 23212 | 20128 | 20743 | 64083 | # # # | # # # | # # # | # # # | 0.893 | 0.876 | 0.839 | 0.87 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.971 | 0.988 | - - - | 0.138 | 1.28 | 1.24 | 1.21 | 1.22 | 1.16 | 1.21 | 49.01 | 54.97 | 58.8 | 0 | - - - | - - - | - - - | - - - | 23212 | 20128 | 20743 | 64083 | Over-range | 10412 | 9712 | 11282 | 31543 | 10119 | 9658 | 10452 | 30584 | 20674 | 17586 | 17350 | 55609 | 20674 | 17586 | 17350 | 55609 | - - - | - - - | - - - | - - -
5/4/2026 | 9:00:00 PM | 284.86 | 282.17 | 282.04 | 493.37 | 486.71 | 490.55 | 78.5243 | 68.7345 | 70.6865 | 2.1937 | 1.432 | 1.429 | 1.431 | 2.018 | 2.035 | 2.115 | Over-range | 59.98 | 20033 | 17017 | 16752 | 53802 | - - - | - - - | - - - | - - - | 20033 | 17017 | 16752 | 53802 | 2328 | 907 | 4052 | 7287 | - - - | - - - | - - - | - - - | 2328 | 907 | 4052 | 7287 | 22294 | 19336 | 19881 | 61511 | # # # | # # # | # # # | # # # | 0.899 | 0.88 | 0.843 | 0.875 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.972 | 0.988 | - - - | 0.135 | 1.29 | 1.23 | 1.22 | 1.22 | 1.16 | 1.22 | 47.58 | 53.81 | 57.9 | 0 | - - - | - - - | - - - | - - - | 22294 | 19336 | 19881 | 61511 | Over-range | 9770 | 9176 | 10700 | 29792 | 9488 | 9131 | 9903 | 28887 | 19969 | 16979 | 16695 | 53643 | 19969 | 16979 | 16695 | 53643 | - - - | - - - | - - - | - - -
5/4/2026 | 9:15:00 PM | 285.37 | 282.58 | 282.58 | 494.12 | 487.5 | 491.52 | 76.848 | 67.0657 | 69.15 | 2.1548 | 1.433 | 1.429 | 1.431 | 2.033 | 2.042 | 2.131 | Over-range | 59.99 | 19603 | 16621 | 16341 | 52565 | - - - | - - - | - - - | - - - | 19603 | 16621 | 16341 | 52565 | 2317 | 868 | 3990 | 7175 | - - - | - - - | - - - | - - - | 2317 | 868 | 3990 | 7175 | 21856 | 18895 | 19481 | 60232 | # # # | # # # | # # # | # # # | 0.897 | 0.88 | 0.839 | 0.873 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.971 | 0.988 | - - - | 0.137 | 1.31 | 1.25 | 1.24 | 1.24 | 1.19 | 1.24 | 48.02 | 53.95 | 58.84 | 0 | - - - | - - - | - - - | - - - | 21856 | 18895 | 19481 | 60232 | Over-range | 9651 | 8980 | 10600 | 29383 | 9368 | 8937 | 9820 | 28493 | 19539 | 16580 | 16284 | 52402 | 19539 | 16580 | 16284 | 52402 | - - - | - - - | - - - | - - -
5/4/2026 | 9:30:00 PM | 285.79 | 283.04 | 283.03 | 494.88 | 488.31 | 492.24 | 80.135 | 69.9536 | 71.5726 | 2.2426 | 1.433 | 1.43 | 1.432 | 2.039 | 2.082 | 2.159 | Over-range | 59.99 | 20331 | 17276 | 16801 | 54408 | - - - | - - - | - - - | - - - | 20331 | 17276 | 16801 | 54408 | 2584 | 889 | 4197 | 7670 | - - - | - - - | - - - | - - - | 2584 | 889 | 4197 | 7670 | 22845 | 19756 | 20215 | 62815 | # # # | # # # | # # # | # # # | 0.89 | 0.875 | 0.831 | 0.866 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.97 | 0.987 | - - - | 0.141 | 1.32 | 1.26 | 1.26 | 1.25 | 1.2 | 1.26 | 49.85 | 55.46 | 60.72 | 0 | - - - | - - - | - - - | - - - | 22845 | 19756 | 20215 | 62815 | Over-range | 10409 | 9579 | 11235 | 31376 | 10083 | 9537 | 10422 | 30424 | 20252 | 17234 | 16740 | 54225 | 20252 | 17234 | 16740 | 54225 | - - - | - - - | - - - | - - -
5/4/2026 | 9:45:00 PM | 285.04 | 282.28 | 282.31 | 493.55 | 487.04 | 490.99 | 78.0567 | 68.1136 | 70.0168 | 2.1923 | 1.432 | 1.429 | 1.431 | 2.042 | 2.064 | 2.149 | Over-range | 59.99 | 19795 | 16807 | 16432 | 53034 | - - - | - - - | - - - | - - - | 19795 | 16807 | 16432 | 53034 | 2437 | 872 | 4061 | 7370 | - - - | - - - | - - - | - - - | 2437 | 872 | 4061 | 7370 | 22171 | 19166 | 19704 | 61041 | # # # | # # # | # # # | # # # | 0.893 | 0.877 | 0.834 | 0.869 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.971 | 0.988 | - - - | 0.139 | 1.31 | 1.24 | 1.24 | 1.23 | 1.18 | 1.24 | 49.09 | 54.74 | 60.04 | 0 | - - - | - - - | - - - | - - - | 22171 | 19166 | 19704 | 61041 | Over-range | 9975 | 9206 | 10867 | 30201 | 9672 | 9164 | 10080 | 29287 | 19727 | 16765 | 16375 | 52866 | 19727 | 16765 | 16375 | 52866 | - - - | - - - | - - - | - - -
5/4/2026 | 10:00:00 PM | 284.14 | 281.46 | 281.43 | 492.07 | 485.6 | 489.41 | 76.3457 | 66.9257 | 68.4878 | 2.145 | 1.432 | 1.428 | 1.429 | 2.03 | 2.048 | 2.134 | Over-range | 59.99 | 19364 | 16517 | 16095 | 51976 | - - - | - - - | - - - | - - - | 19364 | 16517 | 16095 | 51976 | 2384 | 840 | 3910 | 7134 | - - - | - - - | - - - | - - - | 2384 | 840 | 3910 | 7134 | 21621 | 18779 | 19218 | 59619 | # # # | # # # | # # # | # # # | 0.896 | 0.879 | 0.838 | 0.872 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.971 | 0.988 | - - - | 0.137 | 1.3 | 1.23 | 1.22 | 1.22 | 1.17 | 1.23 | 48.27 | 54 | 59.29 | 0 | - - - | - - - | - - - | - - - | 21621 | 18779 | 19218 | 59619 | Over-range | 9605 | 8930 | 10496 | 29181 | 9304 | 8890 | 9741 | 28296 | 19294 | 16480 | 16039 | 51813 | 19294 | 16480 | 16039 | 51813 | - - - | - - - | - - - | - - -
5/4/2026 | 10:15:00 PM | 283.47 | 280.82 | 280.77 | 490.93 | 484.49 | 488.25 | 83.1837 | 72.6832 | 77.1248 | 2.1484 | 1.433 | 1.43 | 1.429 | 2.039 | 2 | 2.08 | Over-range | 59.99 | 21167 | 17867 | 18290 | 57324 | - - - | - - - | - - - | - - - | 21167 | 17867 | 18290 | 57324 | 2175 | 1378 | 4434 | 7987 | - - - | - - - | - - - | - - - | 2175 | 1378 | 4434 | 7987 | 23456 | 20313 | 21541 | 65310 | # # # | # # # | # # # | # # # | 0.902 | 0.88 | 0.849 | 0.878 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.139 | 1.48 | 1.44 | 1.43 | 1.42 | 1.4 | 1.43 | 47.03 | 53.78 | 56.29 | 0 | - - - | - - - | - - - | - - - | 23456 | 20313 | 21541 | 65310 | Over-range | 10096 | 9659 | 11374 | 31276 | 9858 | 9560 | 10474 | 30239 | 21085 | 17805 | 18223 | 57113 | 21085 | 17805 | 18223 | 57113 | - - - | - - - | - - - | - - -
5/4/2026 | 10:30:00 PM | 282.95 | 280.08 | 280.02 | 489.9 | 483.06 | 487.22 | 89.9767 | 77.4368 | 83.447 | 2.1848 | 1.434 | 1.431 | 1.43 | 2.054 | 2.021 | 2.103 | Over-range | 59.98 | 22897 | 18993 | 19737 | 61628 | - - - | - - - | - - - | - - - | 22897 | 18993 | 19737 | 61628 | 2228 | 1480 | 4968 | 8676 | - - - | - - - | - - - | - - - | 2228 | 1480 | 4968 | 8676 | 25418 | 21658 | 23334 | 70410 | # # # | # # # | # # # | # # # | 0.901 | 0.877 | 0.846 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.969 | 0.987 | - - - | 0.141 | 1.52 | 1.48 | 1.48 | 1.46 | 1.44 | 1.48 | 47.78 | 54.64 | 56.76 | 0 | - - - | - - - | - - - | - - - | 25418 | 21658 | 23334 | 70410 | Over-range | 11030 | 10405 | 12442 | 34039 | 10802 | 10299 | 11406 | 32915 | 22803 | 18929 | 19655 | 61387 | 22803 | 18929 | 19655 | 61387 | - - - | - - - | - - - | - - -
5/4/2026 | 10:45:00 PM | 283.49 | 280.65 | 280.55 | 490.89 | 484.03 | 488.11 | 90.5952 | 78.1202 | 83.7771 | 2.24 | 1.434 | 1.431 | 1.43 | 2.046 | 2.019 | 2.099 | Over-range | 59.98 | 23122 | 19228 | 19884 | 62234 | - - - | - - - | - - - | - - - | 23122 | 19228 | 19884 | 62234 | 2277 | 1476 | 4986 | 8738 | - - - | - - - | - - - | - - - | 2277 | 1476 | 4986 | 8738 | 25635 | 21890 | 23466 | 70991 | # # # | # # # | # # # | # # # | 0.902 | 0.878 | 0.847 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.987 | - - - | 0.14 | 1.53 | 1.49 | 1.48 | 1.47 | 1.45 | 1.49 | 47.39 | 54.24 | 56.4 | 0 | - - - | - - - | - - - | - - - | 25635 | 21890 | 23466 | 70991 | Over-range | 11059 | 10458 | 12455 | 34137 | 10822 | 10353 | 11413 | 32999 | 23035 | 19170 | 19787 | 61993 | 23035 | 19170 | 19787 | 61993 | - - - | - - - | - - - | - - -
5/4/2026 | 11:00:00 PM | 283.92 | 281.12 | 281.04 | 491.65 | 484.89 | 488.9 | 88.8589 | 77.0292 | 82.3821 | 2.2263 | 1.434 | 1.431 | 1.43 | 2.038 | 2.001 | 2.082 | Over-range | 60 | 22770 | 19040 | 19668 | 61478 | - - - | - - - | - - - | - - - | 22770 | 19040 | 19668 | 61478 | 2219 | 1480 | 4831 | 8531 | - - - | - - - | - - - | - - - | 2219 | 1480 | 4831 | 8531 | 25175 | 21613 | 23110 | 69898 | # # # | # # # | # # # | # # # | 0.905 | 0.881 | 0.851 | 0.879 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.139 | 1.54 | 1.53 | 1.5 | 1.5 | 1.47 | 1.51 | 46.62 | 53.49 | 55.65 | 0 | - - - | - - - | - - - | - - - | 25175 | 21613 | 23110 | 69898 | Over-range | 10725 | 10225 | 12128 | 33240 | 10493 | 10117 | 11124 | 32126 | 22687 | 18984 | 19569 | 61241 | 22687 | 18984 | 19569 | 61241 | - - - | - - - | - - - | - - -
5/4/2026 | 11:15:00 PM | 284.1 | 281.05 | 281.02 | 491.78 | 484.68 | 489.13 | 90.9637 | 77.7367 | 84.1384 | 2.1894 | 1.435 | 1.432 | 1.43 | 2.052 | 2.02 | 2.106 | Over-range | 59.97 | 23305 | 19157 | 19982 | 62443 | - - - | - - - | - - - | - - - | 23305 | 19157 | 19982 | 62443 | 2205 | 1430 | 5123 | 8759 | - - - | - - - | - - - | - - - | 2205 | 1430 | 5123 | 8759 | 25805 | 21819 | 23616 | 71240 | # # # | # # # | # # # | # # # | 0.903 | 0.878 | 0.846 | 0.876 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.968 | 0.987 | - - - | 0.14 | 1.57 | 1.53 | 1.54 | 1.51 | 1.51 | 1.54 | 47.25 | 54.48 | 56.48 | 0 | - - - | - - - | - - - | - - - | 25805 | 21819 | 23616 | 71240 | Over-range | 11073 | 10443 | 12584 | 34282 | 10851 | 10345 | 11493 | 33144 | 23198 | 19094 | 19897 | 62189 | 23198 | 19094 | 19897 | 62189 | - - - | - - - | - - - | - - -
5/4/2026 | 11:30:00 PM | 284.59 | 281.38 | 281.47 | 492.48 | 485.29 | 490.02 | 89.2018 | 75.8218 | 83.0006 | 2.1606 | 1.434 | 1.431 | 1.429 | 2.06 | 2.002 | 2.1 | Over-range | 60 | 22929 | 18698 | 19758 | 61385 | - - - | - - - | - - - | - - - | 22929 | 18698 | 19758 | 61385 | 2003 | 1438 | 5083 | 8525 | - - - | - - - | - - - | - - - | 2003 | 1438 | 5083 | 8525 | 25327 | 21295 | 23318 | 69940 | # # # | # # # | # # # | # # # | 0.905 | 0.878 | 0.847 | 0.878 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.968 | 0.987 | - - - | 0.139 | 1.56 | 1.53 | 1.54 | 1.5 | 1.51 | 1.53 | 46.69 | 54.41 | 56.04 | 0 | - - - | - - - | - - - | - - - | 25327 | 21295 | 23318 | 69940 | Over-range | 10745 | 10188 | 12375 | 33497 | 10556 | 10085 | 11283 | 32394 | 22842 | 18622 | 19671 | 61135 | 22842 | 18622 | 19671 | 61135 | - - - | - - - | - - - | - - -
5/4/2026 | 11:45:00 PM | 284.77 | 281.64 | 281.62 | 492.89 | 485.67 | 490.25 | 90.356 | 76.9961 | 83.5214 | 2.1769 | 1.435 | 1.432 | 1.43 | 2.056 | 2.021 | 2.111 | Over-range | 59.99 | 23204 | 18987 | 19847 | 62037 | - - - | - - - | - - - | - - - | 23204 | 18987 | 19847 | 62037 | 2169 | 1398 | 5139 | 8706 | - - - | - - - | - - - | - - - | 2169 | 1398 | 5139 | 8706 | 25685 | 21652 | 23488 | 70824 | # # # | # # # | # # # | # # # | 0.903 | 0.877 | 0.845 | 0.876 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.968 | 0.987 | - - - | 0.14 | 1.59 | 1.56 | 1.56 | 1.53 | 1.54 | 1.56 | 47.17 | 54.78 | 56.66 | 0 | - - - | - - - | - - - | - - - | 25685 | 21652 | 23488 | 70824 | Over-range | 11005 | 10404 | 12556 | 34153 | 10788 | 10310 | 11456 | 33025 | 23104 | 18919 | 19756 | 61778 | 23104 | 18919 | 19756 | 61778 | - - - | - - - | - - - | - - -
5/5/2026 | 12:00:00 AM | 284.97 | 281.9 | 281.84 | 493.3 | 486.1 | 490.59 | 90.0898 | 76.9534 | 83.2195 | 2.1961 | 1.434 | 1.431 | 1.429 | 2.056 | 2.024 | 2.112 | Over-range | 59.99 | 23138 | 18986 | 19775 | 61899 | - - - | - - - | - - - | - - - | 23138 | 18986 | 19775 | 61899 | 2210 | 1399 | 5114 | 8723 | - - - | - - - | - - - | - - - | 2210 | 1399 | 5114 | 8723 | 25627 | 21659 | 23421 | 70706 | # # # | # # # | # # # | # # # | 0.903 | 0.877 | 0.844 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.968 | 0.987 | - - - | 0.141 | 1.57 | 1.54 | 1.54 | 1.51 | 1.51 | 1.54 | 47.29 | 54.89 | 56.87 | 0 | - - - | - - - | - - - | - - - | 25627 | 21659 | 23421 | 70706 | Over-range | 11009 | 10421 | 12544 | 34161 | 10785 | 10327 | 11454 | 33029 | 23037 | 18916 | 19686 | 61639 | 23037 | 18916 | 19686 | 61639 | - - - | - - - | - - - | - - -
5/5/2026 | 12:15:00 AM | 285.01 | 281.87 | 281.78 | 493.35 | 485.97 | 490.57 | 89.3944 | 75.893 | 82.5167 | 2.1823 | 1.433 | 1.43 | 1.427 | 2.065 | 2.026 | 2.123 | Over-range | 59.98 | 22960 | 18716 | 19552 | 61228 | - - - | - - - | - - - | - - - | 22960 | 18716 | 19552 | 61228 | 2134 | 1339 | 5121 | 8594 | - - - | - - - | - - - | - - - | 2134 | 1339 | 5121 | 8594 | 25422 | 21353 | 23209 | 69984 | # # # | # # # | # # # | # # # | 0.903 | 0.876 | 0.842 | 0.875 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.967 | 0.987 | - - - | 0.14 | 1.55 | 1.54 | 1.52 | 1.5 | 1.5 | 1.52 | 47.27 | 54.93 | 57.2 | 0 | - - - | - - - | - - - | - - - | 25422 | 21353 | 23209 | 69984 | Over-range | 10904 | 10277 | 12499 | 33879 | 10693 | 10189 | 11402 | 32771 | 22852 | 18650 | 19462 | 60963 | 22852 | 18650 | 19462 | 60963 | - - - | - - - | - - - | - - -
5/5/2026 | 12:30:00 AM | 285.11 | 282.06 | 281.86 | 493.63 | 486.24 | 490.67 | 90.9991 | 77.343 | 83.4486 | 2.2396 | 1.433 | 1.43 | 1.427 | 2.066 | 2.051 | 2.14 | Over-range | 59.98 | 23322 | 19058 | 19709 | 62089 | - - - | - - - | - - - | - - - | 23322 | 19058 | 19709 | 62089 | 2306 | 1301 | 5212 | 8820 | - - - | - - - | - - - | - - - | 2306 | 1301 | 5212 | 8820 | 25906 | 21788 | 23492 | 71186 | # # # | # # # | # # # | # # # | 0.9 | 0.875 | 0.839 | 0.872 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.967 | 0.987 | - - - | 0.142 | 1.54 | 1.52 | 1.51 | 1.49 | 1.49 | 1.51 | 48.03 | 55.52 | 58.05 | 0 | - - - | - - - | - - - | - - - | 25906 | 21788 | 23492 | 71186 | Over-range | 11273 | 10557 | 12780 | 34808 | 11034 | 10476 | 11669 | 33672 | 23217 | 18981 | 19625 | 61823 | 23217 | 18981 | 19625 | 61823 | - - - | - - - | - - - | - - -
5/5/2026 | 12:45:00 AM | 285.4 | 282.2 | 282.08 | 494.01 | 486.48 | 491.18 | 88.876 | 75.223 | 81.9664 | 2.138 | 1.433 | 1.429 | 1.427 | 2.068 | 2.027 | 2.128 | Over-range | 59.99 | 22862 | 18567 | 19407 | 60836 | - - - | - - - | - - - | - - - | 22862 | 18567 | 19407 | 60836 | 2122 | 1286 | 5122 | 8530 | - - - | - - - | - - - | - - - | 2122 | 1286 | 5122 | 8530 | 25300 | 21184 | 23069 | 69552 | # # # | # # # | # # # | # # # | 0.904 | 0.876 | 0.841 | 0.875 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.967 | 0.987 | - - - | 0.14 | 1.55 | 1.53 | 1.5 | 1.49 | 1.49 | 1.5 | 47.13 | 54.97 | 57.38 | 0 | - - - | - - - | - - - | - - - | 25300 | 21184 | 23069 | 69552 | Over-range | 10824 | 10194 | 12465 | 33691 | 10614 | 10112 | 11363 | 32593 | 22744 | 18503 | 19319 | 60566 | 22744 | 18503 | 19319 | 60566 | - - - | - - - | - - - | - - -
5/5/2026 | 1:00:00 AM | 285.77 | 282.69 | 282.54 | 494.73 | 487.35 | 491.85 | 90.7032 | 77.0147 | 83.2664 | 2.2243 | 1.433 | 1.429 | 1.427 | 2.074 | 2.054 | 2.146 | Over-range | 59.99 | 23274 | 18998 | 19666 | 61939 | - - - | - - - | - - - | - - - | 23274 | 18998 | 19666 | 61939 | 2309 | 1317 | 5222 | 8848 | - - - | - - - | - - - | - - - | 2309 | 1317 | 5222 | 8848 | 25880 | 21742 | 23495 | 71117 | # # # | # # # | # # # | # # # | 0.899 | 0.874 | 0.837 | 0.871 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.966 | 0.986 | - - - | 0.143 | 1.56 | 1.54 | 1.52 | 1.5 | 1.5 | 1.52 | 48.27 | 55.74 | 58.54 | 0 | - - - | - - - | - - - | - - - | 25880 | 21742 | 23495 | 71117 | Over-range | 11309 | 10571 | 12851 | 34933 | 11070 | 10488 | 11742 | 33793 | 23173 | 18931 | 19563 | 61667 | 23173 | 18931 | 19563 | 61667 | - - - | - - - | - - - | - - -
5/5/2026 | 1:15:00 AM | 285.05 | 281.89 | 281.92 | 493.34 | 486.14 | 490.77 | 87.4829 | 74.5602 | 81.2543 | 2.1818 | 1.432 | 1.428 | 1.426 | 2.076 | 2.019 | 2.118 | Over-range | 59.98 | 22441 | 18366 | 19270 | 60077 | - - - | - - - | - - - | - - - | 22441 | 18366 | 19270 | 60077 | 2047 | 1419 | 4980 | 8447 | - - - | - - - | - - - | - - - | 2047 | 1419 | 4980 | 8447 | 24873 | 20974 | 22858 | 68705 | # # # | # # # | # # # | # # # | 0.902 | 0.876 | 0.843 | 0.874 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.968 | 0.987 | - - - | 0.141 | 1.53 | 1.52 | 1.48 | 1.48 | 1.48 | 1.48 | 47.54 | 55.07 | 57.24 | 0 | - - - | - - - | - - - | - - - | 24873 | 20974 | 22858 | 68705 | Over-range | 10717 | 10125 | 12287 | 33313 | 10519 | 10024 | 11233 | 32225 | 22341 | 18303 | 19169 | 59813 | 22341 | 18303 | 19169 | 59813 | - - - | - - - | - - - | - - -
5/5/2026 | 1:30:00 AM | 285.15 | 282.01 | 281.95 | 493.57 | 486.24 | 490.85 | 89.9469 | 76.5016 | 82.8333 | 2.2301 | 1.432 | 1.428 | 1.426 | 2.08 | 2.051 | 2.143 | Over-range | 59.98 | 23011 | 18812 | 19533 | 61356 | - - - | - - - | - - - | - - - | 23011 | 18812 | 19533 | 61356 | 2253 | 1358 | 5151 | 8763 | - - - | - - - | - - - | - - - | 2253 | 1358 | 5151 | 8763 | 25603 | 21540 | 23319 | 70462 | # # # | # # # | # # # | # # # | 0.899 | 0.873 | 0.838 | 0.871 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.967 | 0.987 | - - - | 0.143 | 1.54 | 1.52 | 1.5 | 1.49 | 1.49 | 1.5 | 48.51 | 55.83 | 58.49 | 0 | - - - | - - - | - - - | - - - | 25603 | 21540 | 23319 | 70462 | Over-range | 11218 | 10489 | 12733 | 34633 | 10989 | 10400 | 11645 | 33506 | 22900 | 18745 | 19433 | 61079 | 22900 | 18745 | 19433 | 61079 | - - - | - - - | - - - | - - -
5/5/2026 | 1:45:00 AM | 285.65 | 282.57 | 282.55 | 494.46 | 487.31 | 491.8 | 87.931 | 75.0658 | 81.0419 | 2.2174 | 1.432 | 1.428 | 1.426 | 2.075 | 2.042 | 2.135 | Over-range | 59.99 | 22541 | 18510 | 19180 | 60231 | - - - | - - - | - - - | - - - | 22541 | 18510 | 19180 | 60231 | 2216 | 1347 | 4999 | 8563 | - - - | - - - | - - - | - - - | 2216 | 1347 | 4999 | 8563 | 25057 | 21167 | 22852 | 69076 | # # # | # # # | # # # | # # # | 0.9 | 0.875 | 0.839 | 0.872 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.967 | 0.987 | - - - | 0.142 | 1.56 | 1.54 | 1.52 | 1.51 | 1.51 | 1.52 | 48.17 | 55.49 | 58.1 | 0 | - - - | - - - | - - - | - - - | 25057 | 21167 | 22852 | 69076 | Over-range | 10934 | 10263 | 12417 | 33800 | 10707 | 10174 | 11366 | 32698 | 22443 | 18433 | 19097 | 59972 | 22443 | 18433 | 19097 | 59972 | - - - | - - - | - - - | - - -
5/5/2026 | 2:00:00 AM | 286.11 | 283.21 | 283.15 | 495.38 | 488.48 | 492.65 | 86.6477 | 74.5782 | 79.9109 | 2.1774 | 1.432 | 1.427 | 1.426 | 2.068 | 2.037 | 2.122 | Over-range | 60.01 | 22252 | 18444 | 19012 | 59707 | - - - | - - - | - - - | - - - | 22252 | 18444 | 19012 | 59707 | 2250 | 1373 | 4856 | 8479 | - - - | - - - | - - - | - - - | 2250 | 1373 | 4856 | 8479 | 24726 | 21075 | 22580 | 68382 | # # # | # # # | # # # | # # # | 0.9 | 0.875 | 0.842 | 0.873 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.969 | 0.987 | - - - | 0.142 | 1.55 | 1.53 | 1.51 | 1.5 | 1.5 | 1.51 | 47.99 | 55.3 | 57.68 | 0 | - - - | - - - | - - - | - - - | 24726 | 21075 | 22580 | 68382 | Over-range | 10772 | 10194 | 12177 | 33315 | 10534 | 10100 | 11167 | 32218 | 22155 | 18358 | 18930 | 59443 | 22155 | 18358 | 18930 | 59443 | - - - | - - - | - - - | - - -
5/5/2026 | 2:15:00 AM | 286 | 283.22 | 283.19 | 495.24 | 488.6 | 492.56 | 87.937 | 76.0403 | 81.1613 | 2.2448 | 1.432 | 1.427 | 1.426 | 2.072 | 2.049 | 2.125 | Over-range | 59.99 | 22514 | 18766 | 19294 | 60573 | - - - | - - - | - - - | - - - | 22514 | 18766 | 19294 | 60573 | 2331 | 1459 | 4911 | 8700 | - - - | - - - | - - - | - - - | 2331 | 1459 | 4911 | 8700 | 25102 | 21501 | 22949 | 69553 | # # # | # # # | # # # | # # # | 0.897 | 0.873 | 0.841 | 0.871 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.969 | 0.987 | - - - | 0.144 | 1.55 | 1.54 | 1.52 | 1.51 | 1.5 | 1.51 | 48.83 | 55.86 | 58.15 | 0 | - - - | - - - | - - - | - - - | 25102 | 21501 | 22949 | 69553 | Over-range | 11093 | 10492 | 12421 | 34167 | 10845 | 10390 | 11409 | 33041 | 22413 | 18701 | 19195 | 60309 | 22413 | 18701 | 19195 | 60309 | - - - | - - - | - - - | - - -
5/5/2026 | 2:30:00 AM | 285.94 | 283.13 | 283.18 | 495.07 | 488.52 | 492.53 | 85.3822 | 73.8344 | 79.2827 | 2.1486 | 1.431 | 1.427 | 1.426 | 2.068 | 2.022 | 2.105 | Over-range | 59.99 | 21929 | 18253 | 18934 | 59116 | - - - | - - - | - - - | - - - | 21929 | 18253 | 18934 | 59116 | 2148 | 1459 | 4755 | 8362 | - - - | - - - | - - - | - - - | 2148 | 1459 | 4755 | 8362 | 24351 | 20858 | 22404 | 67613 | # # # | # # # | # # # | # # # | 0.901 | 0.875 | 0.845 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.987 | - - - | 0.141 | 1.57 | 1.53 | 1.53 | 1.51 | 1.51 | 1.52 | 47.86 | 55.13 | 57.05 | 0 | - - - | - - - | - - - | - - - | 24351 | 20858 | 22404 | 67613 | Over-range | 10577 | 10090 | 11970 | 32795 | 10356 | 9983 | 10985 | 31711 | 21833 | 18189 | 18839 | 58861 | 21833 | 18189 | 18839 | 58861 | - - - | - - - | - - - | - - -
5/5/2026 | 2:45:00 AM | 286.07 | 283.34 | 283.31 | 495.39 | 488.82 | 492.7 | 86.8924 | 75.1461 | 80.3892 | 2.1342 | 1.433 | 1.428 | 1.427 | 2.07 | 2.041 | 2.118 | Over-range | 59.98 | 22277 | 18562 | 19152 | 59991 | - - - | - - - | - - - | - - - | 22277 | 18562 | 19152 | 59991 | 2281 | 1454 | 4841 | 8576 | - - - | - - - | - - - | - - - | 2281 | 1454 | 4841 | 8576 | 24807 | 21253 | 22735 | 68795 | # # # | # # # | # # # | # # # | 0.898 | 0.873 | 0.842 | 0.872 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.969 | 0.987 | - - - | 0.143 | 1.58 | 1.53 | 1.52 | 1.52 | 1.5 | 1.52 | 48.53 | 55.74 | 57.76 | 0 | - - - | - - - | - - - | - - - | 24807 | 21253 | 22735 | 68795 | Over-range | 10904 | 10347 | 12247 | 33656 | 10663 | 10244 | 11249 | 32545 | 22186 | 18481 | 19056 | 59723 | 22186 | 18481 | 19056 | 59723 | - - - | - - - | - - - | - - -
5/5/2026 | 3:00:00 AM | 286.2 | 283.53 | 283.57 | 495.61 | 489.27 | 493.04 | 84.2669 | 73.2971 | 78.3763 | 2.1162 | 1.432 | 1.427 | 1.426 | 2.064 | 2.018 | 2.096 | Over-range | 59.99 | 21666 | 18152 | 18787 | 58605 | - - - | - - - | - - - | - - - | 21666 | 18152 | 18787 | 58605 | 2140 | 1473 | 4637 | 8250 | - - - | - - - | - - - | - - - | 2140 | 1473 | 4637 | 8250 | 24052 | 20734 | 22176 | 66963 | # # # | # # # | # # # | # # # | 0.901 | 0.875 | 0.847 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.141 | 1.57 | 1.53 | 1.51 | 1.51 | 1.49 | 1.52 | 47.73 | 55.01 | 56.71 | 0 | - - - | - - - | - - - | - - - | 24052 | 20734 | 22176 | 66963 | Over-range | 10433 | 10016 | 11775 | 32372 | 10211 | 9907 | 10823 | 31303 | 21570 | 18095 | 18690 | 58356 | 21570 | 18095 | 18690 | 58356 | - - - | - - - | - - - | - - -
5/5/2026 | 3:15:00 AM | 286.2 | 283.58 | 283.55 | 495.68 | 489.31 | 492.99 | 86.1267 | 74.8009 | 79.664 | 2.15 | 1.433 | 1.427 | 1.426 | 2.065 | 2.04 | 2.112 | Over-range | 59.98 | 22096 | 18505 | 19027 | 59629 | - - - | - - - | - - - | - - - | 22096 | 18505 | 19027 | 59629 | 2288 | 1449 | 4760 | 8497 | - - - | - - - | - - - | - - - | 2288 | 1449 | 4760 | 8497 | 24598 | 21174 | 22547 | 68319 | # # # | # # # | # # # | # # # | 0.898 | 0.874 | 0.844 | 0.873 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.987 | - - - | 0.142 | 1.58 | 1.54 | 1.54 | 1.52 | 1.51 | 1.54 | 48.39 | 55.53 | 57.47 | 0 | - - - | - - - | - - - | - - - | 24598 | 21174 | 22547 | 68319 | Over-range | 10801 | 10287 | 12093 | 33332 | 10556 | 10184 | 11117 | 32231 | 22003 | 18427 | 18944 | 59374 | 22003 | 18427 | 18944 | 59374 | - - - | - - - | - - - | - - -
5/5/2026 | 3:30:00 AM | 286.31 | 283.69 | 283.75 | 495.81 | 489.61 | 493.28 | 84.6817 | 73.8753 | 78.8487 | 2.1139 | 1.433 | 1.428 | 1.426 | 2.061 | 2.018 | 2.09 | Over-range | 59.99 | 21764 | 18292 | 18928 | 58984 | - - - | - - - | - - - | - - - | 21764 | 18292 | 18928 | 58984 | 2174 | 1517 | 4644 | 8335 | - - - | - - - | - - - | - - - | 2174 | 1517 | 4644 | 8335 | 24181 | 20910 | 22324 | 67415 | # # # | # # # | # # # | # # # | 0.9 | 0.875 | 0.848 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.141 | 1.59 | 1.54 | 1.53 | 1.52 | 1.51 | 1.54 | 47.91 | 55.17 | 56.58 | 0 | - - - | - - - | - - - | - - - | 24181 | 20910 | 22324 | 67415 | Over-range | 10528 | 10126 | 11829 | 32625 | 10301 | 10012 | 10879 | 31542 | 21670 | 18228 | 18841 | 58739 | 21670 | 18228 | 18841 | 58739 | - - - | - - - | - - - | - - -
5/5/2026 | 3:45:00 AM | 286.39 | 283.84 | 283.81 | 496.06 | 489.81 | 493.36 | 84.975 | 74.2904 | 78.7668 | 2.1609 | 1.432 | 1.427 | 1.426 | 2.059 | 2.03 | 2.097 | Over-range | 59.99 | 21827 | 18405 | 18890 | 59122 | - - - | - - - | - - - | - - - | 21827 | 18405 | 18890 | 59122 | 2262 | 1490 | 4637 | 8389 | - - - | - - - | - - - | - - - | 2262 | 1490 | 4637 | 8389 | 24277 | 21041 | 22309 | 67627 | # # # | # # # | # # # | # # # | 0.899 | 0.875 | 0.847 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.142 | 1.57 | 1.53 | 1.52 | 1.52 | 1.5 | 1.53 | 48.09 | 55.24 | 56.92 | 0 | - - - | - - - | - - - | - - - | 24277 | 21041 | 22309 | 67627 | Over-range | 10616 | 10193 | 11862 | 32812 | 10372 | 10083 | 10918 | 31722 | 21741 | 18332 | 18796 | 58868 | 21741 | 18332 | 18796 | 58868 | - - - | - - - | - - - | - - -
5/5/2026 | 4:00:00 AM | 286.33 | 283.77 | 283.79 | 495.91 | 489.73 | 493.31 | 85.3605 | 74.3938 | 79.2724 | 2.1207 | 1.433 | 1.427 | 1.427 | 2.062 | 2.031 | 2.098 | Over-range | 60 | 21921 | 18421 | 19018 | 59360 | - - - | - - - | - - - | - - - | 21921 | 18421 | 19018 | 59360 | 2226 | 1507 | 4687 | 8420 | - - - | - - - | - - - | - - - | 2226 | 1507 | 4687 | 8420 | 24392 | 21073 | 22457 | 67921 | # # # | # # # | # # # | # # # | 0.899 | 0.874 | 0.847 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.142 | 1.61 | 1.57 | 1.55 | 1.54 | 1.53 | 1.57 | 48.24 | 55.44 | 56.8 | 0 | - - - | - - - | - - - | - - - | 24392 | 21073 | 22457 | 67921 | Over-range | 10688 | 10231 | 11938 | 32996 | 10453 | 10120 | 10980 | 31904 | 21842 | 18339 | 18934 | 59114 | 21842 | 18339 | 18934 | 59114 | - - - | - - - | - - - | - - -
5/5/2026 | 4:15:00 AM | 286.2 | 283.74 | 283.68 | 495.8 | 489.65 | 493.04 | 82.5517 | 72.5263 | 76.4696 | 2.1083 | 1.431 | 1.427 | 1.426 | 2.045 | 2.017 | 2.081 | Over-range | 59.98 | 21226 | 18004 | 18401 | 57630 | - - - | - - - | - - - | - - - | 21226 | 18004 | 18401 | 57630 | 2201 | 1435 | 4423 | 8059 | - - - | - - - | - - - | - - - | 2201 | 1435 | 4423 | 8059 | 23555 | 20525 | 21640 | 65720 | # # # | # # # | # # # | # # # | 0.901 | 0.877 | 0.85 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.14 | 1.59 | 1.53 | 1.55 | 1.52 | 1.51 | 1.55 | 47.42 | 54.49 | 56.09 | 0 | - - - | - - - | - - - | - - - | 23555 | 20525 | 21640 | 65720 | Over-range | 10200 | 9850 | 11381 | 31565 | 9960 | 9745 | 10487 | 30519 | 21151 | 17945 | 18308 | 57404 | 21151 | 17945 | 18308 | 57404 | - - - | - - - | - - - | - - -
5/5/2026 | 4:30:00 AM | 286.12 | 283.62 | 283.63 | 495.59 | 489.49 | 492.97 | 84.7064 | 74.268 | 78.4388 | 2.1827 | 1.432 | 1.427 | 1.427 | 2.064 | 2.046 | 2.105 | Over-range | 59.99 | 21658 | 18345 | 18750 | 58753 | - - - | - - - | - - - | - - - | 21658 | 18345 | 18750 | 58753 | 2309 | 1503 | 4594 | 8407 | - - - | - - - | - - - | - - - | 2309 | 1503 | 4594 | 8407 | 24185 | 21023 | 22205 | 67412 | # # # | # # # | # # # | # # # | 0.896 | 0.873 | 0.844 | 0.872 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.971 | 0.987 | - - - | 0.143 | 1.59 | 1.54 | 1.55 | 1.52 | 1.52 | 1.55 | 49.05 | 55.75 | 57.54 | 0 | - - - | - - - | - - - | - - - | 24185 | 21023 | 22205 | 67412 | Over-range | 10756 | 10264 | 11890 | 33040 | 10505 | 10154 | 10967 | 31952 | 21561 | 18286 | 18667 | 58514 | 21561 | 18286 | 18667 | 58514 | - - - | - - - | - - - | - - -
5/5/2026 | 4:45:00 AM | 285.61 | 283.03 | 283.04 | 494.65 | 488.43 | 492.03 | 81.9692 | 71.8834 | 75.9337 | 2.1257 | 1.431 | 1.427 | 1.427 | 2.055 | 2.028 | 2.091 | Over-range | 59.99 | 20983 | 17764 | 18174 | 56921 | - - - | - - - | - - - | - - - | 20983 | 17764 | 18174 | 56921 | 2185 | 1423 | 4413 | 8020 | - - - | - - - | - - - | - - - | 2185 | 1423 | 4413 | 8020 | 23349 | 20298 | 21444 | 65091 | # # # | # # # | # # # | # # # | 0.899 | 0.875 | 0.848 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.141 | 1.58 | 1.54 | 1.56 | 1.52 | 1.52 | 1.55 | 48.12 | 55.02 | 56.72 | 0 | - - - | - - - | - - - | - - - | 23349 | 20298 | 21444 | 65091 | Over-range | 10231 | 9817 | 11376 | 31553 | 9995 | 9713 | 10485 | 30517 | 20894 | 17709 | 18105 | 56707 | 20894 | 17709 | 18105 | 56707 | - - - | - - - | - - - | - - -
5/5/2026 | 5:00:00 AM | 285.59 | 283 | 283.03 | 494.61 | 488.4 | 492.02 | 79.7096 | 70.0486 | 74.0164 | 2.076 | 1.431 | 1.427 | 1.427 | 2.046 | 2.008 | 2.074 | Over-range | 59.99 | 20464 | 17351 | 17791 | 55607 | - - - | - - - | - - - | - - - | 20464 | 17351 | 17791 | 55607 | 2063 | 1397 | 4247 | 7707 | - - - | - - - | - - - | - - - | 2063 | 1397 | 4247 | 7707 | 22690 | 19767 | 20894 | 63351 | # # # | # # # | # # # | # # # | 0.902 | 0.878 | 0.852 | 0.878 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.139 | 1.6 | 1.54 | 1.56 | 1.52 | 1.53 | 1.56 | 47.2 | 54.25 | 55.76 | 0 | - - - | - - - | - - - | - - - | 22690 | 19767 | 20894 | 63351 | Over-range | 9788 | 9465 | 10948 | 30329 | 9568 | 9361 | 10090 | 29333 | 20386 | 17303 | 17713 | 55402 | 20386 | 17303 | 17713 | 55402 | - - - | - - - | - - - | - - -
5/5/2026 | 5:15:00 AM | 284.98 | 282.27 | 282.29 | 493.49 | 487.05 | 490.89 | 82.5453 | 72.2487 | 76.3162 | 2.1314 | 1.432 | 1.428 | 1.428 | 2.055 | 2.038 | 2.096 | Over-range | 60.01 | 21058 | 17790 | 18202 | 57051 | - - - | - - - | - - - | - - - | 21058 | 17790 | 18202 | 57051 | 2183 | 1403 | 4428 | 8014 | - - - | - - - | - - - | - - - | 2183 | 1403 | 4428 | 8014 | 23465 | 20348 | 21497 | 65310 | # # # | # # # | # # # | # # # | 0.897 | 0.874 | 0.847 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.141 | 1.59 | 1.55 | 1.58 | 1.52 | 1.55 | 1.58 | 48.44 | 55.22 | 56.87 | 0 | - - - | - - - | - - - | - - - | 23465 | 20348 | 21497 | 65310 | Over-range | 10342 | 9872 | 11431 | 31771 | 10108 | 9772 | 10539 | 30744 | 20977 | 17742 | 18124 | 56843 | 20977 | 17742 | 18124 | 56843 | - - - | - - - | - - - | - - -
5/5/2026 | 5:30:00 AM | 284.47 | 281.57 | 281.54 | 492.52 | 485.66 | 489.84 | 81.3497 | 70.8027 | 74.8744 | 2.0747 | 1.432 | 1.428 | 1.428 | 2.049 | 2.034 | 2.098 | Over-range | 60.01 | 20769 | 17435 | 17817 | 56021 | - - - | - - - | - - - | - - - | 20769 | 17435 | 17817 | 56021 | 2123 | 1261 | 4361 | 7745 | - - - | - - - | - - - | - - - | 2123 | 1261 | 4361 | 7745 | 23074 | 19886 | 21030 | 63990 | # # # | # # # | # # # | # # # | 0.9 | 0.877 | 0.847 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.138 | 1.58 | 1.55 | 1.59 | 1.51 | 1.55 | 1.57 | 47.7 | 54.64 | 56.54 | 0 | - - - | - - - | - - - | - - - | 23074 | 19886 | 21030 | 63990 | Over-range | 10043 | 9560 | 11164 | 30906 | 9816 | 9477 | 10277 | 29919 | 20688 | 17379 | 17760 | 55827 | 20688 | 17379 | 17760 | 55827 | - - - | - - - | - - - | - - -
5/5/2026 | 5:45:00 AM | 284.29 | 281.28 | 281.32 | 492.1 | 485.19 | 489.55 | 79.1772 | 69.1094 | 73.0478 | 2.0684 | 1.431 | 1.429 | 1.428 | 2.047 | 2.022 | 2.09 | Over-range | 60 | 20237 | 17031 | 17421 | 54689 | - - - | - - - | - - - | - - - | 20237 | 17031 | 17421 | 54689 | 2026 | 1240 | 4195 | 7462 | - - - | - - - | - - - | - - - | 2026 | 1240 | 4195 | 7462 | 22444 | 19387 | 20505 | 62336 | # # # | # # # | # # # | # # # | 0.902 | 0.878 | 0.85 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.136 | 1.58 | 1.57 | 1.6 | 1.52 | 1.56 | 1.59 | 47.24 | 54.14 | 56.07 | 0 | - - - | - - - | - - - | - - - | 22444 | 19387 | 20505 | 62336 | Over-range | 9691 | 9258 | 10808 | 29891 | 9476 | 9174 | 9961 | 28945 | 20154 | 16977 | 17375 | 54507 | 20154 | 16977 | 17375 | 54507 | - - - | - - - | - - - | - - -
5/5/2026 | 6:00:00 AM | 284.07 | 281.33 | 281.35 | 491.89 | 485.4 | 489.3 | 78.0157 | 68.7828 | 72.1855 | 2.0745 | 1.432 | 1.429 | 1.428 | 2.036 | 2.013 | 2.07 | Over-range | 60.01 | 19923 | 16973 | 17282 | 54178 | - - - | - - - | - - - | - - - | 19923 | 16973 | 17282 | 54178 | 2017 | 1292 | 4040 | 7348 | - - - | - - - | - - - | - - - | 2017 | 1292 | 4040 | 7348 | 22091 | 19293 | 20253 | 61638 | # # # | # # # | # # # | # # # | 0.902 | 0.88 | 0.853 | 0.879 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.974 | 0.989 | - - - | 0.136 | 1.62 | 1.58 | 1.63 | 1.55 | 1.58 | 1.62 | 47.11 | 53.62 | 55.44 | 0 | - - - | - - - | - - - | - - - | 22091 | 19293 | 20253 | 61638 | Over-range | 9532 | 9170 | 10555 | 29374 | 9316 | 9078 | 9751 | 28440 | 19843 | 16951 | 17220 | 54014 | 19843 | 16951 | 17220 | 54014 | - - - | - - - | - - - | - - -
5/5/2026 | 6:15:00 AM | 283.51 | 280.82 | 280.84 | 490.94 | 484.55 | 488.36 | 77.0824 | 68.3621 | 71.4455 | 2.0209 | 1.433 | 1.431 | 1.43 | 2.02 | 1.997 | 2.047 | Over-range | 60 | 19671 | 16883 | 17169 | 53723 | - - - | - - - | - - - | - - - | 19671 | 16883 | 17169 | 53723 | 1976 | 1297 | 3875 | 7149 | - - - | - - - | - - - | - - - | 1976 | 1297 | 3875 | 7149 | 21782 | 19138 | 20012 | 60931 | # # # | # # # | # # # | # # # | 0.903 | 0.882 | 0.858 | 0.882 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.975 | 0.989 | - - - | 0.133 | 1.76 | 1.7 | 1.76 | 1.67 | 1.71 | 1.76 | 46.56 | 52.84 | 54.35 | 0 | - - - | - - - | - - - | - - - | 21782 | 19138 | 20012 | 60931 | Over-range | 9342 | 9007 | 10276 | 28728 | 9130 | 8913 | 9517 | 27825 | 19624 | 16854 | 17117 | 53596 | 19624 | 16854 | 17117 | 53596 | - - - | - - - | - - - | - - -
5/5/2026 | 6:30:00 AM | 283.06 | 280.46 | 280.36 | 490.28 | 483.85 | 487.49 | 76.8701 | 68.4184 | 70.8214 | 2.0143 | 1.433 | 1.431 | 1.43 | 2.007 | 2.005 | 2.046 | Over-range | 60 | 19592 | 16903 | 17007 | 53502 | - - - | - - - | - - - | - - - | 19592 | 16903 | 17007 | 53502 | 2048 | 1224 | 3793 | 7066 | - - - | - - - | - - - | - - - | 2048 | 1224 | 3793 | 7066 | 21693 | 19131 | 19804 | 60627 | # # # | # # # | # # # | # # # | 0.903 | 0.883 | 0.859 | 0.882 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.989 | - - - | 0.132 | 1.78 | 1.72 | 1.78 | 1.68 | 1.73 | 1.79 | 46.36 | 52.51 | 54.19 | 0 | - - - | - - - | - - - | - - - | 21693 | 19131 | 19804 | 60627 | Over-range | 9299 | 8956 | 10141 | 28496 | 9070 | 8872 | 9405 | 27606 | 19558 | 16865 | 16964 | 53386 | 19558 | 16865 | 16964 | 53386 | - - - | - - - | - - - | - - -
5/5/2026 | 6:45:00 AM | 283.32 | 280.68 | 280.67 | 490.67 | 484.3 | 488.02 | 76.2366 | 67.6609 | 70.4721 | 2.0218 | 1.433 | 1.431 | 1.43 | 2.014 | 1.999 | 2.046 | Over-range | 60.01 | 19463 | 16737 | 16947 | 53146 | - - - | - - - | - - - | - - - | 19463 | 16737 | 16947 | 53146 | 1967 | 1235 | 3797 | 7000 | - - - | - - - | - - - | - - - | 1967 | 1235 | 3797 | 7000 | 21525 | 18932 | 19722 | 60179 | # # # | # # # | # # # | # # # | 0.904 | 0.884 | 0.859 | 0.883 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.989 | - - - | 0.132 | 1.77 | 1.69 | 1.76 | 1.67 | 1.7 | 1.77 | 46.2 | 52.31 | 53.93 | 0 | - - - | - - - | - - - | - - - | 21525 | 18932 | 19722 | 60179 | Over-range | 9181 | 8844 | 10081 | 28207 | 8967 | 8757 | 9338 | 27325 | 19405 | 16706 | 16919 | 53030 | 19405 | 16706 | 16919 | 53030 | - - - | - - - | - - - | - - -
5/5/2026 | 7:00:00 AM | 283.29 | 280.59 | 280.54 | 490.6 | 484.07 | 487.89 | 75.0795 | 66.4275 | 69.248 | 1.9747 | 1.432 | 1.431 | 1.429 | 2.011 | 1.993 | 2.049 | Over-range | 60.02 | 19210 | 16460 | 16650 | 52320 | - - - | - - - | - - - | - - - | 19210 | 16460 | 16650 | 52320 | 1925 | 1148 | 3757 | 6830 | - - - | - - - | - - - | - - - | 1925 | 1148 | 3757 | 6830 | 21201 | 18583 | 19374 | 59158 | # # # | # # # | # # # | # # # | 0.906 | 0.886 | 0.859 | 0.884 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.975 | 0.989 | - - - | 0.131 | 1.77 | 1.68 | 1.75 | 1.65 | 1.69 | 1.77 | 45.69 | 51.9 | 53.78 | 0 | - - - | - - - | - - - | - - - | 21201 | 18583 | 19374 | 59158 | Over-range | 8958 | 8622 | 9898 | 27588 | 8748 | 8545 | 9158 | 26729 | 19136 | 16438 | 16635 | 52210 | 19136 | 16438 | 16635 | 52210 | - - - | - - - | - - - | - - -
5/5/2026 | 7:15:00 AM | 282.92 | 280.18 | 280.28 | 489.85 | 483.51 | 487.4 | 74.497 | 66.0822 | 69.3004 | 1.9343 | 1.431 | 1.431 | 1.428 | 2.015 | 1.979 | 2.034 | Over-range | 59.99 | 19036 | 16353 | 16699 | 52087 | - - - | - - - | - - - | - - - | 19036 | 16353 | 16699 | 52087 | 1833 | 1257 | 3687 | 6778 | - - - | - - - | - - - | - - - | 1833 | 1257 | 3687 | 6778 | 21009 | 18460 | 19373 | 58841 | # # # | # # # | # # # | # # # | 0.906 | 0.886 | 0.862 | 0.885 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.99 | - - - | 0.13 | 1.77 | 1.69 | 1.77 | 1.66 | 1.71 | 1.78 | 45.71 | 51.73 | 53.3 | 0 | - - - | - - - | - - - | - - - | 21009 | 18460 | 19373 | 58841 | Over-range | 8876 | 8559 | 9814 | 27349 | 8684 | 8466 | 9095 | 26496 | 18997 | 16322 | 16667 | 51986 | 18997 | 16322 | 16667 | 51986 | - - - | - - - | - - - | - - -
5/5/2026 | 7:30:00 AM | 282.91 | 280.08 | 280.18 | 489.77 | 483.28 | 487.34 | 75.1916 | 66.506 | 69.7632 | 1.9763 | 1.431 | 1.431 | 1.428 | 2.017 | 1.985 | 2.043 | Over-range | 60.02 | 19209 | 16443 | 16775 | 52426 | - - - | - - - | - - - | - - - | 19209 | 16443 | 16775 | 52426 | 1866 | 1227 | 3745 | 6839 | - - - | - - - | - - - | - - - | 1866 | 1227 | 3745 | 6839 | 21207 | 18569 | 19495 | 59271 | # # # | # # # | # # # | # # # | 0.906 | 0.885 | 0.861 | 0.884 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.99 | - - - | 0.13 | 1.76 | 1.71 | 1.8 | 1.67 | 1.73 | 1.79 | 45.77 | 51.91 | 53.59 | 0 | - - - | - - - | - - - | - - - | 21207 | 18569 | 19495 | 59271 | Over-range | 8974 | 8623 | 9927 | 27629 | 8778 | 8536 | 9194 | 26770 | 19181 | 16386 | 16759 | 52326 | 19181 | 16386 | 16759 | 52326 | - - - | - - - | - - - | - - -
5/5/2026 | 7:45:00 AM | 282.93 | 280.01 | 280.25 | 489.68 | 483.28 | 487.48 | 76.1592 | 67.189 | 71.0614 | 1.9987 | 1.432 | 1.431 | 1.428 | 2.025 | 1.98 | 2.041 | Over-range | 60.01 | 19435 | 16583 | 17083 | 53102 | - - - | - - - | - - - | - - - | 19435 | 16583 | 17083 | 53102 | 1814 | 1310 | 3846 | 6970 | - - - | - - - | - - - | - - - | 1814 | 1310 | 3846 | 6970 | 21477 | 18755 | 19862 | 60094 | # # # | # # # | # # # | # # # | 0.905 | 0.884 | 0.86 | 0.884 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.975 | 0.989 | - - - | 0.131 | 1.78 | 1.72 | 1.79 | 1.67 | 1.73 | 1.79 | 46.14 | 52.19 | 53.58 | 0 | - - - | - - - | - - - | - - - | 21477 | 18755 | 19862 | 60094 | Over-range | 9128 | 8757 | 10124 | 28112 | 8945 | 8658 | 9365 | 27235 | 19373 | 16553 | 17068 | 52994 | 19373 | 16553 | 17068 | 52994 | - - - | - - - | - - - | - - -
5/5/2026 | 8:00:00 AM | 282.65 | 279.8 | 280.07 | 489.21 | 482.98 | 487.06 | 77.4245 | 68.5439 | 72.2226 | 1.9787 | 1.432 | 1.432 | 1.428 | 2.021 | 1.985 | 2.039 | Over-range | 60.01 | 19698 | 16897 | 17345 | 53939 | - - - | - - - | - - - | - - - | 19698 | 16897 | 17345 | 53939 | 1919 | 1356 | 3871 | 7145 | - - - | - - - | - - - | - - - | 1919 | 1356 | 3871 | 7145 | 21814 | 19124 | 20173 | 61110 | # # # | # # # | # # # | # # # | 0.903 | 0.883 | 0.86 | 0.883 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.989 | - - - | 0.133 | 1.77 | 1.68 | 1.79 | 1.65 | 1.72 | 1.79 | 46.62 | 52.38 | 53.74 | 0 | - - - | - - - | - - - | - - - | 21814 | 19124 | 20173 | 61110 | Over-range | 9359 | 8952 | 10292 | 28700 | 9160 | 8849 | 9537 | 27796 | 19644 | 16853 | 17333 | 53830 | 19644 | 16853 | 17333 | 53830 | - - - | - - - | - - - | - - -
5/5/2026 | 8:15:00 AM | 282.43 | 279.37 | 279.84 | 488.59 | 482.35 | 486.8 | 78.5425 | 68.9797 | 73.6162 | 1.9726 | 1.433 | 1.433 | 1.429 | 2.032 | 1.982 | 2.044 | Over-range | 60.01 | 19967 | 16960 | 17647 | 54574 | - - - | - - - | - - - | - - - | 19967 | 16960 | 17647 | 54574 | 1820 | 1421 | 3997 | 7239 | - - - | - - - | - - - | - - - | 1820 | 1421 | 3997 | 7239 | 22117 | 19222 | 20548 | 61886 | # # # | # # # | # # # | # # # | 0.903 | 0.882 | 0.859 | 0.882 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.975 | 0.989 | - - - | 0.133 | 1.74 | 1.7 | 1.78 | 1.64 | 1.72 | 1.77 | 46.8 | 52.64 | 53.97 | 0 | - - - | - - - | - - - | - - - | 22117 | 19222 | 20548 | 61886 | Over-range | 9501 | 9041 | 10517 | 29159 | 9325 | 8929 | 9728 | 28246 | 19933 | 16935 | 17587 | 54455 | 19933 | 16935 | 17587 | 54455 | - - - | - - - | - - - | - - -
5/5/2026 | 8:30:00 AM | 282.47 | 279.32 | 279.81 | 488.61 | 482.23 | 486.84 | 78.299 | 68.5669 | 73.3555 | 1.9857 | 1.433 | 1.432 | 1.429 | 2.032 | 1.978 | 2.045 | Over-range | 60.01 | 19931 | 16859 | 17591 | 54381 | - - - | - - - | - - - | - - - | 19931 | 16859 | 17591 | 54381 | 1786 | 1385 | 4020 | 7191 | - - - | - - - | - - - | - - - | 1786 | 1385 | 4020 | 7191 | 22045 | 19099 | 20472 | 61615 | # # # | # # # | # # # | # # # | 0.904 | 0.883 | 0.859 | 0.883 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.975 | 0.989 | - - - | 0.132 | 1.69 | 1.64 | 1.73 | 1.59 | 1.66 | 1.71 | 46.48 | 52.61 | 53.65 | 0 | - - - | - - - | - - - | - - - | 22045 | 19099 | 20472 | 61615 | Over-range | 9406 | 8970 | 10461 | 28941 | 9234 | 8862 | 9658 | 28034 | 19877 | 16812 | 17572 | 54261 | 19877 | 16812 | 17572 | 54261 | - - - | - - - | - - - | - - -
5/5/2026 | 8:45:00 AM | 281.69 | 278.59 | 279.08 | 487.28 | 480.99 | 485.53 | 80.9009 | 71.0828 | 75.8376 | 2.0306 | 1.433 | 1.433 | 1.43 | 2.031 | 1.985 | 2.045 | Over-range | 60.01 | 20487 | 17416 | 18114 | 56018 | - - - | - - - | - - - | - - - | 20487 | 17416 | 18114 | 56018 | 1917 | 1490 | 4127 | 7534 | - - - | - - - | - - - | - - - | 1917 | 1490 | 4127 | 7534 | 22734 | 19762 | 21122 | 63618 | # # # | # # # | # # # | # # # | 0.901 | 0.881 | 0.858 | 0.88 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.975 | 0.989 | - - - | 0.135 | 1.67 | 1.64 | 1.7 | 1.58 | 1.65 | 1.7 | 47.33 | 53.02 | 54.28 | 0 | - - - | - - - | - - - | - - - | 22734 | 19762 | 21122 | 63618 | Over-range | 9848 | 9335 | 10856 | 30137 | 9659 | 9215 | 10041 | 29180 | 20436 | 17375 | 18076 | 55887 | 20436 | 17375 | 18076 | 55887 | - - - | - - - | - - - | - - -
5/5/2026 | 9:00:00 AM | 281.46 | 278.34 | 278.8 | 486.89 | 480.51 | 485.09 | 81.1095 | 71.28 | 75.9603 | 2.0766 | 1.433 | 1.433 | 1.43 | 2.025 | 1.979 | 2.039 | Over-range | 60 | 20535 | 17468 | 18141 | 56144 | - - - | - - - | - - - | - - - | 20535 | 17468 | 18141 | 56144 | 1917 | 1483 | 4125 | 7525 | - - - | - - - | - - - | - - - | 1917 | 1483 | 4125 | 7525 | 22764 | 19792 | 21128 | 63684 | # # # | # # # | # # # | # # # | 0.902 | 0.883 | 0.859 | 0.882 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.975 | 0.989 | - - - | 0.134 | 1.68 | 1.64 | 1.7 | 1.58 | 1.66 | 1.7 | 47.03 | 52.65 | 53.99 | 0 | - - - | - - - | - - - | - - - | 22764 | 19792 | 21128 | 63684 | Over-range | 9812 | 9301 | 10822 | 30035 | 9623 | 9182 | 10005 | 29077 | 20482 | 17431 | 18103 | 56016 | 20482 | 17431 | 18103 | 56016 | - - - | - - - | - - - | - - -
5/5/2026 | 9:15:00 AM | 280.94 | 277.74 | 278.28 | 485.88 | 479.52 | 484.23 | 83.4046 | 73.2711 | 78.1895 | 2.1494 | 1.434 | 1.434 | 1.431 | 2.023 | 1.981 | 2.039 | Over-range | 60 | 21062 | 17916 | 18636 | 57614 | - - - | - - - | - - - | - - - | 21062 | 17916 | 18636 | 57614 | 1971 | 1552 | 4252 | 7775 | - - - | - - - | - - - | - - - | 1971 | 1552 | 4252 | 7775 | 23378 | 20309 | 21716 | 65402 | # # # | # # # | # # # | # # # | 0.901 | 0.882 | 0.858 | 0.881 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.975 | 0.989 | - - - | 0.135 | 1.69 | 1.66 | 1.74 | 1.6 | 1.68 | 1.72 | 47.42 | 52.73 | 54.1 | 0 | - - - | - - - | - - - | - - - | 23378 | 20309 | 21716 | 65402 | Over-range | 10134 | 9560 | 11142 | 30935 | 9941 | 9433 | 10299 | 29942 | 20992 | 17885 | 18601 | 57478 | 20992 | 17885 | 18601 | 57478 | - - - | - - - | - - - | - - -
5/5/2026 | 9:30:00 AM | 281.07 | 277.86 | 278.48 | 486.07 | 479.81 | 484.55 | 85.6427 | 75.4808 | 80.7236 | 2.1724 | 1.435 | 1.434 | 1.431 | 2.017 | 1.965 | 2.022 | Over-range | 60.01 | 21678 | 18500 | 19329 | 59507 | - - - | - - - | - - - | - - - | 21678 | 18500 | 19329 | 59507 | 2005 | 1687 | 4339 | 8031 | - - - | - - - | - - - | - - - | 2005 | 1687 | 4339 | 8031 | 24022 | 20932 | 22441 | 67395 | # # # | # # # | # # # | # # # | 0.902 | 0.884 | 0.861 | 0.883 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.976 | 0.989 | - - - | 0.135 | 1.73 | 1.71 | 1.77 | 1.64 | 1.73 | 1.76 | 47 | 52.25 | 53.42 | 0 | - - - | - - - | - - - | - - - | 24022 | 20932 | 22441 | 67395 | Over-range | 10340 | 9791 | 11394 | 31621 | 10143 | 9644 | 10535 | 30584 | 21619 | 18452 | 19297 | 59367 | 21619 | 18452 | 19297 | 59367 | - - - | - - - | - - - | - - -
5/5/2026 | 9:45:00 AM | 280.68 | 277.49 | 278.02 | 485.44 | 479.09 | 483.77 | 87.3399 | 77.2917 | 82.1307 | 2.2272 | 1.435 | 1.436 | 1.432 | 1.992 | 1.947 | 2.002 | Over-range | 60.01 | 22178 | 19045 | 19752 | 60976 | - - - | - - - | - - - | - - - | 22178 | 19045 | 19752 | 60976 | 2082 | 1671 | 4326 | 8079 | - - - | - - - | - - - | - - - | 2082 | 1671 | 4326 | 8079 | 24462 | 21407 | 22792 | 68660 | # # # | # # # | # # # | # # # | 0.907 | 0.89 | 0.867 | 0.888 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.977 | 0.99 | - - - | 0.133 | 1.76 | 1.73 | 1.81 | 1.66 | 1.76 | 1.8 | 45.74 | 50.64 | 52.2 | 0 | - - - | - - - | - - - | - - - | 24462 | 21407 | 22792 | 68660 | Over-range | 10310 | 9770 | 11365 | 31544 | 10098 | 9626 | 10510 | 30492 | 22125 | 18994 | 19717 | 60836 | 22125 | 18994 | 19717 | 60836 | - - - | - - - | - - - | - - -
5/5/2026 | 10:00:00 AM | 280.39 | 277.19 | 277.8 | 484.89 | 478.64 | 483.35 | 91.0161 | 80.8625 | 86.0052 | 2.2938 | 1.435 | 1.435 | 1.433 | 1.985 | 1.934 | 1.988 | Over-range | 60 | 23127 | 19965 | 20765 | 63858 | - - - | - - - | - - - | - - - | 23127 | 19965 | 20765 | 63858 | 2137 | 1833 | 4445 | 8415 | - - - | - - - | - - - | - - - | 2137 | 1833 | 4445 | 8415 | 25486 | 22387 | 23866 | 71739 | # # # | # # # | # # # | # # # | 0.908 | 0.892 | 0.87 | 0.89 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.978 | 0.99 | - - - | 0.132 | 1.76 | 1.74 | 1.82 | 1.67 | 1.76 | 1.8 | 45.55 | 49.95 | 51.52 | 0 | - - - | - - - | - - - | - - - | 25486 | 22387 | 23866 | 71739 | Over-range | 10701 | 10125 | 11759 | 32676 | 10485 | 9957 | 10887 | 31574 | 23069 | 19927 | 20726 | 63722 | 23069 | 19927 | 20726 | 63722 | - - - | - - - | - - - | - - -
5/5/2026 | 10:15:00 AM | 280.14 | 277.06 | 277.53 | 484.61 | 478.32 | 482.83 | 93.243 | 83.3425 | 87.6682 | 2.3548 | 1.436 | 1.437 | 1.434 | 1.964 | 1.934 | 1.978 | Over-range | 60.02 | 23687 | 20623 | 21186 | 65496 | - - - | - - - | - - - | - - - | 23687 | 20623 | 21186 | 65496 | 2313 | 1830 | 4447 | 8589 | - - - | - - - | - - - | - - - | 2313 | 1830 | 4447 | 8589 | 26083 | 23061 | 24299 | 73442 | # # # | # # # | # # # | # # # | 0.908 | 0.894 | 0.872 | 0.892 | # # # | # # # | # # # | - - - | 0.995 | 0.996 | 0.979 | 0.99 | - - - | 0.131 | 1.79 | 1.77 | 1.84 | 1.7 | 1.79 | 1.83 | 45.14 | 49.25 | 51.13 | 0 | - - - | - - - | - - - | - - - | 26083 | 23061 | 24299 | 73442 | Over-range | 10913 | 10316 | 11893 | 33212 | 10665 | 10152 | 11031 | 32082 | 23639 | 20589 | 21146 | 65373 | 23639 | 20589 | 21146 | 65373 | - - - | - - - | - - - | - - -
5/5/2026 | 10:30:00 AM | 279.9 | 276.8 | 277.28 | 484.17 | 477.87 | 482.41 | 93.4786 | 83.8707 | 88.3519 | 2.3473 | 1.434 | 1.435 | 1.432 | 1.951 | 1.907 | 1.954 | Over-range | 60.01 | 23815 | 20818 | 21464 | 66097 | - - - | - - - | - - - | - - - | 23815 | 20818 | 21464 | 66097 | 2237 | 1878 | 4372 | 8488 | - - - | - - - | - - - | - - - | 2237 | 1878 | 4372 | 8488 | 26113 | 23177 | 24458 | 73748 | # # # | # # # | # # # | # # # | 0.912 | 0.898 | 0.878 | 0.896 | # # # | # # # | # # # | - - - | 0.996 | 0.996 | 0.98 | 0.99 | - - - | 0.128 | 1.77 | 1.76 | 1.82 | 1.68 | 1.77 | 1.8 | 44.05 | 48.04 | 49.76 | 0 | - - - | - - - | - - - | - - - | 26113 | 23177 | 24458 | 73748 | Over-range | 10702 | 10181 | 11716 | 32686 | 10465 | 10006 | 10870 | 31564 | 23769 | 20787 | 21424 | 65981 | 23769 | 20787 | 21424 | 65981 | - - - | - - - | - - - | - - -
5/5/2026 | 10:45:00 AM | 279.58 | 276.4 | 276.87 | 483.58 | 477.12 | 481.8 | 98.5528 | 88.4197 | 93.0262 | 2.5622 | 1.434 | 1.436 | 1.433 | 1.945 | 1.904 | 1.954 | Over-range | 60.02 | 25102 | 21955 | 22579 | 69636 | - - - | - - - | - - - | - - - | 25102 | 21955 | 22579 | 69636 | 2395 | 1991 | 4624 | 9010 | - - - | - - - | - - - | - - - | 2395 | 1991 | 4624 | 9010 | 27523 | 24417 | 25731 | 77671 | # # # | # # # | # # # | # # # | 0.912 | 0.899 | 0.877 | 0.897 | # # # | # # # | # # # | - - - | 0.995 | 0.996 | 0.98 | 0.99 | - - - | 0.129 | 1.77 | 1.78 | 1.85 | 1.69 | 1.8 | 1.82 | 44.06 | 47.8 | 49.8 | 0 | - - - | - - - | - - - | - - - | 27523 | 24417 | 25731 | 77671 | Over-range | 11281 | 10681 | 12336 | 34391 | 11024 | 10494 | 11437 | 33189 | 25052 | 21920 | 22541 | 69512 | 25052 | 21920 | 22541 | 69512 | - - - | - - - | - - - | - - -
5/5/2026 | 11:00:00 AM | 279.25 | 276.12 | 276.49 | 483.09 | 476.55 | 481.16 | 99.3084 | 89.1745 | 93.4768 | 2.5613 | 1.434 | 1.436 | 1.433 | 1.939 | 1.906 | 1.954 | Over-range | 60 | 25275 | 22144 | 22669 | 70088 | - - - | - - - | - - - | - - - | 25275 | 22144 | 22669 | 70088 | 2454 | 1949 | 4624 | 9027 | - - - | - - - | - - - | - - - | 2454 | 1949 | 4624 | 9027 | 27708 | 24605 | 25827 | 78140 | # # # | # # # | # # # | # # # | 0.912 | 0.9 | 0.878 | 0.897 | # # # | # # # | # # # | - - - | 0.995 | 0.996 | 0.98 | 0.99 | - - - | 0.129 | 1.8 | 1.79 | 1.86 | 1.71 | 1.81 | 1.84 | 43.96 | 47.6 | 49.73 | 0 | - - - | - - - | - - - | - - - | 27708 | 24605 | 25827 | 78140 | Over-range | 11348 | 10722 | 12371 | 34533 | 11080 | 10543 | 11474 | 33333 | 25222 | 22112 | 22645 | 69979 | 25222 | 22112 | 22645 | 69979 | - - - | - - - | - - - | - - -
5/5/2026 | 11:15:00 AM | 278.82 | 275.8 | 276.19 | 482.4 | 476.09 | 480.51 | 97.6927 | 87.6419 | 90.9106 | 2.6121 | 1.432 | 1.432 | 1.431 | 1.938 | 1.917 | 1.97 | Over-range | 60 | 24770 | 21703 | 21992 | 68465 | - - - | - - - | - - - | - - - | 24770 | 21703 | 21992 | 68465 | 2483 | 1728 | 4467 | 8678 | - - - | - - - | - - - | - - - | 2483 | 1728 | 4467 | 8678 | 27212 | 24153 | 25089 | 76453 | # # # | # # # | # # # | # # # | 0.91 | 0.899 | 0.877 | 0.896 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.98 | 0.991 | - - - | 0.127 | 1.53 | 1.48 | 1.54 | 1.43 | 1.47 | 1.53 | 44.3 | 48.07 | 50.02 | 0 | - - - | - - - | - - - | - - - | 27212 | 24153 | 25089 | 76453 | Over-range | 11259 | 10595 | 12069 | 34008 | 10981 | 10453 | 11211 | 32882 | 24732 | 21681 | 21966 | 68379 | 24732 | 21681 | 21966 | 68379 | - - - | - - - | - - - | - - -
5/5/2026 | 11:30:00 AM | 279.09 | 276.09 | 276.43 | 482.91 | 476.54 | 480.92 | 92.7675 | 83.5759 | 86.5129 | 2.8497 | 1.432 | 1.432 | 1.431 | 1.939 | 1.911 | 1.966 | Over-range | 60 | 23525 | 20689 | 20931 | 65145 | - - - | - - - | - - - | - - - | 23525 | 20689 | 20931 | 65145 | 2326 | 1662 | 4262 | 8249 | - - - | - - - | - - - | - - - | 2326 | 1662 | 4262 | 8249 | 25827 | 23020 | 23865 | 72711 | # # # | # # # | # # # | # # # | 0.911 | 0.899 | 0.877 | 0.896 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.98 | 0.991 | - - - | 0.127 | 1.52 | 1.47 | 1.52 | 1.42 | 1.46 | 1.52 | 44.07 | 47.94 | 49.79 | 0 | - - - | - - - | - - - | - - - | 25827 | 23020 | 23865 | 72711 | Over-range | 10646 | 10087 | 11455 | 32270 | 10388 | 9949 | 10632 | 31197 | 23492 | 20670 | 20907 | 65069 | 23492 | 20670 | 20907 | 65069 | - - - | - - - | - - - | - - -
5/5/2026 | 11:45:00 AM | 278.88 | 275.87 | 276.27 | 482.5 | 476.23 | 480.62 | 89.5301 | 79.8508 | 83.4498 | 2.3424 | 1.432 | 1.432 | 1.431 | 1.969 | 1.938 | 1.996 | Over-range | 60 | 22577 | 19612 | 20027 | 62216 | - - - | - - - | - - - | - - - | 22577 | 19612 | 20027 | 62216 | 2204 | 1553 | 4189 | 7946 | - - - | - - - | - - - | - - - | 2204 | 1553 | 4189 | 7946 | 24920 | 21989 | 23020 | 69929 | # # # | # # # | # # # | # # # | 0.906 | 0.892 | 0.87 | 0.89 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.979 | 0.99 | - - - | 0.128 | 1.49 | 1.45 | 1.5 | 1.4 | 1.44 | 1.5 | 45.57 | 49.91 | 51.54 | 0 | - - - | - - - | - - - | - - - | 24920 | 21989 | 23020 | 69929 | Over-range | 10539 | 9940 | 11344 | 31906 | 10306 | 9818 | 10542 | 30900 | 22541 | 19591 | 20007 | 62139 | 22541 | 19591 | 20007 | 62139 | - - - | - - - | - - - | - - -
5/5/2026 | 12:00:00 PM | 278.56 | 275.7 | 276.02 | 482.07 | 475.93 | 480.06 | 87.5098 | 78.462 | 81.3911 | 2.5159 | 1.432 | 1.432 | 1.431 | 1.97 | 1.95 | 2.001 | Over-range | 60.01 | 21989 | 19223 | 19467 | 60679 | - - - | - - - | - - - | - - - | 21989 | 19223 | 19467 | 60679 | 2249 | 1528 | 4093 | 7870 | - - - | - - - | - - - | - - - | 2249 | 1528 | 4093 | 7870 | 24328 | 21595 | 22428 | 68350 | # # # | # # # | # # # | # # # | 0.904 | 0.89 | 0.868 | 0.888 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.979 | 0.99 | - - - | 0.13 | 1.47 | 1.43 | 1.48 | 1.38 | 1.41 | 1.47 | 46.08 | 50.4 | 52.06 | 0 | - - - | - - - | - - - | - - - | 24328 | 21595 | 22428 | 68350 | Over-range | 10396 | 9832 | 11129 | 31436 | 10150 | 9712 | 10349 | 30435 | 21959 | 19201 | 19444 | 60604 | 21959 | 19201 | 19444 | 60604 | - - - | - - - | - - - | - - -
5/5/2026 | 12:15:00 PM | 278.49 | 275.56 | 275.91 | 481.9 | 475.67 | 479.94 | 87.2476 | 77.9127 | 81.1966 | 2.4772 | 1.432 | 1.432 | 1.432 | 1.972 | 1.945 | 2.002 | Over-range | 59.99 | 21948 | 19092 | 19420 | 60460 | - - - | - - - | - - - | - - - | 21948 | 19092 | 19420 | 60460 | 2179 | 1494 | 4108 | 7781 | - - - | - - - | - - - | - - - | 2179 | 1494 | 4108 | 7781 | 24243 | 21425 | 22360 | 68028 | # # # | # # # | # # # | # # # | 0.905 | 0.891 | 0.869 | 0.889 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.129 | 1.49 | 1.45 | 1.5 | 1.4 | 1.43 | 1.49 | 45.71 | 50.14 | 51.82 | 0 | - - - | - - - | - - - | - - - | 24243 | 21425 | 22360 | 68028 | Over-range | 10285 | 9719 | 11074 | 31162 | 10052 | 9604 | 10284 | 30175 | 21914 | 19072 | 19394 | 60380 | 21914 | 19072 | 19394 | 60380 | - - - | - - - | - - - | - - -
5/5/2026 | 12:30:00 PM | 278.68 | 275.72 | 276.09 | 482.2 | 475.95 | 480.27 | 88.1483 | 78.6302 | 81.8275 | 2.7459 | 1.434 | 1.434 | 1.433 | 1.98 | 1.953 | 2.015 | Over-range | 60 | 22149 | 19253 | 19518 | 60920 | - - - | - - - | - - - | - - - | 22149 | 19253 | 19518 | 60920 | 2224 | 1542 | 4224 | 7990 | - - - | - - - | - - - | - - - | 2224 | 1542 | 4224 | 7990 | 24520 | 21645 | 22558 | 68723 | # # # | # # # | # # # | # # # | 0.903 | 0.889 | 0.865 | 0.886 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.977 | 0.99 | - - - | 0.131 | 1.55 | 1.5 | 1.55 | 1.45 | 1.48 | 1.55 | 46.31 | 50.58 | 52.55 | 0 | - - - | - - - | - - - | - - - | 24520 | 21645 | 22558 | 68723 | Over-range | 10511 | 9887 | 11305 | 31789 | 10273 | 9765 | 10486 | 30769 | 22114 | 19234 | 19495 | 60842 | 22114 | 19234 | 19495 | 60842 | - - - | - - - | - - - | - - -
5/5/2026 | 12:45:00 PM | 280.2 | 277.31 | 277.64 | 484.9 | 478.72 | 482.89 | 85.8702 | 77.0431 | 79.8276 | 2.5627 | 1.433 | 1.433 | 1.433 | 1.967 | 1.942 | 1.996 | Over-range | 60.02 | 21725 | 18997 | 19219 | 59940 | - - - | - - - | - - - | - - - | 21725 | 18997 | 19219 | 59940 | 2194 | 1509 | 4037 | 7741 | - - - | - - - | - - - | - - - | 2194 | 1509 | 4037 | 7741 | 23999 | 21313 | 22115 | 67426 | # # # | # # # | # # # | # # # | 0.905 | 0.891 | 0.869 | 0.889 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.979 | 0.99 | - - - | 0.129 | 1.54 | 1.5 | 1.55 | 1.45 | 1.48 | 1.55 | 45.63 | 50.01 | 51.72 | 0 | - - - | - - - | - - - | - - - | 23999 | 21313 | 22115 | 67426 | Over-range | 10184 | 9658 | 10934 | 30856 | 9945 | 9539 | 10161 | 29869 | 21691 | 18978 | 19198 | 59867 | 21691 | 18978 | 19198 | 59867 | - - - | - - - | - - - | - - -
5/5/2026 | 1:00:00 PM | 279.75 | 276.62 | 277.04 | 483.93 | 477.48 | 482.09 | 89.2898 | 79.5338 | 83.0187 | 2.7366 | 1.433 | 1.434 | 1.433 | 1.98 | 1.952 | 2.013 | Over-range | 60.01 | 22525 | 19531 | 19885 | 61941 | - - - | - - - | - - - | - - - | 22525 | 19531 | 19885 | 61941 | 2213 | 1589 | 4296 | 8098 | - - - | - - - | - - - | - - - | 2213 | 1589 | 4296 | 8098 | 24937 | 21966 | 22968 | 69872 | # # # | # # # | # # # | # # # | 0.903 | 0.889 | 0.866 | 0.886 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.977 | 0.99 | - - - | 0.131 | 1.54 | 1.53 | 1.59 | 1.45 | 1.52 | 1.56 | 46.33 | 50.62 | 52.36 | 0 | - - - | - - - | - - - | - - - | 24937 | 21966 | 22968 | 69872 | Over-range | 10692 | 10051 | 11489 | 32318 | 10460 | 9924 | 10656 | 31287 | 22496 | 19515 | 19865 | 61876 | 22496 | 19515 | 19865 | 61876 | - - - | - - - | - - - | - - -
5/5/2026 | 1:15:00 PM | 280.11 | 277.01 | 277.33 | 484.62 | 478.06 | 482.6 | 87.343 | 77.3757 | 80.9103 | 2.253 | 1.433 | 1.433 | 1.433 | 1.966 | 1.943 | 2.001 | Over-range | 60.01 | 22141 | 19072 | 19462 | 60675 | - - - | - - - | - - - | - - - | 22141 | 19072 | 19462 | 60675 | 2132 | 1447 | 4131 | 7711 | - - - | - - - | - - - | - - - | 2132 | 1447 | 4131 | 7711 | 24405 | 21388 | 22394 | 68187 | # # # | # # # | # # # | # # # | 0.907 | 0.892 | 0.869 | 0.89 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.127 | 1.53 | 1.51 | 1.57 | 1.44 | 1.5 | 1.55 | 45.16 | 49.95 | 51.57 | 0 | - - - | - - - | - - - | - - - | 24405 | 21388 | 22394 | 68187 | Over-range | 10253 | 9676 | 11070 | 31090 | 10029 | 9567 | 10271 | 30119 | 22109 | 19057 | 19444 | 60610 | 22109 | 19057 | 19444 | 60610 | - - - | - - - | - - - | - - -
5/5/2026 | 1:30:00 PM | 280.12 | 277.01 | 277.28 | 484.67 | 478 | 482.57 | 89.3316 | 79.1085 | 82.4276 | 2.715 | 1.433 | 1.434 | 1.433 | 1.981 | 1.967 | 2.03 | Over-range | 60 | 22567 | 19444 | 19701 | 61713 | - - - | - - - | - - - | - - - | 22567 | 19444 | 19701 | 61713 | 2242 | 1485 | 4352 | 8078 | - - - | - - - | - - - | - - - | 2242 | 1485 | 4352 | 8078 | 24987 | 21886 | 22829 | 69702 | # # # | # # # | # # # | # # # | 0.903 | 0.888 | 0.863 | 0.885 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.99 | - - - | 0.131 | 1.51 | 1.49 | 1.54 | 1.42 | 1.48 | 1.52 | 46.35 | 50.92 | 52.91 | 0 | - - - | - - - | - - - | - - - | 24987 | 21886 | 22829 | 69702 | Over-range | 10719 | 10043 | 11528 | 32386 | 10481 | 9932 | 10675 | 31362 | 22535 | 19425 | 19684 | 61644 | 22535 | 19425 | 19684 | 61644 | - - - | - - - | - - - | - - -
5/5/2026 | 1:45:00 PM | 280.22 | 277.13 | 277.49 | 484.8 | 478.31 | 482.85 | 86.2221 | 76.6557 | 80.137 | 2.6109 | 1.433 | 1.434 | 1.433 | 1.982 | 1.948 | 2.012 | Over-range | 60.01 | 21808 | 18850 | 19221 | 59880 | - - - | - - - | - - - | - - - | 21808 | 18850 | 19221 | 59880 | 2110 | 1499 | 4170 | 7779 | - - - | - - - | - - - | - - - | 2110 | 1499 | 4170 | 7779 | 24097 | 21192 | 22189 | 67478 | # # # | # # # | # # # | # # # | 0.905 | 0.889 | 0.866 | 0.887 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.977 | 0.99 | - - - | 0.13 | 1.52 | 1.49 | 1.54 | 1.42 | 1.48 | 1.53 | 45.82 | 50.52 | 52.16 | 0 | - - - | - - - | - - - | - - - | 24097 | 21192 | 22189 | 67478 | Over-range | 10239 | 9678 | 11078 | 31084 | 10018 | 9560 | 10263 | 30095 | 21778 | 18834 | 19201 | 59812 | 21778 | 18834 | 19201 | 59812 | - - - | - - - | - - - | - - -
5/5/2026 | 2:00:00 PM | 280.41 | 277.36 | 277.68 | 485.17 | 478.69 | 483.15 | 87.3025 | 77.4626 | 80.7834 | 2.7463 | 1.434 | 1.434 | 1.434 | 1.99 | 1.97 | 2.032 | Over-range | 60.01 | 22037 | 19021 | 19296 | 60354 | - - - | - - - | - - - | - - - | 22037 | 19021 | 19296 | 60354 | 2208 | 1491 | 4286 | 7985 | - - - | - - - | - - - | - - - | 2208 | 1491 | 4286 | 7985 | 24434 | 21449 | 22397 | 68281 | # # # | # # # | # # # | # # # | 0.902 | 0.887 | 0.862 | 0.884 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.989 | - - - | 0.132 | 1.53 | 1.5 | 1.55 | 1.44 | 1.48 | 1.54 | 46.72 | 51.35 | 53.29 | 0 | - - - | - - - | - - - | - - - | 24434 | 21449 | 22397 | 68281 | Over-range | 10547 | 9910 | 11366 | 31917 | 10313 | 9797 | 10527 | 30902 | 22001 | 19003 | 19274 | 60277 | 22001 | 19003 | 19274 | 60277 | - - - | - - - | - - - | - - -
5/5/2026 | 2:15:00 PM | 280.41 | 277.27 | 277.63 | 485.11 | 478.53 | 483.15 | 86.6368 | 76.7685 | 80.4337 | 2.7191 | 1.434 | 1.434 | 1.433 | 1.988 | 1.953 | 2.021 | Over-range | 60.02 | 21921 | 18878 | 19259 | 60059 | - - - | - - - | - - - | - - - | 21921 | 18878 | 19259 | 60059 | 2105 | 1489 | 4247 | 7841 | - - - | - - - | - - - | - - - | 2105 | 1489 | 4247 | 7841 | 24238 | 21242 | 22288 | 67768 | # # # | # # # | # # # | # # # | 0.904 | 0.889 | 0.864 | 0.886 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.99 | - - - | 0.131 | 1.53 | 1.49 | 1.54 | 1.43 | 1.47 | 1.54 | 46.02 | 50.75 | 52.58 | 0 | - - - | - - - | - - - | - - - | 24238 | 21242 | 22288 | 67768 | Over-range | 10329 | 9734 | 11210 | 31369 | 10112 | 9619 | 10374 | 30373 | 21889 | 18861 | 19241 | 59991 | 21889 | 18861 | 19241 | 59991 | - - - | - - - | - - - | - - -
5/5/2026 | 2:30:00 PM | 280.29 | 277.23 | 277.59 | 484.93 | 478.5 | 482.99 | 86.5973 | 76.874 | 80.2971 | 2.6785 | 1.433 | 1.434 | 1.433 | 1.99 | 1.962 | 2.026 | Over-range | 60.01 | 21863 | 18871 | 19194 | 59928 | - - - | - - - | - - - | - - - | 21863 | 18871 | 19194 | 59928 | 2155 | 1491 | 4229 | 7876 | - - - | - - - | - - - | - - - | 2155 | 1491 | 4229 | 7876 | 24220 | 21270 | 22251 | 67741 | # # # | # # # | # # # | # # # | 0.903 | 0.887 | 0.863 | 0.885 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.99 | - - - | 0.131 | 1.52 | 1.48 | 1.53 | 1.42 | 1.46 | 1.52 | 46.49 | 51.2 | 53.02 | 0 | - - - | - - - | - - - | - - - | 24220 | 21270 | 22251 | 67741 | Over-range | 10414 | 9809 | 11249 | 31565 | 10188 | 9695 | 10424 | 30566 | 21831 | 18851 | 19174 | 59857 | 21831 | 18851 | 19174 | 59857 | - - - | - - - | - - - | - - -
5/5/2026 | 2:45:00 PM | 280.19 | 277.21 | 277.54 | 484.84 | 478.48 | 482.83 | 87.4955 | 77.7624 | 81.0364 | 2.6738 | 1.434 | 1.435 | 1.434 | 1.987 | 1.966 | 2.026 | Over-range | 60.01 | 22073 | 19090 | 19367 | 60530 | - - - | - - - | - - - | - - - | 22073 | 19090 | 19367 | 60530 | 2199 | 1515 | 4247 | 7960 | - - - | - - - | - - - | - - - | 2199 | 1515 | 4247 | 7960 | 24471 | 21521 | 22456 | 68447 | # # # | # # # | # # # | # # # | 0.902 | 0.887 | 0.862 | 0.884 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.977 | 0.99 | - - - | 0.132 | 1.52 | 1.48 | 1.53 | 1.43 | 1.47 | 1.52 | 46.68 | 51.24 | 53.15 | 0 | - - - | - - - | - - - | - - - | 24471 | 21521 | 22456 | 68447 | Over-range | 10555 | 9933 | 11361 | 31940 | 10324 | 9816 | 10537 | 30932 | 22037 | 19074 | 19347 | 60459 | 22037 | 19074 | 19347 | 60459 | - - - | - - - | - - - | - - -
5/5/2026 | 3:00:00 PM | 279.96 | 276.88 | 277.24 | 484.34 | 477.89 | 482.41 | 86.0068 | 76.3272 | 79.9548 | 2.7133 | 1.433 | 1.434 | 1.434 | 1.986 | 1.95 | 2.017 | Over-range | 60 | 21730 | 18749 | 19129 | 59608 | - - - | - - - | - - - | - - - | 21730 | 18749 | 19129 | 59608 | 2069 | 1502 | 4187 | 7758 | - - - | - - - | - - - | - - - | 2069 | 1502 | 4187 | 7758 | 24022 | 21091 | 22121 | 67233 | # # # | # # # | # # # | # # # | 0.905 | 0.889 | 0.865 | 0.887 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.977 | 0.99 | - - - | 0.13 | 1.52 | 1.49 | 1.54 | 1.43 | 1.48 | 1.52 | 45.96 | 50.62 | 52.45 | 0 | - - - | - - - | - - - | - - - | 24022 | 21091 | 22121 | 67233 | Over-range | 10228 | 9652 | 11102 | 31076 | 10017 | 9535 | 10282 | 30092 | 21698 | 18732 | 19113 | 59543 | 21698 | 18732 | 19113 | 59543 | - - - | - - - | - - - | - - -
5/5/2026 | 3:15:00 PM | 280.01 | 277.08 | 277.35 | 484.57 | 478.21 | 482.48 | 88.2497 | 78.1463 | 81.4621 | 2.3747 | 1.434 | 1.435 | 1.434 | 1.985 | 1.972 | 2.03 | Over-range | 60.03 | 22248 | 19177 | 19448 | 60873 | - - - | - - - | - - - | - - - | 22248 | 19177 | 19448 | 60873 | 2233 | 1467 | 4233 | 7933 | - - - | - - - | - - - | - - - | 2233 | 1467 | 4233 | 7933 | 24673 | 21621 | 22564 | 68858 | # # # | # # # | # # # | # # # | 0.902 | 0.887 | 0.862 | 0.884 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.977 | 0.99 | - - - | 0.13 | 1.54 | 1.51 | 1.55 | 1.45 | 1.48 | 1.54 | 46.75 | 51.33 | 53.39 | 0 | - - - | - - - | - - - | - - - | 24673 | 21621 | 22564 | 68858 | Over-range | 10658 | 9983 | 11437 | 32170 | 10422 | 9874 | 10624 | 31177 | 22215 | 19160 | 19429 | 60803 | 22215 | 19160 | 19429 | 60803 | - - - | - - - | - - - | - - -
5/5/2026 | 3:30:00 PM | 279.99 | 277.08 | 277.42 | 484.52 | 478.31 | 482.54 | 85.6609 | 76.441 | 79.5797 | 2.4008 | 1.434 | 1.435 | 1.434 | 1.972 | 1.945 | 2.001 | Over-range | 60 | 21664 | 18819 | 19123 | 59606 | - - - | - - - | - - - | - - - | 21664 | 18819 | 19123 | 59606 | 2123 | 1492 | 4031 | 7647 | - - - | - - - | - - - | - - - | 2123 | 1492 | 4031 | 7647 | 23923 | 21130 | 22032 | 67085 | # # # | # # # | # # # | # # # | 0.906 | 0.891 | 0.868 | 0.888 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.128 | 1.53 | 1.5 | 1.53 | 1.44 | 1.47 | 1.53 | 45.63 | 50.21 | 51.99 | 0 | - - - | - - - | - - - | - - - | 23923 | 21130 | 22032 | 67085 | Over-range | 10137 | 9604 | 10934 | 30760 | 9912 | 9487 | 10163 | 29795 | 21633 | 18801 | 19104 | 59538 | 21633 | 18801 | 19104 | 59538 | - - - | - - - | - - - | - - -
5/5/2026 | 3:45:00 PM | 280.12 | 277.09 | 277.42 | 484.67 | 478.24 | 482.69 | 89.1888 | 78.5013 | 82.5392 | 1.9317 | 1.435 | 1.436 | 1.435 | 1.98 | 1.966 | 2.022 | Over-range | 59.99 | 22545 | 19300 | 19774 | 61619 | - - - | - - - | - - - | - - - | 22545 | 19300 | 19774 | 61619 | 2215 | 1436 | 4248 | 7899 | - - - | - - - | - - - | - - - | 2215 | 1436 | 4248 | 7899 | 24946 | 21723 | 22870 | 69538 | # # # | # # # | # # # | # # # | 0.904 | 0.888 | 0.865 | 0.886 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.128 | 1.56 | 1.53 | 1.58 | 1.47 | 1.51 | 1.57 | 46.21 | 50.95 | 52.77 | 0 | - - - | - - - | - - - | - - - | 24946 | 21723 | 22870 | 69538 | Over-range | 10671 | 9967 | 11484 | 32214 | 10439 | 9863 | 10670 | 31231 | 22512 | 19284 | 19754 | 61550 | 22512 | 19284 | 19754 | 61550 | - - - | - - - | - - - | - - -
5/5/2026 | 4:00:00 PM | 279.71 | 276.65 | 276.96 | 483.96 | 477.44 | 481.93 | 87.2348 | 76.9376 | 80.7505 | 2.1356 | 1.434 | 1.435 | 1.435 | 1.972 | 1.95 | 2.009 | Over-range | 60.01 | 22065 | 18921 | 19355 | 60341 | - - - | - - - | - - - | - - - | 22065 | 18921 | 19355 | 60341 | 2096 | 1407 | 4137 | 7639 | - - - | - - - | - - - | - - - | 2096 | 1407 | 4137 | 7639 | 24340 | 21236 | 22319 | 67895 | # # # | # # # | # # # | # # # | 0.907 | 0.891 | 0.867 | 0.889 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.127 | 1.55 | 1.52 | 1.57 | 1.46 | 1.51 | 1.56 | 45.41 | 50.19 | 52.04 | 0 | - - - | - - - | - - - | - - - | 24340 | 21236 | 22319 | 67895 | Over-range | 10263 | 9637 | 11106 | 31100 | 10047 | 9534 | 10306 | 30148 | 22031 | 18908 | 19335 | 60274 | 22031 | 18908 | 19335 | 60274 | - - - | - - - | - - - | - - -
5/5/2026 | 4:15:00 PM | 279.73 | 276.74 | 277.1 | 484 | 477.68 | 482.07 | 88.9913 | 78.6333 | 82.5216 | 2.0001 | 1.435 | 1.436 | 1.435 | 1.979 | 1.957 | 2.013 | Over-range | 60.01 | 22474 | 19327 | 19785 | 61586 | - - - | - - - | - - - | - - - | 22474 | 19327 | 19785 | 61586 | 2185 | 1477 | 4185 | 7848 | - - - | - - - | - - - | - - - | 2185 | 1477 | 4185 | 7848 | 24850 | 21727 | 22835 | 69412 | # # # | # # # | # # # | # # # | 0.904 | 0.889 | 0.866 | 0.887 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.127 | 1.56 | 1.52 | 1.57 | 1.47 | 1.5 | 1.57 | 46.03 | 50.6 | 52.4 | 0 | - - - | - - - | - - - | - - - | 24850 | 21727 | 22835 | 69412 | Over-range | 10596 | 9924 | 11396 | 32004 | 10368 | 9813 | 10599 | 31027 | 22444 | 19308 | 19768 | 61519 | 22444 | 19308 | 19768 | 61519 | - - - | - - - | - - - | - - -
5/5/2026 | 4:30:00 PM | 279.55 | 276.55 | 276.75 | 483.77 | 477.18 | 481.57 | 88.4092 | 77.9624 | 81.4021 | 2.1033 | 1.435 | 1.436 | 1.435 | 1.968 | 1.96 | 2.017 | Over-range | 60.01 | 22347 | 19184 | 19482 | 61014 | - - - | - - - | - - - | - - - | 22347 | 19184 | 19482 | 61014 | 2202 | 1357 | 4166 | 7725 | - - - | - - - | - - - | - - - | 2202 | 1357 | 4166 | 7725 | 24668 | 21524 | 22494 | 68687 | # # # | # # # | # # # | # # # | 0.906 | 0.891 | 0.866 | 0.888 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.978 | 0.99 | - - - | 0.127 | 1.59 | 1.54 | 1.6 | 1.5 | 1.53 | 1.6 | 45.53 | 50.16 | 52.34 | 0 | - - - | - - - | - - - | - - - | 24668 | 21524 | 22494 | 68687 | Over-range | 10437 | 9756 | 11237 | 31527 | 10201 | 9661 | 10436 | 30566 | 22319 | 19173 | 19465 | 60957 | 22319 | 19173 | 19465 | 60957 | - - - | - - - | - - - | - - -
5/5/2026 | 4:45:00 PM | 279.2 | 276.07 | 276.3 | 483.07 | 476.3 | 480.93 | 88.474 | 77.885 | 81.4833 | 2.3216 | 1.435 | 1.436 | 1.435 | 1.968 | 1.959 | 2.018 | Over-range | 60 | 22337 | 19126 | 19457 | 60919 | - - - | - - - | - - - | - - - | 22337 | 19126 | 19457 | 60919 | 2165 | 1360 | 4221 | 7746 | - - - | - - - | - - - | - - - | 2165 | 1360 | 4221 | 7746 | 24642 | 21455 | 22470 | 68566 | # # # | # # # | # # # | # # # | 0.906 | 0.891 | 0.866 | 0.888 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.977 | 0.99 | - - - | 0.127 | 1.57 | 1.55 | 1.6 | 1.48 | 1.54 | 1.59 | 45.38 | 50.09 | 52.21 | 0 | - - - | - - - | - - - | - - - | 24642 | 21455 | 22470 | 68566 | Over-range | 10397 | 9717 | 11231 | 31446 | 10169 | 9622 | 10407 | 30477 | 22309 | 19110 | 19440 | 60859 | 22309 | 19110 | 19440 | 60859 | - - - | - - - | - - - | - - -
5/5/2026 | 5:00:00 PM | 279.16 | 275.85 | 276.18 | 482.84 | 475.93 | 480.88 | 91.571 | 80.1067 | 84.4674 | 2.1518 | 1.435 | 1.437 | 1.436 | 1.971 | 1.957 | 2.019 | Over-range | 60.01 | 23152 | 19686 | 20194 | 63031 | - - - | - - - | - - - | - - - | 23152 | 19686 | 20194 | 63031 | 2162 | 1403 | 4384 | 7950 | - - - | - - - | - - - | - - - | 2162 | 1403 | 4384 | 7950 | 25524 | 22068 | 23300 | 70892 | # # # | # # # | # # # | # # # | 0.907 | 0.892 | 0.867 | 0.889 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.977 | 0.99 | - - - | 0.126 | 1.59 | 1.58 | 1.63 | 1.5 | 1.57 | 1.62 | 45.35 | 49.95 | 52.03 | 0 | - - - | - - - | - - - | - - - | 25524 | 22068 | 23300 | 70892 | Over-range | 10740 | 9969 | 11618 | 32431 | 10519 | 9870 | 10759 | 31442 | 23120 | 19673 | 20179 | 62972 | 23120 | 19673 | 20179 | 62972 | - - - | - - - | - - - | - - -
5/5/2026 | 5:15:00 PM | 280.46 | 277.32 | 277.6 | 485.21 | 478.52 | 483.16 | 89.2864 | 78.6029 | 82.423 | 2.0149 | 1.435 | 1.436 | 1.436 | 1.959 | 1.944 | 2.001 | Over-range | 60.02 | 22733 | 19463 | 19890 | 62086 | - - - | - - - | - - - | - - - | 22733 | 19463 | 19890 | 62086 | 2160 | 1386 | 4203 | 7749 | - - - | - - - | - - - | - - - | 2160 | 1386 | 4203 | 7749 | 24985 | 21755 | 22840 | 69579 | # # # | # # # | # # # | # # # | 0.91 | 0.895 | 0.871 | 0.892 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.991 | - - - | 0.125 | 1.59 | 1.56 | 1.61 | 1.5 | 1.54 | 1.6 | 44.46 | 49.23 | 51.17 | 0 | - - - | - - - | - - - | - - - | 24985 | 21755 | 22840 | 69579 | Over-range | 10353 | 9715 | 11219 | 31387 | 10125 | 9615 | 10402 | 30415 | 22700 | 19445 | 19868 | 62013 | 22700 | 19445 | 19868 | 62013 | - - - | - - - | - - - | - - -
5/5/2026 | 5:30:00 PM | 280.43 | 277.22 | 277.53 | 485.1 | 478.34 | 483.1 | 91.3095 | 79.989 | 84.3634 | 2.0234 | 1.436 | 1.437 | 1.437 | 1.973 | 1.959 | 2.018 | Over-range | 60.01 | 23197 | 19751 | 20283 | 63231 | - - - | - - - | - - - | - - - | 23197 | 19751 | 20283 | 63231 | 2190 | 1431 | 4377 | 7998 | - - - | - - - | - - - | - - - | 2190 | 1431 | 4377 | 7998 | 25563 | 22141 | 23379 | 71083 | # # # | # # # | # # # | # # # | 0.907 | 0.892 | 0.868 | 0.889 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.977 | 0.99 | - - - | 0.127 | 1.57 | 1.54 | 1.6 | 1.48 | 1.52 | 1.58 | 45.28 | 50.01 | 51.94 | 0 | - - - | - - - | - - - | - - - | 25563 | 22141 | 23379 | 71083 | Over-range | 10735 | 10002 | 11623 | 32462 | 10509 | 9899 | 10767 | 31462 | 23160 | 19732 | 20260 | 63153 | 23160 | 19732 | 20260 | 63153 | - - - | - - - | - - - | - - -
5/5/2026 | 5:45:00 PM | 281.11 | 277.95 | 278.19 | 486.36 | 479.55 | 484.22 | 88.8663 | 78.0515 | 81.8616 | 2.1198 | 1.436 | 1.437 | 1.437 | 1.965 | 1.949 | 2.01 | Over-range | 60 | 22680 | 19356 | 19765 | 61801 | - - - | - - - | - - - | - - - | 22680 | 19356 | 19765 | 61801 | 2137 | 1354 | 4241 | 7732 | - - - | - - - | - - - | - - - | 2137 | 1354 | 4241 | 7732 | 24924 | 21652 | 22732 | 69308 | # # # | # # # | # # # | # # # | 0.91 | 0.894 | 0.87 | 0.892 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.978 | 0.99 | - - - | 0.125 | 1.57 | 1.54 | 1.59 | 1.48 | 1.52 | 1.58 | 44.51 | 49.49 | 51.45 | 0 | - - - | - - - | - - - | - - - | 24924 | 21652 | 22732 | 69308 | Over-range | 10323 | 9697 | 11220 | 31347 | 10099 | 9602 | 10387 | 30378 | 22641 | 19334 | 19740 | 61715 | 22641 | 19334 | 19740 | 61715 | - - - | - - - | - - - | - - -
5/5/2026 | 6:00:00 PM | 281.27 | 278.14 | 278.38 | 486.65 | 479.9 | 484.52 | 90.2259 | 79.4459 | 82.8662 | 2.5145 | 1.436 | 1.437 | 1.437 | 1.976 | 1.972 | 2.031 | Over-range | 60.01 | 22964 | 19665 | 19928 | 62557 | - - - | - - - | - - - | - - - | 22964 | 19665 | 19928 | 62557 | 2242 | 1418 | 4383 | 8044 | - - - | - - - | - - - | - - - | 2242 | 1418 | 4383 | 8044 | 25339 | 22068 | 23040 | 70447 | # # # | # # # | # # # | # # # | 0.906 | 0.891 | 0.865 | 0.888 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.977 | 0.99 | - - - | 0.129 | 1.53 | 1.5 | 1.55 | 1.44 | 1.48 | 1.54 | 45.61 | 50.33 | 52.55 | 0 | - - - | - - - | - - - | - - - | 25339 | 22068 | 23040 | 70447 | Over-range | 10704 | 10011 | 11557 | 32379 | 10467 | 9909 | 10694 | 31364 | 22917 | 19642 | 19895 | 62455 | 22917 | 19642 | 19895 | 62455 | - - - | - - - | - - - | - - -
5/5/2026 | 6:15:00 PM | 282.11 | 279.02 | 279.28 | 488.13 | 481.46 | 486.02 | 90.2084 | 79.1237 | 83.2207 | 2.4042 | 1.435 | 1.435 | 1.436 | 1.983 | 1.962 | 2.03 | Over-range | 60.01 | 23064 | 19641 | 20096 | 62802 | - - - | - - - | - - - | - - - | 23064 | 19641 | 20096 | 62802 | 2150 | 1432 | 4430 | 8012 | - - - | - - - | - - - | - - - | 2150 | 1432 | 4430 | 8012 | 25402 | 22039 | 23209 | 70649 | # # # | # # # | # # # | # # # | 0.908 | 0.891 | 0.866 | 0.889 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.976 | 0.99 | - - - | 0.128 | 1.44 | 1.4 | 1.42 | 1.36 | 1.35 | 1.42 | 45.29 | 50.37 | 52.36 | 0 | - - - | - - - | - - - | - - - | 25402 | 22039 | 23209 | 70649 | Over-range | 10635 | 9994 | 11603 | 32344 | 10414 | 9890 | 10724 | 31336 | 23016 | 19610 | 20055 | 62681 | 23016 | 19610 | 20055 | 62681 | - - - | - - - | - - - | - - -
5/5/2026 | 6:30:00 PM | 282.12 | 279.06 | 279.22 | 488.22 | 481.44 | 485.94 | 89.1875 | 77.9595 | 82.0281 | 2.1776 | 1.435 | 1.434 | 1.436 | 1.98 | 1.969 | 2.034 | Over-range | 60 | 22801 | 19340 | 19779 | 61920 | - - - | - - - | - - - | - - - | 22801 | 19340 | 19779 | 61920 | 2141 | 1330 | 4378 | 7850 | - - - | - - - | - - - | - - - | 2141 | 1330 | 4378 | 7850 | 25108 | 21715 | 22865 | 69688 | # # # | # # # | # # # | # # # | 0.908 | 0.891 | 0.865 | 0.888 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.976 | 0.99 | - - - | 0.127 | 1.41 | 1.38 | 1.4 | 1.34 | 1.33 | 1.39 | 45.21 | 50.56 | 52.52 | 0 | - - - | - - - | - - - | - - - | 25108 | 21715 | 22865 | 69688 | Over-range | 10502 | 9869 | 11464 | 31950 | 10281 | 9779 | 10595 | 30971 | 22748 | 19310 | 19740 | 61798 | 22748 | 19310 | 19740 | 61798 | - - - | - - - | - - - | - - -
5/5/2026 | 6:45:00 PM | 282.33 | 279.28 | 279.44 | 488.59 | 481.83 | 486.3 | 90.9216 | 79.4472 | 83.4589 | 2.3229 | 1.435 | 1.434 | 1.435 | 1.99 | 1.986 | 2.049 | Over-range | 59.99 | 23203 | 19680 | 20065 | 62948 | - - - | - - - | - - - | - - - | 23203 | 19680 | 20065 | 62948 | 2232 | 1378 | 4513 | 8123 | - - - | - - - | - - - | - - - | 2232 | 1378 | 4513 | 8123 | 25632 | 22160 | 23293 | 71084 | # # # | # # # | # # # | # # # | 0.905 | 0.888 | 0.861 | 0.885 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.975 | 0.99 | - - - | 0.129 | 1.4 | 1.36 | 1.38 | 1.33 | 1.32 | 1.37 | 46.07 | 51.3 | 53.41 | 0 | - - - | - - - | - - - | - - - | 25632 | 22160 | 23293 | 71084 | Over-range | 10884 | 10182 | 11825 | 33008 | 10652 | 10088 | 10930 | 31993 | 23151 | 19650 | 20023 | 62824 | 23151 | 19650 | 20023 | 62824 | - - - | - - - | - - - | - - -
5/5/2026 | 7:00:00 PM | 282.68 | 279.64 | 279.77 | 489.21 | 482.43 | 486.88 | 89.1165 | 77.6269 | 82.039 | 2.0647 | 1.434 | 1.433 | 1.434 | 1.986 | 1.97 | 2.038 | Over-range | 60 | 22836 | 19278 | 19796 | 61910 | - - - | - - - | - - - | - - - | 22836 | 19278 | 19796 | 61910 | 2132 | 1306 | 4431 | 7869 | - - - | - - - | - - - | - - - | 2132 | 1306 | 4431 | 7869 | 25133 | 21665 | 22912 | 69711 | # # # | # # # | # # # | # # # | 0.909 | 0.89 | 0.864 | 0.888 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.976 | 0.99 | - - - | 0.127 | 1.37 | 1.32 | 1.33 | 1.3 | 1.27 | 1.33 | 45.15 | 50.85 | 52.73 | 0 | - - - | - - - | - - - | - - - | 25133 | 21665 | 22912 | 69711 | Over-range | 10487 | 9880 | 11527 | 32019 | 10268 | 9793 | 10641 | 31037 | 22778 | 19245 | 19749 | 61772 | 22778 | 19245 | 19749 | 61772 | - - - | - - - | - - - | - - -
5/5/2026 | 7:15:00 PM | 282.58 | 279.66 | 279.63 | 489.21 | 482.34 | 486.6 | 91.2626 | 79.5174 | 83.2492 | 2.2954 | 1.435 | 1.433 | 1.434 | 1.984 | 1.993 | 2.058 | Over-range | 60 | 23338 | 19734 | 19997 | 63069 | - - - | - - - | - - - | - - - | 23338 | 19734 | 19997 | 63069 | 2310 | 1254 | 4568 | 8132 | - - - | - - - | - - - | - - - | 2310 | 1254 | 4568 | 8132 | 25750 | 22207 | 23251 | 71208 | # # # | # # # | # # # | # # # | 0.906 | 0.889 | 0.86 | 0.886 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.975 | 0.989 | - - - | 0.129 | 1.35 | 1.3 | 1.3 | 1.29 | 1.24 | 1.3 | 45.74 | 51.3 | 53.69 | 0 | - - - | - - - | - - - | - - - | 25750 | 22207 | 23251 | 71208 | Over-range | 10872 | 10182 | 11858 | 33044 | 10624 | 10104 | 10943 | 32028 | 23278 | 19701 | 19947 | 62927 | 23278 | 19701 | 19947 | 62927 | - - - | - - - | - - - | - - -
5/5/2026 | 7:30:00 PM | 282.99 | 280.12 | 280.05 | 489.96 | 483.11 | 487.28 | 88.2546 | 77.5249 | 80.5647 | 2.835 | 1.434 | 1.432 | 1.434 | 1.976 | 1.972 | 2.043 | Over-range | 60 | 22664 | 19335 | 19446 | 61445 | - - - | - - - | - - - | - - - | 22664 | 19335 | 19446 | 61445 | 2187 | 1273 | 4405 | 7865 | - - - | - - - | - - - | - - - | 2187 | 1273 | 4405 | 7865 | 24915 | 21672 | 22517 | 69104 | # # # | # # # | # # # | # # # | 0.91 | 0.892 | 0.864 | 0.889 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.975 | 0.99 | - - - | 0.128 | 1.33 | 1.28 | 1.26 | 1.26 | 1.2 | 1.27 | 44.75 | 50.2 | 52.71 | 0 | - - - | - - - | - - - | - - - | 24915 | 21672 | 22517 | 69104 | Over-range | 10336 | 9783 | 11343 | 31594 | 10102 | 9700 | 10453 | 30599 | 22608 | 19303 | 19397 | 61308 | 22608 | 19303 | 19397 | 61308 | - - - | - - - | - - - | - - -
5/5/2026 | 7:45:00 PM | 283.12 | 280.43 | 280.31 | 490.32 | 483.69 | 487.55 | 90.3284 | 80.0144 | 82.1016 | 3.0791 | 1.435 | 1.432 | 1.434 | 1.978 | 2.001 | 2.06 | Over-range | 59.99 | 23093 | 19925 | 19762 | 62781 | - - - | - - - | - - - | - - - | 23093 | 19925 | 19762 | 62781 | 2475 | 1312 | 4514 | 8300 | - - - | - - - | - - - | - - - | 2475 | 1312 | 4514 | 8300 | 25536 | 22408 | 22986 | 70930 | # # # | # # # | # # # | # # # | 0.904 | 0.889 | 0.86 | 0.885 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.975 | 0.989 | - - - | 0.132 | 1.34 | 1.28 | 1.26 | 1.27 | 1.2 | 1.28 | 46.13 | 51.11 | 53.81 | 0 | - - - | - - - | - - - | - - - | 25536 | 22408 | 22986 | 70930 | Over-range | 10889 | 10248 | 11735 | 32994 | 10604 | 10164 | 10832 | 31932 | 23031 | 19891 | 19710 | 62633 | 23031 | 19891 | 19710 | 62633 | - - - | - - - | - - - | - - -
5/5/2026 | 8:00:00 PM | 283.6 | 280.9 | 280.73 | 491.18 | 484.45 | 488.32 | 87.8689 | 77.5212 | 79.9552 | 2.8852 | 1.434 | 1.431 | 1.433 | 1.982 | 1.994 | 2.059 | Over-range | 60 | 22532 | 19324 | 19265 | 61121 | - - - | - - - | - - - | - - - | 22532 | 19324 | 19265 | 61121 | 2354 | 1233 | 4432 | 8019 | - - - | - - - | - - - | - - - | 2354 | 1233 | 4432 | 8019 | 24865 | 21731 | 22408 | 69003 | # # # | # # # | # # # | # # # | 0.906 | 0.889 | 0.86 | 0.886 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.974 | 0.989 | - - - | 0.131 | 1.31 | 1.25 | 1.23 | 1.25 | 1.17 | 1.24 | 45.63 | 51.12 | 53.7 | 0 | - - - | - - - | - - - | - - - | 24865 | 21731 | 22408 | 69003 | Over-range | 10502 | 9936 | 11437 | 32003 | 10234 | 9859 | 10543 | 30982 | 22473 | 19288 | 19212 | 60974 | 22473 | 19288 | 19212 | 60974 | - - - | - - - | - - - | - - -
5/5/2026 | 8:15:00 PM | 283.96 | 281.25 | 281.07 | 491.8 | 485.05 | 488.93 | 88.3287 | 77.567 | 80.5302 | 2.5136 | 1.434 | 1.432 | 1.433 | 1.987 | 2 | 2.064 | Over-range | 60 | 22659 | 19328 | 19400 | 61387 | - - - | - - - | - - - | - - - | 22659 | 19328 | 19400 | 61387 | 2367 | 1194 | 4475 | 8037 | - - - | - - - | - - - | - - - | 2367 | 1194 | 4475 | 8037 | 25030 | 21775 | 22597 | 69402 | # # # | # # # | # # # | # # # | 0.905 | 0.888 | 0.859 | 0.884 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.974 | 0.989 | - - - | 0.131 | 1.3 | 1.25 | 1.22 | 1.24 | 1.16 | 1.23 | 45.93 | 51.62 | 54.04 | 0 | - - - | - - - | - - - | - - - | 25030 | 21775 | 22597 | 69402 | Over-range | 10621 | 10024 | 11581 | 32355 | 10353 | 9952 | 10681 | 31341 | 22594 | 19289 | 19344 | 61227 | 22594 | 19289 | 19344 | 61227 | - - - | - - - | - - - | - - -
5/5/2026 | 8:30:00 PM | 283.23 | 280.6 | 280.28 | 490.66 | 483.79 | 487.55 | 88.581 | 77.6541 | 80.0825 | 2.4312 | 1.433 | 1.431 | 1.433 | 1.98 | 2.019 | 2.077 | Over-range | 60 | 22632 | 19279 | 19175 | 61085 | - - - | - - - | - - - | - - - | 22632 | 19279 | 19175 | 61085 | 2466 | 1064 | 4473 | 8004 | - - - | - - - | - - - | - - - | 2466 | 1064 | 4473 | 8004 | 25038 | 21749 | 22409 | 69196 | # # # | # # # | # # # | # # # | 0.904 | 0.886 | 0.856 | 0.883 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.974 | 0.989 | - - - | 0.131 | 1.28 | 1.23 | 1.2 | 1.22 | 1.14 | 1.21 | 46.21 | 52.01 | 54.67 | 0 | - - - | - - - | - - - | - - - | 25038 | 21749 | 22409 | 69196 | Over-range | 10700 | 10062 | 11591 | 32487 | 10412 | 10006 | 10693 | 31486 | 22566 | 19247 | 19124 | 60937 | 22566 | 19247 | 19124 | 60937 | - - - | - - - | - - - | - - -
5/5/2026 | 8:45:00 PM | 283.14 | 280.45 | 280.2 | 490.43 | 483.59 | 487.45 | 86.3577 | 75.5559 | 78.3513 | 2.3668 | 1.433 | 1.431 | 1.432 | 1.983 | 2 | 2.069 | Over-range | 60 | 22097 | 18754 | 18770 | 59622 | - - - | - - - | - - - | - - - | 22097 | 18754 | 18770 | 59622 | 2315 | 1057 | 4380 | 7752 | - - - | - - - | - - - | - - - | 2315 | 1057 | 4380 | 7752 | 24386 | 21137 | 21910 | 67433 | # # # | # # # | # # # | # # # | 0.906 | 0.887 | 0.857 | 0.884 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.974 | 0.989 | - - - | 0.13 | 1.3 | 1.23 | 1.21 | 1.23 | 1.14 | 1.22 | 45.63 | 51.75 | 54.35 | 0 | - - - | - - - | - - - | - - - | 24386 | 21137 | 21910 | 67433 | Over-range | 10303 | 9744 | 11293 | 31480 | 10039 | 9686 | 10409 | 30511 | 22037 | 18718 | 18719 | 59474 | 22037 | 18718 | 18719 | 59474 | - - - | - - - | - - - | - - -
5/5/2026 | 9:00:00 PM | 283.55 | 280.84 | 280.52 | 491.17 | 484.18 | 488.06 | 88.9528 | 77.4516 | 80.0632 | 2.3883 | 1.434 | 1.432 | 1.433 | 1.988 | 2.027 | 2.093 | Over-range | 60.01 | 22752 | 19231 | 19118 | 61102 | - - - | - - - | - - - | - - - | 22752 | 19231 | 19118 | 61102 | 2465 | 1011 | 4563 | 8039 | - - - | - - - | - - - | - - - | 2465 | 1011 | 4563 | 8039 | 25184 | 21722 | 22433 | 69339 | # # # | # # # | # # # | # # # | 0.903 | 0.885 | 0.852 | 0.881 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.972 | 0.989 | - - - | 0.132 | 1.32 | 1.25 | 1.23 | 1.25 | 1.17 | 1.25 | 46.41 | 52.4 | 55.39 | 0 | - - - | - - - | - - - | - - - | 25184 | 21722 | 22433 | 69339 | Over-range | 10788 | 10095 | 11730 | 32761 | 10502 | 10044 | 10806 | 31760 | 22687 | 19194 | 19064 | 60946 | 22687 | 19194 | 19064 | 60946 | - - - | - - - | - - - | - - -
5/5/2026 | 9:15:00 PM | 283.66 | 281.06 | 280.72 | 491.43 | 484.59 | 488.28 | 84.6196 | 74.1169 | 76.5337 | 2.2972 | 1.433 | 1.43 | 1.432 | 1.979 | 1.996 | 2.068 | Over-range | 60 | 21728 | 18463 | 18379 | 58571 | - - - | - - - | - - - | - - - | 21728 | 18463 | 18379 | 58571 | 2285 | 992 | 4267 | 7544 | - - - | - - - | - - - | - - - | 2285 | 992 | 4267 | 7544 | 23937 | 20778 | 21438 | 66153 | # # # | # # # | # # # | # # # | 0.908 | 0.889 | 0.857 | 0.885 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.974 | 0.989 | - - - | 0.129 | 1.31 | 1.24 | 1.21 | 1.24 | 1.15 | 1.23 | 45.15 | 51.42 | 54.26 | 0 | - - - | - - - | - - - | - - - | 23937 | 20778 | 21438 | 66153 | Over-range | 10030 | 9525 | 11029 | 30729 | 9765 | 9473 | 10170 | 29788 | 21669 | 18427 | 18327 | 58423 | 21669 | 18427 | 18327 | 58423 | - - - | - - - | - - - | - - -
5/5/2026 | 9:30:00 PM | 283.96 | 281.34 | 281.12 | 491.88 | 485.2 | 488.93 | 87.651 | 76.742 | 79.3637 | 2.3818 | 1.433 | 1.431 | 1.432 | 1.999 | 2.024 | 2.09 | Over-range | 60.01 | 22404 | 19045 | 18980 | 60428 | - - - | - - - | - - - | - - - | 22404 | 19045 | 18980 | 60428 | 2434 | 1101 | 4479 | 8013 | - - - | - - - | - - - | - - - | 2434 | 1101 | 4479 | 8013 | 24845 | 21556 | 22280 | 68681 | # # # | # # # | # # # | # # # | 0.902 | 0.883 | 0.852 | 0.88 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.973 | 0.989 | - - - | 0.133 | 1.3 | 1.24 | 1.21 | 1.24 | 1.15 | 1.23 | 46.9 | 52.85 | 55.65 | 0 | - - - | - - - | - - - | - - - | 24845 | 21556 | 22280 | 68681 | Over-range | 10730 | 10093 | 11663 | 32623 | 10450 | 10033 | 10768 | 31624 | 22337 | 19007 | 18923 | 60267 | 22337 | 19007 | 18923 | 60267 | - - - | - - - | - - - | - - -
5/5/2026 | 9:45:00 PM | 284.37 | 281.78 | 281.52 | 492.63 | 485.94 | 489.61 | 84.6045 | 74.1431 | 76.6709 | 2.3281 | 1.432 | 1.43 | 1.431 | 1.992 | 2.005 | 2.077 | Over-range | 60.01 | 21710 | 18450 | 18399 | 58558 | - - - | - - - | - - - | - - - | 21710 | 18450 | 18399 | 58558 | 2309 | 1045 | 4313 | 7667 | - - - | - - - | - - - | - - - | 2309 | 1045 | 4313 | 7667 | 23985 | 20831 | 21531 | 66348 | # # # | # # # | # # # | # # # | 0.905 | 0.886 | 0.855 | 0.883 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.973 | 0.989 | - - - | 0.131 | 1.3 | 1.24 | 1.21 | 1.24 | 1.16 | 1.22 | 45.92 | 52.23 | 54.95 | 0 | - - - | - - - | - - - | - - - | 23985 | 20831 | 21531 | 66348 | Over-range | 10186 | 9668 | 11178 | 31173 | 9920 | 9611 | 10312 | 30216 | 21646 | 18411 | 18350 | 58408 | 21646 | 18411 | 18350 | 58408 | - - - | - - - | - - - | - - -
5/5/2026 | 10:00:00 PM | 284.5 | 281.9 | 281.7 | 492.81 | 486.21 | 489.9 | 84.8018 | 74.1273 | 76.8734 | 2.3237 | 1.433 | 1.43 | 1.431 | 2.007 | 2.023 | 2.093 | Over-range | 60.01 | 21692 | 18376 | 18360 | 58428 | - - - | - - - | - - - | - - - | 21692 | 18376 | 18360 | 58428 | 2347 | 1079 | 4396 | 7822 | - - - | - - - | - - - | - - - | 2347 | 1079 | 4396 | 7822 | 24067 | 20850 | 21612 | 66530 | # # # | # # # | # # # | # # # | 0.901 | 0.881 | 0.85 | 0.878 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.972 | 0.988 | - - - | 0.134 | 1.32 | 1.25 | 1.23 | 1.25 | 1.17 | 1.24 | 47.02 | 53.42 | 56.1 | 0 | - - - | - - - | - - - | - - - | 24067 | 20850 | 21612 | 66530 | Over-range | 10416 | 9847 | 11394 | 31797 | 10147 | 9787 | 10512 | 30820 | 21625 | 18338 | 18301 | 58264 | 21625 | 18338 | 18301 | 58264 | - - - | - - - | - - - | - - -
5/5/2026 | 10:15:00 PM | 284.48 | 281.79 | 281.53 | 492.76 | 485.9 | 489.75 | 85.73 | 74.5386 | 77.3134 | 2.3315 | 1.433 | 1.43 | 1.432 | 2.008 | 2.035 | 2.107 | Over-range | 60.01 | 21920 | 18449 | 18392 | 58761 | - - - | - - - | - - - | - - - | 21920 | 18449 | 18392 | 58761 | 2408 | 1023 | 4516 | 7947 | - - - | - - - | - - - | - - - | 2408 | 1023 | 4516 | 7947 | 24337 | 20963 | 21728 | 67029 | # # # | # # # | # # # | # # # | 0.901 | 0.88 | 0.847 | 0.877 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.971 | 0.988 | - - - | 0.135 | 1.35 | 1.28 | 1.26 | 1.28 | 1.21 | 1.28 | 47.2 | 53.86 | 56.68 | 0 | - - - | - - - | - - - | - - - | 24337 | 20963 | 21728 | 67029 | Over-range | 10565 | 9951 | 11565 | 32233 | 10286 | 9898 | 10646 | 31238 | 21851 | 18408 | 18337 | 58596 | 21851 | 18408 | 18337 | 58596 | - - - | - - - | - - - | - - -
5/5/2026 | 10:30:00 PM | 284.6 | 281.83 | 281.6 | 492.9 | 485.96 | 489.95 | 84.3544 | 73.2412 | 76.336 | 2.2958 | 1.433 | 1.43 | 1.432 | 2.006 | 2.017 | 2.095 | Over-range | 60 | 21643 | 18165 | 18222 | 58031 | - - - | - - - | - - - | - - - | 21643 | 18165 | 18222 | 58031 | 2277 | 1010 | 4444 | 7731 | - - - | - - - | - - - | - - - | 2277 | 1010 | 4444 | 7731 | 23941 | 20590 | 21448 | 65979 | # # # | # # # | # # # | # # # | 0.904 | 0.882 | 0.85 | 0.879 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.971 | 0.988 | - - - | 0.133 | 1.33 | 1.26 | 1.24 | 1.26 | 1.19 | 1.25 | 46.32 | 53.24 | 55.85 | 0 | - - - | - - - | - - - | - - - | 23941 | 20590 | 21448 | 65979 | Over-range | 10222 | 9689 | 11305 | 31373 | 9965 | 9636 | 10395 | 30405 | 21572 | 18123 | 18167 | 57862 | 21572 | 18123 | 18167 | 57862 | - - - | - - - | - - - | - - -
5/5/2026 | 10:45:00 PM | 284.63 | 281.7 | 281.54 | 492.82 | 485.72 | 489.99 | 87.584 | 75.4997 | 79.2095 | 2.3926 | 1.433 | 1.43 | 1.432 | 2.021 | 2.038 | 2.117 | Over-range | 60 | 22409 | 18661 | 18818 | 59888 | - - - | - - - | - - - | - - - | 22409 | 18661 | 18818 | 59888 | 2344 | 1063 | 4718 | 8125 | - - - | - - - | - - - | - - - | 2344 | 1063 | 4718 | 8125 | 24880 | 21230 | 22268 | 68378 | # # # | # # # | # # # | # # # | 0.901 | 0.879 | 0.845 | 0.876 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.97 | 0.988 | - - - | 0.136 | 1.33 | 1.27 | 1.25 | 1.26 | 1.2 | 1.26 | 47.39 | 54.19 | 56.82 | 0 | - - - | - - - | - - - | - - - | 24880 | 21230 | 22268 | 68378 | Over-range | 10801 | 10120 | 11900 | 32984 | 10543 | 10064 | 10925 | 31968 | 22337 | 18617 | 18754 | 59708 | 22337 | 18617 | 18754 | 59708 | - - - | - - - | - - - | - - -
5/5/2026 | 11:00:00 PM | 285.25 | 282.34 | 282.14 | 493.93 | 486.78 | 491.03 | 84.1126 | 72.5731 | 76.2311 | 2.2871 | 1.433 | 1.43 | 1.432 | 2.011 | 2.009 | 2.095 | Over-range | 60.01 | 21678 | 18044 | 18243 | 57965 | - - - | - - - | - - - | - - - | 21678 | 18044 | 18243 | 57965 | 2178 | 993 | 4504 | 7675 | - - - | - - - | - - - | - - - | 2178 | 993 | 4504 | 7675 | 23923 | 20436 | 21458 | 65817 | # # # | # # # | # # # | # # # | 0.906 | 0.883 | 0.85 | 0.881 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.971 | 0.988 | - - - | 0.132 | 1.33 | 1.28 | 1.26 | 1.27 | 1.21 | 1.27 | 45.83 | 53.06 | 55.56 | 0 | - - - | - - - | - - - | - - - | 23923 | 20436 | 21458 | 65817 | Over-range | 10104 | 9591 | 11290 | 31154 | 9866 | 9539 | 10353 | 30194 | 21610 | 18001 | 18185 | 57796 | 21610 | 18001 | 18185 | 57796 | - - - | - - - | - - - | - - -
5/5/2026 | 11:15:00 PM | 285.07 | 282.07 | 282 | 493.5 | 486.42 | 490.81 | 88.3644 | 76.1234 | 80.3047 | 2.3826 | 1.433 | 1.43 | 1.432 | 2.025 | 2.032 | 2.11 | Over-range | 60 | 22674 | 18853 | 19160 | 60687 | - - - | - - - | - - - | - - - | 22674 | 18853 | 19160 | 60687 | 2299 | 1139 | 4779 | 8217 | - - - | - - - | - - - | - - - | 2299 | 1139 | 4779 | 8217 | 25152 | 21445 | 22617 | 69214 | # # # | # # # | # # # | # # # | 0.902 | 0.879 | 0.847 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.97 | 0.988 | - - - | 0.135 | 1.34 | 1.29 | 1.28 | 1.27 | 1.22 | 1.28 | 47.29 | 54.14 | 56.34 | 0 | - - - | - - - | - - - | - - - | 25152 | 21445 | 22617 | 69214 | Over-range | 10878 | 10216 | 12011 | 33263 | 10632 | 10152 | 11019 | 32232 | 22595 | 18805 | 19094 | 60493 | 22595 | 18805 | 19094 | 60493 | - - - | - - - | - - - | - - -
5/5/2026 | 11:30:00 PM | 285.32 | 282.09 | 281.99 | 493.81 | 486.29 | 491.08 | 90.0344 | 77.0062 | 82.7906 | 2.3966 | 1.435 | 1.432 | 1.431 | 2.027 | 1.997 | 2.091 | Over-range | 60 | 23275 | 19163 | 19849 | 62287 | - - - | - - - | - - - | - - - | 23275 | 19163 | 19849 | 62287 | 2117 | 1256 | 4963 | 8336 | - - - | - - - | - - - | - - - | 2117 | 1256 | 4963 | 8336 | 25607 | 21661 | 23269 | 70538 | # # # | # # # | # # # | # # # | 0.909 | 0.885 | 0.853 | 0.883 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.97 | 0.988 | - - - | 0.134 | 1.46 | 1.41 | 1.42 | 1.39 | 1.38 | 1.41 | 45.45 | 52.64 | 54.76 | 0 | - - - | - - - | - - - | - - - | 25607 | 21661 | 23269 | 70538 | Over-range | 10665 | 10095 | 12135 | 33081 | 10452 | 10015 | 11074 | 32013 | 23195 | 19100 | 19778 | 62073 | 23195 | 19100 | 19778 | 62073 | - - - | - - - | - - - | - - -
5/5/2026 | 11:45:00 PM | 285.13 | 281.93 | 281.79 | 493.53 | 485.97 | 490.73 | 100.301 | 86.3572 | 92.9066 | 2.387 | 1.437 | 1.435 | 1.432 | 2.007 | 1.972 | 2.061 | Over-range | 60.01 | 26061 | 21678 | 22510 | 70248 | - - - | - - - | - - - | - - - | 26061 | 21678 | 22510 | 70248 | 2392 | 1581 | 5423 | 9396 | - - - | - - - | - - - | - - - | 2392 | 1581 | 5423 | 9396 | 28573 | 24327 | 26161 | 79061 | # # # | # # # | # # # | # # # | 0.912 | 0.891 | 0.86 | 0.888 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.972 | 0.988 | - - - | 0.134 | 1.59 | 1.57 | 1.56 | 1.53 | 1.54 | 1.56 | 44.65 | 50.85 | 53.29 | 0 | - - - | - - - | - - - | - - - | 28573 | 24327 | 26161 | 79061 | Over-range | 11709 | 11037 | 13322 | 36258 | 11462 | 10923 | 12168 | 35019 | 25962 | 21611 | 22413 | 69986 | 25962 | 21611 | 22413 | 69986 | - - - | - - - | - - - | - - -
5/6/2026 | 12:00:00 AM | 284.96 | 281.8 | 281.68 | 493.24 | 485.79 | 490.48 | 105.499 | 91.7332 | 97.9794 | 2.6668 | 1.436 | 1.434 | 1.431 | 1.986 | 1.95 | 2.036 | Over-range | 60.02 | 27459 | 23122 | 23876 | 74458 | - - - | - - - | - - - | - - - | 27459 | 23122 | 23876 | 74458 | 2572 | 1781 | 5589 | 9942 | - - - | - - - | - - - | - - - | 2572 | 1781 | 5589 | 9942 | 30051 | 25840 | 27589 | 83480 | # # # | # # # | # # # | # # # | 0.914 | 0.895 | 0.865 | 0.892 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.134 | 1.59 | 1.56 | 1.56 | 1.53 | 1.54 | 1.56 | 44.08 | 49.7 | 52.24 | 0 | - - - | - - - | - - - | - - - | 30051 | 25840 | 27589 | 83480 | Over-range | 12204 | 11535 | 13820 | 37741 | 11929 | 11396 | 12639 | 36408 | 27359 | 23058 | 23785 | 74203 | 27359 | 23058 | 23785 | 74203 | - - - | - - - | - - - | - - -
5/6/2026 | 12:15:00 AM | 284.97 | 281.69 | 281.51 | 493.22 | 485.47 | 490.36 | 106.2795 | 91.6765 | 98.5597 | 2.6868 | 1.435 | 1.433 | 1.429 | 1.989 | 1.944 | 2.041 | Over-range | 59.98 | 27707 | 23107 | 23982 | 74796 | - - - | - - - | - - - | - - - | 27707 | 23107 | 23982 | 74796 | 2476 | 1711 | 5710 | 9896 | - - - | - - - | - - - | - - - | 2476 | 1711 | 5710 | 9896 | 30255 | 25805 | 27724 | 83783 | # # # | # # # | # # # | # # # | 0.916 | 0.896 | 0.865 | 0.893 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.132 | 1.58 | 1.56 | 1.56 | 1.52 | 1.53 | 1.55 | 43.55 | 49.52 | 52.09 | 0 | - - - | - - - | - - - | - - - | 30255 | 25805 | 27724 | 83783 | Over-range | 12145 | 11484 | 13904 | 37738 | 11890 | 11356 | 12677 | 36417 | 27603 | 23045 | 23892 | 74539 | 27603 | 23045 | 23892 | 74539 | - - - | - - - | - - - | - - -
5/6/2026 | 12:30:00 AM | 285.24 | 281.92 | 281.83 | 493.61 | 485.95 | 490.91 | 108.4042 | 93.6 | 101.0124 | 2.7633 | 1.435 | 1.433 | 1.429 | 1.99 | 1.936 | 2.035 | Over-range | 60 | 28311 | 23628 | 24660 | 76598 | - - - | - - - | - - - | - - - | 28311 | 23628 | 24660 | 76598 | 2469 | 1832 | 5837 | 10139 | - - - | - - - | - - - | - - - | 2469 | 1832 | 5837 | 10139 | 30897 | 26371 | 28451 | 85719 | # # # | # # # | # # # | # # # | 0.916 | 0.896 | 0.867 | 0.894 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.132 | 1.58 | 1.57 | 1.56 | 1.53 | 1.54 | 1.55 | 43.51 | 49.36 | 51.73 | 0 | - - - | - - - | - - - | - - - | 30897 | 26371 | 28451 | 85719 | Over-range | 12372 | 11709 | 14188 | 38470 | 12123 | 11564 | 12931 | 37110 | 28203 | 23557 | 24568 | 76329 | 28203 | 23557 | 24568 | 76329 | - - - | - - - | - - - | - - -
5/6/2026 | 12:45:00 AM | 285.64 | 282.45 | 282.3 | 494.42 | 486.88 | 491.59 | 109.6134 | 94.9936 | 101.8318 | 2.8418 | 1.436 | 1.433 | 1.43 | 1.981 | 1.932 | 2.03 | Over-range | 60.01 | 28688 | 24047 | 24916 | 77650 | - - - | - - - | - - - | - - - | 28688 | 24047 | 24916 | 77650 | 2595 | 1836 | 5884 | 10315 | - - - | - - - | - - - | - - - | 2595 | 1836 | 5884 | 10315 | 31287 | 26816 | 28733 | 86836 | # # # | # # # | # # # | # # # | 0.917 | 0.897 | 0.867 | 0.894 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.133 | 1.6 | 1.58 | 1.58 | 1.55 | 1.55 | 1.57 | 43.23 | 49.16 | 51.66 | 0 | - - - | - - - | - - - | - - - | 31287 | 26816 | 28733 | 86836 | Over-range | 12481 | 11866 | 14307 | 38862 | 12208 | 11723 | 13041 | 37469 | 28582 | 23978 | 24814 | 77374 | 28582 | 23978 | 24814 | 77374 | - - - | - - - | - - - | - - -
5/6/2026 | 1:00:00 AM | 285.53 | 282.31 | 282.14 | 494.22 | 486.59 | 491.36 | 109.0937 | 94.3107 | 101.1692 | 2.7601 | 1.436 | 1.433 | 1.43 | 1.978 | 1.931 | 2.031 | Over-range | 60 | 28586 | 23899 | 24765 | 77250 | - - - | - - - | - - - | - - - | 28586 | 23899 | 24765 | 77250 | 2568 | 1734 | 5852 | 10154 | - - - | - - - | - - - | - - - | 2568 | 1734 | 5852 | 10154 | 31123 | 26608 | 28527 | 86258 | # # # | # # # | # # # | # # # | 0.919 | 0.898 | 0.868 | 0.896 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.131 | 1.6 | 1.57 | 1.57 | 1.55 | 1.54 | 1.57 | 42.86 | 48.87 | 51.41 | 0 | - - - | - - - | - - - | - - - | 31123 | 26608 | 28527 | 86258 | Over-range | 12305 | 11695 | 14155 | 38370 | 12033 | 11566 | 12888 | 37002 | 28464 | 23828 | 24670 | 76962 | 28464 | 23828 | 24670 | 76962 | - - - | - - - | - - - | - - -
5/6/2026 | 1:15:00 AM | 285.33 | 282.14 | 282.11 | 493.82 | 486.47 | 491.21 | 107.9992 | 93.8221 | 100.9513 | 2.7082 | 1.437 | 1.434 | 1.431 | 1.981 | 1.919 | 2.016 | Over-range | 59.98 | 28287 | 23771 | 24791 | 76850 | - - - | - - - | - - - | - - - | 28287 | 23771 | 24791 | 76850 | 2477 | 1874 | 5732 | 10083 | - - - | - - - | - - - | - - - | 2477 | 1874 | 5732 | 10083 | 30786 | 26451 | 28458 | 85695 | # # # | # # # | # # # | # # # | 0.919 | 0.899 | 0.871 | 0.897 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.974 | 0.989 | - - - | 0.131 | 1.6 | 1.57 | 1.57 | 1.55 | 1.54 | 1.56 | 42.8 | 48.65 | 50.87 | 0 | - - - | - - - | - - - | - - - | 30786 | 26451 | 28458 | 85695 | Over-range | 12142 | 11599 | 13967 | 37904 | 11886 | 11446 | 12737 | 36538 | 28175 | 23693 | 24680 | 76548 | 28175 | 23693 | 24680 | 76548 | - - - | - - - | - - - | - - -
5/6/2026 | 1:30:00 AM | 285.39 | 282.12 | 282.1 | 493.87 | 486.41 | 491.27 | 107.5499 | 93.3468 | 100.5215 | 2.7168 | 1.436 | 1.433 | 1.43 | 1.977 | 1.915 | 2.012 | Over-range | 60.01 | 28193 | 23663 | 24714 | 76570 | - - - | - - - | - - - | - - - | 28193 | 23663 | 24714 | 76570 | 2427 | 1852 | 5704 | 9983 | - - - | - - - | - - - | - - - | 2427 | 1852 | 5704 | 9983 | 30651 | 26307 | 28328 | 85286 | # # # | # # # | # # # | # # # | 0.92 | 0.9 | 0.872 | 0.898 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.974 | 0.989 | - - - | 0.13 | 1.59 | 1.58 | 1.56 | 1.54 | 1.54 | 1.56 | 42.5 | 48.42 | 50.47 | 0 | - - - | - - - | - - - | - - - | 30651 | 26307 | 28328 | 85286 | Over-range | 12018 | 11492 | 13839 | 37543 | 11770 | 11341 | 12608 | 36192 | 28076 | 23575 | 24624 | 76275 | 28076 | 23575 | 24624 | 76275 | - - - | - - - | - - - | - - -
5/6/2026 | 1:45:00 AM | 285.62 | 282.29 | 282.33 | 494.2 | 486.74 | 491.7 | 109.0489 | 94.6879 | 102.1658 | 2.765 | 1.436 | 1.433 | 1.43 | 1.982 | 1.918 | 2.015 | Over-range | 60.01 | 28589 | 24003 | 25132 | 77724 | - - - | - - - | - - - | - - - | 28589 | 24003 | 25132 | 77724 | 2464 | 1949 | 5813 | 10226 | - - - | - - - | - - - | - - - | 2464 | 1949 | 5813 | 10226 | 31121 | 26712 | 28827 | 86659 | # # # | # # # | # # # | # # # | 0.919 | 0.899 | 0.872 | 0.897 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.974 | 0.989 | - - - | 0.132 | 1.63 | 1.59 | 1.59 | 1.56 | 1.57 | 1.59 | 42.88 | 48.67 | 50.65 | 0 | - - - | - - - | - - - | - - - | 31121 | 26712 | 28827 | 86659 | Over-range | 12288 | 11719 | 14115 | 38313 | 12037 | 11556 | 12863 | 36924 | 28477 | 23920 | 25025 | 77422 | 28477 | 23920 | 25025 | 77422 | - - - | - - - | - - - | - - -
5/6/2026 | 2:00:00 AM | 285.68 | 282.35 | 282.32 | 494.34 | 486.76 | 491.73 | 110.8666 | 96.2016 | 103.5644 | 2.8185 | 1.436 | 1.434 | 1.43 | 1.973 | 1.915 | 2.011 | Over-range | 60.01 | 29122 | 24443 | 25510 | 79075 | - - - | - - - | - - - | - - - | 29122 | 24443 | 25510 | 79075 | 2539 | 1913 | 5910 | 10362 | - - - | - - - | - - - | - - - | 2539 | 1913 | 5910 | 10362 | 31647 | 27146 | 29221 | 88014 | # # # | # # # | # # # | # # # | 0.92 | 0.9 | 0.873 | 0.898 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.974 | 0.989 | - - - | 0.131 | 1.65 | 1.61 | 1.61 | 1.58 | 1.59 | 1.61 | 42.39 | 48.2 | 50.29 | 0 | - - - | - - - | - - - | - - - | 31647 | 27146 | 29221 | 88014 | Over-range | 12381 | 11806 | 14246 | 38634 | 12118 | 11650 | 12962 | 37219 | 29005 | 24358 | 25406 | 78769 | 29005 | 24358 | 25406 | 78769 | - - - | - - - | - - - | - - -
5/6/2026 | 2:15:00 AM | 285.7 | 282.38 | 282.29 | 494.41 | 486.75 | 491.71 | 115.8397 | 100.6609 | 107.6354 | 3.0536 | 1.438 | 1.435 | 1.432 | 1.961 | 1.917 | 2.012 | Over-range | 60 | 30480 | 25656 | 26546 | 82682 | - - - | - - - | - - - | - - - | 30480 | 25656 | 26546 | 82682 | 2755 | 1919 | 6149 | 10824 | - - - | - - - | - - - | - - - | 2755 | 1919 | 6149 | 10824 | 33091 | 28420 | 30381 | 91891 | # # # | # # # | # # # | # # # | 0.921 | 0.903 | 0.874 | 0.9 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.974 | 0.989 | - - - | 0.131 | 1.68 | 1.65 | 1.66 | 1.62 | 1.63 | 1.66 | 42.06 | 47.58 | 50.08 | 0 | - - - | - - - | - - - | - - - | 33091 | 28420 | 30381 | 91891 | Over-range | 12881 | 12225 | 14774 | 40094 | 12583 | 12073 | 13434 | 38606 | 30364 | 25574 | 26443 | 82381 | 30364 | 25574 | 26443 | 82381 | - - - | - - - | - - - | - - -
5/6/2026 | 2:30:00 AM | 285.77 | 282.42 | 282.44 | 494.46 | 486.93 | 491.94 | 121.7126 | 106.0301 | 112.9103 | 3.348 | 1.437 | 1.434 | 1.431 | 1.942 | 1.893 | 1.997 | Over-range | 60 | 32159 | 27125 | 27962 | 87246 | - - - | - - - | - - - | - - - | 32159 | 27125 | 27962 | 87246 | 2911 | 1948 | 6432 | 11291 | - - - | - - - | - - - | - - - | 2911 | 1948 | 6432 | 11291 | 34774 | 29937 | 31886 | 96598 | # # # | # # # | # # # | # # # | 0.925 | 0.906 | 0.877 | 0.903 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.974 | 0.989 | - - - | 0.129 | 1.67 | 1.65 | 1.66 | 1.61 | 1.63 | 1.65 | 40.88 | 46.63 | 49.23 | 0 | - - - | - - - | - - - | - - - | 34774 | 29937 | 31886 | 96598 | Over-range | 13230 | 12666 | 15325 | 41462 | 12905 | 12514 | 13910 | 39895 | 32043 | 27044 | 27856 | 86943 | 32043 | 27044 | 27856 | 86943 | - - - | - - - | - - - | - - -
5/6/2026 | 2:45:00 AM | 285.82 | 282.47 | 282.43 | 494.57 | 486.94 | 491.95 | 128.4401 | 111.5567 | 116.9776 | 3.5868 | 1.437 | 1.434 | 1.432 | 1.902 | 1.872 | 1.992 | Over-range | 60.01 | 34149 | 28683 | 28988 | 91820 | - - - | - - - | - - - | - - - | 34149 | 28683 | 28988 | 91820 | 3282 | 1560 | 6774 | 11616 | - - - | - - - | - - - | - - - | 3282 | 1560 | 6774 | 11616 | 36673 | 31485 | 33017 | 101174 | # # # | # # # | # # # | # # # | 0.931 | 0.911 | 0.878 | 0.908 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.974 | 0.989 | - - - | 0.127 | 1.7 | 1.69 | 1.7 | 1.64 | 1.68 | 1.69 | 38.65 | 45.37 | 48.67 | 0 | - - - | - - - | - - - | - - - | 36673 | 31485 | 33017 | 101174 | Over-range | 13365 | 12982 | 15800 | 42480 | 12955 | 12886 | 14274 | 40861 | 34028 | 28605 | 28878 | 91512 | 34028 | 28605 | 28878 | 91512 | - - - | - - - | - - - | - - -
5/6/2026 | 3:00:00 AM | 285.88 | 282.46 | 282.48 | 494.6 | 486.95 | 492.08 | 140.8392 | 121.2172 | 124.7502 | 4.7062 | 1.437 | 1.435 | 1.432 | 1.875 | 1.869 | 2.015 | Over-range | 60.01 | 37642 | 31278 | 30788 | 99708 | - - - | - - - | - - - | - - - | 37642 | 31278 | 30788 | 99708 | 3854 | 1079 | 7644 | 12576 | - - - | - - - | - - - | - - - | 3854 | 1079 | 7644 | 12576 | 40251 | 34231 | 35231 | 109713 | # # # | # # # | # # # | # # # | 0.935 | 0.914 | 0.874 | 0.909 | # # # | # # # | # # # | - - - | 0.995 | 0.999 | 0.97 | 0.988 | - - - | 0.126 | 1.71 | 1.71 | 1.74 | 1.65 | 1.71 | 1.71 | 37.16 | 44.73 | 49.03 | 0 | - - - | - - - | - - - | - - - | 40251 | 34231 | 35231 | 109713 | Over-range | 14256 | 13908 | 17126 | 45774 | 13725 | 13865 | 15325 | 44012 | 37513 | 31210 | 30673 | 99396 | 37513 | 31210 | 30673 | 99396 | - - - | - - - | - - - | - - -
5/6/2026 | 3:15:00 AM | 285.5 | 282.12 | 282.12 | 493.98 | 486.37 | 491.42 | 145.2714 | 125.752 | 128.7061 | 5.0952 | 1.437 | 1.434 | 1.432 | 1.849 | 1.84 | 1.985 | Over-range | 60 | 38918 | 32541 | 31952 | 103412 | - - - | - - - | - - - | - - - | 38918 | 32541 | 31952 | 103412 | 3931 | 1122 | 7748 | 12801 | - - - | - - - | - - - | - - - | 3931 | 1122 | 7748 | 12801 | 41457 | 35462 | 36299 | 113218 | # # # | # # # | # # # | # # # | 0.939 | 0.918 | 0.88 | 0.913 | # # # | # # # | # # # | - - - | 0.995 | 0.999 | 0.972 | 0.989 | - - - | 0.124 | 1.72 | 1.72 | 1.74 | 1.65 | 1.71 | 1.72 | 35.92 | 43.52 | 47.46 | 0 | - - - | - - - | - - - | - - - | 41457 | 35462 | 36299 | 113218 | Over-range | 14281 | 14092 | 17220 | 46083 | 13729 | 14047 | 15378 | 44269 | 38796 | 32476 | 31837 | 103109 | 38796 | 32476 | 31837 | 103109 | - - - | - - - | - - - | - - -
5/6/2026 | 3:30:00 AM | 285.81 | 282.48 | 282.49 | 494.54 | 487.02 | 492 | 148.0481 | 129.4094 | 131.456 | 4.9482 | 1.437 | 1.435 | 1.433 | 1.84 | 1.846 | 1.973 | Over-range | 60.01 | 39671 | 33621 | 32811 | 106103 | - - - | - - - | - - - | - - - | 39671 | 33621 | 32811 | 106103 | 4215 | 1277 | 7674 | 13166 | - - - | - - - | - - - | - - - | 4215 | 1277 | 7674 | 13166 | 42313 | 36554 | 37133 | 116000 | # # # | # # # | # # # | # # # | 0.938 | 0.92 | 0.884 | 0.915 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.974 | 0.989 | - - - | 0.124 | 1.74 | 1.75 | 1.78 | 1.68 | 1.75 | 1.75 | 36.16 | 42.86 | 46.96 | 0 | - - - | - - - | - - - | - - - | 42313 | 36554 | 37133 | 116000 | Over-range | 14718 | 14345 | 17385 | 46883 | 14101 | 14288 | 15600 | 44996 | 39544 | 33553 | 32700 | 105796 | 39544 | 33553 | 32700 | 105796 | - - - | - - - | - - - | - - -
5/6/2026 | 3:45:00 AM | 285.97 | 282.61 | 282.68 | 494.77 | 487.3 | 492.33 | 148.2769 | 130.1702 | 132.4603 | 4.8048 | 1.438 | 1.435 | 1.433 | 1.835 | 1.837 | 1.958 | Over-range | 60 | 39773 | 33885 | 33213 | 106872 | - - - | - - - | - - - | - - - | 39773 | 33885 | 33213 | 106872 | 4167 | 1430 | 7557 | 13154 | - - - | - - - | - - - | - - - | 4167 | 1430 | 7557 | 13154 | 42402 | 36786 | 37443 | 116631 | # # # | # # # | # # # | # # # | 0.938 | 0.921 | 0.887 | 0.916 | # # # | # # # | # # # | - - - | 0.995 | 0.999 | 0.975 | 0.99 | - - - | 0.123 | 1.76 | 1.75 | 1.79 | 1.69 | 1.76 | 1.76 | 36.03 | 42.38 | 46.28 | 0 | - - - | - - - | - - - | - - - | 42402 | 36786 | 37443 | 116631 | Over-range | 14698 | 14319 | 17286 | 46703 | 14094 | 14247 | 15546 | 44813 | 39649 | 33818 | 33104 | 106571 | 39649 | 33818 | 33104 | 106571 | - - - | - - - | - - - | - - -
5/6/2026 | 4:00:00 AM | 285.97 | 282.65 | 282.67 | 494.82 | 487.34 | 492.29 | 147.5974 | 130.2527 | 132.0684 | 4.5867 | 1.437 | 1.435 | 1.433 | 1.819 | 1.825 | 1.938 | Over-range | 60.01 | 39633 | 33980 | 33255 | 106868 | - - - | - - - | - - - | - - - | 39633 | 33980 | 33255 | 106868 | 4163 | 1441 | 7335 | 12940 | - - - | - - - | - - - | - - - | 4163 | 1441 | 7335 | 12940 | 42191 | 36803 | 37318 | 116312 | # # # | # # # | # # # | # # # | 0.939 | 0.923 | 0.891 | 0.919 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.976 | 0.99 | - - - | 0.121 | 1.76 | 1.75 | 1.79 | 1.69 | 1.76 | 1.77 | 35.49 | 41.69 | 45.41 | 0 | - - - | - - - | - - - | - - - | 42191 | 36803 | 37318 | 116312 | Over-range | 14462 | 14135 | 16930 | 45902 | 13850 | 14061 | 15259 | 44041 | 39515 | 33912 | 33150 | 106577 | 39515 | 33912 | 33150 | 106577 | - - - | - - - | - - - | - - -
5/6/2026 | 4:15:00 AM | 285.71 | 282.49 | 282.53 | 494.4 | 487.14 | 491.93 | 150.3262 | 133.6737 | 135.1399 | 4.5788 | 1.438 | 1.436 | 1.435 | 1.809 | 1.82 | 1.921 | Over-range | 60 | 40320 | 34915 | 34147 | 109382 | - - - | - - - | - - - | - - - | 40320 | 34915 | 34147 | 109382 | 4304 | 1613 | 7296 | 13212 | - - - | - - - | - - - | - - - | 4304 | 1613 | 7296 | 13212 | 42948 | 37760 | 38180 | 118888 | # # # | # # # | # # # | # # # | 0.939 | 0.925 | 0.894 | 0.92 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.978 | 0.991 | - - - | 0.121 | 1.82 | 1.82 | 1.88 | 1.75 | 1.84 | 1.86 | 35.59 | 41.18 | 44.76 | 0 | - - - | - - - | - - - | - - - | 42948 | 37760 | 38180 | 118888 | Over-range | 14794 | 14378 | 17079 | 46582 | 14154 | 14286 | 15442 | 44669 | 40208 | 34854 | 34054 | 109116 | 40208 | 34854 | 34054 | 109116 | - - - | - - - | - - - | - - -
5/6/2026 | 4:30:00 AM | 285.53 | 282.26 | 282.26 | 494.1 | 486.67 | 491.53 | 150.8631 | 133.9412 | 135.3476 | 4.5724 | 1.437 | 1.436 | 1.435 | 1.809 | 1.824 | 1.924 | Over-range | 60.01 | 40436 | 34953 | 34143 | 109533 | - - - | - - - | - - - | - - - | 40436 | 34953 | 34143 | 109533 | 4327 | 1566 | 7332 | 13224 | - - - | - - - | - - - | - - - | 4327 | 1566 | 7332 | 13224 | 43076 | 37806 | 38202 | 119084 | # # # | # # # | # # # | # # # | 0.939 | 0.925 | 0.894 | 0.92 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.978 | 0.991 | - - - | 0.121 | 1.81 | 1.8 | 1.87 | 1.73 | 1.83 | 1.84 | 35.59 | 41.22 | 44.86 | 0 | - - - | - - - | - - - | - - - | 43076 | 37806 | 38202 | 119084 | Over-range | 14846 | 14407 | 17136 | 46728 | 14201 | 14321 | 15489 | 44818 | 40328 | 34895 | 34051 | 109274 | 40328 | 34895 | 34051 | 109274 | - - - | - - - | - - - | - - -
5/6/2026 | 4:45:00 AM | 285.6 | 282.34 | 282.39 | 494.19 | 486.87 | 491.72 | 151.7141 | 134.8352 | 136.5575 | 4.6196 | 1.438 | 1.436 | 1.435 | 1.806 | 1.815 | 1.915 | Over-range | 60.01 | 40698 | 35214 | 34518 | 110430 | - - - | - - - | - - - | - - - | 40698 | 35214 | 34518 | 110430 | 4296 | 1658 | 7373 | 13327 | - - - | - - - | - - - | - - - | 4296 | 1658 | 7373 | 13327 | 43329 | 38069 | 38562 | 119960 | # # # | # # # | # # # | # # # | 0.939 | 0.925 | 0.895 | 0.921 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.978 | 0.991 | - - - | 0.121 | 1.83 | 1.82 | 1.89 | 1.75 | 1.85 | 1.86 | 35.44 | 41.04 | 44.5 | 0 | - - - | - - - | - - - | - - - | 43329 | 38069 | 38562 | 119960 | Over-range | 14868 | 14465 | 17190 | 46857 | 14234 | 14369 | 15529 | 44922 | 40587 | 35157 | 34428 | 110172 | 40587 | 35157 | 34428 | 110172 | - - - | - - - | - - - | - - -
5/6/2026 | 5:00:00 AM | 285.39 | 282.18 | 282.24 | 493.85 | 486.64 | 491.4 | 152.3689 | 136.0008 | 137.5791 | 4.5162 | 1.438 | 1.437 | 1.436 | 1.799 | 1.81 | 1.902 | Over-range | 60.01 | 40847 | 35529 | 34851 | 111227 | - - - | - - - | - - - | - - - | 40847 | 35529 | 34851 | 111227 | 4318 | 1752 | 7280 | 13351 | - - - | - - - | - - - | - - - | 4318 | 1752 | 7280 | 13351 | 43483 | 38375 | 38829 | 120688 | # # # | # # # | # # # | # # # | 0.939 | 0.926 | 0.898 | 0.922 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.979 | 0.991 | - - - | 0.12 | 1.86 | 1.85 | 1.92 | 1.77 | 1.87 | 1.89 | 35.35 | 40.73 | 43.98 | 0 | - - - | - - - | - - - | - - - | 43483 | 38375 | 38829 | 120688 | Over-range | 14910 | 14503 | 17120 | 46840 | 14270 | 14396 | 15495 | 44897 | 40741 | 35472 | 34766 | 110979 | 40741 | 35472 | 34766 | 110979 | - - - | - - - | - - - | - - -
5/6/2026 | 5:15:00 AM | 285.37 | 282.14 | 282.13 | 493.85 | 486.47 | 491.27 | 155.7515 | 139.2525 | 140.4097 | 4.5395 | 1.438 | 1.437 | 1.437 | 1.782 | 1.8 | 1.887 | Over-range | 60.01 | 41811 | 36451 | 35656 | 113918 | - - - | - - - | - - - | - - - | 41811 | 36451 | 35656 | 113918 | 4430 | 1733 | 7336 | 13500 | - - - | - - - | - - - | - - - | 4430 | 1733 | 7336 | 13500 | 44445 | 39288 | 39612 | 123345 | # # # | # # # | # # # | # # # | 0.941 | 0.928 | 0.9 | 0.924 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.979 | 0.991 | - - - | 0.118 | 1.87 | 1.86 | 1.93 | 1.78 | 1.88 | 1.91 | 34.8 | 40.07 | 43.31 | 0 | - - - | - - - | - - - | - - - | 44445 | 39288 | 39612 | 123345 | Over-range | 15074 | 14658 | 17255 | 47293 | 14408 | 14554 | 15618 | 45326 | 41713 | 36407 | 35578 | 113698 | 41713 | 36407 | 35578 | 113698 | - - - | - - - | - - - | - - -
5/6/2026 | 5:30:00 AM | 285.09 | 281.8 | 281.9 | 493.26 | 485.98 | 490.89 | 155.2711 | 138.7745 | 140.4911 | 4.5173 | 1.439 | 1.438 | 1.437 | 1.782 | 1.792 | 1.88 | Over-range | 60.01 | 41666 | 36297 | 35699 | 113662 | - - - | - - - | - - - | - - - | 41666 | 36297 | 35699 | 113662 | 4298 | 1779 | 7293 | 13370 | - - - | - - - | - - - | - - - | 4298 | 1779 | 7293 | 13370 | 44266 | 39106 | 39605 | 122977 | # # # | # # # | # # # | # # # | 0.941 | 0.928 | 0.901 | 0.924 | # # # | # # # | # # # | - - - | 0.995 | 0.999 | 0.98 | 0.991 | - - - | 0.118 | 1.88 | 1.87 | 1.95 | 1.79 | 1.9 | 1.93 | 34.71 | 39.94 | 42.99 | 0 | - - - | - - - | - - - | - - - | 44266 | 39106 | 39605 | 122977 | Over-range | 14948 | 14555 | 17150 | 46951 | 14316 | 14445 | 15522 | 45008 | 41573 | 36247 | 35622 | 113442 | 41573 | 36247 | 35622 | 113442 | - - - | - - - | - - - | - - -
5/6/2026 | 5:45:00 AM | 284.89 | 281.73 | 281.77 | 493.02 | 485.87 | 490.54 | 154.8832 | 139.2126 | 140.0562 | 4.3479 | 1.439 | 1.438 | 1.438 | 1.772 | 1.793 | 1.87 | Over-range | 60 | 41506 | 36436 | 35622 | 113565 | - - - | - - - | - - - | - - - | 41506 | 36436 | 35622 | 113565 | 4427 | 1777 | 7098 | 13303 | - - - | - - - | - - - | - - - | 4427 | 1777 | 7098 | 13303 | 44124 | 39221 | 39464 | 122808 | # # # | # # # | # # # | # # # | 0.941 | 0.929 | 0.903 | 0.925 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.981 | 0.991 | - - - | 0.117 | 1.93 | 1.91 | 2 | 1.84 | 1.95 | 1.98 | 34.73 | 39.61 | 42.8 | 0 | - - - | - - - | - - - | - - - | 44124 | 39221 | 39464 | 122808 | Over-range | 14971 | 14515 | 16983 | 46743 | 14301 | 14406 | 15428 | 44810 | 41420 | 36398 | 35553 | 113371 | 41420 | 36398 | 35553 | 113371 | - - - | - - - | - - - | - - -
5/6/2026 | 6:00:00 AM | 284.43 | 281.3 | 281.35 | 492.23 | 485.15 | 489.78 | 154.5043 | 139.23 | 140.078 | 4.1324 | 1.44 | 1.439 | 1.438 | 1.765 | 1.789 | 1.86 | Over-range | 60.01 | 41326 | 36396 | 35625 | 113347 | - - - | - - - | - - - | - - - | 41326 | 36396 | 35625 | 113347 | 4394 | 1813 | 6948 | 13155 | - - - | - - - | - - - | - - - | 4394 | 1813 | 6948 | 13155 | 43946 | 39165 | 39411 | 122522 | # # # | # # # | # # # | # # # | 0.94 | 0.929 | 0.904 | 0.925 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.981 | 0.992 | - - - | 0.116 | 2.01 | 1.98 | 2.09 | 1.9 | 2.03 | 2.07 | 34.74 | 39.42 | 42.53 | 0 | - - - | - - - | - - - | - - - | 43946 | 39165 | 39411 | 122522 | Over-range | 14947 | 14465 | 16855 | 46520 | 14286 | 14350 | 15356 | 44621 | 41250 | 36368 | 35573 | 113191 | 41250 | 36368 | 35573 | 113191 | - - - | - - - | - - - | - - -
5/6/2026 | 6:15:00 AM | 283.76 | 280.74 | 280.66 | 491.21 | 484.09 | 488.53 | 153.8171 | 139.5268 | 139.3243 | 3.9485 | 1.441 | 1.441 | 1.44 | 1.748 | 1.785 | 1.843 | Over-range | 59.99 | 41031 | 36461 | 35438 | 112930 | - - - | - - - | - - - | - - - | 41031 | 36461 | 35438 | 112930 | 4493 | 1798 | 6671 | 12961 | - - - | - - - | - - - | - - - | 4493 | 1798 | 6671 | 12961 | 43647 | 39170 | 39103 | 121920 | # # # | # # # | # # # | # # # | 0.94 | 0.931 | 0.906 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.115 | 2.16 | 2.13 | 2.26 | 2.05 | 2.19 | 2.24 | 34.61 | 38.83 | 42.02 | 0 | - - - | - - - | - - - | - - - | 43647 | 39170 | 39103 | 121920 | Over-range | 14883 | 14314 | 16528 | 45948 | 14188 | 14200 | 15122 | 44082 | 40973 | 36445 | 35402 | 112820 | 40973 | 36445 | 35402 | 112820 | - - - | - - - | - - - | - - -
5/6/2026 | 6:30:00 AM | 283.87 | 280.85 | 280.76 | 491.41 | 484.27 | 488.7 | 153.7846 | 139.4635 | 139.2919 | 3.9189 | 1.442 | 1.443 | 1.442 | 1.75 | 1.786 | 1.844 | Over-range | 59.99 | 41039 | 36454 | 35440 | 112933 | - - - | - - - | - - - | - - - | 41039 | 36454 | 35440 | 112933 | 4491 | 1798 | 6677 | 12966 | - - - | - - - | - - - | - - - | 4491 | 1798 | 6677 | 12966 | 43654 | 39168 | 39107 | 121929 | # # # | # # # | # # # | # # # | 0.94 | 0.931 | 0.906 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.115 | 2.22 | 2.18 | 2.3 | 2.1 | 2.24 | 2.29 | 34.59 | 38.86 | 42.03 | 0 | - - - | - - - | - - - | - - - | 43654 | 39168 | 39107 | 121929 | Over-range | 14882 | 14326 | 16534 | 45966 | 14187 | 14212 | 15125 | 44099 | 40987 | 36438 | 35400 | 112825 | 40987 | 36438 | 35400 | 112825 | - - - | - - - | - - - | - - -
5/6/2026 | 6:45:00 AM | 283.83 | 280.89 | 280.89 | 491.34 | 484.49 | 488.79 | 153.2713 | 139.5892 | 139.4176 | 3.9538 | 1.442 | 1.442 | 1.441 | 1.749 | 1.779 | 1.835 | Over-range | 60 | 40901 | 36508 | 35541 | 112950 | - - - | - - - | - - - | - - - | 40901 | 36508 | 35541 | 112950 | 4468 | 1907 | 6585 | 12960 | - - - | - - - | - - - | - - - | 4468 | 1907 | 6585 | 12960 | 43503 | 39209 | 39161 | 121872 | # # # | # # # | # # # | # # # | 0.94 | 0.931 | 0.908 | 0.927 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.115 | 2.16 | 2.11 | 2.23 | 2.04 | 2.16 | 2.23 | 34.6 | 38.73 | 41.81 | 0 | - - - | - - - | - - - | - - - | 43503 | 39209 | 39161 | 121872 | Over-range | 14819 | 14300 | 16443 | 45772 | 14129 | 14172 | 15066 | 43899 | 40844 | 36489 | 35495 | 112828 | 40844 | 36489 | 35495 | 112828 | - - - | - - - | - - - | - - -
5/6/2026 | 7:00:00 AM | 283.84 | 280.85 | 280.75 | 491.38 | 484.27 | 488.67 | 153.957 | 139.5014 | 139.2472 | 3.9627 | 1.442 | 1.443 | 1.441 | 1.748 | 1.783 | 1.845 | Over-range | 60.02 | 41105 | 36497 | 35422 | 113024 | - - - | - - - | - - - | - - - | 41105 | 36497 | 35422 | 113024 | 4537 | 1760 | 6709 | 13006 | - - - | - - - | - - - | - - - | 4537 | 1760 | 6709 | 13006 | 43699 | 39178 | 39094 | 121972 | # # # | # # # | # # # | # # # | 0.941 | 0.932 | 0.906 | 0.927 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.982 | 0.992 | - - - | 0.115 | 2.13 | 2.07 | 2.2 | 2.01 | 2.12 | 2.2 | 34.43 | 38.66 | 42.06 | 0 | - - - | - - - | - - - | - - - | 43699 | 39178 | 39094 | 121972 | Over-range | 14833 | 14244 | 16540 | 45854 | 14122 | 14135 | 15118 | 43971 | 41039 | 36475 | 35384 | 112898 | 41039 | 36475 | 35384 | 112898 | - - - | - - - | - - - | - - -
5/6/2026 | 7:15:00 AM | 283.8 | 280.82 | 280.76 | 491.3 | 484.28 | 488.65 | 153.4506 | 139.3808 | 139.0804 | 3.946 | 1.442 | 1.443 | 1.441 | 1.746 | 1.777 | 1.838 | Over-range | 59.99 | 40963 | 36481 | 35412 | 112855 | - - - | - - - | - - - | - - - | 40963 | 36481 | 35412 | 112855 | 4519 | 1802 | 6617 | 12937 | - - - | - - - | - - - | - - - | 4519 | 1802 | 6617 | 12937 | 43549 | 39141 | 39048 | 121739 | # # # | # # # | # # # | # # # | 0.941 | 0.932 | 0.907 | 0.927 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.115 | 2.14 | 2.08 | 2.2 | 2.02 | 2.12 | 2.21 | 34.4 | 38.45 | 41.91 | 0 | - - - | - - - | - - - | - - - | 43549 | 39141 | 39048 | 121739 | Over-range | 14784 | 14184 | 16455 | 45651 | 14075 | 14069 | 15066 | 43779 | 40909 | 36465 | 35371 | 112745 | 40909 | 36465 | 35371 | 112745 | - - - | - - - | - - - | - - -
5/6/2026 | 7:30:00 AM | 283.4 | 280.5 | 280.46 | 490.64 | 483.78 | 488.02 | 153.2705 | 139.8889 | 139.0992 | 3.9416 | 1.442 | 1.443 | 1.441 | 1.74 | 1.776 | 1.831 | Over-range | 60.01 | 40832 | 36579 | 35415 | 112827 | - - - | - - - | - - - | - - - | 40832 | 36579 | 35415 | 112827 | 4579 | 1860 | 6499 | 12938 | - - - | - - - | - - - | - - - | 4579 | 1860 | 6499 | 12938 | 43437 | 39239 | 39011 | 121687 | # # # | # # # | # # # | # # # | 0.94 | 0.932 | 0.908 | 0.927 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.984 | 0.992 | - - - | 0.115 | 2.15 | 2.1 | 2.22 | 2.03 | 2.14 | 2.22 | 34.52 | 38.38 | 41.77 | 0 | - - - | - - - | - - - | - - - | 43437 | 39239 | 39011 | 121687 | Over-range | 14816 | 14200 | 16358 | 45582 | 14090 | 14077 | 15011 | 43708 | 40776 | 36562 | 35380 | 112718 | 40776 | 36562 | 35380 | 112718 | - - - | - - - | - - - | - - -
5/6/2026 | 7:45:00 AM | 283.01 | 279.96 | 280.04 | 489.81 | 482.9 | 487.39 | 153.7691 | 139.8317 | 140.0138 | 3.9382 | 1.442 | 1.443 | 1.441 | 1.747 | 1.773 | 1.832 | Over-range | 60 | 40925 | 36471 | 35578 | 112974 | - - - | - - - | - - - | - - - | 40925 | 36471 | 35578 | 112974 | 4449 | 1920 | 6602 | 12971 | - - - | - - - | - - - | - - - | 4449 | 1920 | 6602 | 12971 | 43518 | 39147 | 39208 | 121873 | # # # | # # # | # # # | # # # | 0.94 | 0.932 | 0.907 | 0.927 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.115 | 2.14 | 2.09 | 2.21 | 2.02 | 2.13 | 2.2 | 34.51 | 38.54 | 41.8 | 0 | - - - | - - - | - - - | - - - | 43518 | 39147 | 39208 | 121873 | Over-range | 14796 | 14225 | 16477 | 45715 | 14111 | 14094 | 15096 | 43837 | 40872 | 36452 | 35542 | 112866 | 40872 | 36452 | 35542 | 112866 | - - - | - - - | - - - | - - -
5/6/2026 | 8:00:00 AM | 282.33 | 279.31 | 279.45 | 488.6 | 481.87 | 486.32 | 153.7114 | 140.1549 | 140.4276 | 3.9491 | 1.441 | 1.442 | 1.441 | 1.745 | 1.769 | 1.824 | Over-range | 60 | 40815 | 36480 | 35658 | 112953 | - - - | - - - | - - - | - - - | 40815 | 36480 | 35658 | 112953 | 4419 | 2003 | 6538 | 12960 | - - - | - - - | - - - | - - - | 4419 | 2003 | 6538 | 12960 | 43397 | 39146 | 39243 | 121786 | # # # | # # # | # # # | # # # | 0.941 | 0.932 | 0.909 | 0.928 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.984 | 0.992 | - - - | 0.115 | 2.07 | 2.03 | 2.14 | 1.96 | 2.07 | 2.13 | 34.53 | 38.47 | 41.56 | 0 | - - - | - - - | - - - | - - - | 43397 | 39146 | 39243 | 121786 | Over-range | 14745 | 14201 | 16385 | 45535 | 14066 | 14059 | 15024 | 43652 | 40752 | 36456 | 35622 | 112830 | 40752 | 36456 | 35622 | 112830 | - - - | - - - | - - - | - - -
5/6/2026 | 8:15:00 AM | 281.9 | 278.86 | 279.08 | 487.81 | 481.17 | 485.64 | 153.8893 | 140.4935 | 141.0594 | 3.9836 | 1.442 | 1.444 | 1.442 | 1.744 | 1.764 | 1.817 | Over-range | 60.01 | 40804 | 36502 | 35795 | 113101 | - - - | - - - | - - - | - - - | 40804 | 36502 | 35795 | 113101 | 4394 | 2092 | 6550 | 13036 | - - - | - - - | - - - | - - - | 4394 | 2092 | 6550 | 13036 | 43381 | 39178 | 39366 | 121924 | # # # | # # # | # # # | # # # | 0.941 | 0.932 | 0.909 | 0.928 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.984 | 0.992 | - - - | 0.115 | 2.11 | 2.06 | 2.19 | 1.99 | 2.11 | 2.18 | 34.48 | 38.46 | 41.35 | 0 | - - - | - - - | - - - | - - - | 43381 | 39178 | 39366 | 121924 | Over-range | 14727 | 14230 | 16382 | 45536 | 14056 | 14075 | 15015 | 43631 | 40749 | 36483 | 35756 | 112988 | 40749 | 36483 | 35756 | 112988 | - - - | - - - | - - - | - - -
5/6/2026 | 8:30:00 AM | 281.75 | 278.62 | 278.87 | 487.47 | 480.74 | 485.38 | 156.3649 | 142.1605 | 143.3825 | 4.0415 | 1.443 | 1.444 | 1.443 | 1.749 | 1.764 | 1.823 | Over-range | 60.01 | 41409 | 36865 | 36277 | 114551 | - - - | - - - | - - - | - - - | 41409 | 36865 | 36277 | 114551 | 4453 | 2180 | 6802 | 13435 | - - - | - - - | - - - | - - - | 4453 | 2180 | 6802 | 13435 | 44055 | 39608 | 39985 | 123649 | # # # | # # # | # # # | # # # | 0.94 | 0.931 | 0.907 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.117 | 2.12 | 2.07 | 2.2 | 2 | 2.13 | 2.2 | 34.74 | 38.77 | 41.77 | 0 | - - - | - - - | - - - | - - - | 44055 | 39608 | 39985 | 123649 | Over-range | 15037 | 14484 | 16817 | 46552 | 14362 | 14319 | 15380 | 44571 | 41349 | 36841 | 36237 | 114427 | 41349 | 36841 | 36237 | 114427 | - - - | - - - | - - - | - - -
5/6/2026 | 8:45:00 AM | 281.82 | 278.67 | 278.83 | 487.64 | 480.7 | 485.38 | 157.5137 | 143.058 | 144.0016 | 4.0342 | 1.442 | 1.444 | 1.442 | 1.748 | 1.769 | 1.828 | Over-range | 60.01 | 41697 | 37093 | 36378 | 115168 | - - - | - - - | - - - | - - - | 41697 | 37093 | 36378 | 115168 | 4572 | 2154 | 6877 | 13603 | - - - | - - - | - - - | - - - | 4572 | 2154 | 6877 | 13603 | 44390 | 39865 | 40152 | 124408 | # # # | # # # | # # # | # # # | 0.939 | 0.931 | 0.906 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.118 | 2.1 | 2.05 | 2.18 | 1.98 | 2.1 | 2.18 | 34.89 | 38.89 | 42.09 | 0 | - - - | - - - | - - - | - - - | 44390 | 39865 | 40152 | 124408 | Over-range | 15227 | 14606 | 16995 | 47049 | 14524 | 14446 | 15541 | 45040 | 41639 | 37065 | 36338 | 115041 | 41639 | 37065 | 36338 | 115041 | - - - | - - - | - - - | - - -
5/6/2026 | 9:00:00 AM | 281.43 | 278.23 | 278.44 | 486.9 | 479.97 | 484.74 | 159.3638 | 144.7545 | 145.9061 | 4.1059 | 1.442 | 1.444 | 1.443 | 1.747 | 1.764 | 1.824 | Over-range | 60.01 | 42121 | 37461 | 36805 | 116388 | - - - | - - - | - - - | - - - | 42121 | 37461 | 36805 | 116388 | 4597 | 2261 | 6972 | 13830 | - - - | - - - | - - - | - - - | 4597 | 2261 | 6972 | 13830 | 44848 | 40272 | 40625 | 125744 | # # # | # # # | # # # | # # # | 0.939 | 0.93 | 0.906 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.982 | 0.992 | - - - | 0.119 | 2.13 | 2.1 | 2.23 | 2.01 | 2.16 | 2.21 | 34.9 | 38.89 | 42.03 | 0 | - - - | - - - | - - - | - - - | 44848 | 40272 | 40625 | 125744 | Over-range | 15399 | 14781 | 17196 | 47597 | 14695 | 14607 | 15719 | 45543 | 42064 | 37441 | 36768 | 116273 | 42064 | 37441 | 36768 | 116273 | - - - | - - - | - - - | - - -
5/6/2026 | 9:15:00 AM | 280.7 | 277.4 | 277.68 | 485.54 | 478.56 | 483.5 | 161.0765 | 146.024 | 147.5274 | 4.1823 | 1.442 | 1.444 | 1.443 | 1.748 | 1.76 | 1.824 | Over-range | 60.01 | 42485 | 37671 | 37102 | 117259 | - - - | - - - | - - - | - - - | 42485 | 37671 | 37102 | 117259 | 4584 | 2267 | 7086 | 13938 | - - - | - - - | - - - | - - - | 4584 | 2267 | 7086 | 13938 | 45214 | 40507 | 40965 | 126686 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.906 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.982 | 0.992 | - - - | 0.119 | 2.14 | 2.12 | 2.26 | 2.02 | 2.18 | 2.24 | 34.79 | 38.97 | 42.05 | 0 | - - - | - - - | - - - | - - - | 45214 | 40507 | 40965 | 126686 | Over-range | 15468 | 14889 | 17365 | 47955 | 14773 | 14715 | 15853 | 45885 | 42429 | 37651 | 37065 | 117145 | 42429 | 37651 | 37065 | 117145 | - - - | - - - | - - - | - - -
5/6/2026 | 9:30:00 AM | 280.43 | 276.97 | 277.37 | 484.91 | 477.86 | 483.08 | 162.528 | 146.4973 | 149.0251 | 4.3525 | 1.442 | 1.445 | 1.443 | 1.754 | 1.753 | 1.829 | Over-range | 60 | 42872 | 37718 | 37411 | 118002 | - - - | - - - | - - - | - - - | 42872 | 37718 | 37411 | 118002 | 4452 | 2300 | 7315 | 14067 | - - - | - - - | - - - | - - - | 4452 | 2300 | 7315 | 14067 | 45577 | 40575 | 41334 | 127486 | # # # | # # # | # # # | # # # | 0.941 | 0.93 | 0.905 | 0.926 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.981 | 0.991 | - - - | 0.119 | 2.16 | 2.13 | 2.29 | 2.03 | 2.21 | 2.26 | 34.58 | 39.08 | 42 | 0 | - - - | - - - | - - - | - - - | 45577 | 40575 | 41334 | 127486 | Over-range | 15466 | 14955 | 17575 | 48251 | 14811 | 14776 | 15980 | 46154 | 42812 | 37699 | 37374 | 117886 | 42812 | 37699 | 37374 | 117886 | - - - | - - - | - - - | - - -
5/6/2026 | 9:45:00 AM | 279.66 | 276.21 | 276.55 | 483.61 | 476.48 | 481.68 | 163.0235 | 147.069 | 149.0837 | 4.3837 | 1.441 | 1.444 | 1.443 | 1.751 | 1.76 | 1.83 | Over-range | 60.01 | 42861 | 37768 | 37319 | 117948 | - - - | - - - | - - - | - - - | 42861 | 37768 | 37319 | 117948 | 4517 | 2228 | 7266 | 14011 | - - - | - - - | - - - | - - - | 4517 | 2228 | 7266 | 14011 | 45590 | 40622 | 41229 | 127441 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.905 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.982 | 0.992 | - - - | 0.119 | 2.08 | 2.06 | 2.21 | 1.96 | 2.13 | 2.18 | 34.7 | 39.07 | 42.01 | 0 | - - - | - - - | - - - | - - - | 45590 | 40622 | 41229 | 127441 | Over-range | 15537 | 14957 | 17524 | 48265 | 14865 | 14790 | 15946 | 46186 | 42808 | 37746 | 37282 | 117836 | 42808 | 37746 | 37282 | 117836 | - - - | - - - | - - - | - - -
5/6/2026 | 10:00:00 AM | 279.57 | 276.2 | 276.47 | 483.54 | 476.42 | 481.49 | 161.4479 | 145.2365 | 144.8443 | 4.3191 | 1.443 | 1.445 | 1.444 | 1.738 | 1.779 | 1.841 | Over-range | 60.01 | 42381 | 37318 | 36248 | 115947 | - - - | - - - | - - - | - - - | 42381 | 37318 | 36248 | 115947 | 4782 | 1886 | 7016 | 13684 | - - - | - - - | - - - | - - - | 4782 | 1886 | 7016 | 13684 | 45134 | 40110 | 40038 | 125282 | # # # | # # # | # # # | # # # | 0.939 | 0.93 | 0.905 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.982 | 0.992 | - - - | 0.118 | 1.96 | 1.9 | 2.04 | 1.83 | 1.94 | 2.03 | 34.78 | 38.96 | 41.99 | 0 | - - - | - - - | - - - | - - - | 45134 | 40110 | 40038 | 125282 | Over-range | 15521 | 14703 | 17004 | 47454 | 14765 | 14579 | 15488 | 45438 | 42333 | 37301 | 36217 | 115851 | 42333 | 37301 | 36217 | 115851 | - - - | - - - | - - - | - - -
5/6/2026 | 10:15:00 AM | 279.97 | 276.47 | 276.87 | 484.08 | 476.96 | 482.27 | 155.8103 | 139.2531 | 138.5797 | 3.1851 | 1.439 | 1.443 | 1.439 | 1.737 | 1.775 | 1.841 | Over-range | 60.02 | 41009 | 35863 | 34788 | 111660 | - - - | - - - | - - - | - - - | 41009 | 35863 | 34788 | 111660 | 4510 | 1567 | 6498 | 12575 | - - - | - - - | - - - | - - - | 4510 | 1567 | 6498 | 12575 | 43615 | 38495 | 38363 | 120473 | # # # | # # # | # # # | # # # | 0.94 | 0.932 | 0.907 | 0.927 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.113 | 1.89 | 1.88 | 2 | 1.78 | 1.93 | 1.97 | 34.42 | 38.63 | 41.81 | 0 | - - - | - - - | - - - | - - - | 43615 | 38495 | 38363 | 120473 | Over-range | 14848 | 13992 | 16171 | 45230 | 14145 | 13903 | 14807 | 43447 | 40968 | 35853 | 34767 | 111587 | 40968 | 35853 | 34767 | 111587 | - - - | - - - | - - - | - - -
5/6/2026 | 10:30:00 AM | 280.94 | 277.52 | 277.97 | 485.79 | 478.89 | 484.03 | 141.2233 | 128.7844 | 127.4496 | 3.5384 | 1.437 | 1.44 | 1.437 | 1.757 | 1.782 | 1.839 | Over-range | 60.01 | 37075 | 33180 | 32063 | 102319 | - - - | - - - | - - - | - - - | 37075 | 33180 | 32063 | 102319 | 4222 | 1715 | 5710 | 11647 | - - - | - - - | - - - | - - - | 4222 | 1715 | 5710 | 11647 | 39585 | 35682 | 35373 | 110641 | # # # | # # # | # # # | # # # | 0.937 | 0.93 | 0.906 | 0.925 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.984 | 0.992 | - - - | 0.114 | 1.84 | 1.83 | 1.93 | 1.74 | 1.86 | 1.91 | 35.57 | 39.09 | 42.35 | 0 | - - - | - - - | - - - | - - - | 39585 | 35682 | 35373 | 110641 | Over-range | 13867 | 13124 | 14935 | 42087 | 13207 | 13008 | 13799 | 40444 | 37032 | 33164 | 32040 | 102236 | 37032 | 33164 | 32040 | 102236 | - - - | - - - | - - - | - - -
5/6/2026 | 10:45:00 AM | 282.1 | 278.72 | 279.28 | 487.77 | 481.12 | 486.2 | 128.9534 | 120.2109 | 120.6367 | 4.0121 | 1.438 | 1.44 | 1.438 | 1.801 | 1.79 | 1.827 | Over-range | 60.01 | 33822 | 31019 | 30602 | 95443 | - - - | - - - | - - - | - - - | 33822 | 31019 | 30602 | 95443 | 3602 | 2395 | 5121 | 11117 | - - - | - - - | - - - | - - - | 3602 | 2395 | 5121 | 11117 | 36370 | 33500 | 33687 | 103557 | # # # | # # # | # # # | # # # | 0.93 | 0.926 | 0.908 | 0.922 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.986 | 0.993 | - - - | 0.117 | 1.86 | 1.81 | 1.91 | 1.75 | 1.83 | 1.9 | 38.09 | 40.02 | 42.35 | 0 | - - - | - - - | - - - | - - - | 36370 | 33500 | 33687 | 103557 | Over-range | 13374 | 12651 | 14081 | 40180 | 12879 | 12421 | 13116 | 38612 | 33775 | 30986 | 30571 | 95332 | 33775 | 30986 | 30571 | 95332 | - - - | - - - | - - - | - - -
5/6/2026 | 11:00:00 AM | 282.09 | 278.72 | 279.2 | 487.8 | 481.04 | 486.09 | 122.0203 | 113.9809 | 114.5296 | 4.3703 | 1.437 | 1.44 | 1.438 | 1.808 | 1.797 | 1.829 | Over-range | 60.01 | 31947 | 29378 | 29027 | 90352 | - - - | - - - | - - - | - - - | 31947 | 29378 | 29027 | 90352 | 3286 | 2328 | 4905 | 10519 | - - - | - - - | - - - | - - - | 3286 | 2328 | 4905 | 10519 | 34403 | 31757 | 31964 | 98125 | # # # | # # # | # # # | # # # | 0.929 | 0.925 | 0.908 | 0.921 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.986 | 0.993 | - - - | 0.116 | 1.83 | 1.79 | 1.89 | 1.73 | 1.81 | 1.87 | 38.59 | 40.24 | 42.31 | 0 | - - - | - - - | - - - | - - - | 34403 | 31757 | 31964 | 98125 | Over-range | 12760 | 12058 | 13378 | 38260 | 12329 | 11831 | 12446 | 36786 | 31899 | 29342 | 29000 | 90242 | 31899 | 29342 | 29000 | 90242 | - - - | - - - | - - - | - - -
5/6/2026 | 11:15:00 AM | 282.56 | 279.23 | 279.67 | 488.67 | 481.89 | 486.88 | 119.1686 | 110.4474 | 111.591 | 4.5656 | 1.437 | 1.439 | 1.438 | 1.825 | 1.81 | 1.853 | Over-range | 60.02 | 31216 | 28440 | 28197 | 87853 | - - - | - - - | - - - | - - - | 31216 | 28440 | 28197 | 87853 | 3138 | 2136 | 5028 | 10302 | - - - | - - - | - - - | - - - | 3138 | 2136 | 5028 | 10302 | 33649 | 30822 | 31190 | 95661 | # # # | # # # | # # # | # # # | 0.928 | 0.923 | 0.904 | 0.918 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.984 | 0.992 | - - - | 0.117 | 1.82 | 1.77 | 1.87 | 1.71 | 1.79 | 1.86 | 38.94 | 41.03 | 43.13 | 0 | - - - | - - - | - - - | - - - | 33649 | 30822 | 31190 | 95661 | Over-range | 12558 | 11878 | 13326 | 37840 | 12159 | 11684 | 12340 | 36410 | 31174 | 28410 | 28170 | 87754 | 31174 | 28410 | 28170 | 87754 | - - - | - - - | - - - | - - -
5/6/2026 | 11:30:00 AM | 282.27 | 279.02 | 279.45 | 488.21 | 481.57 | 486.42 | 117.8889 | 109.1055 | 110.5884 | 4.5089 | 1.437 | 1.439 | 1.438 | 1.83 | 1.814 | 1.857 | Over-range | 60 | 30830 | 28038 | 27891 | 86760 | - - - | - - - | - - - | - - - | 30830 | 28038 | 27891 | 86760 | 3079 | 2118 | 5021 | 10217 | - - - | - - - | - - - | - - - | 3079 | 2118 | 5021 | 10217 | 33252 | 30424 | 30886 | 94563 | # # # | # # # | # # # | # # # | 0.927 | 0.922 | 0.903 | 0.918 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.984 | 0.992 | - - - | 0.118 | 1.82 | 1.76 | 1.87 | 1.71 | 1.78 | 1.86 | 39.1 | 41.35 | 43.34 | 0 | - - - | - - - | - - - | - - - | 33252 | 30424 | 30886 | 94563 | Over-range | 12453 | 11808 | 13263 | 37603 | 12066 | 11616 | 12276 | 36189 | 30793 | 28013 | 27865 | 86672 | 30793 | 28013 | 27865 | 86672 | - - - | - - - | - - - | - - -
5/6/2026 | 11:45:00 AM | 281.66 | 278.42 | 278.81 | 487.17 | 480.47 | 485.33 | 119.2142 | 109.9809 | 111.5456 | 4.6566 | 1.438 | 1.44 | 1.439 | 1.84 | 1.833 | 1.876 | Over-range | 59.99 | 31049 | 28140 | 27962 | 87152 | - - - | - - - | - - - | - - - | 31049 | 28140 | 27962 | 87152 | 3181 | 2097 | 5197 | 10475 | - - - | - - - | - - - | - - - | 3181 | 2097 | 5197 | 10475 | 33577 | 30618 | 31099 | 95294 | # # # | # # # | # # # | # # # | 0.925 | 0.919 | 0.899 | 0.915 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.983 | 0.992 | - - - | 0.12 | 1.82 | 1.78 | 1.88 | 1.71 | 1.8 | 1.86 | 39.88 | 42.19 | 44.31 | 0 | - - - | - - - | - - - | - - - | 33577 | 30618 | 31099 | 95294 | Over-range | 12781 | 12067 | 13610 | 38542 | 12378 | 11883 | 12579 | 37092 | 31007 | 28115 | 27934 | 87055 | 31007 | 28115 | 27934 | 87055 | - - - | - - - | - - - | - - -
5/6/2026 | 12:00:00 PM | 281.2 | 277.89 | 278.38 | 486.28 | 479.64 | 484.6 | 118.8221 | 109.2785 | 111.4836 | 4.6685 | 1.439 | 1.442 | 1.439 | 1.845 | 1.827 | 1.877 | Over-range | 59.99 | 30919 | 27902 | 27899 | 86720 | - - - | - - - | - - - | - - - | 30919 | 27902 | 27899 | 86720 | 3085 | 2107 | 5246 | 10438 | - - - | - - - | - - - | - - - | 3085 | 2107 | 5246 | 10438 | 33412 | 30366 | 31034 | 94813 | # # # | # # # | # # # | # # # | 0.925 | 0.919 | 0.899 | 0.915 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.983 | 0.992 | - - - | 0.12 | 1.85 | 1.81 | 1.91 | 1.74 | 1.82 | 1.89 | 39.74 | 42.22 | 44.25 | 0 | - - - | - - - | - - - | - - - | 33412 | 30366 | 31034 | 94813 | Over-range | 12664 | 11982 | 13594 | 38329 | 12282 | 11795 | 12541 | 36881 | 30880 | 27877 | 27871 | 86628 | 30880 | 27877 | 27871 | 86628 | - - - | - - - | - - - | - - -
5/6/2026 | 12:15:00 PM | 281.09 | 277.89 | 278.33 | 486.18 | 479.64 | 484.43 | 117.6317 | 108.2756 | 110.1258 | 4.5404 | 1.44 | 1.442 | 1.44 | 1.84 | 1.828 | 1.877 | Over-range | 60 | 30625 | 27662 | 27570 | 85857 | - - - | - - - | - - - | - - - | 30625 | 27662 | 27570 | 85857 | 3093 | 2007 | 5142 | 10242 | - - - | - - - | - - - | - - - | 3093 | 2007 | 5142 | 10242 | 33052 | 30076 | 30643 | 93772 | # # # | # # # | # # # | # # # | 0.927 | 0.92 | 0.9 | 0.916 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.983 | 0.992 | - - - | 0.119 | 1.83 | 1.78 | 1.87 | 1.72 | 1.79 | 1.87 | 39.35 | 42 | 44.11 | 0 | - - - | - - - | - - - | - - - | 33052 | 30076 | 30643 | 93772 | Over-range | 12433 | 11804 | 13376 | 37705 | 12041 | 11630 | 12348 | 36287 | 30582 | 27637 | 27545 | 85764 | 30582 | 27637 | 27545 | 85764 | - - - | - - - | - - - | - - -
5/6/2026 | 12:30:00 PM | 280.57 | 277.42 | 277.85 | 485.31 | 478.84 | 483.54 | 116.6852 | 107.2014 | 109.7512 | 4.1836 | 1.44 | 1.443 | 1.441 | 1.845 | 1.831 | 1.876 | Over-range | 60.01 | 30301 | 27312 | 27424 | 85037 | - - - | - - - | - - - | - - - | 30301 | 27312 | 27424 | 85037 | 3040 | 2110 | 5112 | 10263 | - - - | - - - | - - - | - - - | 3040 | 2110 | 5112 | 10263 | 32737 | 29739 | 30493 | 92968 | # # # | # # # | # # # | # # # | 0.926 | 0.918 | 0.899 | 0.915 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.983 | 0.992 | - - - | 0.121 | 1.87 | 1.84 | 1.92 | 1.77 | 1.84 | 1.91 | 39.62 | 42.27 | 44.17 | 0 | - - - | - - - | - - - | - - - | 32737 | 29739 | 30493 | 92968 | Over-range | 12391 | 11766 | 13332 | 37574 | 12012 | 11575 | 12313 | 36145 | 30265 | 27292 | 27402 | 84959 | 30265 | 27292 | 27402 | 84959 | - - - | - - - | - - - | - - -
5/6/2026 | 12:45:00 PM | 280.81 | 277.75 | 278.09 | 485.82 | 479.36 | 483.9 | 120.1172 | 110.9616 | 112.5586 | 4.2837 | 1.441 | 1.443 | 1.442 | 1.83 | 1.829 | 1.867 | Over-range | 60 | 31212 | 28343 | 28178 | 87733 | - - - | - - - | - - - | - - - | 31212 | 28343 | 28178 | 87733 | 3253 | 2141 | 5141 | 10535 | - - - | - - - | - - - | - - - | 3253 | 2141 | 5141 | 10535 | 33724 | 30812 | 31297 | 95832 | # # # | # # # | # # # | # # # | 0.926 | 0.92 | 0.9 | 0.916 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.984 | 0.992 | - - - | 0.12 | 1.9 | 1.86 | 1.94 | 1.8 | 1.87 | 1.94 | 39.52 | 41.85 | 44.05 | 0 | - - - | - - - | - - - | - - - | 33724 | 30812 | 31297 | 95832 | Over-range | 12770 | 12084 | 13620 | 38558 | 12348 | 11892 | 12612 | 37091 | 31173 | 28323 | 28155 | 87651 | 31173 | 28323 | 28155 | 87651 | - - - | - - - | - - - | - - -
5/6/2026 | 1:00:00 PM | 280.77 | 277.78 | 278.07 | 485.82 | 479.4 | 483.81 | 124.3369 | 114.7927 | 116.4839 | 4.1487 | 1.443 | 1.445 | 1.444 | 1.822 | 1.825 | 1.863 | Over-range | 60 | 32281 | 29309 | 29112 | 90702 | - - - | - - - | - - - | - - - | 32281 | 29309 | 29112 | 90702 | 3476 | 2242 | 5341 | 11059 | - - - | - - - | - - - | - - - | 3476 | 2242 | 5341 | 11059 | 34907 | 31885 | 32389 | 99181 | # # # | # # # | # # # | # # # | 0.925 | 0.919 | 0.899 | 0.915 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.984 | 0.992 | - - - | 0.122 | 1.96 | 1.9 | 1.99 | 1.85 | 1.91 | 2 | 39.67 | 42.04 | 44.47 | 0 | - - - | - - - | - - - | - - - | 34907 | 31885 | 32389 | 99181 | Over-range | 13283 | 12556 | 14195 | 40125 | 12820 | 12353 | 13152 | 38572 | 32239 | 29289 | 29088 | 90615 | 32239 | 29289 | 29088 | 90615 | - - - | - - - | - - - | - - -
5/6/2026 | 1:15:00 PM | 280.33 | 277.27 | 277.65 | 484.97 | 478.59 | 483.12 | 127.053 | 117.3133 | 119.233 | 3.9805 | 1.443 | 1.445 | 1.445 | 1.823 | 1.817 | 1.858 | Over-range | 60.01 | 32944 | 29886 | 29758 | 92588 | - - - | - - - | - - - | - - - | 32944 | 29886 | 29758 | 92588 | 3523 | 2382 | 5413 | 11319 | - - - | - - - | - - - | - - - | 3523 | 2382 | 5413 | 11319 | 35613 | 32524 | 33103 | 101239 | # # # | # # # | # # # | # # # | 0.925 | 0.919 | 0.899 | 0.915 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.984 | 0.992 | - - - | 0.122 | 1.95 | 1.89 | 1.99 | 1.84 | 1.9 | 2 | 39.62 | 42.08 | 44.52 | 0 | - - - | - - - | - - - | - - - | 35613 | 32524 | 33103 | 101239 | Over-range | 13527 | 12829 | 14500 | 40950 | 13060 | 12605 | 13451 | 39354 | 32898 | 29863 | 29734 | 92495 | 32898 | 29863 | 29734 | 92495 | - - - | - - - | - - - | - - -
5/6/2026 | 1:30:00 PM | 279.89 | 276.9 | 277.17 | 484.31 | 477.86 | 482.28 | 128.6126 | 118.7805 | 120.0733 | 3.9656 | 1.443 | 1.446 | 1.445 | 1.813 | 1.82 | 1.857 | Over-range | 59.99 | 33308 | 30250 | 29917 | 93475 | - - - | - - - | - - - | - - - | 33308 | 30250 | 29917 | 93475 | 3645 | 2305 | 5427 | 11377 | - - - | - - - | - - - | - - - | 3645 | 2305 | 5427 | 11377 | 35996 | 32889 | 33280 | 102166 | # # # | # # # | # # # | # # # | 0.925 | 0.92 | 0.899 | 0.915 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.984 | 0.992 | - - - | 0.122 | 1.97 | 1.92 | 2.01 | 1.86 | 1.92 | 2.02 | 39.44 | 41.88 | 44.54 | 0 | - - - | - - - | - - - | - - - | 35996 | 32889 | 33280 | 102166 | Over-range | 13648 | 12910 | 14578 | 41234 | 13152 | 12702 | 13531 | 39634 | 33265 | 30227 | 29892 | 93383 | 33265 | 30227 | 29892 | 93383 | - - - | - - - | - - - | - - -
5/6/2026 | 1:45:00 PM | 279.47 | 276.45 | 276.79 | 483.52 | 477.13 | 481.61 | 130.3999 | 120.1324 | 121.1438 | 4.0171 | 1.443 | 1.446 | 1.445 | 1.811 | 1.819 | 1.862 | Over-range | 60 | 33749 | 30552 | 30103 | 94404 | - - - | - - - | - - - | - - - | 33749 | 30552 | 30103 | 94404 | 3731 | 2196 | 5524 | 11451 | - - - | - - - | - - - | - - - | 3731 | 2196 | 5524 | 11451 | 36438 | 33206 | 33529 | 103174 | # # # | # # # | # # # | # # # | 0.926 | 0.92 | 0.898 | 0.915 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.984 | 0.992 | - - - | 0.121 | 1.96 | 1.92 | 2.02 | 1.86 | 1.93 | 2.02 | 39.13 | 41.84 | 44.77 | 0 | - - - | - - - | - - - | - - - | 36438 | 33206 | 33529 | 103174 | Over-range | 13738 | 13009 | 14764 | 41625 | 13222 | 12821 | 13692 | 40019 | 33706 | 30532 | 30076 | 94313 | 33706 | 30532 | 30076 | 94313 | - - - | - - - | - - - | - - -
5/6/2026 | 2:00:00 PM | 279.54 | 276.57 | 276.95 | 483.65 | 477.41 | 481.82 | 131.643 | 121.7085 | 122.4608 | 4.1096 | 1.443 | 1.446 | 1.445 | 1.808 | 1.81 | 1.855 | Over-range | 60 | 34115 | 31002 | 30495 | 95612 | - - - | - - - | - - - | - - - | 34115 | 31002 | 30495 | 95612 | 3780 | 2239 | 5516 | 11536 | - - - | - - - | - - - | - - - | 3780 | 2239 | 5516 | 11536 | 36798 | 33659 | 33915 | 104372 | # # # | # # # | # # # | # # # | 0.927 | 0.921 | 0.899 | 0.916 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.984 | 0.992 | - - - | 0.121 | 1.97 | 1.92 | 2.01 | 1.86 | 1.92 | 2.01 | 38.82 | 41.5 | 44.48 | 0 | - - - | - - - | - - - | - - - | 36798 | 33659 | 33915 | 104372 | Over-range | 13794 | 13107 | 14841 | 41854 | 13265 | 12913 | 13778 | 40233 | 34073 | 30985 | 30470 | 95528 | 34073 | 30985 | 30470 | 95528 | - - - | - - - | - - - | - - -
5/6/2026 | 2:15:00 PM | 279.47 | 276.58 | 276.93 | 483.59 | 477.46 | 481.7 | 131.8276 | 122.0324 | 122.3485 | 4.0825 | 1.443 | 1.446 | 1.445 | 1.802 | 1.812 | 1.854 | Over-range | 60.01 | 34155 | 31094 | 30469 | 95718 | - - - | - - - | - - - | - - - | 34155 | 31094 | 30469 | 95718 | 3863 | 2216 | 5510 | 11590 | - - - | - - - | - - - | - - - | 3863 | 2216 | 5510 | 11590 | 36840 | 33751 | 33882 | 104473 | # # # | # # # | # # # | # # # | 0.927 | 0.921 | 0.899 | 0.916 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.984 | 0.992 | - - - | 0.121 | 2 | 1.96 | 2.05 | 1.9 | 1.96 | 2.05 | 38.72 | 41.45 | 44.44 | 0 | - - - | - - - | - - - | - - - | 36840 | 33751 | 33882 | 104473 | Over-range | 13806 | 13126 | 14818 | 41863 | 13254 | 12937 | 13756 | 40227 | 34112 | 31076 | 30444 | 95633 | 34112 | 31076 | 30444 | 95633 | - - - | - - - | - - - | - - -
5/6/2026 | 2:30:00 PM | 279.76 | 276.88 | 277.23 | 484.1 | 477.96 | 482.21 | 137.3971 | 126.3765 | 125.4392 | 4.6808 | 1.444 | 1.446 | 1.446 | 1.789 | 1.808 | 1.871 | Over-range | 60.01 | 35754 | 32290 | 31170 | 99214 | - - - | - - - | - - - | - - - | 35754 | 32290 | 31170 | 99214 | 4231 | 1806 | 5956 | 11992 | - - - | - - - | - - - | - - - | 4231 | 1806 | 5956 | 11992 | 38431 | 34985 | 34772 | 108188 | # # # | # # # | # # # | # # # | 0.93 | 0.923 | 0.896 | 0.917 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.982 | 0.991 | - - - | 0.121 | 2.06 | 2.01 | 2.12 | 1.95 | 2.03 | 2.12 | 37.47 | 41.12 | 44.78 | 0 | - - - | - - - | - - - | - - - | 38431 | 34985 | 34772 | 108188 | Over-range | 14093 | 13465 | 15412 | 43143 | 13442 | 13342 | 14214 | 41443 | 35716 | 32280 | 31147 | 99143 | 35716 | 32280 | 31147 | 99143 | - - - | - - - | - - - | - - -
5/6/2026 | 2:45:00 PM | 279.61 | 276.76 | 277.07 | 483.89 | 477.74 | 481.93 | 142.9863 | 130.3081 | 128.3468 | 4.8713 | 1.444 | 1.447 | 1.446 | 1.774 | 1.811 | 1.886 | Over-range | 60.01 | 37276 | 33290 | 31765 | 102331 | - - - | - - - | - - - | - - - | 37276 | 33290 | 31765 | 102331 | 4527 | 1400 | 6362 | 12289 | - - - | - - - | - - - | - - - | 4527 | 1400 | 6362 | 12289 | 39977 | 36062 | 35559 | 111598 | # # # | # # # | # # # | # # # | 0.932 | 0.923 | 0.893 | 0.917 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.98 | 0.991 | - - - | 0.12 | 2.11 | 2.07 | 2.17 | 2 | 2.09 | 2.17 | 36.64 | 41.2 | 45.24 | 0 | - - - | - - - | - - - | - - - | 39977 | 36062 | 35559 | 111598 | Over-range | 14444 | 13864 | 15982 | 44524 | 13715 | 13792 | 14661 | 42794 | 37237 | 33288 | 31740 | 102265 | 37237 | 33288 | 31740 | 102265 | - - - | - - - | - - - | - - -
5/6/2026 | 3:00:00 PM | 279.67 | 276.98 | 277.25 | 484.1 | 478.16 | 482.06 | 140.2612 | 128.7343 | 126.5322 | 4.5949 | 1.445 | 1.447 | 1.447 | 1.773 | 1.812 | 1.873 | Over-range | 60.01 | 36508 | 32922 | 31415 | 100845 | - - - | - - - | - - - | - - - | 36508 | 32922 | 31415 | 100845 | 4485 | 1609 | 6068 | 12163 | - - - | - - - | - - - | - - - | 4485 | 1609 | 6068 | 12163 | 39224 | 35655 | 35080 | 109959 | # # # | # # # | # # # | # # # | 0.931 | 0.923 | 0.896 | 0.917 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.982 | 0.991 | - - - | 0.121 | 2.12 | 2.07 | 2.18 | 2.01 | 2.09 | 2.18 | 37.14 | 41.07 | 44.92 | 0 | - - - | - - - | - - - | - - - | 39224 | 35655 | 35080 | 109959 | Over-range | 14343 | 13691 | 15609 | 43833 | 13624 | 13596 | 14381 | 42112 | 36472 | 32917 | 31395 | 100784 | 36472 | 32917 | 31395 | 100784 | - - - | - - - | - - - | - - -
5/6/2026 | 3:15:00 PM | 279.63 | 276.93 | 277.23 | 484 | 478.11 | 482.03 | 143.4281 | 131.1016 | 128.8157 | 4.6706 | 1.445 | 1.448 | 1.447 | 1.766 | 1.805 | 1.876 | Over-range | 60.01 | 37418 | 33556 | 31980 | 102954 | - - - | - - - | - - - | - - - | 37418 | 33556 | 31980 | 102954 | 4567 | 1424 | 6254 | 12246 | - - - | - - - | - - - | - - - | 4567 | 1424 | 6254 | 12246 | 40104 | 36304 | 35710 | 112119 | # # # | # # # | # # # | # # # | 0.933 | 0.924 | 0.896 | 0.918 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.981 | 0.991 | - - - | 0.119 | 2.14 | 2.09 | 2.2 | 2.03 | 2.11 | 2.2 | 36.41 | 40.82 | 44.79 | 0 | - - - | - - - | - - - | - - - | 40104 | 36304 | 35710 | 112119 | Over-range | 14430 | 13857 | 15889 | 44397 | 13687 | 13783 | 14606 | 42674 | 37381 | 33557 | 31960 | 102899 | 37381 | 33557 | 31960 | 102899 | - - - | - - - | - - - | - - -
5/6/2026 | 3:30:00 PM | 279.36 | 276.75 | 276.98 | 483.62 | 477.77 | 481.55 | 147.0468 | 134.1747 | 132.2306 | 4.7867 | 1.445 | 1.447 | 1.447 | 1.757 | 1.793 | 1.865 | Over-range | 60.01 | 38410 | 34351 | 32890 | 105651 | - - - | - - - | - - - | - - - | 38410 | 34351 | 32890 | 105651 | 4566 | 1398 | 6443 | 12407 | - - - | - - - | - - - | - - - | 4566 | 1398 | 6443 | 12407 | 41078 | 37131 | 36625 | 114834 | # # # | # # # | # # # | # # # | 0.935 | 0.925 | 0.898 | 0.92 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.981 | 0.991 | - - - | 0.117 | 2.18 | 2.13 | 2.24 | 2.07 | 2.14 | 2.24 | 35.8 | 40.56 | 44 | 0 | - - - | - - - | - - - | - - - | 41078 | 37131 | 36625 | 114834 | Over-range | 14563 | 14098 | 16112 | 44997 | 13828 | 14028 | 14768 | 43253 | 38378 | 34354 | 32873 | 105605 | 38378 | 34354 | 32873 | 105605 | - - - | - - - | - - - | - - -
5/6/2026 | 3:45:00 PM | 279.12 | 276.57 | 276.85 | 483.22 | 477.55 | 481.21 | 146.0007 | 133.3668 | 131.4872 | 4.5644 | 1.445 | 1.447 | 1.447 | 1.758 | 1.794 | 1.863 | Over-range | 60 | 38080 | 34113 | 32694 | 104887 | - - - | - - - | - - - | - - - | 38080 | 34113 | 32694 | 104887 | 4590 | 1462 | 6363 | 12415 | - - - | - - - | - - - | - - - | 4590 | 1462 | 6363 | 12415 | 40749 | 36883 | 36400 | 114032 | # # # | # # # | # # # | # # # | 0.935 | 0.925 | 0.898 | 0.92 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.982 | 0.991 | - - - | 0.118 | 2.18 | 2.14 | 2.23 | 2.08 | 2.15 | 2.24 | 35.92 | 40.59 | 44.01 | 0 | - - - | - - - | - - - | - - - | 40749 | 36883 | 36400 | 114032 | Over-range | 14506 | 14023 | 16002 | 44745 | 13760 | 13946 | 14683 | 42988 | 38048 | 34118 | 32678 | 104845 | 38048 | 34118 | 32678 | 104845 | - - - | - - - | - - - | - - -
5/6/2026 | 4:00:00 PM | 279.35 | 276.79 | 277.06 | 483.61 | 477.92 | 481.6 | 144.9303 | 132.4004 | 130.2177 | 4.4049 | 1.445 | 1.447 | 1.447 | 1.759 | 1.798 | 1.867 | Over-range | 60 | 37814 | 33891 | 32373 | 104077 | - - - | - - - | - - - | - - - | 37814 | 33891 | 32373 | 104077 | 4623 | 1435 | 6284 | 12341 | - - - | - - - | - - - | - - - | 4623 | 1435 | 6284 | 12341 | 40483 | 36645 | 36077 | 113205 | # # # | # # # | # # # | # # # | 0.934 | 0.925 | 0.897 | 0.919 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.982 | 0.991 | - - - | 0.119 | 2.17 | 2.11 | 2.22 | 2.06 | 2.12 | 2.23 | 36.01 | 40.61 | 44.3 | 0 | - - - | - - - | - - - | - - - | 40483 | 36645 | 36077 | 113205 | Over-range | 14458 | 13937 | 15922 | 44533 | 13698 | 13862 | 14630 | 42789 | 37783 | 33897 | 32356 | 104035 | 37783 | 33897 | 32356 | 104035 | - - - | - - - | - - - | - - -
5/6/2026 | 4:15:00 PM | 279.59 | 277.08 | 277.26 | 484.11 | 478.34 | 481.94 | 146.9996 | 134.5392 | 131.928 | 4.6573 | 1.445 | 1.448 | 1.447 | 1.754 | 1.795 | 1.864 | Over-range | 60.01 | 38412 | 34511 | 32855 | 105778 | - - - | - - - | - - - | - - - | 38412 | 34511 | 32855 | 105778 | 4693 | 1360 | 6334 | 12387 | - - - | - - - | - - - | - - - | 4693 | 1360 | 6334 | 12387 | 41098 | 37277 | 36578 | 114953 | # # # | # # # | # # # | # # # | 0.935 | 0.926 | 0.898 | 0.92 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.982 | 0.991 | - - - | 0.117 | 2.17 | 2.11 | 2.22 | 2.06 | 2.13 | 2.23 | 35.8 | 40.35 | 44.09 | 0 | - - - | - - - | - - - | - - - | 41098 | 37277 | 36578 | 114953 | Over-range | 14615 | 14092 | 16077 | 45002 | 13840 | 14026 | 14776 | 43264 | 38381 | 34516 | 32840 | 105737 | 38381 | 34516 | 32840 | 105737 | - - - | - - - | - - - | - - -
5/6/2026 | 4:30:00 PM | 279.69 | 277.13 | 277.33 | 484.25 | 478.42 | 482.1 | 146.2985 | 133.9182 | 131.1288 | 4.7203 | 1.445 | 1.447 | 1.447 | 1.757 | 1.798 | 1.869 | Over-range | 60 | 38224 | 34342 | 32623 | 105189 | - - - | - - - | - - - | - - - | 38224 | 34342 | 32623 | 105189 | 4701 | 1341 | 6320 | 12363 | - - - | - - - | - - - | - - - | 4701 | 1341 | 6320 | 12363 | 40916 | 37111 | 36364 | 114390 | # # # | # # # | # # # | # # # | 0.934 | 0.925 | 0.897 | 0.92 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.982 | 0.991 | - - - | 0.117 | 2.14 | 2.09 | 2.2 | 2.04 | 2.1 | 2.2 | 35.94 | 40.48 | 44.39 | 0 | - - - | - - - | - - - | - - - | 40916 | 37111 | 36364 | 114390 | Over-range | 14594 | 14065 | 16065 | 44948 | 13816 | 14000 | 14769 | 43215 | 38192 | 34348 | 32605 | 105144 | 38192 | 34348 | 32605 | 105144 | - - - | - - - | - - - | - - -
5/6/2026 | 4:45:00 PM | 280.1 | 277.47 | 277.67 | 484.91 | 478.97 | 482.76 | 141.5082 | 130.0853 | 127.2324 | 4.8456 | 1.446 | 1.448 | 1.447 | 1.763 | 1.801 | 1.867 | Over-range | 60 | 36980 | 33418 | 31711 | 102108 | - - - | - - - | - - - | - - - | 36980 | 33418 | 31711 | 102108 | 4554 | 1431 | 6074 | 12058 | - - - | - - - | - - - | - - - | 4554 | 1431 | 6074 | 12058 | 39633 | 36093 | 35327 | 111053 | # # # | # # # | # # # | # # # | 0.933 | 0.926 | 0.898 | 0.92 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.982 | 0.991 | - - - | 0.118 | 2.14 | 2.07 | 2.19 | 2.03 | 2.08 | 2.2 | 36.37 | 40.35 | 44.39 | 0 | - - - | - - - | - - - | - - - | 39633 | 36093 | 35327 | 111053 | Over-range | 14257 | 13638 | 15570 | 43667 | 13510 | 13562 | 14336 | 41969 | 36941 | 33416 | 31688 | 102045 | 36941 | 33416 | 31688 | 102045 | - - - | - - - | - - - | - - -
5/6/2026 | 5:00:00 PM | 280.17 | 277.55 | 277.66 | 485.08 | 479.01 | 482.8 | 142.1906 | 130.5704 | 127.5233 | 4.9193 | 1.446 | 1.448 | 1.447 | 1.761 | 1.804 | 1.872 | Over-range | 60 | 37177 | 33556 | 31760 | 102492 | - - - | - - - | - - - | - - - | 37177 | 33556 | 31760 | 102492 | 4627 | 1353 | 6142 | 12123 | - - - | - - - | - - - | - - - | 4627 | 1353 | 6142 | 12123 | 39835 | 36238 | 35408 | 111481 | # # # | # # # | # # # | # # # | 0.933 | 0.926 | 0.897 | 0.919 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.982 | 0.991 | - - - | 0.118 | 2.15 | 2.07 | 2.19 | 2.03 | 2.08 | 2.2 | 36.25 | 40.35 | 44.49 | 0 | - - - | - - - | - - - | - - - | 39835 | 36238 | 35408 | 111481 | Over-range | 14309 | 13683 | 15653 | 43856 | 13539 | 13615 | 14397 | 42147 | 37137 | 33554 | 31738 | 102430 | 37137 | 33554 | 31738 | 102430 | - - - | - - - | - - - | - - -
5/6/2026 | 5:15:00 PM | 280.58 | 277.91 | 278.04 | 485.76 | 479.62 | 483.5 | 146.3953 | 133.5592 | 130.6109 | 5.0552 | 1.445 | 1.447 | 1.448 | 1.757 | 1.799 | 1.878 | Over-range | 60.02 | 38421 | 34368 | 32550 | 105339 | - - - | - - - | - - - | - - - | 38421 | 34368 | 32550 | 105339 | 4696 | 1169 | 6451 | 12316 | - - - | - - - | - - - | - - - | 4696 | 1169 | 6451 | 12316 | 41071 | 37115 | 36312 | 114498 | # # # | # # # | # # # | # # # | 0.936 | 0.926 | 0.896 | 0.92 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.981 | 0.991 | - - - | 0.117 | 2.1 | 2.03 | 2.15 | 1.99 | 2.05 | 2.16 | 35.62 | 40.43 | 44.48 | 0 | - - - | - - - | - - - | - - - | 41071 | 37115 | 36312 | 114498 | Over-range | 14514 | 14012 | 16096 | 44872 | 13733 | 13963 | 14746 | 43149 | 38378 | 34366 | 32519 | 105263 | 38378 | 34366 | 32519 | 105263 | - - - | - - - | - - - | - - -
5/6/2026 | 5:30:00 PM | 280.4 | 277.81 | 277.96 | 485.49 | 479.52 | 483.26 | 150.4348 | 137.5797 | 135.2432 | 4.988 | 1.445 | 1.447 | 1.447 | 1.746 | 1.782 | 1.853 | Over-range | 60.01 | 39521 | 35436 | 33875 | 108833 | - - - | - - - | - - - | - - - | 39521 | 35436 | 33875 | 108833 | 4706 | 1354 | 6541 | 12601 | - - - | - - - | - - - | - - - | 4706 | 1354 | 6541 | 12601 | 42181 | 38219 | 37590 | 117990 | # # # | # # # | # # # | # # # | 0.937 | 0.927 | 0.901 | 0.922 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.982 | 0.991 | - - - | 0.116 | 2.13 | 2.06 | 2.19 | 2.02 | 2.08 | 2.2 | 35.21 | 40.03 | 43.29 | 0 | - - - | - - - | - - - | - - - | 42181 | 38219 | 37590 | 117990 | Over-range | 14740 | 14317 | 16293 | 45574 | 13968 | 14252 | 14922 | 43797 | 39480 | 35431 | 33844 | 108756 | 39480 | 35431 | 33844 | 108756 | - - - | - - - | - - - | - - -
5/6/2026 | 5:45:00 PM | 280.45 | 277.94 | 278.03 | 485.65 | 479.72 | 483.32 | 152.7028 | 140.4686 | 137.7375 | 5.0504 | 1.445 | 1.447 | 1.448 | 1.735 | 1.774 | 1.837 | Over-range | 60.01 | 40139 | 36259 | 34624 | 111022 | - - - | - - - | - - - | - - - | 40139 | 36259 | 34624 | 111022 | 4835 | 1446 | 6491 | 12772 | - - - | - - - | - - - | - - - | 4835 | 1446 | 6491 | 12772 | 42824 | 39040 | 38294 | 120158 | # # # | # # # | # # # | # # # | 0.937 | 0.929 | 0.904 | 0.924 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.983 | 0.992 | - - - | 0.115 | 2.16 | 2.08 | 2.22 | 2.05 | 2.11 | 2.23 | 35.02 | 39.53 | 42.65 | 0 | - - - | - - - | - - - | - - - | 42824 | 39040 | 38294 | 120158 | Over-range | 14923 | 14472 | 16358 | 45955 | 14117 | 14399 | 15014 | 44145 | 40099 | 36252 | 34593 | 110943 | 40099 | 36252 | 34593 | 110943 | - - - | - - - | - - - | - - -
5/6/2026 | 6:00:00 PM | 280.59 | 278 | 278.15 | 485.81 | 479.85 | 483.58 | 154.4281 | 142.0623 | 139.4757 | 5.3313 | 1.445 | 1.446 | 1.448 | 1.733 | 1.766 | 1.831 | Over-range | 60.01 | 40672 | 36718 | 35143 | 112532 | - - - | - - - | - - - | - - - | 40672 | 36718 | 35143 | 112532 | 4779 | 1474 | 6578 | 12831 | - - - | - - - | - - - | - - - | 4779 | 1474 | 6578 | 12831 | 43329 | 39492 | 38794 | 121615 | # # # | # # # | # # # | # # # | 0.939 | 0.93 | 0.906 | 0.925 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.983 | 0.992 | - - - | 0.114 | 2.13 | 2.05 | 2.18 | 2.02 | 2.07 | 2.19 | 34.69 | 39.23 | 42.17 | 0 | - - - | - - - | - - - | - - - | 43329 | 39492 | 38794 | 121615 | Over-range | 14940 | 14541 | 16431 | 46117 | 14154 | 14465 | 15056 | 44296 | 40627 | 36708 | 35107 | 112442 | 40627 | 36708 | 35107 | 112442 | - - - | - - - | - - - | - - -
5/6/2026 | 6:15:00 PM | 281.63 | 279.28 | 279.34 | 487.81 | 482.1 | 485.42 | 152.8474 | 140.9293 | 138.3999 | 5.3309 | 1.444 | 1.444 | 1.446 | 1.741 | 1.775 | 1.84 | Over-range | 60.01 | 40350 | 36537 | 34967 | 111854 | - - - | - - - | - - - | - - - | 40350 | 36537 | 34967 | 111854 | 4842 | 1485 | 6559 | 12886 | - - - | - - - | - - - | - - - | 4842 | 1485 | 6559 | 12886 | 43043 | 39355 | 38658 | 121055 | # # # | # # # | # # # | # # # | 0.938 | 0.928 | 0.905 | 0.924 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.983 | 0.992 | - - - | 0.115 | 2.02 | 1.93 | 2.04 | 1.91 | 1.93 | 2.05 | 35.12 | 39.74 | 42.69 | 0 | - - - | - - - | - - - | - - - | 43043 | 39355 | 38658 | 121055 | Over-range | 14983 | 14623 | 16485 | 46292 | 14179 | 14547 | 15124 | 44462 | 40294 | 36520 | 34917 | 111731 | 40294 | 36520 | 34917 | 111731 | - - - | - - - | - - - | - - -
5/6/2026 | 6:30:00 PM | 281.58 | 279.29 | 279.3 | 487.79 | 482.1 | 485.31 | 151.2875 | 138.8297 | 136.7459 | 4.9637 | 1.444 | 1.443 | 1.446 | 1.747 | 1.783 | 1.852 | Over-range | 60 | 39918 | 35949 | 34469 | 110336 | - - - | - - - | - - - | - - - | 39918 | 35949 | 34469 | 110336 | 4809 | 1449 | 6586 | 12844 | - - - | - - - | - - - | - - - | 4809 | 1449 | 6586 | 12844 | 42598 | 38773 | 38192 | 119564 | # # # | # # # | # # # | # # # | 0.937 | 0.927 | 0.903 | 0.923 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.982 | 0.992 | - - - | 0.116 | 1.99 | 1.9 | 1.99 | 1.88 | 1.89 | 2.01 | 35.28 | 40.16 | 43.17 | 0 | - - - | - - - | - - - | - - - | 42598 | 38773 | 38192 | 119564 | Over-range | 14873 | 14527 | 16447 | 46060 | 14074 | 14454 | 15071 | 44233 | 39859 | 35925 | 34411 | 110195 | 39859 | 35925 | 34411 | 110195 | - - - | - - - | - - - | - - -
5/6/2026 | 6:45:00 PM | 281.69 | 279.53 | 279.48 | 488.07 | 482.52 | 485.51 | 148.8293 | 136.7251 | 134.4063 | 4.7251 | 1.444 | 1.443 | 1.445 | 1.75 | 1.791 | 1.857 | Over-range | 59.99 | 39235 | 35399 | 33858 | 108493 | - - - | - - - | - - - | - - - | 39235 | 35399 | 33858 | 108493 | 4813 | 1437 | 6452 | 12702 | - - - | - - - | - - - | - - - | 4813 | 1437 | 6452 | 12702 | 41922 | 38217 | 37563 | 117701 | # # # | # # # | # # # | # # # | 0.936 | 0.926 | 0.901 | 0.922 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.982 | 0.991 | - - - | 0.117 | 1.95 | 1.86 | 1.95 | 1.85 | 1.84 | 1.97 | 35.6 | 40.45 | 43.56 | 0 | - - - | - - - | - - - | - - - | 41922 | 38217 | 37563 | 117701 | Over-range | 14765 | 14401 | 16266 | 45638 | 13958 | 14329 | 14931 | 43835 | 39174 | 35376 | 33803 | 108353 | 39174 | 35376 | 33803 | 108353 | - - - | - - - | - - - | - - -
5/6/2026 | 7:00:00 PM | 281.81 | 279.71 | 279.6 | 488.36 | 482.8 | 485.67 | 147.4128 | 135.0487 | 132.3456 | 4.5111 | 1.443 | 1.442 | 1.444 | 1.756 | 1.807 | 1.874 | Over-range | 60 | 38822 | 34938 | 33234 | 106994 | - - - | - - - | - - - | - - - | 38822 | 34938 | 33234 | 106994 | 4886 | 1291 | 6425 | 12602 | - - - | - - - | - - - | - - - | 4886 | 1291 | 6425 | 12602 | 41541 | 37774 | 37003 | 116318 | # # # | # # # | # # # | # # # | 0.935 | 0.925 | 0.898 | 0.92 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.982 | 0.991 | - - - | 0.118 | 1.85 | 1.76 | 1.84 | 1.76 | 1.74 | 1.86 | 36.02 | 40.95 | 44.47 | 0 | - - - | - - - | - - - | - - - | 41541 | 37774 | 37003 | 116318 | Over-range | 14782 | 14358 | 16269 | 45628 | 13951 | 14300 | 14947 | 43853 | 38753 | 34910 | 33171 | 106834 | 38753 | 34910 | 33171 | 106834 | - - - | - - - | - - - | - - -
5/6/2026 | 7:15:00 PM | 282.22 | 280.09 | 280.06 | 489.02 | 483.53 | 486.46 | 151.5123 | 139.2828 | 136.7084 | 5.0014 | 1.443 | 1.441 | 1.444 | 1.75 | 1.792 | 1.86 | Over-range | 60 | 40024 | 36131 | 34493 | 110647 | - - - | - - - | - - - | - - - | 40024 | 36131 | 34493 | 110647 | 4926 | 1438 | 6610 | 12975 | - - - | - - - | - - - | - - - | 4926 | 1438 | 6610 | 12975 | 42754 | 39005 | 38280 | 120039 | # # # | # # # | # # # | # # # | 0.936 | 0.926 | 0.901 | 0.922 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.982 | 0.991 | - - - | 0.117 | 1.88 | 1.79 | 1.87 | 1.79 | 1.77 | 1.89 | 35.58 | 40.5 | 43.67 | 0 | - - - | - - - | - - - | - - - | 42754 | 39005 | 38280 | 120039 | Over-range | 15033 | 14695 | 16600 | 46545 | 14203 | 14624 | 15227 | 44700 | 39953 | 36097 | 34426 | 110476 | 39953 | 36097 | 34426 | 110476 | - - - | - - - | - - - | - - -
5/6/2026 | 7:30:00 PM | 282.41 | 280.39 | 280.3 | 489.44 | 484.05 | 486.79 | 156.9428 | 146.043 | 142.2091 | 4.6207 | 1.443 | 1.441 | 1.444 | 1.727 | 1.773 | 1.822 | Over-range | 60 | 41512 | 38051 | 36178 | 115740 | - - - | - - - | - - - | - - - | 41512 | 38051 | 36178 | 115740 | 5122 | 1951 | 6395 | 13467 | - - - | - - - | - - - | - - - | 5122 | 1951 | 6395 | 13467 | 44321 | 40947 | 39860 | 125128 | # # # | # # # | # # # | # # # | 0.937 | 0.929 | 0.908 | 0.925 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.985 | 0.992 | - - - | 0.116 | 1.93 | 1.83 | 1.92 | 1.84 | 1.81 | 1.94 | 35.36 | 39.43 | 42.35 | 0 | - - - | - - - | - - - | - - - | 44321 | 40947 | 39860 | 125128 | Over-range | 15528 | 15127 | 16732 | 47553 | 14659 | 14999 | 15462 | 45606 | 41442 | 38016 | 36115 | 115573 | 41442 | 38016 | 36115 | 115573 | - - - | - - - | - - - | - - -
5/6/2026 | 7:45:00 PM | 282.38 | 280.28 | 280.22 | 489.33 | 483.85 | 486.72 | 157.0484 | 145.6027 | 141.8163 | 4.8776 | 1.443 | 1.441 | 1.444 | 1.732 | 1.777 | 1.834 | Over-range | 59.99 | 41545 | 37904 | 35992 | 115440 | - - - | - - - | - - - | - - - | 41545 | 37904 | 35992 | 115440 | 5095 | 1777 | 6526 | 13398 | - - - | - - - | - - - | - - - | 5095 | 1777 | 6526 | 13398 | 44347 | 40809 | 39739 | 124894 | # # # | # # # | # # # | # # # | 0.937 | 0.929 | 0.906 | 0.924 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.984 | 0.992 | - - - | 0.116 | 1.91 | 1.81 | 1.9 | 1.81 | 1.79 | 1.92 | 35.35 | 39.64 | 42.74 | 0 | - - - | - - - | - - - | - - - | 44347 | 40809 | 39739 | 124894 | Over-range | 15514 | 15122 | 16845 | 47667 | 14653 | 15016 | 15529 | 45746 | 41471 | 37869 | 35927 | 115267 | 41471 | 37869 | 35927 | 115267 | - - - | - - - | - - - | - - -
5/6/2026 | 8:00:00 PM | 282.47 | 280.27 | 280.26 | 489.4 | 483.84 | 486.87 | 155.8703 | 143.9222 | 140.5051 | 5.2341 | 1.442 | 1.44 | 1.443 | 1.741 | 1.782 | 1.847 | Over-range | 60 | 41243 | 37426 | 35576 | 114246 | - - - | - - - | - - - | - - - | 41243 | 37426 | 35576 | 114246 | 5006 | 1595 | 6663 | 13264 | - - - | - - - | - - - | - - - | 5006 | 1595 | 6663 | 13264 | 44027 | 40336 | 39377 | 123741 | # # # | # # # | # # # | # # # | 0.937 | 0.928 | 0.904 | 0.923 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.983 | 0.992 | - - - | 0.116 | 1.88 | 1.78 | 1.87 | 1.78 | 1.77 | 1.89 | 35.41 | 39.99 | 43.13 | 0 | - - - | - - - | - - - | - - - | 44027 | 40336 | 39377 | 123741 | Over-range | 15408 | 15043 | 16879 | 47537 | 14571 | 14957 | 15509 | 45649 | 41171 | 37390 | 35512 | 114073 | 41171 | 37390 | 35512 | 114073 | - - - | - - - | - - - | - - -
5/6/2026 | 8:15:00 PM | 282.56 | 280.38 | 280.23 | 489.65 | 483.88 | 486.87 | 157.3964 | 145.9485 | 141.6118 | 5.1394 | 1.442 | 1.44 | 1.443 | 1.732 | 1.782 | 1.839 | Over-range | 59.99 | 41637 | 38006 | 35907 | 115550 | - - - | - - - | - - - | - - - | 41637 | 38006 | 35907 | 115550 | 5166 | 1661 | 6561 | 13388 | - - - | - - - | - - - | - - - | 5166 | 1661 | 6561 | 13388 | 44473 | 40921 | 39683 | 125077 | # # # | # # # | # # # | # # # | 0.936 | 0.929 | 0.905 | 0.924 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.984 | 0.992 | - - - | 0.116 | 1.88 | 1.78 | 1.87 | 1.78 | 1.76 | 1.89 | 35.48 | 39.69 | 42.93 | 0 | - - - | - - - | - - - | - - - | 44473 | 40921 | 39683 | 125077 | Over-range | 15627 | 15168 | 16894 | 47879 | 14748 | 15076 | 15568 | 45969 | 41565 | 37972 | 35841 | 115378 | 41565 | 37972 | 35841 | 115378 | - - - | - - - | - - - | - - -
5/6/2026 | 8:30:00 PM | 282.57 | 280.38 | 280.27 | 489.64 | 483.92 | 486.94 | 156.8498 | 145.1439 | 140.5354 | 5.2953 | 1.442 | 1.44 | 1.443 | 1.735 | 1.785 | 1.847 | Over-range | 59.99 | 41507 | 37780 | 35594 | 114881 | - - - | - - - | - - - | - - - | 41507 | 37780 | 35594 | 114881 | 5132 | 1588 | 6618 | 13338 | - - - | - - - | - - - | - - - | 5132 | 1588 | 6618 | 13338 | 44321 | 40695 | 39388 | 124403 | # # # | # # # | # # # | # # # | 0.937 | 0.928 | 0.904 | 0.924 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.983 | 0.992 | - - - | 0.116 | 1.87 | 1.78 | 1.87 | 1.77 | 1.77 | 1.89 | 35.4 | 39.82 | 43.13 | 0 | - - - | - - - | - - - | - - - | 44321 | 40695 | 39388 | 124403 | Over-range | 15540 | 15123 | 16866 | 47733 | 14668 | 15039 | 15512 | 45832 | 41439 | 37747 | 35529 | 114715 | 41439 | 37747 | 35529 | 114715 | - - - | - - - | - - - | - - -
5/6/2026 | 8:45:00 PM | 283.01 | 280.86 | 280.73 | 490.44 | 484.75 | 487.68 | 155.4196 | 143.5161 | 139.0512 | 5.169 | 1.442 | 1.44 | 1.444 | 1.739 | 1.792 | 1.855 | Over-range | 59.99 | 41164 | 37380 | 35212 | 113755 | - - - | - - - | - - - | - - - | 41164 | 37380 | 35212 | 113755 | 5143 | 1518 | 6637 | 13299 | - - - | - - - | - - - | - - - | 5143 | 1518 | 6637 | 13299 | 43984 | 40307 | 39034 | 123325 | # # # | # # # | # # # | # # # | 0.936 | 0.927 | 0.902 | 0.922 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.983 | 0.992 | - - - | 0.117 | 1.88 | 1.78 | 1.87 | 1.77 | 1.77 | 1.89 | 35.57 | 40.16 | 43.49 | 0 | - - - | - - - | - - - | - - - | 43984 | 40307 | 39034 | 123325 | Over-range | 15496 | 15079 | 16845 | 47630 | 14618 | 15002 | 15482 | 45736 | 41094 | 37348 | 35149 | 113590 | 41094 | 37348 | 35149 | 113590 | - - - | - - - | - - - | - - -
5/6/2026 | 9:00:00 PM | 281.92 | 279.76 | 279.54 | 488.58 | 482.75 | 485.69 | 153.7609 | 141.2479 | 137.1634 | 5.1606 | 1.44 | 1.439 | 1.442 | 1.747 | 1.807 | 1.874 | Over-range | 60 | 40492 | 36559 | 34423 | 111473 | - - - | - - - | - - - | - - - | 40492 | 36559 | 34423 | 111473 | 5171 | 1361 | 6737 | 13270 | - - - | - - - | - - - | - - - | 5171 | 1361 | 6737 | 13270 | 43347 | 39515 | 38342 | 121204 | # # # | # # # | # # # | # # # | 0.934 | 0.925 | 0.898 | 0.92 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.981 | 0.991 | - - - | 0.119 | 1.82 | 1.74 | 1.83 | 1.72 | 1.73 | 1.84 | 36 | 40.81 | 44.36 | 0 | - - - | - - - | - - - | - - - | 43347 | 39515 | 38342 | 121204 | Over-range | 15472 | 14996 | 16887 | 47583 | 14582 | 14934 | 15485 | 45695 | 40430 | 36536 | 34371 | 111337 | 40430 | 36536 | 34371 | 111337 | - - - | - - - | - - - | - - -
5/6/2026 | 9:15:00 PM | 281.95 | 279.91 | 279.7 | 488.71 | 483.08 | 485.82 | 152.5313 | 140.6101 | 137.0294 | 5.0665 | 1.44 | 1.438 | 1.441 | 1.753 | 1.807 | 1.87 | Over-range | 59.98 | 40124 | 36379 | 34413 | 110915 | - - - | - - - | - - - | - - - | 40124 | 36379 | 34413 | 110915 | 5133 | 1514 | 6651 | 13298 | - - - | - - - | - - - | - - - | 5133 | 1514 | 6651 | 13298 | 43006 | 39357 | 38326 | 120689 | # # # | # # # | # # # | # # # | 0.933 | 0.924 | 0.898 | 0.919 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.982 | 0.991 | - - - | 0.12 | 1.81 | 1.74 | 1.81 | 1.72 | 1.72 | 1.83 | 36.36 | 41 | 44.43 | 0 | - - - | - - - | - - - | - - - | 43006 | 39357 | 38326 | 120689 | Over-range | 15479 | 15019 | 16871 | 47578 | 14602 | 14942 | 15504 | 45682 | 40064 | 36358 | 34362 | 110784 | 40064 | 36358 | 34362 | 110784 | - - - | - - - | - - - | - - -
5/6/2026 | 9:30:00 PM | 281.96 | 279.98 | 279.7 | 488.8 | 483.16 | 485.79 | 152.6298 | 140.8068 | 136.6958 | 4.976 | 1.44 | 1.438 | 1.441 | 1.747 | 1.808 | 1.868 | Over-range | 60.01 | 40154 | 36465 | 34346 | 110966 | - - - | - - - | - - - | - - - | 40154 | 36465 | 34346 | 110966 | 5178 | 1477 | 6586 | 13241 | - - - | - - - | - - - | - - - | 5178 | 1477 | 6586 | 13241 | 43035 | 39422 | 38233 | 120690 | # # # | # # # | # # # | # # # | 0.933 | 0.925 | 0.898 | 0.919 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.982 | 0.991 | - - - | 0.119 | 1.83 | 1.74 | 1.82 | 1.73 | 1.72 | 1.84 | 36.27 | 40.79 | 44.35 | 0 | - - - | - - - | - - - | - - - | 43035 | 39422 | 38233 | 120690 | Over-range | 15481 | 14979 | 16795 | 47462 | 14589 | 14906 | 15450 | 45578 | 40097 | 36448 | 34297 | 110842 | 40097 | 36448 | 34297 | 110842 | - - - | - - - | - - - | - - -
5/6/2026 | 9:45:00 PM | 282.02 | 279.97 | 279.68 | 488.86 | 483.08 | 485.83 | 152.6022 | 140.3825 | 136.0973 | 5.1118 | 1.439 | 1.438 | 1.44 | 1.749 | 1.811 | 1.876 | Over-range | 60.01 | 40153 | 36337 | 34141 | 110632 | - - - | - - - | - - - | - - - | 40153 | 36337 | 34141 | 110632 | 5142 | 1409 | 6654 | 13204 | - - - | - - - | - - - | - - - | 5142 | 1409 | 6654 | 13204 | 43035 | 39301 | 38062 | 120398 | # # # | # # # | # # # | # # # | 0.933 | 0.925 | 0.897 | 0.919 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.981 | 0.991 | - - - | 0.119 | 1.82 | 1.73 | 1.81 | 1.72 | 1.71 | 1.83 | 36.28 | 40.9 | 44.56 | 0 | - - - | - - - | - - - | - - - | 43035 | 39301 | 38062 | 120398 | Over-range | 15483 | 14972 | 16825 | 47501 | 14604 | 14906 | 15453 | 45629 | 40101 | 36323 | 34098 | 110523 | 40101 | 36323 | 34098 | 110523 | - - - | - - - | - - - | - - -
5/6/2026 | 10:00:00 PM | 282.4 | 280.42 | 280.06 | 489.6 | 483.83 | 486.45 | 155.0505 | 143.8656 | 138.9381 | 4.9157 | 1.44 | 1.438 | 1.44 | 1.736 | 1.797 | 1.85 | Over-range | 60.01 | 40876 | 37382 | 35084 | 113342 | - - - | - - - | - - - | - - - | 40876 | 37382 | 35084 | 113342 | 5223 | 1663 | 6459 | 13345 | - - - | - - - | - - - | - - - | 5223 | 1663 | 6459 | 13345 | 43784 | 40338 | 38906 | 123028 | # # # | # # # | # # # | # # # | 0.934 | 0.927 | 0.902 | 0.921 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.983 | 0.992 | - - - | 0.118 | 1.85 | 1.75 | 1.83 | 1.75 | 1.73 | 1.86 | 36.1 | 40.18 | 43.65 | 0 | - - - | - - - | - - - | - - - | 43784 | 40338 | 38906 | 123028 | Over-range | 15692 | 15157 | 16811 | 47845 | 14796 | 15062 | 15520 | 45946 | 40823 | 37363 | 35040 | 113227 | 40823 | 37363 | 35040 | 113227 | - - - | - - - | - - - | - - -
5/6/2026 | 10:15:00 PM | 281.75 | 279.68 | 279.33 | 488.42 | 482.52 | 485.29 | 163.1662 | 151.892 | 147.5855 | 4.5821 | 1.439 | 1.437 | 1.44 | 1.72 | 1.76 | 1.806 | Over-range | 60 | 43054 | 39489 | 37504 | 120046 | - - - | - - - | - - - | - - - | 43054 | 39489 | 37504 | 120046 | 5130 | 2267 | 6466 | 13863 | - - - | - - - | - - - | - - - | 5130 | 2267 | 6466 | 13863 | 45968 | 42479 | 41223 | 129671 | # # # | # # # | # # # | # # # | 0.937 | 0.93 | 0.91 | 0.926 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.985 | 0.992 | - - - | 0.116 | 1.9 | 1.8 | 1.9 | 1.8 | 1.79 | 1.93 | 35.35 | 39.09 | 41.72 | 0 | - - - | - - - | - - - | - - - | 45968 | 42479 | 41223 | 129671 | Over-range | 16108 | 15656 | 17112 | 49024 | 15269 | 15490 | 15843 | 47023 | 43004 | 39471 | 37464 | 119939 | 43004 | 39471 | 37464 | 119939 | - - - | - - - | - - - | - - -
5/6/2026 | 10:30:00 PM | 281.72 | 279.45 | 279.1 | 488.24 | 482 | 485.13 | 146.124 | 134.3555 | 131.1389 | 5.06 | 1.439 | 1.437 | 1.439 | 1.77 | 1.821 | 1.878 | Over-range | 60 | 38203 | 34565 | 32742 | 105510 | - - - | - - - | - - - | - - - | 38203 | 34565 | 32742 | 105510 | 4722 | 1708 | 6381 | 12811 | - - - | - - - | - - - | - - - | 4722 | 1708 | 6381 | 12811 | 41057 | 37448 | 36519 | 115024 | # # # | # # # | # # # | # # # | 0.931 | 0.923 | 0.897 | 0.917 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.981 | 0.991 | - - - | 0.121 | 1.76 | 1.66 | 1.74 | 1.66 | 1.64 | 1.77 | 37.43 | 41.35 | 44.77 | 0 | - - - | - - - | - - - | - - - | 41057 | 37448 | 36519 | 115024 | Over-range | 15030 | 14407 | 16165 | 45790 | 14266 | 14297 | 14850 | 43962 | 38149 | 34545 | 32698 | 105392 | 38149 | 34545 | 32698 | 105392 | - - - | - - - | - - - | - - -
5/6/2026 | 10:45:00 PM | 282.59 | 280.25 | 279.91 | 489.71 | 483.34 | 486.61 | 123.6174 | 114.922 | 113.9667 | 4.1352 | 1.438 | 1.437 | 1.437 | 1.81 | 1.852 | 1.876 | Over-range | 60.01 | 32296 | 29667 | 28717 | 90680 | - - - | - - - | - - - | - - - | 32296 | 29667 | 28717 | 90680 | 3747 | 1958 | 5134 | 10839 | - - - | - - - | - - - | - - - | 3747 | 1958 | 5134 | 10839 | 34927 | 32201 | 31896 | 99025 | # # # | # # # | # # # | # # # | 0.925 | 0.921 | 0.9 | 0.916 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.984 | 0.992 | - - - | 0.119 | 1.58 | 1.5 | 1.52 | 1.49 | 1.44 | 1.54 | 39.61 | 41.75 | 44.47 | 0 | - - - | - - - | - - - | - - - | 34927 | 32201 | 31896 | 99025 | Over-range | 13300 | 12522 | 13881 | 39788 | 12761 | 12368 | 12897 | 38283 | 32236 | 29633 | 28671 | 90539 | 32236 | 29633 | 28671 | 90539 | - - - | - - - | - - - | - - -
5/6/2026 | 11:00:00 PM | 282.89 | 280.47 | 280.17 | 490.15 | 483.72 | 487.13 | 121.1055 | 112.5509 | 111.9908 | 4.207 | 1.436 | 1.436 | 1.434 | 1.822 | 1.854 | 1.884 | Over-range | 60.01 | 31662 | 29060 | 28224 | 88946 | - - - | - - - | - - - | - - - | 31662 | 29060 | 28224 | 88946 | 3636 | 1912 | 5064 | 10612 | - - - | - - - | - - - | - - - | 3636 | 1912 | 5064 | 10612 | 34258 | 31566 | 31375 | 97200 | # # # | # # # | # # # | # # # | 0.924 | 0.921 | 0.9 | 0.915 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.984 | 0.992 | - - - | 0.119 | 1.54 | 1.47 | 1.49 | 1.47 | 1.41 | 1.5 | 39.83 | 41.98 | 44.68 | 0 | - - - | - - - | - - - | - - - | 34258 | 31566 | 31375 | 97200 | Over-range | 13083 | 12326 | 13704 | 39197 | 12567 | 12176 | 12734 | 37733 | 31599 | 29025 | 28179 | 88803 | 31599 | 29025 | 28179 | 88803 | - - - | - - - | - - - | - - -
5/6/2026 | 11:15:00 PM | 283 | 280.32 | 280 | 490.21 | 483.29 | 487.16 | 119.7786 | 110.1673 | 110.1359 | 4.0258 | 1.436 | 1.436 | 1.434 | 1.823 | 1.851 | 1.891 | Over-range | 59.99 | 31371 | 28435 | 27702 | 87508 | - - - | - - - | - - - | - - - | 31371 | 28435 | 27702 | 87508 | 3569 | 1777 | 5136 | 10482 | - - - | - - - | - - - | - - - | 3569 | 1777 | 5136 | 10482 | 33875 | 30865 | 30824 | 95565 | # # # | # # # | # # # | # # # | 0.926 | 0.921 | 0.899 | 0.916 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.12 | 1.55 | 1.49 | 1.5 | 1.47 | 1.44 | 1.51 | 39.26 | 41.84 | 44.63 | 0 | - - - | - - - | - - - | - - - | 33875 | 30865 | 30824 | 95565 | Over-range | 12776 | 12002 | 13512 | 38391 | 12267 | 11869 | 12498 | 36932 | 31304 | 28395 | 27653 | 87352 | 31304 | 28395 | 27653 | 87352 | - - - | - - - | - - - | - - -
5/6/2026 | 11:30:00 PM | 283.55 | 280.9 | 280.57 | 491.18 | 484.3 | 488.11 | 118.3128 | 108.7338 | 109.1451 | 4.1482 | 1.436 | 1.436 | 1.434 | 1.833 | 1.852 | 1.897 | Over-range | 60 | 31029 | 28080 | 27469 | 86578 | - - - | - - - | - - - | - - - | 31029 | 28080 | 27469 | 86578 | 3513 | 1778 | 5175 | 10466 | - - - | - - - | - - - | - - - | 3513 | 1778 | 5175 | 10466 | 33525 | 30527 | 30608 | 94660 | # # # | # # # | # # # | # # # | 0.926 | 0.92 | 0.897 | 0.915 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.991 | - - - | 0.121 | 1.56 | 1.5 | 1.51 | 1.49 | 1.45 | 1.53 | 39.44 | 42.26 | 44.88 | 0 | - - - | - - - | - - - | - - - | 33525 | 30527 | 30608 | 94660 | Over-range | 12688 | 11971 | 13498 | 38258 | 12191 | 11838 | 12466 | 36799 | 30966 | 28041 | 27417 | 86425 | 30966 | 28041 | 27417 | 86425 | - - - | - - - | - - - | - - -
5/6/2026 | 11:45:00 PM | 283.56 | 281.02 | 280.67 | 491.28 | 484.54 | 488.16 | 118.0949 | 109.0161 | 109.043 | 4.2398 | 1.435 | 1.434 | 1.433 | 1.831 | 1.854 | 1.895 | Over-range | 60 | 30942 | 28151 | 27449 | 86542 | - - - | - - - | - - - | - - - | 30942 | 28151 | 27449 | 86542 | 3544 | 1795 | 5119 | 10459 | - - - | - - - | - - - | - - - | 3544 | 1795 | 5119 | 10459 | 33464 | 30618 | 30588 | 94671 | # # # | # # # | # # # | # # # | 0.925 | 0.919 | 0.897 | 0.914 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.983 | 0.992 | - - - | 0.121 | 1.55 | 1.49 | 1.5 | 1.47 | 1.44 | 1.51 | 39.68 | 42.38 | 44.98 | 0 | - - - | - - - | - - - | - - - | 33464 | 30618 | 30588 | 94671 | Over-range | 12738 | 12040 | 13493 | 38367 | 12235 | 11905 | 12485 | 36914 | 30876 | 28111 | 27401 | 86389 | 30876 | 28111 | 27401 | 86389 | - - - | - - - | - - - | - - -
5/7/2026 | 12:00:00 AM | 284.05 | 281.49 | 281.05 | 492.17 | 485.24 | 488.89 | 118.3462 | 108.8058 | 108.6863 | 4.0518 | 1.435 | 1.435 | 1.433 | 1.83 | 1.859 | 1.903 | Over-range | 60.01 | 31074 | 28140 | 27371 | 86585 | - - - | - - - | - - - | - - - | 31074 | 28140 | 27371 | 86585 | 3616 | 1716 | 5162 | 10494 | - - - | - - - | - - - | - - - | 3616 | 1716 | 5162 | 10494 | 33594 | 30610 | 30530 | 94735 | # # # | # # # | # # # | # # # | 0.925 | 0.919 | 0.897 | 0.914 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.983 | 0.991 | - - - | 0.121 | 1.56 | 1.5 | 1.51 | 1.49 | 1.45 | 1.53 | 39.5 | 42.45 | 45.14 | 0 | - - - | - - - | - - - | - - - | 33594 | 30610 | 30530 | 94735 | Over-range | 12759 | 12044 | 13521 | 38427 | 12235 | 11921 | 12497 | 36967 | 31010 | 28105 | 27321 | 86435 | 31010 | 28105 | 27321 | 86435 | - - - | - - - | - - - | - - -
5/7/2026 | 12:15:00 AM | 284.35 | 281.71 | 281.38 | 492.59 | 485.7 | 489.49 | 118.3831 | 108.2983 | 109.003 | 3.9786 | 1.435 | 1.434 | 1.432 | 1.843 | 1.858 | 1.91 | Over-range | 59.99 | 31119 | 28011 | 27459 | 86589 | - - - | - - - | - - - | - - - | 31119 | 28011 | 27459 | 86589 | 3516 | 1761 | 5249 | 10526 | - - - | - - - | - - - | - - - | 3516 | 1761 | 5249 | 10526 | 33637 | 30490 | 30653 | 94781 | # # # | # # # | # # # | # # # | 0.925 | 0.919 | 0.896 | 0.914 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.982 | 0.991 | - - - | 0.122 | 1.54 | 1.49 | 1.49 | 1.47 | 1.43 | 1.51 | 39.59 | 42.62 | 45.24 | 0 | - - - | - - - | - - - | - - - | 33637 | 30490 | 30653 | 94781 | Over-range | 12764 | 12040 | 13619 | 38530 | 12270 | 11910 | 12566 | 37065 | 31051 | 27973 | 27407 | 86431 | 31051 | 27973 | 27407 | 86431 | - - - | - - - | - - - | - - -
5/7/2026 | 12:30:00 AM | 284.67 | 282.21 | 281.82 | 493.29 | 486.61 | 490.07 | 115.9622 | 106.9934 | 107.2146 | 4.0761 | 1.434 | 1.433 | 1.432 | 1.833 | 1.848 | 1.894 | Over-range | 60.01 | 30517 | 27741 | 27112 | 85370 | - - - | - - - | - - - | - - - | 30517 | 27741 | 27112 | 85370 | 3468 | 1782 | 5041 | 10292 | - - - | - - - | - - - | - - - | 3468 | 1782 | 5041 | 10292 | 32972 | 30166 | 30188 | 93327 | # # # | # # # | # # # | # # # | 0.926 | 0.92 | 0.898 | 0.915 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.121 | 1.53 | 1.47 | 1.48 | 1.46 | 1.42 | 1.5 | 39.39 | 42.29 | 44.77 | 0 | - - - | - - - | - - - | - - - | 32972 | 30166 | 30188 | 93327 | Over-range | 12475 | 11845 | 13269 | 37685 | 11983 | 11710 | 12274 | 36252 | 30454 | 27704 | 27064 | 85222 | 30454 | 27704 | 27064 | 85222 | - - - | - - - | - - - | - - -
5/7/2026 | 12:45:00 AM | 284.88 | 282.23 | 281.91 | 493.49 | 486.61 | 490.41 | 116.8218 | 106.756 | 107.7215 | 4.0131 | 1.434 | 1.433 | 1.432 | 1.852 | 1.863 | 1.916 | Over-range | 60 | 30728 | 27615 | 27138 | 85481 | - - - | - - - | - - - | - - - | 30728 | 27615 | 27138 | 85481 | 3465 | 1786 | 5257 | 10508 | - - - | - - - | - - - | - - - | 3465 | 1786 | 5257 | 10508 | 33256 | 30110 | 30350 | 93717 | # # # | # # # | # # # | # # # | 0.924 | 0.917 | 0.894 | 0.912 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.982 | 0.991 | - - - | 0.123 | 1.52 | 1.47 | 1.48 | 1.45 | 1.42 | 1.49 | 39.98 | 43.09 | 45.63 | 0 | - - - | - - - | - - - | - - - | 33256 | 30110 | 30350 | 93717 | Over-range | 12711 | 12000 | 13584 | 38403 | 12229 | 11866 | 12526 | 36937 | 30659 | 27572 | 27082 | 85313 | 30659 | 27572 | 27082 | 85313 | - - - | - - - | - - - | - - -
5/7/2026 | 1:00:00 AM | 285.09 | 282.42 | 282.1 | 493.85 | 486.92 | 490.77 | 117.2293 | 106.9708 | 108.036 | 3.9785 | 1.435 | 1.434 | 1.432 | 1.853 | 1.865 | 1.918 | Over-range | 60.01 | 30857 | 27681 | 27216 | 85755 | - - - | - - - | - - - | - - - | 30857 | 27681 | 27216 | 85755 | 3499 | 1787 | 5308 | 10594 | - - - | - - - | - - - | - - - | 3499 | 1787 | 5308 | 10594 | 33397 | 30191 | 30459 | 94047 | # # # | # # # | # # # | # # # | 0.924 | 0.917 | 0.893 | 0.912 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.981 | 0.991 | - - - | 0.124 | 1.53 | 1.47 | 1.49 | 1.46 | 1.42 | 1.5 | 39.99 | 43.18 | 45.76 | 0 | - - - | - - - | - - - | - - - | 33397 | 30191 | 30459 | 94047 | Over-range | 12769 | 12048 | 13671 | 38600 | 12280 | 11915 | 12598 | 37118 | 30788 | 27638 | 27159 | 85585 | 30788 | 27638 | 27159 | 85585 | - - - | - - - | - - - | - - -
5/7/2026 | 1:15:00 AM | 284.99 | 282.3 | 282.09 | 493.59 | 486.83 | 490.7 | 116.8642 | 106.778 | 108.0081 | 4.073 | 1.434 | 1.433 | 1.432 | 1.856 | 1.861 | 1.915 | Over-range | 60 | 30751 | 27622 | 27228 | 85601 | - - - | - - - | - - - | - - - | 30751 | 27622 | 27228 | 85601 | 3440 | 1840 | 5301 | 10582 | - - - | - - - | - - - | - - - | 3440 | 1840 | 5301 | 10582 | 33280 | 30125 | 30451 | 93856 | # # # | # # # | # # # | # # # | 0.924 | 0.917 | 0.894 | 0.912 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.981 | 0.991 | - - - | 0.124 | 1.55 | 1.49 | 1.51 | 1.47 | 1.45 | 1.52 | 40.04 | 43.17 | 45.6 | 0 | - - - | - - - | - - - | - - - | 33280 | 30125 | 30451 | 93856 | Over-range | 12718 | 12021 | 13629 | 38475 | 12243 | 11879 | 12555 | 36991 | 30680 | 27578 | 27170 | 85428 | 30680 | 27578 | 27170 | 85428 | - - - | - - - | - - - | - - -
5/7/2026 | 1:30:00 AM | 285.11 | 282.43 | 282.22 | 493.82 | 487.06 | 490.92 | 116.9762 | 106.985 | 108.3882 | 4.0862 | 1.435 | 1.434 | 1.432 | 1.859 | 1.86 | 1.913 | Over-range | 60.01 | 30802 | 27684 | 27342 | 85828 | - - - | - - - | - - - | - - - | 30802 | 27684 | 27342 | 85828 | 3416 | 1899 | 5318 | 10634 | - - - | - - - | - - - | - - - | 3416 | 1899 | 5318 | 10634 | 33326 | 30198 | 30570 | 94094 | # # # | # # # | # # # | # # # | 0.924 | 0.917 | 0.894 | 0.912 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.982 | 0.991 | - - - | 0.124 | 1.58 | 1.52 | 1.54 | 1.5 | 1.48 | 1.55 | 40.03 | 43.2 | 45.58 | 0 | - - - | - - - | - - - | - - - | 33326 | 30198 | 30570 | 94094 | Over-range | 12717 | 12059 | 13667 | 38551 | 12249 | 11908 | 12590 | 37055 | 30725 | 27637 | 27279 | 85641 | 30725 | 27637 | 27279 | 85641 | - - - | - - - | - - - | - - -
5/7/2026 | 1:45:00 AM | 285.28 | 282.4 | 282.12 | 494.04 | 486.82 | 491.02 | 127.8347 | 114.0274 | 117.2977 | 3.3004 | 1.438 | 1.435 | 1.434 | 1.863 | 1.862 | 1.935 | Over-range | 60.01 | 33905 | 29550 | 29486 | 92941 | - - - | - - - | - - - | - - - | 33905 | 29550 | 29486 | 92941 | 3432 | 1828 | 6059 | 11319 | - - - | - - - | - - - | - - - | 3432 | 1828 | 6059 | 11319 | 36433 | 32170 | 33071 | 101674 | # # # | # # # | # # # | # # # | 0.931 | 0.919 | 0.892 | 0.914 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.979 | 0.991 | - - - | 0.122 | 1.71 | 1.68 | 1.69 | 1.65 | 1.66 | 1.7 | 38.53 | 42.89 | 46.07 | 0 | - - - | - - - | - - - | - - - | 36433 | 32170 | 33071 | 101674 | Over-range | 13332 | 12712 | 14972 | 41216 | 12880 | 12578 | 13690 | 39631 | 33800 | 29488 | 29397 | 92685 | 33800 | 29488 | 29397 | 92685 | - - - | - - - | - - - | - - -
5/7/2026 | 2:00:00 AM | 285.37 | 282.52 | 282.24 | 494.2 | 487.05 | 491.2 | 145.8673 | 129.9863 | 130.3087 | 4.3188 | 1.439 | 1.436 | 1.436 | 1.812 | 1.841 | 1.932 | Over-range | 60.02 | 38923 | 33901 | 32764 | 105588 | - - - | - - - | - - - | - - - | 38923 | 33901 | 32764 | 105588 | 4397 | 1475 | 6978 | 12850 | - - - | - - - | - - - | - - - | 4397 | 1475 | 6978 | 12850 | 41598 | 36703 | 36761 | 115062 | # # # | # # # | # # # | # # # | 0.936 | 0.924 | 0.891 | 0.918 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.978 | 0.99 | - - - | 0.122 | 1.78 | 1.74 | 1.78 | 1.7 | 1.74 | 1.78 | 36.43 | 41.47 | 45.73 | 0 | - - - | - - - | - - - | - - - | 41598 | 36703 | 36761 | 115062 | Over-range | 14676 | 14064 | 16670 | 45720 | 14001 | 13985 | 15138 | 43878 | 38817 | 33847 | 32671 | 105335 | 38817 | 33847 | 32671 | 105335 | - - - | - - - | - - - | - - -
5/7/2026 | 2:15:00 AM | 285.26 | 282.48 | 282.17 | 494.07 | 486.99 | 491.01 | 152.0402 | 135.6718 | 135.2864 | 5.0609 | 1.439 | 1.436 | 1.437 | 1.796 | 1.825 | 1.921 | Over-range | 60 | 40672 | 35464 | 34099 | 110235 | - - - | - - - | - - - | - - - | 40672 | 35464 | 34099 | 110235 | 4560 | 1508 | 7335 | 13403 | - - - | - - - | - - - | - - - | 4560 | 1508 | 7335 | 13403 | 43369 | 38323 | 38172 | 119864 | # # # | # # # | # # # | # # # | 0.938 | 0.925 | 0.893 | 0.92 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.978 | 0.99 | - - - | 0.122 | 1.8 | 1.77 | 1.82 | 1.73 | 1.77 | 1.82 | 35.67 | 40.92 | 44.99 | 0 | - - - | - - - | - - - | - - - | 43369 | 38323 | 38172 | 119864 | Over-range | 15055 | 14522 | 17157 | 47068 | 14347 | 14443 | 15509 | 45119 | 40566 | 35413 | 34005 | 109984 | 40566 | 35413 | 34005 | 109984 | - - - | - - - | - - - | - - -
5/7/2026 | 2:30:00 AM | 285.29 | 282.52 | 282.28 | 494.1 | 487.15 | 491.15 | 154.1284 | 137.7948 | 137.6149 | 5.0233 | 1.44 | 1.436 | 1.437 | 1.791 | 1.815 | 1.908 | Over-range | 60.01 | 41261 | 36063 | 34785 | 112108 | - - - | - - - | - - - | - - - | 41261 | 36063 | 34785 | 112108 | 4579 | 1656 | 7377 | 13612 | - - - | - - - | - - - | - - - | 4579 | 1656 | 7377 | 13612 | 43971 | 38929 | 38845 | 121745 | # # # | # # # | # # # | # # # | 0.938 | 0.926 | 0.896 | 0.921 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.978 | 0.991 | - - - | 0.121 | 1.85 | 1.81 | 1.86 | 1.76 | 1.81 | 1.86 | 35.5 | 40.57 | 44.47 | 0 | - - - | - - - | - - - | - - - | 43971 | 38929 | 38845 | 121745 | Over-range | 15198 | 14662 | 17290 | 47471 | 14491 | 14567 | 15636 | 45478 | 41160 | 36011 | 34693 | 111865 | 41160 | 36011 | 34693 | 111865 | - - - | - - - | - - - | - - -
5/7/2026 | 2:45:00 AM | 285.49 | 282.78 | 282.46 | 494.51 | 487.53 | 491.44 | 156.5803 | 140.0594 | 139.3786 | 5.3227 | 1.44 | 1.436 | 1.437 | 1.785 | 1.813 | 1.906 | Over-range | 60 | 41948 | 36699 | 35248 | 113895 | - - - | - - - | - - - | - - - | 41948 | 36699 | 35248 | 113895 | 4713 | 1691 | 7532 | 13936 | - - - | - - - | - - - | - - - | 4713 | 1691 | 7532 | 13936 | 44701 | 39604 | 39368 | 123674 | # # # | # # # | # # # | # # # | 0.938 | 0.927 | 0.895 | 0.921 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.978 | 0.99 | - - - | 0.122 | 1.85 | 1.82 | 1.87 | 1.77 | 1.82 | 1.87 | 35.44 | 40.48 | 44.42 | 0 | - - - | - - - | - - - | - - - | 44701 | 39604 | 39368 | 123674 | Over-range | 15445 | 14889 | 17534 | 48198 | 14708 | 14792 | 15833 | 46140 | 41846 | 36648 | 35156 | 113650 | 41846 | 36648 | 35156 | 113650 | - - - | - - - | - - - | - - -
5/7/2026 | 3:00:00 AM | 285.54 | 282.87 | 282.6 | 494.6 | 487.76 | 491.6 | 157.9067 | 141.8006 | 141.1435 | 5.3247 | 1.44 | 1.436 | 1.437 | 1.782 | 1.808 | 1.895 | Over-range | 60.01 | 42313 | 37193 | 35783 | 115289 | - - - | - - - | - - - | - - - | 42313 | 37193 | 35783 | 115289 | 4766 | 1808 | 7530 | 14104 | - - - | - - - | - - - | - - - | 4766 | 1808 | 7530 | 14104 | 45088 | 40110 | 39885 | 125083 | # # # | # # # | # # # | # # # | 0.939 | 0.927 | 0.897 | 0.922 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.978 | 0.991 | - - - | 0.122 | 1.86 | 1.82 | 1.87 | 1.78 | 1.83 | 1.87 | 35.41 | 40.26 | 44.05 | 0 | - - - | - - - | - - - | - - - | 45088 | 40110 | 39885 | 125083 | Over-range | 15573 | 15016 | 17618 | 48520 | 14825 | 14907 | 15927 | 46425 | 42208 | 37140 | 35692 | 115040 | 42208 | 37140 | 35692 | 115040 | - - - | - - - | - - - | - - -
5/7/2026 | 3:15:00 AM | 285.56 | 282.92 | 282.58 | 494.68 | 487.79 | 491.58 | 158.8853 | 142.5962 | 141.8906 | 5.1511 | 1.44 | 1.436 | 1.437 | 1.779 | 1.809 | 1.895 | Over-range | 60.01 | 42574 | 37408 | 35968 | 115950 | - - - | - - - | - - - | - - - | 42574 | 37408 | 35968 | 115950 | 4840 | 1787 | 7554 | 14181 | - - - | - - - | - - - | - - - | 4840 | 1787 | 7554 | 14181 | 45370 | 40341 | 40095 | 125806 | # # # | # # # | # # # | # # # | 0.938 | 0.927 | 0.897 | 0.922 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.979 | 0.991 | - - - | 0.122 | 1.84 | 1.8 | 1.86 | 1.76 | 1.81 | 1.86 | 35.4 | 40.26 | 44.11 | 0 | - - - | - - - | - - - | - - - | 45370 | 40341 | 40095 | 125806 | Over-range | 15682 | 15102 | 17716 | 48814 | 14915 | 14995 | 16025 | 46709 | 42470 | 37354 | 35872 | 115696 | 42470 | 37354 | 35872 | 115696 | - - - | - - - | - - - | - - -
5/7/2026 | 3:30:00 AM | 284.65 | 282.15 | 281.79 | 493.22 | 486.51 | 490.06 | 247.6057 | 234.6065 | 227.0923 | 8.9634 | 1.442 | 1.438 | 1.436 | 1.61 | 1.584 | 1.745 | Over-range | 60.01 | 63702 | 60294 | 56460 | 180456 | - - - | - - - | - - - | - - - | 63702 | 60294 | 56460 | 180456 | 22221 | 17736 | 22214 | 62170 | - - - | - - - | - - - | - - - | 22221 | 17736 | 22214 | 62170 | 69279 | 64846 | 62811 | 196936 | # # # | # # # | # # # | # # # | 0.92 | 0.93 | 0.899 | 0.916 | # # # | # # # | # # # | - - - | 0.94 | 0.955 | 0.928 | 0.941 | - - - | 0.344 | 1.83 | 1.81 | 1.88 | 1.76 | 1.82 | 1.86 | 22.77 | 24.82 | 27.22 | 0 | - - - | - - - | - - - | - - - | 69279 | 64846 | 62811 | 196936 | Over-range | 27136 | 23786 | 27469 | 78668 | 13947 | 14181 | 15042 | 43863 | 63449 | 60225 | 56268 | 179943 | 63449 | 60225 | 56268 | 179943 | - - - | - - - | - - - | - - -
5/7/2026 | 3:45:00 AM | 284.83 | 282.43 | 282.19 | 493.51 | 487.2 | 490.56 | 281.1343 | 265.0718 | 255.9686 | 9.3956 | 1.44 | 1.436 | 1.435 | 1.55 | 1.523 | 1.717 | Over-range | 60 | 73731 | 69867 | 64841 | 208439 | - - - | - - - | - - - | - - - | 73731 | 69867 | 64841 | 208439 | 27650 | 22000 | 27438 | 77088 | - - - | - - - | - - - | - - - | 27650 | 22000 | 27438 | 77088 | 80072 | 74863 | 72227 | 227162 | # # # | # # # | # # # | # # # | 0.921 | 0.933 | 0.898 | 0.918 | # # # | # # # | # # # | - - - | 0.936 | 0.954 | 0.92 | 0.937 | - - - | 0.37 | 1.93 | 1.93 | 2 | 1.84 | 1.95 | 1.98 | 19.57 | 21.87 | 23.71 | 0 | - - - | - - - | - - - | - - - | 80072 | 74863 | 72227 | 227162 | Over-range | 31228 | 26891 | 31815 | 90309 | 14511 | 15464 | 16105 | 47044 | 73456 | 69826 | 64593 | 207875 | 73456 | 69826 | 64593 | 207875 | - - - | - - - | - - - | - - -
5/7/2026 | 4:00:00 AM | 285.13 | 282.69 | 282.39 | 494.03 | 487.54 | 490.99 | 261.441 | 250.0101 | 240.9509 | 8.6662 | 1.44 | 1.436 | 1.436 | 1.575 | 1.533 | 1.709 | Over-range | 60.02 | 68033 | 65610 | 61003 | 194646 | - - - | - - - | - - - | - - - | 68033 | 65610 | 61003 | 194646 | 27180 | 22215 | 26285 | 75679 | - - - | - - - | - - - | - - - | 27180 | 22215 | 26285 | 75679 | 74506 | 70656 | 68025 | 213187 | # # # | # # # | # # # | # # # | 0.913 | 0.929 | 0.897 | 0.913 | # # # | # # # | # # # | - - - | 0.928 | 0.947 | 0.918 | 0.931 | - - - | 0.389 | 1.84 | 1.81 | 1.89 | 1.75 | 1.84 | 1.87 | 19.69 | 20.93 | 22.96 | 0 | - - - | - - - | - - - | - - - | 74506 | 70656 | 68025 | 213187 | Over-range | 30373 | 26212 | 30100 | 86953 | 13555 | 13893 | 14664 | 42798 | 67769 | 65554 | 60774 | 194097 | 67769 | 65554 | 60774 | 194097 | - - - | - - - | - - - | - - -
5/7/2026 | 4:15:00 AM | 285.11 | 282.57 | 282.38 | 493.89 | 487.41 | 491.03 | 243.1106 | 237.2886 | 229.6987 | 7.7197 | 1.44 | 1.436 | 1.436 | 1.588 | 1.566 | 1.681 | Over-range | 60 | 62988 | 61677 | 58371 | 183035 | - - - | - - - | - - - | - - - | 62988 | 61677 | 58371 | 183035 | 25990 | 23150 | 25013 | 74153 | - - - | - - - | - - - | - - - | 25990 | 23150 | 25013 | 74153 | 69308 | 67048 | 64858 | 201214 | # # # | # # # | # # # | # # # | 0.909 | 0.92 | 0.9 | 0.91 | # # # | # # # | # # # | - - - | 0.924 | 0.936 | 0.919 | 0.926 | - - - | 0.405 | 1.79 | 1.77 | 1.81 | 1.71 | 1.77 | 1.82 | 19.83 | 19.96 | 21.7 | 0 | - - - | - - - | - - - | - - - | 69308 | 67048 | 64858 | 201214 | Over-range | 28916 | 26293 | 28274 | 83576 | 12674 | 12461 | 13181 | 38548 | 62759 | 61604 | 58128 | 182492 | 62759 | 61604 | 58128 | 182492 | - - - | - - - | - - - | - - -
5/7/2026 | 4:30:00 AM | 284.9 | 282.48 | 282.23 | 493.62 | 487.26 | 490.67 | 236.6767 | 232.3255 | 224.3634 | 7.547 | 1.44 | 1.436 | 1.436 | 1.597 | 1.573 | 1.675 | Over-range | 60 | 61106 | 60202 | 56970 | 178278 | - - - | - - - | - - - | - - - | 61106 | 60202 | 56970 | 178278 | 25678 | 23181 | 24642 | 73500 | - - - | - - - | - - - | - - - | 25678 | 23181 | 24642 | 73500 | 67427 | 65625 | 63320 | 196372 | # # # | # # # | # # # | # # # | 0.906 | 0.917 | 0.9 | 0.908 | # # # | # # # | # # # | - - - | 0.922 | 0.933 | 0.917 | 0.924 | - - - | 0.412 | 1.8 | 1.73 | 1.81 | 1.71 | 1.75 | 1.81 | 19.76 | 19.71 | 21.26 | 0 | - - - | - - - | - - - | - - - | 67427 | 65625 | 63320 | 196372 | Over-range | 28502 | 26122 | 27639 | 82334 | 12370 | 12042 | 12516 | 37101 | 60940 | 59992 | 56817 | 177749 | 60940 | 59992 | 56817 | 177749 | - - - | - - - | - - - | - - -
5/7/2026 | 4:45:00 AM | 284.82 | 282.33 | 282.11 | 493.43 | 486.99 | 490.52 | 233.631 | 227.8451 | 220.7265 | 7.4396 | 1.44 | 1.436 | 1.436 | 1.592 | 1.569 | 1.686 | Over-range | 60 | 60249 | 58956 | 55803 | 175009 | - - - | - - - | - - - | - - - | 60249 | 58956 | 55803 | 175009 | 25550 | 22840 | 24708 | 73098 | - - - | - - - | - - - | - - - | 25550 | 22840 | 24708 | 73098 | 66542 | 64326 | 62268 | 193136 | # # # | # # # | # # # | # # # | 0.905 | 0.917 | 0.896 | 0.906 | # # # | # # # | # # # | - - - | 0.92 | 0.932 | 0.914 | 0.922 | - - - | 0.418 | 1.79 | 1.74 | 1.83 | 1.71 | 1.76 | 1.81 | 19.62 | 19.68 | 21.35 | 0 | - - - | - - - | - - - | - - - | 66542 | 64326 | 62268 | 193136 | Over-range | 28247 | 25728 | 27628 | 81692 | 12045 | 11844 | 12363 | 36472 | 60146 | 58761 | 55576 | 174484 | 60146 | 58761 | 55576 | 174484 | - - - | - - - | - - - | - - -
5/7/2026 | 5:00:00 AM | 285.07 | 282.63 | 282.36 | 493.91 | 487.47 | 490.93 | 233.0287 | 226.5106 | 219.4466 | 7.3643 | 1.44 | 1.437 | 1.436 | 1.59 | 1.566 | 1.69 | Over-range | 60.02 | 60145 | 58661 | 55445 | 174251 | - - - | - - - | - - - | - - - | 60145 | 58661 | 55445 | 174251 | 25521 | 22798 | 24723 | 73042 | - - - | - - - | - - - | - - - | 25521 | 22798 | 24723 | 73042 | 66429 | 64017 | 61962 | 192408 | # # # | # # # | # # # | # # # | 0.905 | 0.916 | 0.895 | 0.906 | # # # | # # # | # # # | - - - | 0.92 | 0.932 | 0.913 | 0.922 | - - - | 0.419 | 1.81 | 1.77 | 1.82 | 1.72 | 1.77 | 1.83 | 19.52 | 19.71 | 21.34 | 0 | - - - | - - - | - - - | - - - | 66429 | 64017 | 61962 | 192408 | Over-range | 28201 | 25634 | 27661 | 81592 | 11998 | 11720 | 12405 | 36360 | 59897 | 58594 | 55252 | 173743 | 59897 | 58594 | 55252 | 173743 | - - - | - - - | - - - | - - -
5/7/2026 | 5:15:00 AM | 284.62 | 282.28 | 281.96 | 493.23 | 486.87 | 490.15 | 233.5888 | 227.4563 | 219.4163 | 7.3317 | 1.441 | 1.438 | 1.437 | 1.59 | 1.56 | 1.684 | Over-range | 60 | 60220 | 58901 | 55441 | 174562 | - - - | - - - | - - - | - - - | 60220 | 58901 | 55441 | 174562 | 25523 | 22703 | 24570 | 72796 | - - - | - - - | - - - | - - - | 25523 | 22703 | 24570 | 72796 | 66484 | 64206 | 61865 | 192555 | # # # | # # # | # # # | # # # | 0.906 | 0.917 | 0.896 | 0.907 | # # # | # # # | # # # | - - - | 0.92 | 0.933 | 0.914 | 0.922 | - - - | 0.417 | 1.87 | 1.78 | 1.87 | 1.75 | 1.81 | 1.88 | 19.28 | 19.57 | 21.18 | 0 | - - - | - - - | - - - | - - - | 66484 | 64206 | 61865 | 192555 | Over-range | 28173 | 25555 | 27452 | 81275 | 11927 | 11731 | 12244 | 36144 | 60027 | 58742 | 55303 | 174072 | 60027 | 58742 | 55303 | 174072 | - - - | - - - | - - - | - - -
5/7/2026 | 5:30:00 AM | 284.43 | 282.07 | 281.79 | 492.86 | 486.54 | 489.85 | 235.0294 | 228.45 | 220.703 | 7.3215 | 1.442 | 1.438 | 1.437 | 1.585 | 1.556 | 1.687 | Over-range | 60.01 | 60606 | 59186 | 55730 | 175522 | - - - | - - - | - - - | - - - | 60606 | 59186 | 55730 | 175522 | 25580 | 22532 | 24657 | 72770 | - - - | - - - | - - - | - - - | 25580 | 22532 | 24657 | 72770 | 66848 | 64439 | 62190 | 193477 | # # # | # # # | # # # | # # # | 0.907 | 0.919 | 0.896 | 0.907 | # # # | # # # | # # # | - - - | 0.921 | 0.934 | 0.914 | 0.923 | - - - | 0.415 | 1.85 | 1.8 | 1.88 | 1.76 | 1.81 | 1.88 | 19.18 | 19.62 | 21.34 | 0 | - - - | - - - | - - - | - - - | 66848 | 64439 | 62190 | 193477 | Over-range | 28206 | 25483 | 27600 | 81396 | 11883 | 11902 | 12401 | 36468 | 60518 | 59004 | 55520 | 175042 | 60518 | 59004 | 55520 | 175042 | - - - | - - - | - - - | - - -
5/7/2026 | 5:45:00 AM | 283.73 | 281.31 | 280.99 | 491.63 | 485.14 | 488.57 | 234.9704 | 228.1695 | 220.0095 | 7.242 | 1.441 | 1.438 | 1.437 | 1.587 | 1.554 | 1.688 | Over-range | 60 | 60440 | 58984 | 55407 | 174831 | - - - | - - - | - - - | - - - | 60440 | 58984 | 55407 | 174831 | 25497 | 22400 | 24414 | 72311 | - - - | - - - | - - - | - - - | 25497 | 22400 | 24414 | 72311 | 66668 | 64185 | 61819 | 192671 | # # # | # # # | # # # | # # # | 0.907 | 0.919 | 0.896 | 0.907 | # # # | # # # | # # # | - - - | 0.921 | 0.935 | 0.915 | 0.923 | - - - | 0.414 | 1.83 | 1.8 | 1.86 | 1.74 | 1.8 | 1.86 | 19.25 | 19.59 | 21.4 | 0 | - - - | - - - | - - - | - - - | 66668 | 64185 | 61819 | 192671 | Over-range | 28135 | 25310 | 27417 | 80972 | 11894 | 11782 | 12475 | 36436 | 60228 | 58938 | 55197 | 174363 | 60228 | 58938 | 55197 | 174363 | - - - | - - - | - - - | - - -
5/7/2026 | 6:00:00 AM | 283.31 | 280.97 | 280.74 | 490.89 | 484.7 | 487.98 | 232.5665 | 226.8113 | 219.3313 | 7.1853 | 1.442 | 1.438 | 1.438 | 1.586 | 1.561 | 1.679 | Over-range | 60.02 | 59727 | 58484 | 55248 | 173460 | - - - | - - - | - - - | - - - | 59727 | 58484 | 55248 | 173460 | 25231 | 22483 | 24272 | 71986 | - - - | - - - | - - - | - - - | 25231 | 22483 | 24272 | 71986 | 65887 | 63726 | 61574 | 191187 | # # # | # # # | # # # | # # # | 0.907 | 0.918 | 0.897 | 0.907 | # # # | # # # | # # # | - - - | 0.921 | 0.933 | 0.915 | 0.923 | - - - | 0.415 | 1.89 | 1.83 | 1.89 | 1.78 | 1.84 | 1.91 | 19.12 | 19.42 | 21.06 | 0 | - - - | - - - | - - - | - - - | 65887 | 63726 | 61574 | 191187 | Over-range | 27817 | 25309 | 27185 | 80401 | 11712 | 11622 | 12243 | 35809 | 59543 | 58419 | 55049 | 173012 | 59543 | 58419 | 55049 | 173012 | - - - | - - - | - - - | - - -
5/7/2026 | 6:15:00 AM | 282.44 | 280.12 | 279.77 | 489.46 | 483.1 | 486.37 | 233.1726 | 227.144 | 218.7481 | 7.0358 | 1.443 | 1.441 | 1.44 | 1.585 | 1.55 | 1.677 | Over-range | 59.98 | 59698 | 58501 | 54942 | 173142 | - - - | - - - | - - - | - - - | 59698 | 58501 | 54942 | 173142 | 25253 | 22194 | 24062 | 71509 | - - - | - - - | - - - | - - - | 25253 | 22194 | 24062 | 71509 | 65857 | 63626 | 61199 | 190682 | # # # | # # # | # # # | # # # | 0.907 | 0.92 | 0.898 | 0.908 | # # # | # # # | # # # | - - - | 0.921 | 0.935 | 0.916 | 0.924 | - - - | 0.413 | 2 | 1.93 | 2.03 | 1.89 | 1.96 | 2.04 | 18.91 | 19.24 | 20.98 | 0 | - - - | - - - | - - - | - - - | 65857 | 63626 | 61199 | 190682 | Over-range | 27809 | 25017 | 26956 | 79886 | 11644 | 11546 | 12151 | 35610 | 59528 | 58426 | 54775 | 172729 | 59528 | 58426 | 54775 | 172729 | - - - | - - - | - - - | - - -
5/7/2026 | 6:30:00 AM | 281.61 | 279.25 | 278.99 | 487.94 | 481.68 | 485.01 | 233.8292 | 227.6661 | 219.3736 | 7.0619 | 1.443 | 1.442 | 1.44 | 1.582 | 1.55 | 1.676 | Over-range | 59.99 | 59771 | 58491 | 55000 | 173263 | - - - | - - - | - - - | - - - | 59771 | 58491 | 55000 | 173263 | 25042 | 22115 | 23919 | 71076 | - - - | - - - | - - - | - - - | 25042 | 22115 | 23919 | 71076 | 65849 | 63574 | 61203 | 190627 | # # # | # # # | # # # | # # # | 0.908 | 0.92 | 0.899 | 0.909 | # # # | # # # | # # # | - - - | 0.922 | 0.935 | 0.917 | 0.925 | - - - | 0.41 | 2 | 1.97 | 2.07 | 1.9 | 1.99 | 2.07 | 18.87 | 19.15 | 20.93 | 0 | - - - | - - - | - - - | - - - | 65849 | 63574 | 61203 | 190627 | Over-range | 27631 | 24909 | 26848 | 79489 | 11678 | 11463 | 12193 | 35590 | 59535 | 58459 | 54874 | 172868 | 59535 | 58459 | 54874 | 172868 | - - - | - - - | - - - | - - -
5/7/2026 | 6:45:00 AM | 281.24 | 278.85 | 278.58 | 487.29 | 480.95 | 484.34 | 234.2423 | 227.8583 | 219.2187 | 7.0646 | 1.443 | 1.442 | 1.44 | 1.581 | 1.547 | 1.676 | Over-range | 60 | 59818 | 58499 | 54893 | 173210 | - - - | - - - | - - - | - - - | 59818 | 58499 | 54893 | 173210 | 25011 | 22004 | 23838 | 70853 | - - - | - - - | - - - | - - - | 25011 | 22004 | 23838 | 70853 | 65879 | 63537 | 61069 | 190486 | # # # | # # # | # # # | # # # | 0.908 | 0.921 | 0.899 | 0.909 | # # # | # # # | # # # | - - - | 0.922 | 0.936 | 0.917 | 0.925 | - - - | 0.409 | 1.99 | 1.91 | 2.01 | 1.86 | 1.94 | 2.02 | 18.85 | 19.15 | 20.96 | 0 | - - - | - - - | - - - | - - - | 65879 | 63537 | 61069 | 190486 | Over-range | 27601 | 24795 | 26763 | 79266 | 11673 | 11430 | 12166 | 35537 | 59579 | 58448 | 54786 | 172813 | 59579 | 58448 | 54786 | 172813 | - - - | - - - | - - - | - - -
5/7/2026 | 7:00:00 AM | 281.18 | 278.92 | 278.69 | 487.24 | 481.2 | 484.36 | 233.4082 | 227.7938 | 219.4639 | 7.0655 | 1.443 | 1.442 | 1.44 | 1.582 | 1.55 | 1.671 | Over-range | 60.01 | 59595 | 58458 | 55028 | 173081 | - - - | - - - | - - - | - - - | 59595 | 58458 | 55028 | 173081 | 24891 | 22120 | 23826 | 70838 | - - - | - - - | - - - | - - - | 24891 | 22120 | 23826 | 70838 | 65630 | 63535 | 61162 | 190327 | # # # | # # # | # # # | # # # | 0.908 | 0.92 | 0.9 | 0.909 | # # # | # # # | # # # | - - - | 0.922 | 0.935 | 0.918 | 0.925 | - - - | 0.409 | 1.96 | 1.86 | 1.98 | 1.83 | 1.89 | 1.99 | 18.85 | 19.12 | 20.82 | 0 | - - - | - - - | - - - | - - - | 65630 | 63535 | 61162 | 190327 | Over-range | 27490 | 24888 | 26698 | 79168 | 11667 | 11406 | 12045 | 35349 | 59372 | 58334 | 54970 | 172676 | 59372 | 58334 | 54970 | 172676 | - - - | - - - | - - - | - - -
5/7/2026 | 7:15:00 AM | 281.96 | 279.68 | 279.46 | 488.58 | 482.52 | 485.7 | 235.9256 | 228.9024 | 220.2931 | 7.1962 | 1.444 | 1.442 | 1.44 | 1.578 | 1.544 | 1.68 | Over-range | 60 | 60440 | 58972 | 55280 | 174692 | - - - | - - - | - - - | - - - | 60440 | 58972 | 55280 | 174692 | 25145 | 22014 | 24136 | 71295 | - - - | - - - | - - - | - - - | 25145 | 22014 | 24136 | 71295 | 66520 | 64020 | 61563 | 192102 | # # # | # # # | # # # | # # # | 0.909 | 0.921 | 0.898 | 0.909 | # # # | # # # | # # # | - - - | 0.923 | 0.937 | 0.916 | 0.925 | - - - | 0.408 | 1.98 | 1.91 | 2 | 1.87 | 1.93 | 2.02 | 18.78 | 19.29 | 21.14 | 0 | - - - | - - - | - - - | - - - | 66520 | 64020 | 61563 | 192102 | Over-range | 27782 | 24916 | 27095 | 79913 | 11814 | 11671 | 12311 | 36098 | 60264 | 58815 | 55220 | 174300 | 60264 | 58815 | 55220 | 174300 | - - - | - - - | - - - | - - -
5/7/2026 | 7:30:00 AM | 282.27 | 280.02 | 279.73 | 489.18 | 483.04 | 486.18 | 238.1091 | 229.9883 | 220.6078 | 7.5652 | 1.443 | 1.442 | 1.44 | 1.578 | 1.535 | 1.686 | Over-range | 60.01 | 61075 | 59403 | 55317 | 175795 | - - - | - - - | - - - | - - - | 61075 | 59403 | 55317 | 175795 | 25399 | 21890 | 24346 | 71635 | - - - | - - - | - - - | - - - | 25399 | 21890 | 24346 | 71635 | 67209 | 64400 | 61710 | 193320 | # # # | # # # | # # # | # # # | 0.909 | 0.922 | 0.896 | 0.909 | # # # | # # # | # # # | - - - | 0.923 | 0.938 | 0.915 | 0.925 | - - - | 0.407 | 1.99 | 1.95 | 2.03 | 1.89 | 1.96 | 2.04 | 18.73 | 19.41 | 21.29 | 0 | - - - | - - - | - - - | - - - | 67209 | 64400 | 61710 | 193320 | Over-range | 28053 | 24872 | 27354 | 80428 | 11911 | 11806 | 12469 | 36565 | 60847 | 59305 | 55259 | 175411 | 60847 | 59305 | 55259 | 175411 | - - - | - - - | - - - | - - -
5/7/2026 | 7:45:00 AM | 282.01 | 279.68 | 279.49 | 488.62 | 482.52 | 485.79 | 232.9214 | 226.9131 | 219.1957 | 7.2181 | 1.443 | 1.442 | 1.44 | 1.58 | 1.549 | 1.674 | Over-range | 60.01 | 59600 | 58380 | 55013 | 172993 | - - - | - - - | - - - | - - - | 59600 | 58380 | 55013 | 172993 | 25049 | 22117 | 24063 | 71229 | - - - | - - - | - - - | - - - | 25049 | 22117 | 24063 | 71229 | 65684 | 63462 | 61262 | 190408 | # # # | # # # | # # # | # # # | 0.907 | 0.92 | 0.898 | 0.909 | # # # | # # # | # # # | - - - | 0.921 | 0.935 | 0.916 | 0.924 | - - - | 0.412 | 1.96 | 1.86 | 1.96 | 1.84 | 1.89 | 1.97 | 18.79 | 19.13 | 20.87 | 0 | - - - | - - - | - - - | - - - | 65684 | 63462 | 61262 | 190408 | Over-range | 27610 | 24884 | 26954 | 79553 | 11613 | 11403 | 12144 | 35426 | 59357 | 58315 | 54924 | 172596 | 59357 | 58315 | 54924 | 172596 | - - - | - - - | - - - | - - -
5/7/2026 | 8:00:00 AM | 281.86 | 279.5 | 279.28 | 488.37 | 482.15 | 485.49 | 229.6582 | 224.1626 | 217.0324 | 6.8241 | 1.443 | 1.442 | 1.44 | 1.582 | 1.556 | 1.671 | Over-range | 60.02 | 58664 | 57527 | 54436 | 170627 | - - - | - - - | - - - | - - - | 58664 | 57527 | 54436 | 170627 | 24867 | 22154 | 23860 | 70881 | - - - | - - - | - - - | - - - | 24867 | 22154 | 23860 | 70881 | 64731 | 62652 | 60612 | 187996 | # # # | # # # | # # # | # # # | 0.906 | 0.918 | 0.898 | 0.908 | # # # | # # # | # # # | - - - | 0.92 | 0.933 | 0.916 | 0.923 | - - - | 0.415 | 1.9 | 1.85 | 1.91 | 1.8 | 1.85 | 1.93 | 18.82 | 19 | 20.7 | 0 | - - - | - - - | - - - | - - - | 64731 | 62652 | 60612 | 187996 | Over-range | 27361 | 24819 | 26657 | 78924 | 11413 | 11189 | 11887 | 34711 | 58475 | 57452 | 54295 | 170222 | 58475 | 57452 | 54295 | 170222 | - - - | - - - | - - - | - - -
5/7/2026 | 8:15:00 AM | 281.55 | 279.03 | 278.93 | 487.67 | 481.39 | 484.99 | 230.324 | 224.1168 | 217.4367 | 6.941 | 1.444 | 1.443 | 1.44 | 1.575 | 1.554 | 1.672 | Over-range | 60 | 58832 | 57460 | 54440 | 170732 | - - - | - - - | - - - | - - - | 58832 | 57460 | 54440 | 170732 | 24785 | 21990 | 23987 | 70762 | - - - | - - - | - - - | - - - | 24785 | 21990 | 23987 | 70762 | 64847 | 62536 | 60649 | 188032 | # # # | # # # | # # # | # # # | 0.907 | 0.919 | 0.898 | 0.908 | # # # | # # # | # # # | - - - | 0.921 | 0.933 | 0.915 | 0.923 | - - - | 0.414 | 1.9 | 1.87 | 1.95 | 1.81 | 1.87 | 1.95 | 18.71 | 18.97 | 20.73 | 0 | - - - | - - - | - - - | - - - | 64847 | 62536 | 60649 | 188032 | Over-range | 27276 | 24678 | 26733 | 78783 | 11387 | 11201 | 11801 | 34633 | 58736 | 57244 | 54339 | 170319 | 58736 | 57244 | 54339 | 170319 | - - - | - - - | - - - | - - -
5/7/2026 | 8:30:00 AM | 281.28 | 278.85 | 278.64 | 487.32 | 481 | 484.45 | 230.1113 | 224.2224 | 216.6133 | 7.0119 | 1.444 | 1.443 | 1.44 | 1.578 | 1.549 | 1.671 | Over-range | 60.01 | 58685 | 57483 | 54192 | 170359 | - - - | - - - | - - - | - - - | 58685 | 57483 | 54192 | 170359 | 24838 | 21911 | 23848 | 70597 | - - - | - - - | - - - | - - - | 24838 | 21911 | 23848 | 70597 | 64726 | 62525 | 60356 | 187607 | # # # | # # # | # # # | # # # | 0.907 | 0.919 | 0.898 | 0.908 | # # # | # # # | # # # | - - - | 0.921 | 0.934 | 0.915 | 0.923 | - - - | 0.414 | 1.94 | 1.87 | 1.92 | 1.83 | 1.86 | 1.96 | 18.66 | 18.94 | 20.69 | 0 | - - - | - - - | - - - | - - - | 64726 | 62525 | 60356 | 187607 | Over-range | 27305 | 24599 | 26572 | 78575 | 11340 | 11180 | 11719 | 34496 | 58592 | 57269 | 54091 | 169952 | 58592 | 57269 | 54091 | 169952 | - - - | - - - | - - - | - - -
5/7/2026 | 8:45:00 AM | 282.1 | 279.51 | 279.32 | 488.63 | 482.07 | 485.79 | 229.2974 | 222.8491 | 215.5438 | 6.9813 | 1.444 | 1.443 | 1.44 | 1.579 | 1.553 | 1.678 | Over-range | 60.02 | 58600 | 57218 | 53954 | 169773 | - - - | - - - | - - - | - - - | 58600 | 57218 | 53954 | 169773 | 24930 | 21960 | 23970 | 70860 | - - - | - - - | - - - | - - - | 24930 | 21960 | 23970 | 70860 | 64683 | 62289 | 60204 | 187176 | # # # | # # # | # # # | # # # | 0.906 | 0.919 | 0.896 | 0.907 | # # # | # # # | # # # | - - - | 0.92 | 0.933 | 0.914 | 0.922 | - - - | 0.417 | 1.94 | 1.87 | 1.92 | 1.82 | 1.87 | 1.95 | 18.72 | 19 | 20.81 | 0 | - - - | - - - | - - - | - - - | 64683 | 62289 | 60204 | 187176 | Over-range | 27385 | 24616 | 26711 | 78817 | 11334 | 11122 | 11786 | 34512 | 58439 | 57063 | 53845 | 169346 | 58439 | 57063 | 53845 | 169346 | - - - | - - - | - - - | - - -
5/7/2026 | 9:00:00 AM | 281.85 | 279.25 | 279.03 | 488.21 | 481.58 | 485.33 | 228.6256 | 222.5025 | 215.0298 | 6.796 | 1.443 | 1.443 | 1.44 | 1.578 | 1.552 | 1.674 | Over-range | 60.02 | 58367 | 57068 | 53818 | 169252 | - - - | - - - | - - - | - - - | 58367 | 57068 | 53818 | 169252 | 24862 | 22013 | 23793 | 70668 | - - - | - - - | - - - | - - - | 24862 | 22013 | 23793 | 70668 | 64438 | 62133 | 59999 | 186570 | # # # | # # # | # # # | # # # | 0.906 | 0.919 | 0.897 | 0.907 | # # # | # # # | # # # | - - - | 0.919 | 0.933 | 0.914 | 0.922 | - - - | 0.418 | 1.94 | 1.86 | 1.94 | 1.84 | 1.87 | 1.96 | 18.7 | 18.85 | 20.68 | 0 | - - - | - - - | - - - | - - - | 64438 | 62133 | 59999 | 186570 | Over-range | 27304 | 24573 | 26525 | 78500 | 11287 | 10921 | 11723 | 34178 | 58106 | 56980 | 53740 | 168825 | 58106 | 56980 | 53740 | 168825 | - - - | - - - | - - - | - - -
5/7/2026 | 9:15:00 AM | 281.42 | 278.85 | 278.67 | 487.45 | 480.94 | 484.66 | 228.8073 | 222.9459 | 215.3326 | 6.8821 | 1.443 | 1.443 | 1.44 | 1.581 | 1.554 | 1.673 | Over-range | 59.99 | 58322 | 57097 | 53845 | 169265 | - - - | - - - | - - - | - - - | 58322 | 57097 | 53845 | 169265 | 24837 | 21973 | 23731 | 70541 | - - - | - - - | - - - | - - - | 24837 | 21973 | 23731 | 70541 | 64391 | 62167 | 60006 | 186564 | # # # | # # # | # # # | # # # | 0.906 | 0.918 | 0.897 | 0.907 | # # # | # # # | # # # | - - - | 0.92 | 0.933 | 0.915 | 0.923 | - - - | 0.417 | 1.92 | 1.86 | 1.93 | 1.82 | 1.86 | 1.94 | 18.79 | 18.96 | 20.74 | 0 | - - - | - - - | - - - | - - - | 64391 | 62167 | 60006 | 186564 | Over-range | 27289 | 24589 | 26484 | 78457 | 11304 | 11037 | 11758 | 34343 | 58106 | 57017 | 53718 | 168840 | 58106 | 57017 | 53718 | 168840 | - - - | - - - | - - - | - - -
5/7/2026 | 9:30:00 AM | 281.15 | 278.32 | 278.3 | 486.75 | 480.08 | 484.21 | 229.5125 | 222.6789 | 215.9471 | 6.9735 | 1.443 | 1.443 | 1.44 | 1.575 | 1.556 | 1.678 | Over-range | 60 | 58518 | 56946 | 53876 | 169340 | - - - | - - - | - - - | - - - | 58518 | 56946 | 53876 | 169340 | 24731 | 21834 | 23836 | 70402 | - - - | - - - | - - - | - - - | 24731 | 21834 | 23836 | 70402 | 64526 | 61977 | 60098 | 186600 | # # # | # # # | # # # | # # # | 0.907 | 0.919 | 0.897 | 0.908 | # # # | # # # | # # # | - - - | 0.921 | 0.934 | 0.914 | 0.923 | - - - | 0.416 | 1.9 | 1.86 | 1.93 | 1.8 | 1.87 | 1.93 | 18.79 | 19.02 | 20.88 | 0 | - - - | - - - | - - - | - - - | 64526 | 61977 | 60098 | 186600 | Over-range | 27190 | 24459 | 26628 | 78381 | 11297 | 11024 | 11869 | 34455 | 58288 | 56890 | 53734 | 168912 | 58288 | 56890 | 53734 | 168912 | - - - | - - - | - - - | - - -
5/7/2026 | 9:45:00 AM | 281.09 | 278.32 | 278.19 | 486.75 | 479.98 | 484.03 | 229.9684 | 222.6158 | 215.0538 | 7.1044 | 1.443 | 1.443 | 1.44 | 1.576 | 1.55 | 1.684 | Over-range | 60 | 58606 | 56978 | 53572 | 169156 | - - - | - - - | - - - | - - - | 58606 | 56978 | 53572 | 169156 | 24804 | 21656 | 23879 | 70339 | - - - | - - - | - - - | - - - | 24804 | 21656 | 23879 | 70339 | 64642 | 61959 | 59826 | 186428 | # # # | # # # | # # # | # # # | 0.907 | 0.92 | 0.896 | 0.907 | # # # | # # # | # # # | - - - | 0.921 | 0.934 | 0.913 | 0.923 | - - - | 0.416 | 1.89 | 1.86 | 1.92 | 1.8 | 1.86 | 1.92 | 18.75 | 19.08 | 21.02 | 0 | - - - | - - - | - - - | - - - | 64642 | 61959 | 59826 | 186428 | Over-range | 27275 | 24340 | 26632 | 78368 | 11343 | 11110 | 11794 | 34554 | 58462 | 56783 | 53482 | 168727 | 58462 | 56783 | 53482 | 168727 | - - - | - - - | - - - | - - -
5/7/2026 | 10:00:00 AM | 280.9 | 278.12 | 278.05 | 486.37 | 479.7 | 483.75 | 230.6032 | 223.2172 | 215.6564 | 7.2418 | 1.443 | 1.442 | 1.44 | 1.575 | 1.552 | 1.684 | Over-range | 60 | 58756 | 57104 | 53699 | 169559 | - - - | - - - | - - - | - - - | 58756 | 57104 | 53699 | 169559 | 24764 | 21632 | 23896 | 70292 | - - - | - - - | - - - | - - - | 24764 | 21632 | 23896 | 70292 | 64775 | 62082 | 59963 | 186820 | # # # | # # # | # # # | # # # | 0.907 | 0.92 | 0.896 | 0.908 | # # # | # # # | # # # | - - - | 0.921 | 0.935 | 0.913 | 0.923 | - - - | 0.415 | 1.88 | 1.85 | 1.91 | 1.79 | 1.85 | 1.92 | 18.79 | 19.18 | 21.13 | 0 | - - - | - - - | - - - | - - - | 64775 | 62082 | 59963 | 186820 | Over-range | 27267 | 24357 | 26683 | 78431 | 11413 | 11195 | 11873 | 34791 | 58611 | 56898 | 53621 | 169129 | 58611 | 56898 | 53621 | 169129 | - - - | - - - | - - - | - - -
5/7/2026 | 10:15:00 AM | 280.78 | 278.03 | 277.87 | 486.22 | 479.46 | 483.47 | 231.5901 | 223.9592 | 215.6918 | 7.5497 | 1.442 | 1.442 | 1.44 | 1.578 | 1.549 | 1.687 | Over-range | 60.01 | 58968 | 57350 | 53643 | 169962 | - - - | - - - | - - - | - - - | 58968 | 57350 | 53643 | 169962 | 24882 | 21483 | 23898 | 70263 | - - - | - - - | - - - | - - - | 24882 | 21483 | 23898 | 70263 | 65024 | 62267 | 59935 | 187226 | # # # | # # # | # # # | # # # | 0.907 | 0.921 | 0.895 | 0.908 | # # # | # # # | # # # | - - - | 0.921 | 0.936 | 0.913 | 0.924 | - - - | 0.413 | 1.87 | 1.84 | 1.92 | 1.78 | 1.85 | 1.91 | 18.84 | 19.26 | 21.22 | 0 | - - - | - - - | - - - | - - - | 65024 | 62267 | 59935 | 187226 | Over-range | 27402 | 24250 | 26732 | 78526 | 11479 | 11247 | 11977 | 35063 | 58752 | 57230 | 53553 | 169535 | 58752 | 57230 | 53553 | 169535 | - - - | - - - | - - - | - - -
5/7/2026 | 10:30:00 AM | 280.78 | 277.92 | 277.89 | 486.1 | 479.35 | 483.55 | 232.6027 | 224.2721 | 216.5098 | 7.6129 | 1.441 | 1.442 | 1.439 | 1.576 | 1.551 | 1.691 | Over-range | 60 | 59270 | 57416 | 53804 | 170490 | - - - | - - - | - - - | - - - | 59270 | 57416 | 53804 | 170490 | 24919 | 21399 | 24012 | 70329 | - - - | - - - | - - - | - - - | 24919 | 21399 | 24012 | 70329 | 65310 | 62330 | 60166 | 187806 | # # # | # # # | # # # | # # # | 0.908 | 0.921 | 0.894 | 0.908 | # # # | # # # | # # # | - - - | 0.922 | 0.937 | 0.913 | 0.924 | - - - | 0.412 | 1.86 | 1.84 | 1.91 | 1.77 | 1.86 | 1.9 | 18.92 | 19.41 | 21.41 | 0 | - - - | - - - | - - - | - - - | 65310 | 62330 | 60166 | 187806 | Over-range | 27430 | 24258 | 26926 | 78766 | 11467 | 11426 | 12183 | 35466 | 59145 | 57338 | 53585 | 170068 | 59145 | 57338 | 53585 | 170068 | - - - | - - - | - - - | - - -
5/7/2026 | 10:45:00 AM | 280.51 | 277.78 | 277.72 | 485.72 | 479.14 | 483.13 | 232.8095 | 224.7497 | 216.6279 | 7.6376 | 1.442 | 1.442 | 1.439 | 1.576 | 1.548 | 1.688 | Over-range | 60 | 59282 | 57534 | 53843 | 170659 | - - - | - - - | - - - | - - - | 59282 | 57534 | 53843 | 170659 | 24845 | 21425 | 23954 | 70224 | - - - | - - - | - - - | - - - | 24845 | 21425 | 23954 | 70224 | 65306 | 62430 | 60162 | 187898 | # # # | # # # | # # # | # # # | 0.908 | 0.922 | 0.895 | 0.908 | # # # | # # # | # # # | - - - | 0.922 | 0.937 | 0.913 | 0.924 | - - - | 0.411 | 1.86 | 1.84 | 1.92 | 1.78 | 1.85 | 1.91 | 18.83 | 19.35 | 21.29 | 0 | - - - | - - - | - - - | - - - | 65306 | 62430 | 60162 | 187898 | Over-range | 27396 | 24237 | 26839 | 78621 | 11543 | 11332 | 12103 | 35353 | 59041 | 57443 | 53762 | 170245 | 59041 | 57443 | 53762 | 170245 | - - - | - - - | - - - | - - -
5/7/2026 | 11:00:00 AM | 280.54 | 277.85 | 277.77 | 485.81 | 479.26 | 483.18 | 234.6044 | 225.7258 | 217.021 | 7.5279 | 1.442 | 1.442 | 1.44 | 1.573 | 1.543 | 1.69 | Over-range | 60 | 59798 | 57869 | 53952 | 171619 | - - - | - - - | - - - | - - - | 59798 | 57869 | 53952 | 171619 | 24979 | 21311 | 23943 | 70233 | - - - | - - - | - - - | - - - | 24979 | 21311 | 23943 | 70233 | 65816 | 62717 | 60281 | 188815 | # # # | # # # | # # # | # # # | 0.909 | 0.923 | 0.895 | 0.909 | # # # | # # # | # # # | - - - | 0.922 | 0.938 | 0.914 | 0.925 | - - - | 0.409 | 1.9 | 1.88 | 1.97 | 1.81 | 1.9 | 1.95 | 18.72 | 19.34 | 21.38 | 0 | - - - | - - - | - - - | - - - | 65816 | 62717 | 60281 | 188815 | Over-range | 27495 | 24179 | 26888 | 78726 | 11491 | 11422 | 12234 | 35569 | 59574 | 57846 | 53791 | 171210 | 59574 | 57846 | 53791 | 171210 | - - - | - - - | - - - | - - -
5/7/2026 | 11:15:00 AM | 280.85 | 278.13 | 278.18 | 486.25 | 479.89 | 483.85 | 237.5997 | 226.9971 | 219.1403 | 7.1904 | 1.442 | 1.442 | 1.44 | 1.568 | 1.543 | 1.696 | Over-range | 60.01 | 60709 | 58299 | 54493 | 173501 | - - - | - - - | - - - | - - - | 60709 | 58299 | 54493 | 173501 | 25112 | 21225 | 24280 | 70617 | - - - | - - - | - - - | - - - | 25112 | 21225 | 24280 | 70617 | 66728 | 63134 | 60960 | 190821 | # # # | # # # | # # # | # # # | 0.91 | 0.923 | 0.894 | 0.909 | # # # | # # # | # # # | - - - | 0.924 | 0.94 | 0.913 | 0.926 | - - - | 0.407 | 1.91 | 1.91 | 2.02 | 1.84 | 1.93 | 1.99 | 18.72 | 19.61 | 21.67 | 0 | - - - | - - - | - - - | - - - | 66728 | 63134 | 60960 | 190821 | Over-range | 27696 | 24229 | 27324 | 79436 | 11680 | 11684 | 12533 | 36376 | 60474 | 58266 | 54355 | 173094 | 60474 | 58266 | 54355 | 173094 | - - - | - - - | - - - | - - -
5/7/2026 | 11:30:00 AM | 281.24 | 278.51 | 278.58 | 486.91 | 480.56 | 484.54 | 240.1129 | 228.4635 | 220.791 | 7.2427 | 1.442 | 1.442 | 1.439 | 1.569 | 1.544 | 1.701 | Over-range | 60 | 61468 | 58773 | 54910 | 175151 | - - - | - - - | - - - | - - - | 61468 | 58773 | 54910 | 175151 | 25338 | 21181 | 24595 | 71114 | - - - | - - - | - - - | - - - | 25338 | 21181 | 24595 | 71114 | 67529 | 63629 | 61507 | 192665 | # # # | # # # | # # # | # # # | 0.91 | 0.924 | 0.893 | 0.909 | # # # | # # # | # # # | - - - | 0.924 | 0.941 | 0.912 | 0.926 | - - - | 0.406 | 1.93 | 1.9 | 2.02 | 1.84 | 1.94 | 1.99 | 18.84 | 20.02 | 21.93 | 0 | - - - | - - - | - - - | - - - | 67529 | 63629 | 61507 | 192665 | Over-range | 27962 | 24379 | 27713 | 80262 | 11827 | 12071 | 12771 | 37212 | 61320 | 58721 | 54686 | 174728 | 61320 | 58721 | 54686 | 174728 | - - - | - - - | - - - | - - -
5/7/2026 | 11:45:00 AM | 281.71 | 279.03 | 279.15 | 487.73 | 481.55 | 485.44 | 240.416 | 228.8885 | 222.1832 | 7.344 | 1.442 | 1.442 | 1.44 | 1.567 | 1.552 | 1.7 | Over-range | 60 | 61700 | 58937 | 55372 | 176009 | - - - | - - - | - - - | - - - | 61700 | 58937 | 55372 | 176009 | 25271 | 21378 | 24799 | 71448 | - - - | - - - | - - - | - - - | 25271 | 21378 | 24799 | 71448 | 67728 | 63867 | 62021 | 193615 | # # # | # # # | # # # | # # # | 0.911 | 0.923 | 0.893 | 0.909 | # # # | # # # | # # # | - - - | 0.925 | 0.94 | 0.912 | 0.926 | - - - | 0.406 | 1.95 | 1.94 | 2.02 | 1.86 | 1.96 | 2.01 | 18.89 | 20.15 | 21.93 | 0 | - - - | - - - | - - - | - - - | 67728 | 63867 | 62021 | 193615 | Over-range | 27930 | 24605 | 27938 | 80671 | 11893 | 12182 | 12866 | 37455 | 61552 | 58879 | 55143 | 175574 | 61552 | 58879 | 55143 | 175574 | - - - | - - - | - - - | - - -
5/7/2026 | 12:00:00 PM | 281.66 | 278.99 | 279.06 | 487.67 | 481.44 | 485.29 | 240.8876 | 228.8355 | 222.1114 | 7.1762 | 1.442 | 1.442 | 1.44 | 1.566 | 1.548 | 1.702 | Over-range | 60 | 61821 | 58947 | 55325 | 176093 | - - - | - - - | - - - | - - - | 61821 | 58947 | 55325 | 176093 | 25256 | 21278 | 24850 | 71384 | - - - | - - - | - - - | - - - | 25256 | 21278 | 24850 | 71384 | 67846 | 63842 | 61982 | 193670 | # # # | # # # | # # # | # # # | 0.911 | 0.923 | 0.893 | 0.909 | # # # | # # # | # # # | - - - | 0.925 | 0.94 | 0.912 | 0.926 | - - - | 0.405 | 1.96 | 1.94 | 2 | 1.86 | 1.96 | 2 | 18.84 | 20.15 | 21.92 | 0 | - - - | - - - | - - - | - - - | 67846 | 63842 | 61982 | 193670 | Over-range | 27950 | 24517 | 27945 | 80619 | 11972 | 12177 | 12782 | 37464 | 61690 | 58780 | 55192 | 175662 | 61690 | 58780 | 55192 | 175662 | - - - | - - - | - - - | - - -
5/7/2026 | 12:15:00 PM | 281.29 | 278.59 | 278.67 | 487.01 | 480.73 | 484.66 | 239.1212 | 227.6837 | 220.457 | 7.5345 | 1.442 | 1.442 | 1.44 | 1.569 | 1.546 | 1.703 | Over-range | 60.02 | 61226 | 58566 | 54801 | 174593 | - - - | - - - | - - - | - - - | 61226 | 58566 | 54801 | 174593 | 25158 | 21208 | 24693 | 71060 | - - - | - - - | - - - | - - - | 25158 | 21208 | 24693 | 71060 | 67263 | 63430 | 61435 | 192128 | # # # | # # # | # # # | # # # | 0.91 | 0.923 | 0.892 | 0.909 | # # # | # # # | # # # | - - - | 0.924 | 0.94 | 0.912 | 0.925 | - - - | 0.407 | 1.96 | 1.95 | 2.04 | 1.87 | 1.98 | 2.02 | 18.89 | 20.06 | 21.94 | 0 | - - - | - - - | - - - | - - - | 67263 | 63430 | 61435 | 192128 | Over-range | 27850 | 24360 | 27769 | 80190 | 11944 | 11985 | 12702 | 37160 | 61005 | 58430 | 54732 | 174167 | 61005 | 58430 | 54732 | 174167 | - - - | - - - | - - - | - - -
5/7/2026 | 12:30:00 PM | 281.24 | 278.56 | 278.6 | 486.95 | 480.64 | 484.54 | 237.4609 | 226.6927 | 218.9815 | 7.6569 | 1.442 | 1.442 | 1.44 | 1.571 | 1.544 | 1.701 | Over-range | 60.01 | 60727 | 58305 | 54424 | 173456 | - - - | - - - | - - - | - - - | 60727 | 58305 | 54424 | 173456 | 25159 | 21146 | 24582 | 70888 | - - - | - - - | - - - | - - - | 25159 | 21146 | 24582 | 70888 | 66784 | 63146 | 61008 | 190938 | # # # | # # # | # # # | # # # | 0.909 | 0.923 | 0.892 | 0.908 | # # # | # # # | # # # | - - - | 0.924 | 0.94 | 0.911 | 0.925 | - - - | 0.409 | 1.95 | 1.93 | 2.02 | 1.86 | 1.96 | 2 | 18.8 | 19.88 | 21.8 | 0 | - - - | - - - | - - - | - - - | 66784 | 63146 | 61008 | 190938 | Over-range | 27790 | 24247 | 27570 | 79815 | 11802 | 11864 | 12481 | 36678 | 60585 | 58097 | 54346 | 173028 | 60585 | 58097 | 54346 | 173028 | - - - | - - - | - - - | - - -
5/7/2026 | 12:45:00 PM | 281.25 | 278.48 | 278.59 | 486.89 | 480.53 | 484.57 | 235.8518 | 224.7683 | 217.3761 | 7.6005 | 1.442 | 1.442 | 1.44 | 1.571 | 1.545 | 1.704 | Over-range | 60 | 60283 | 57766 | 53950 | 171999 | - - - | - - - | - - - | - - - | 60283 | 57766 | 53950 | 171999 | 25137 | 21023 | 24526 | 70686 | - - - | - - - | - - - | - - - | 25137 | 21023 | 24526 | 70686 | 66333 | 62594 | 60557 | 189484 | # # # | # # # | # # # | # # # | 0.909 | 0.923 | 0.891 | 0.908 | # # # | # # # | # # # | - - - | 0.923 | 0.939 | 0.91 | 0.924 | - - - | 0.411 | 1.94 | 1.94 | 2.01 | 1.85 | 1.95 | 2 | 18.78 | 19.84 | 21.85 | 0 | - - - | - - - | - - - | - - - | 66333 | 62594 | 60557 | 189484 | Over-range | 27677 | 24106 | 27506 | 79502 | 11581 | 11795 | 12452 | 36387 | 60216 | 57622 | 53736 | 171574 | 60216 | 57622 | 53736 | 171574 | - - - | - - - | - - - | - - -
5/7/2026 | 1:00:00 PM | 281.03 | 278.24 | 278.41 | 486.45 | 480.17 | 484.26 | 234.8772 | 224.339 | 217.4429 | 7.6048 | 1.442 | 1.442 | 1.44 | 1.571 | 1.552 | 1.701 | Over-range | 60 | 59984 | 57548 | 53965 | 171497 | - - - | - - - | - - - | - - - | 59984 | 57548 | 53965 | 171497 | 25005 | 21157 | 24438 | 70600 | - - - | - - - | - - - | - - - | 25005 | 21157 | 24438 | 70600 | 66008 | 62419 | 60538 | 188964 | # # # | # # # | # # # | # # # | 0.909 | 0.922 | 0.891 | 0.908 | # # # | # # # | # # # | - - - | 0.923 | 0.938 | 0.91 | 0.924 | - - - | 0.412 | 1.91 | 1.9 | 1.99 | 1.82 | 1.93 | 1.97 | 18.86 | 19.79 | 21.79 | 0 | - - - | - - - | - - - | - - - | 66008 | 62419 | 60538 | 188964 | Over-range | 27549 | 24174 | 27434 | 79350 | 11562 | 11694 | 12465 | 36222 | 59861 | 57470 | 53742 | 171073 | 59861 | 57470 | 53742 | 171073 | - - - | - - - | - - - | - - -
5/7/2026 | 1:15:00 PM | 280.97 | 278.24 | 278.33 | 486.42 | 480.12 | 484.1 | 235.2713 | 224.8578 | 217.3318 | 7.5003 | 1.442 | 1.442 | 1.44 | 1.575 | 1.549 | 1.701 | Over-range | 60.01 | 60045 | 57691 | 53946 | 171682 | - - - | - - - | - - - | - - - | 60045 | 57691 | 53946 | 171682 | 25077 | 21159 | 24394 | 70629 | - - - | - - - | - - - | - - - | 25077 | 21159 | 24394 | 70629 | 66103 | 62564 | 60490 | 189157 | # # # | # # # | # # # | # # # | 0.908 | 0.922 | 0.892 | 0.908 | # # # | # # # | # # # | - - - | 0.923 | 0.939 | 0.911 | 0.924 | - - - | 0.411 | 1.89 | 1.91 | 2 | 1.82 | 1.93 | 1.97 | 18.89 | 19.82 | 21.79 | 0 | - - - | - - - | - - - | - - - | 66103 | 62564 | 60490 | 189157 | Over-range | 27643 | 24207 | 27366 | 79407 | 11630 | 11758 | 12404 | 36290 | 59964 | 57546 | 53747 | 171258 | 59964 | 57546 | 53747 | 171258 | - - - | - - - | - - - | - - -
5/7/2026 | 1:30:00 PM | 280.69 | 277.7 | 277.85 | 485.76 | 479.1 | 483.54 | 234.8601 | 223.8319 | 216.8539 | 7.7029 | 1.441 | 1.442 | 1.439 | 1.57 | 1.548 | 1.706 | Over-range | 60.01 | 59902 | 57347 | 53672 | 170921 | - - - | - - - | - - - | - - - | 59902 | 57347 | 53672 | 170921 | 24977 | 20964 | 24411 | 70352 | - - - | - - - | - - - | - - - | 24977 | 20964 | 24411 | 70352 | 65922 | 62158 | 60253 | 188334 | # # # | # # # | # # # | # # # | 0.909 | 0.923 | 0.891 | 0.908 | # # # | # # # | # # # | - - - | 0.923 | 0.939 | 0.91 | 0.924 | - - - | 0.412 | 1.85 | 1.88 | 1.98 | 1.79 | 1.91 | 1.94 | 18.85 | 19.72 | 21.84 | 0 | - - - | - - - | - - - | - - - | 65922 | 62158 | 60253 | 188334 | Over-range | 27522 | 23978 | 27382 | 79092 | 11559 | 11639 | 12404 | 36140 | 59822 | 57219 | 53466 | 170507 | 59822 | 57219 | 53466 | 170507 | - - - | - - - | - - - | - - -
5/7/2026 | 1:45:00 PM | 280.87 | 277.88 | 278.01 | 486.08 | 479.38 | 483.81 | 233.2572 | 222.8955 | 215.8908 | 7.7642 | 1.442 | 1.442 | 1.44 | 1.572 | 1.551 | 1.702 | Over-range | 60 | 59477 | 57098 | 53465 | 170041 | - - - | - - - | - - - | - - - | 59477 | 57098 | 53465 | 170041 | 24926 | 21053 | 24385 | 70364 | - - - | - - - | - - - | - - - | 24926 | 21053 | 24385 | 70364 | 65513 | 61938 | 60018 | 187469 | # # # | # # # | # # # | # # # | 0.908 | 0.922 | 0.891 | 0.907 | # # # | # # # | # # # | - - - | 0.922 | 0.938 | 0.909 | 0.923 | - - - | 0.414 | 1.88 | 1.85 | 1.95 | 1.78 | 1.89 | 1.93 | 18.84 | 19.65 | 21.68 | 0 | - - - | - - - | - - - | - - - | 65513 | 61938 | 60018 | 187469 | Over-range | 27466 | 24002 | 27271 | 78936 | 11536 | 11526 | 12208 | 35774 | 59397 | 56892 | 53329 | 169618 | 59397 | 56892 | 53329 | 169618 | - - - | - - - | - - - | - - -
5/7/2026 | 2:00:00 PM | 280.85 | 277.94 | 278.06 | 486.09 | 479.52 | 483.83 | 230.2334 | 221.4296 | 214.7083 | 7.6123 | 1.441 | 1.442 | 1.44 | 1.576 | 1.56 | 1.695 | Over-range | 60 | 58643 | 56611 | 53266 | 168521 | - - - | - - - | - - - | - - - | 58643 | 56611 | 53266 | 168521 | 24713 | 21335 | 24164 | 70212 | - - - | - - - | - - - | - - - | 24713 | 21335 | 24164 | 70212 | 64660 | 61542 | 59702 | 185904 | # # # | # # # | # # # | # # # | 0.907 | 0.92 | 0.892 | 0.907 | # # # | # # # | # # # | - - - | 0.921 | 0.935 | 0.91 | 0.922 | - - - | 0.417 | 1.85 | 1.83 | 1.88 | 1.75 | 1.84 | 1.89 | 18.89 | 19.5 | 21.39 | 0 | - - - | - - - | - - - | - - - | 64660 | 61542 | 59702 | 185904 | Over-range | 27237 | 24137 | 26963 | 78492 | 11450 | 11287 | 11963 | 35089 | 58502 | 56402 | 53188 | 168092 | 58502 | 56402 | 53188 | 168092 | - - - | - - - | - - - | - - -
5/7/2026 | 2:15:00 PM | 281.38 | 278.48 | 278.55 | 487.06 | 480.4 | 484.69 | 224.7457 | 217.3845 | 211.7044 | 6.8334 | 1.442 | 1.442 | 1.44 | 1.577 | 1.573 | 1.686 | Over-range | 60.01 | 57246 | 55483 | 52681 | 165411 | - - - | - - - | - - - | - - - | 57246 | 55483 | 52681 | 165411 | 24455 | 21642 | 23835 | 69932 | - - - | - - - | - - - | - - - | 24455 | 21642 | 23835 | 69932 | 63238 | 60536 | 58969 | 182743 | # # # | # # # | # # # | # # # | 0.905 | 0.917 | 0.893 | 0.905 | # # # | # # # | # # # | - - - | 0.919 | 0.931 | 0.911 | 0.92 | - - - | 0.423 | 1.86 | 1.8 | 1.87 | 1.75 | 1.81 | 1.88 | 18.87 | 19.13 | 20.91 | 0 | - - - | - - - | - - - | - - - | 63238 | 60536 | 58969 | 182743 | Over-range | 26868 | 24212 | 26495 | 77680 | 11127 | 10854 | 11569 | 33815 | 57109 | 55317 | 52552 | 164979 | 57109 | 55317 | 52552 | 164979 | - - - | - - - | - - - | - - -
5/7/2026 | 2:30:00 PM | 281.4 | 278.52 | 278.58 | 487.1 | 480.47 | 484.73 | 224.9046 | 217.3123 | 211.3872 | 7.0807 | 1.442 | 1.442 | 1.44 | 1.576 | 1.57 | 1.689 | Over-range | 59.99 | 57280 | 55500 | 52553 | 165334 | - - - | - - - | - - - | - - - | 57280 | 55500 | 52553 | 165334 | 24533 | 21590 | 23861 | 69984 | - - - | - - - | - - - | - - - | 24533 | 21590 | 23861 | 69984 | 63288 | 60525 | 58888 | 182701 | # # # | # # # | # # # | # # # | 0.905 | 0.917 | 0.892 | 0.905 | # # # | # # # | # # # | - - - | 0.919 | 0.932 | 0.91 | 0.92 | - - - | 0.423 | 1.85 | 1.8 | 1.88 | 1.75 | 1.81 | 1.87 | 18.83 | 19.11 | 20.99 | 0 | - - - | - - - | - - - | - - - | 63288 | 60525 | 58888 | 182701 | Over-range | 26915 | 24144 | 26570 | 77746 | 11071 | 10806 | 11687 | 33862 | 57056 | 55461 | 52385 | 164902 | 57056 | 55461 | 52385 | 164902 | - - - | - - - | - - - | - - -
5/7/2026 | 2:45:00 PM | 281.28 | 278.4 | 278.55 | 486.84 | 480.36 | 484.62 | 224.3349 | 216.7912 | 211.4606 | 6.7184 | 1.442 | 1.442 | 1.44 | 1.575 | 1.576 | 1.687 | Over-range | 60 | 57131 | 55294 | 52600 | 165026 | - - - | - - - | - - - | - - - | 57131 | 55294 | 52600 | 165026 | 24395 | 21624 | 23833 | 69852 | - - - | - - - | - - - | - - - | 24395 | 21624 | 23833 | 69852 | 63100 | 60354 | 58901 | 182355 | # # # | # # # | # # # | # # # | 0.905 | 0.916 | 0.893 | 0.905 | # # # | # # # | # # # | - - - | 0.919 | 0.931 | 0.91 | 0.92 | - - - | 0.423 | 1.83 | 1.78 | 1.87 | 1.74 | 1.8 | 1.86 | 18.84 | 19.16 | 20.96 | 0 | - - - | - - - | - - - | - - - | 63100 | 60354 | 58901 | 182355 | Over-range | 26790 | 24189 | 26505 | 77588 | 11073 | 10838 | 11597 | 33773 | 56982 | 55153 | 52459 | 164595 | 56982 | 55153 | 52459 | 164595 | - - - | - - - | - - - | - - -
5/7/2026 | 3:00:00 PM | 281.44 | 278.49 | 278.57 | 487.11 | 480.41 | 484.78 | 219.6755 | 212.7554 | 208.2117 | 5.4395 | 1.442 | 1.441 | 1.439 | 1.579 | 1.583 | 1.681 | Over-range | 60 | 55875 | 54162 | 51892 | 161930 | - - - | - - - | - - - | - - - | 55875 | 54162 | 51892 | 161930 | 24142 | 21650 | 23375 | 69168 | - - - | - - - | - - - | - - - | 24142 | 21650 | 23375 | 69168 | 61823 | 59247 | 58001 | 179071 | # # # | # # # | # # # | # # # | 0.904 | 0.914 | 0.895 | 0.904 | # # # | # # # | # # # | - - - | 0.918 | 0.928 | 0.911 | 0.919 | - - - | 0.427 | 1.77 | 1.72 | 1.79 | 1.68 | 1.73 | 1.79 | 18.8 | 18.8 | 20.53 | 0 | - - - | - - - | - - - | - - - | 61823 | 59247 | 58001 | 179071 | Over-range | 26457 | 24014 | 25909 | 76453 | 10822 | 10388 | 11174 | 32567 | 55715 | 54024 | 51759 | 161497 | 55715 | 54024 | 51759 | 161497 | - - - | - - - | - - - | - - -
5/7/2026 | 3:15:00 PM | 281.36 | 278.41 | 278.47 | 487 | 480.24 | 484.61 | 218.2153 | 211.4922 | 206.7442 | 5.5281 | 1.442 | 1.442 | 1.44 | 1.58 | 1.583 | 1.682 | Over-range | 60.01 | 55447 | 53796 | 51477 | 160720 | - - - | - - - | - - - | - - - | 55447 | 53796 | 51477 | 160720 | 24091 | 21637 | 23299 | 69027 | - - - | - - - | - - - | - - - | 24091 | 21637 | 23299 | 69027 | 61397 | 58881 | 57571 | 177849 | # # # | # # # | # # # | # # # | 0.903 | 0.914 | 0.894 | 0.904 | # # # | # # # | # # # | - - - | 0.917 | 0.927 | 0.911 | 0.918 | - - - | 0.43 | 1.78 | 1.73 | 1.79 | 1.69 | 1.73 | 1.8 | 18.75 | 18.64 | 20.4 | 0 | - - - | - - - | - - - | - - - | 61397 | 58881 | 57571 | 177849 | Over-range | 26367 | 23938 | 25779 | 76155 | 10718 | 10238 | 11030 | 32167 | 55297 | 53659 | 51340 | 160296 | 55297 | 53659 | 51340 | 160296 | - - - | - - - | - - - | - - -
5/7/2026 | 3:30:00 PM | 281.31 | 278.43 | 278.41 | 486.99 | 480.22 | 484.48 | 219.881 | 213.2612 | 207.5795 | 6.366 | 1.443 | 1.442 | 1.441 | 1.581 | 1.577 | 1.683 | Over-range | 60 | 55846 | 54287 | 51599 | 161732 | - - - | - - - | - - - | - - - | 55846 | 54287 | 51599 | 161732 | 24288 | 21674 | 23501 | 69463 | - - - | - - - | - - - | - - - | 24288 | 21674 | 23501 | 69463 | 61853 | 59376 | 57792 | 179022 | # # # | # # # | # # # | # # # | 0.903 | 0.914 | 0.893 | 0.903 | # # # | # # # | # # # | - - - | 0.917 | 0.928 | 0.91 | 0.918 | - - - | 0.43 | 1.84 | 1.8 | 1.87 | 1.75 | 1.8 | 1.87 | 18.75 | 18.79 | 20.58 | 0 | - - - | - - - | - - - | - - - | 61853 | 59376 | 57792 | 179022 | Over-range | 26591 | 24050 | 26029 | 76756 | 10824 | 10422 | 11188 | 32654 | 55670 | 54165 | 51476 | 161311 | 55670 | 54165 | 51476 | 161311 | - - - | - - - | - - - | - - -
5/7/2026 | 3:45:00 PM | 281.56 | 278.69 | 278.69 | 487.42 | 480.7 | 484.93 | 219.3612 | 212.7388 | 207.1021 | 6.3106 | 1.443 | 1.442 | 1.441 | 1.582 | 1.581 | 1.686 | Over-range | 60.02 | 55723 | 54167 | 51485 | 161374 | - - - | - - - | - - - | - - - | 55723 | 54167 | 51485 | 161374 | 24333 | 21694 | 23537 | 69563 | - - - | - - - | - - - | - - - | 24333 | 21694 | 23537 | 69563 | 61762 | 59287 | 57716 | 178765 | # # # | # # # | # # # | # # # | 0.902 | 0.914 | 0.892 | 0.903 | # # # | # # # | # # # | - - - | 0.916 | 0.928 | 0.909 | 0.918 | - - - | 0.431 | 1.84 | 1.79 | 1.86 | 1.74 | 1.79 | 1.87 | 18.83 | 18.91 | 20.72 | 0 | - - - | - - - | - - - | - - - | 61762 | 59287 | 57716 | 178765 | Over-range | 26637 | 24102 | 26086 | 76911 | 10836 | 10500 | 11246 | 32804 | 55579 | 54033 | 51343 | 160955 | 55579 | 54033 | 51343 | 160955 | - - - | - - - | - - - | - - -
5/7/2026 | 4:00:00 PM | 281.48 | 278.55 | 278.62 | 487.21 | 480.51 | 484.84 | 217.8955 | 211.0812 | 206.3586 | 5.643 | 1.443 | 1.442 | 1.44 | 1.582 | 1.588 | 1.687 | Over-range | 60.02 | 55329 | 53651 | 51307 | 160288 | - - - | - - - | - - - | - - - | 55329 | 53651 | 51307 | 160288 | 24145 | 21686 | 23401 | 69232 | - - - | - - - | - - - | - - - | 24145 | 21686 | 23401 | 69232 | 61332 | 58797 | 57495 | 177624 | # # # | # # # | # # # | # # # | 0.902 | 0.913 | 0.892 | 0.902 | # # # | # # # | # # # | - - - | 0.916 | 0.927 | 0.909 | 0.917 | - - - | 0.432 | 1.79 | 1.75 | 1.81 | 1.7 | 1.75 | 1.82 | 18.95 | 18.95 | 20.75 | 0 | - - - | - - - | - - - | - - - | 61332 | 58797 | 57495 | 177624 | Over-range | 26464 | 24055 | 25946 | 76539 | 10833 | 10409 | 11206 | 32636 | 55174 | 53512 | 51177 | 159863 | 55174 | 53512 | 51177 | 159863 | - - - | - - - | - - - | - - -
5/7/2026 | 4:15:00 PM | 281.8 | 278.99 | 278.98 | 487.88 | 481.25 | 485.37 | 213.9943 | 207.7062 | 202.7318 | 5.2597 | 1.444 | 1.442 | 1.44 | 1.586 | 1.583 | 1.681 | Over-range | 60.02 | 54297 | 52833 | 50480 | 157610 | - - - | - - - | - - - | - - - | 54297 | 52833 | 50480 | 157610 | 24074 | 21618 | 23162 | 68855 | - - - | - - - | - - - | - - - | 24074 | 21618 | 23162 | 68855 | 60302 | 57947 | 56556 | 174806 | # # # | # # # | # # # | # # # | 0.9 | 0.912 | 0.893 | 0.902 | # # # | # # # | # # # | - - - | 0.914 | 0.925 | 0.908 | 0.916 | - - - | 0.437 | 1.81 | 1.75 | 1.81 | 1.71 | 1.74 | 1.82 | 18.57 | 18.44 | 20.13 | 0 | - - - | - - - | - - - | - - - | 60302 | 57947 | 56556 | 174806 | Over-range | 26234 | 23801 | 25504 | 75605 | 10422 | 9955 | 10674 | 31226 | 54148 | 52689 | 50349 | 157186 | 54148 | 52689 | 50349 | 157186 | - - - | - - - | - - - | - - -
5/7/2026 | 4:30:00 PM | 281.66 | 278.86 | 278.91 | 487.6 | 481.1 | 485.22 | 212.7784 | 206.6238 | 201.9864 | 5.2188 | 1.444 | 1.442 | 1.44 | 1.586 | 1.586 | 1.679 | Over-range | 60 | 53968 | 52499 | 50286 | 156753 | - - - | - - - | - - - | - - - | 53968 | 52499 | 50286 | 156753 | 23935 | 21608 | 23103 | 68646 | - - - | - - - | - - - | - - - | 23935 | 21608 | 23103 | 68646 | 59931 | 57618 | 56336 | 173885 | # # # | # # # | # # # | # # # | 0.901 | 0.911 | 0.893 | 0.902 | # # # | # # # | # # # | - - - | 0.914 | 0.924 | 0.908 | 0.915 | - - - | 0.438 | 1.77 | 1.72 | 1.79 | 1.69 | 1.71 | 1.79 | 18.49 | 18.34 | 19.98 | 0 | - - - | - - - | - - - | - - - | 59931 | 57618 | 56336 | 173885 | Over-range | 26061 | 23741 | 25398 | 75262 | 10308 | 9833 | 10550 | 30853 | 53816 | 52358 | 50160 | 156334 | 53816 | 52358 | 50160 | 156334 | - - - | - - - | - - - | - - -
5/7/2026 | 4:45:00 PM | 281.9 | 279.1 | 279.12 | 488.04 | 481.48 | 485.58 | 213.8261 | 207.5528 | 202.708 | 5.3916 | 1.444 | 1.443 | 1.441 | 1.585 | 1.584 | 1.681 | Over-range | 60.01 | 54278 | 52792 | 50476 | 157546 | - - - | - - - | - - - | - - - | 54278 | 52792 | 50476 | 157546 | 24061 | 21670 | 23230 | 68961 | - - - | - - - | - - - | - - - | 24061 | 21670 | 23230 | 68961 | 60277 | 57928 | 56579 | 174785 | # # # | # # # | # # # | # # # | 0.901 | 0.911 | 0.892 | 0.901 | # # # | # # # | # # # | - - - | 0.914 | 0.925 | 0.908 | 0.916 | - - - | 0.438 | 1.81 | 1.76 | 1.82 | 1.72 | 1.75 | 1.83 | 18.57 | 18.44 | 20.12 | 0 | - - - | - - - | - - - | - - - | 60277 | 57928 | 56579 | 174785 | Over-range | 26215 | 23847 | 25562 | 75689 | 10406 | 9953 | 10665 | 31196 | 54143 | 52639 | 50337 | 157119 | 54143 | 52639 | 50337 | 157119 | - - - | - - - | - - - | - - -
5/7/2026 | 5:00:00 PM | 281.95 | 279.05 | 279.14 | 488.03 | 481.4 | 485.7 | 213.2726 | 206.5847 | 202.3775 | 5.2523 | 1.444 | 1.443 | 1.44 | 1.583 | 1.587 | 1.684 | Over-range | 60 | 54149 | 52516 | 50356 | 157021 | - - - | - - - | - - - | - - - | 54149 | 52516 | 50356 | 157021 | 24006 | 21603 | 23262 | 68871 | - - - | - - - | - - - | - - - | 24006 | 21603 | 23262 | 68871 | 60132 | 57646 | 56490 | 174268 | # # # | # # # | # # # | # # # | 0.901 | 0.911 | 0.891 | 0.901 | # # # | # # # | # # # | - - - | 0.914 | 0.924 | 0.907 | 0.915 | - - - | 0.439 | 1.79 | 1.73 | 1.79 | 1.69 | 1.72 | 1.8 | 18.57 | 18.48 | 20.21 | 0 | - - - | - - - | - - - | - - - | 60132 | 57646 | 56490 | 174268 | Over-range | 26148 | 23771 | 25602 | 75589 | 10364 | 9916 | 10692 | 31150 | 54005 | 52370 | 50218 | 156592 | 54005 | 52370 | 50218 | 156592 | - - - | - - - | - - - | - - -
5/7/2026 | 5:15:00 PM | 282.4 | 279.7 | 279.72 | 488.96 | 482.57 | 486.51 | 210.3888 | 204.6527 | 199.7722 | 5.1828 | 1.444 | 1.442 | 1.44 | 1.59 | 1.587 | 1.678 | Over-range | 60.01 | 53399 | 52091 | 49827 | 155318 | - - - | - - - | - - - | - - - | 53399 | 52091 | 49827 | 155318 | 24017 | 21670 | 23093 | 68780 | - - - | - - - | - - - | - - - | 24017 | 21670 | 23093 | 68780 | 59412 | 57240 | 55879 | 172531 | # # # | # # # | # # # | # # # | 0.899 | 0.91 | 0.892 | 0.9 | # # # | # # # | # # # | - - - | 0.912 | 0.923 | 0.907 | 0.914 | - - - | 0.443 | 1.74 | 1.69 | 1.73 | 1.66 | 1.67 | 1.75 | 18.34 | 18.22 | 19.77 | 0 | - - - | - - - | - - - | - - - | 59412 | 57240 | 55879 | 172531 | Over-range | 26044 | 23725 | 25292 | 75121 | 10073 | 9657 | 10314 | 30205 | 53241 | 51958 | 49679 | 154878 | 53241 | 51958 | 49679 | 154878 | - - - | - - - | - - - | - - -
5/7/2026 | 5:30:00 PM | 282.49 | 279.87 | 279.89 | 489.16 | 482.91 | 486.71 | 209.2593 | 203.6752 | 198.9179 | 5.1666 | 1.444 | 1.442 | 1.44 | 1.589 | 1.585 | 1.676 | Over-range | 60 | 53124 | 51847 | 49641 | 154613 | - - - | - - - | - - - | - - - | 53124 | 51847 | 49641 | 154613 | 23938 | 21685 | 23070 | 68693 | - - - | - - - | - - - | - - - | 23938 | 21685 | 23070 | 68693 | 59113 | 57001 | 55674 | 171788 | # # # | # # # | # # # | # # # | 0.899 | 0.91 | 0.892 | 0.9 | # # # | # # # | # # # | - - - | 0.911 | 0.922 | 0.906 | 0.913 | - - - | 0.444 | 1.75 | 1.68 | 1.72 | 1.66 | 1.66 | 1.75 | 18.2 | 18.05 | 19.56 | 0 | - - - | - - - | - - - | - - - | 59113 | 57001 | 55674 | 171788 | Over-range | 25927 | 23685 | 25206 | 74874 | 9958 | 9526 | 10153 | 29788 | 52967 | 51706 | 49504 | 154177 | 52967 | 51706 | 49504 | 154177 | - - - | - - - | - - - | - - -
5/7/2026 | 5:45:00 PM | 282.73 | 280.1 | 280.16 | 489.55 | 483.36 | 487.16 | 208.8077 | 203.1765 | 198.767 | 5.0938 | 1.444 | 1.442 | 1.44 | 1.588 | 1.588 | 1.675 | Over-range | 60 | 53042 | 51722 | 49628 | 154392 | - - - | - - - | - - - | - - - | 53042 | 51722 | 49628 | 154392 | 23935 | 21744 | 23129 | 68808 | - - - | - - - | - - - | - - - | 23935 | 21744 | 23129 | 68808 | 59035 | 56909 | 55686 | 171630 | # # # | # # # | # # # | # # # | 0.899 | 0.909 | 0.891 | 0.9 | # # # | # # # | # # # | - - - | 0.911 | 0.921 | 0.906 | 0.913 | - - - | 0.446 | 1.75 | 1.69 | 1.74 | 1.66 | 1.67 | 1.75 | 18.21 | 18.07 | 19.55 | 0 | - - - | - - - | - - - | - - - | 59035 | 56909 | 55686 | 171630 | Over-range | 25918 | 23737 | 25258 | 74967 | 9941 | 9520 | 10150 | 29757 | 52888 | 51585 | 49483 | 153956 | 52888 | 51585 | 49483 | 153956 | - - - | - - - | - - - | - - -
5/7/2026 | 6:00:00 PM | 282.79 | 280.23 | 280.23 | 489.73 | 483.55 | 487.25 | 207.6038 | 202.1429 | 197.4966 | 5.0434 | 1.444 | 1.442 | 1.44 | 1.592 | 1.588 | 1.676 | Over-range | 60 | 52680 | 51443 | 49283 | 153406 | - - - | - - - | - - - | - - - | 52680 | 51443 | 49283 | 153406 | 23959 | 21736 | 23079 | 68774 | - - - | - - - | - - - | - - - | 23959 | 21736 | 23079 | 68774 | 58708 | 56646 | 55344 | 170698 | # # # | # # # | # # # | # # # | 0.897 | 0.908 | 0.89 | 0.899 | # # # | # # # | # # # | - - - | 0.91 | 0.921 | 0.905 | 0.912 | - - - | 0.448 | 1.74 | 1.67 | 1.72 | 1.65 | 1.65 | 1.73 | 18.21 | 18.09 | 19.54 | 0 | - - - | - - - | - - - | - - - | 58708 | 56646 | 55344 | 170698 | Over-range | 25913 | 23713 | 25182 | 74861 | 9871 | 9476 | 10075 | 29568 | 52526 | 51308 | 49129 | 152963 | 52526 | 51308 | 49129 | 152963 | - - - | - - - | - - - | - - -
5/7/2026 | 6:15:00 PM | 283.42 | 280.86 | 280.9 | 490.81 | 484.68 | 488.38 | 207.3038 | 201.4535 | 197.5888 | 5.102 | 1.443 | 1.439 | 1.439 | 1.594 | 1.598 | 1.687 | Over-range | 60 | 52688 | 51277 | 49299 | 153264 | - - - | - - - | - - - | - - - | 52688 | 51277 | 49299 | 153264 | 23983 | 21885 | 23336 | 69204 | - - - | - - - | - - - | - - - | 23983 | 21885 | 23336 | 69204 | 58755 | 56580 | 55502 | 170837 | # # # | # # # | # # # | # # # | 0.897 | 0.906 | 0.888 | 0.897 | # # # | # # # | # # # | - - - | 0.91 | 0.919 | 0.903 | 0.911 | - - - | 0.452 | 1.63 | 1.58 | 1.6 | 1.55 | 1.55 | 1.61 | 18.61 | 18.53 | 19.99 | 0 | - - - | - - - | - - - | - - - | 58755 | 56580 | 55502 | 170837 | Over-range | 26002 | 23916 | 25496 | 75467 | 10046 | 9644 | 10271 | 30103 | 52520 | 51122 | 49137 | 152779 | 52520 | 51122 | 49137 | 152779 | - - - | - - - | - - - | - - -
5/7/2026 | 6:30:00 PM | 283.65 | 281.25 | 281.12 | 491.38 | 485.26 | 488.67 | 206.7841 | 201.3917 | 196.7106 | 5.0747 | 1.442 | 1.439 | 1.438 | 1.601 | 1.594 | 1.686 | Over-range | 59.99 | 52521 | 51327 | 49122 | 152971 | - - - | - - - | - - - | - - - | 52521 | 51327 | 49122 | 152971 | 24103 | 21921 | 23262 | 69286 | - - - | - - - | - - - | - - - | 24103 | 21921 | 23262 | 69286 | 58653 | 56640 | 55299 | 170593 | # # # | # # # | # # # | # # # | 0.895 | 0.906 | 0.888 | 0.897 | # # # | # # # | # # # | - - - | 0.908 | 0.919 | 0.903 | 0.91 | - - - | 0.453 | 1.61 | 1.56 | 1.59 | 1.54 | 1.53 | 1.6 | 18.63 | 18.51 | 19.92 | 0 | - - - | - - - | - - - | - - - | 58653 | 56640 | 55299 | 170593 | Over-range | 26111 | 23951 | 25396 | 75510 | 10041 | 9648 | 10189 | 30020 | 52357 | 51166 | 48965 | 152489 | 52357 | 51166 | 48965 | 152489 | - - - | - - - | - - - | - - -
5/7/2026 | 6:45:00 PM | 283.74 | 281.37 | 281.3 | 491.53 | 485.55 | 488.92 | 206.3699 | 201.2577 | 196.7404 | 5.1051 | 1.442 | 1.438 | 1.438 | 1.603 | 1.6 | 1.686 | Over-range | 60 | 52423 | 51271 | 49158 | 152853 | - - - | - - - | - - - | - - - | 52423 | 51271 | 49158 | 152853 | 24075 | 22004 | 23277 | 69356 | - - - | - - - | - - - | - - - | 24075 | 22004 | 23277 | 69356 | 58556 | 56627 | 55342 | 170525 | # # # | # # # | # # # | # # # | 0.895 | 0.905 | 0.888 | 0.896 | # # # | # # # | # # # | - - - | 0.908 | 0.919 | 0.903 | 0.91 | - - - | 0.454 | 1.6 | 1.55 | 1.56 | 1.53 | 1.51 | 1.57 | 18.71 | 18.63 | 19.97 | 0 | - - - | - - - | - - - | - - - | 58556 | 56627 | 55342 | 170525 | Over-range | 26089 | 24039 | 25420 | 75597 | 10049 | 9680 | 10216 | 30075 | 52245 | 51117 | 48993 | 152355 | 52245 | 51117 | 48993 | 152355 | - - - | - - - | - - - | - - -
5/7/2026 | 7:00:00 PM | 284.04 | 281.59 | 281.5 | 492.02 | 485.88 | 489.36 | 206.1294 | 200.4467 | 196.1507 | 5.1979 | 1.441 | 1.437 | 1.437 | 1.602 | 1.598 | 1.692 | Over-range | 60 | 52414 | 51111 | 48971 | 152496 | - - - | - - - | - - - | - - - | 52414 | 51111 | 48971 | 152496 | 24093 | 21920 | 23378 | 69391 | - - - | - - - | - - - | - - - | 24093 | 21920 | 23378 | 69391 | 58548 | 56444 | 55217 | 170210 | # # # | # # # | # # # | # # # | 0.895 | 0.906 | 0.887 | 0.896 | # # # | # # # | # # # | - - - | 0.908 | 0.919 | 0.902 | 0.91 | - - - | 0.455 | 1.53 | 1.49 | 1.49 | 1.47 | 1.45 | 1.5 | 18.71 | 18.66 | 20.06 | 0 | - - - | - - - | - - - | - - - | 58548 | 56444 | 55217 | 170210 | Over-range | 26090 | 23950 | 25509 | 75605 | 10010 | 9650 | 10206 | 30016 | 52239 | 50944 | 48802 | 151986 | 52239 | 50944 | 48802 | 151986 | - - - | - - - | - - - | - - -
5/7/2026 | 7:15:00 PM | 284.6 | 282.14 | 281.99 | 493.02 | 486.75 | 490.24 | 153.0185 | 145.6313 | 144.3829 | 3.9368 | 1.441 | 1.437 | 1.436 | 1.795 | 1.791 | 1.864 | Over-range | 59.99 | 37238 | 34770 | 33918 | 105926 | - - - | - - - | - - - | - - - | 37238 | 34770 | 33918 | 105926 | 11780 | 10265 | 12712 | 34757 | - - - | - - - | - - - | - - - | 11780 | 10265 | 12712 | 34757 | 41258 | 38458 | 38447 | 118163 | # # # | # # # | # # # | # # # | 0.903 | 0.904 | 0.882 | 0.896 | # # # | # # # | # # # | - - - | 0.942 | 0.948 | 0.93 | 0.94 | - - - | 0.328 | 1.54 | 1.5 | 1.5 | 1.49 | 1.45 | 1.51 | 33.04 | 35.36 | 37.19 | 0 | - - - | - - - | - - - | - - - | 41258 | 38458 | 38447 | 118163 | Over-range | 17740 | 16429 | 18100 | 52360 | 10849 | 10453 | 11126 | 32663 | 37116 | 34663 | 33809 | 105589 | 37116 | 34663 | 33809 | 105589 | - - - | - - - | - - - | - - -
5/7/2026 | 7:30:00 PM | 284.66 | 282.33 | 282.05 | 493.27 | 487.02 | 490.28 | 103.591 | 93.4242 | 96.3054 | 2.4603 | 1.438 | 1.435 | 1.433 | 1.926 | 1.923 | 1.962 | Over-range | 60 | 26977 | 23814 | 23927 | 74718 | - - - | - - - | - - - | - - - | 26977 | 23814 | 23927 | 74718 | 2838 | 1892 | 4851 | 9581 | - - - | - - - | - - - | - - - | 2838 | 1892 | 4851 | 9581 | 29461 | 26354 | 27140 | 82955 | # # # | # # # | # # # | # # # | 0.916 | 0.904 | 0.882 | 0.901 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.98 | 0.99 | - - - | 0.128 | 1.53 | 1.5 | 1.49 | 1.49 | 1.45 | 1.49 | 43.1 | 47.1 | 49.2 | 0 | - - - | - - - | - - - | - - - | 29461 | 26354 | 27140 | 82955 | Over-range | 11833 | 11284 | 12804 | 36022 | 11487 | 11124 | 11849 | 34724 | 26885 | 23749 | 23840 | 74474 | 26885 | 23749 | 23840 | 74474 | - - - | - - - | - - - | - - -
5/7/2026 | 7:45:00 PM | 284.98 | 282.73 | 282.37 | 493.92 | 487.64 | 490.79 | 110.8771 | 100.1587 | 102.8232 | 2.5545 | 1.439 | 1.436 | 1.433 | 1.912 | 1.923 | 1.958 | Over-range | 59.99 | 28955 | 25640 | 25636 | 80231 | - - - | - - - | - - - | - - - | 28955 | 25640 | 25636 | 80231 | 3146 | 2026 | 5169 | 10342 | - - - | - - - | - - - | - - - | 3146 | 2026 | 5169 | 10342 | 31593 | 28314 | 29029 | 88937 | # # # | # # # | # # # | # # # | 0.917 | 0.906 | 0.883 | 0.902 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.98 | 0.99 | - - - | 0.129 | 1.55 | 1.52 | 1.5 | 1.5 | 1.47 | 1.51 | 42.86 | 46.62 | 48.91 | 0 | - - - | - - - | - - - | - - - | 31593 | 28314 | 29029 | 88937 | Over-range | 12639 | 12010 | 13620 | 38376 | 12241 | 11838 | 12601 | 36956 | 28849 | 25569 | 25550 | 79967 | 28849 | 25569 | 25550 | 79967 | - - - | - - - | - - - | - - -
5/7/2026 | 8:00:00 PM | 283.94 | 281.6 | 281.25 | 492.06 | 485.65 | 488.94 | 116.0937 | 104.3238 | 106.7485 | 2.7435 | 1.437 | 1.434 | 1.431 | 1.878 | 1.889 | 1.942 | Over-range | 60 | 30393 | 26752 | 26591 | 83736 | - - - | - - - | - - - | - - - | 30393 | 26752 | 26591 | 83736 | 3232 | 1808 | 5374 | 10413 | - - - | - - - | - - - | - - - | 3232 | 1808 | 5374 | 10413 | 32914 | 29339 | 29987 | 92240 | # # # | # # # | # # # | # # # | 0.923 | 0.912 | 0.887 | 0.908 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.98 | 0.991 | - - - | 0.124 | 1.48 | 1.47 | 1.46 | 1.44 | 1.42 | 1.45 | 40.63 | 44.81 | 47.66 | 0 | - - - | - - - | - - - | - - - | 32914 | 29339 | 29987 | 92240 | Over-range | 12629 | 12046 | 13857 | 38677 | 12208 | 11908 | 12772 | 37249 | 30295 | 26701 | 26504 | 83500 | 30295 | 26701 | 26504 | 83500 | - - - | - - - | - - - | - - -
5/7/2026 | 8:15:00 PM | 283.57 | 281.43 | 280.87 | 491.65 | 485.24 | 488.18 | 120.9545 | 108.9398 | 109.7257 | 2.8371 | 1.436 | 1.433 | 1.429 | 1.848 | 1.885 | 1.938 | Over-range | 59.99 | 31726 | 28039 | 27346 | 87111 | - - - | - - - | - - - | - - - | 31726 | 28039 | 27346 | 87111 | 3592 | 1582 | 5493 | 10667 | - - - | - - - | - - - | - - - | 3592 | 1582 | 5493 | 10667 | 34269 | 30636 | 30799 | 95704 | # # # | # # # | # # # | # # # | 0.926 | 0.915 | 0.888 | 0.91 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.98 | 0.991 | - - - | 0.122 | 1.47 | 1.46 | 1.42 | 1.43 | 1.4 | 1.43 | 39.6 | 43.91 | 47.35 | 0 | - - - | - - - | - - - | - - - | 34269 | 30636 | 30799 | 95704 | Over-range | 12948 | 12340 | 14165 | 39621 | 12439 | 12237 | 13057 | 38158 | 31633 | 27991 | 27266 | 86890 | 31633 | 27991 | 27266 | 86890 | - - - | - - - | - - - | - - -
5/7/2026 | 8:30:00 PM | 283.68 | 281.57 | 281.03 | 491.84 | 485.52 | 488.4 | 125.5384 | 112.8614 | 112.8727 | 2.8902 | 1.436 | 1.433 | 1.429 | 1.831 | 1.879 | 1.938 | Over-range | 60 | 33028 | 29129 | 28159 | 90316 | - - - | - - - | - - - | - - - | 33028 | 29129 | 28159 | 90316 | 3844 | 1397 | 5694 | 10935 | - - - | - - - | - - - | - - - | 3844 | 1397 | 5694 | 10935 | 35586 | 31758 | 31705 | 99049 | # # # | # # # | # # # | # # # | 0.928 | 0.917 | 0.888 | 0.912 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.98 | 0.991 | - - - | 0.121 | 1.48 | 1.46 | 1.44 | 1.43 | 1.41 | 1.44 | 38.76 | 43.42 | 47.2 | 0 | - - - | - - - | - - - | - - - | 35586 | 31758 | 31705 | 99049 | Over-range | 13241 | 12649 | 14566 | 40654 | 12670 | 12570 | 13407 | 39156 | 32932 | 29071 | 28085 | 90088 | 32932 | 29071 | 28085 | 90088 | - - - | - - - | - - - | - - -
5/7/2026 | 8:45:00 PM | 283.7 | 281.58 | 280.96 | 491.91 | 485.44 | 488.34 | 130.3712 | 116.5145 | 115.2732 | 2.9082 | 1.436 | 1.434 | 1.43 | 1.813 | 1.883 | 1.952 | Over-range | 60 | 34379 | 30136 | 28684 | 93199 | - - - | - - - | - - - | - - - | 34379 | 30136 | 28684 | 93199 | 4197 | 1038 | 5948 | 11183 | - - - | - - - | - - - | - - - | 4197 | 1038 | 5948 | 11183 | 36967 | 32793 | 32373 | 102133 | # # # | # # # | # # # | # # # | 0.93 | 0.919 | 0.886 | 0.913 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.979 | 0.991 | - - - | 0.12 | 1.49 | 1.48 | 1.46 | 1.45 | 1.43 | 1.46 | 37.94 | 43.02 | 47.55 | 0 | - - - | - - - | - - - | - - - | 36967 | 32793 | 32373 | 102133 | Over-range | 13580 | 12929 | 15004 | 41761 | 12915 | 12887 | 13774 | 40236 | 34284 | 30084 | 28603 | 92971 | 34284 | 30084 | 28603 | 92971 | - - - | - - - | - - - | - - -
5/7/2026 | 9:00:00 PM | 283.9 | 281.76 | 281.19 | 492.22 | 485.79 | 488.74 | 133.6414 | 119.9118 | 117.7487 | 3.0249 | 1.436 | 1.434 | 1.429 | 1.8 | 1.874 | 1.945 | Over-range | 60.01 | 35304 | 31102 | 29373 | 95778 | - - - | - - - | - - - | - - - | 35304 | 31102 | 29373 | 95778 | 4411 | 999 | 5991 | 11401 | - - - | - - - | - - - | - - - | 4411 | 999 | 5991 | 11401 | 37922 | 33772 | 33094 | 104789 | # # # | # # # | # # # | # # # | 0.931 | 0.921 | 0.887 | 0.914 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.98 | 0.991 | - - - | 0.119 | 1.5 | 1.49 | 1.46 | 1.45 | 1.44 | 1.47 | 37.52 | 42.45 | 47.29 | 0 | - - - | - - - | - - - | - - - | 37922 | 33772 | 33094 | 104789 | Over-range | 13840 | 13158 | 15243 | 42497 | 13118 | 13120 | 14016 | 40939 | 35207 | 31043 | 29295 | 95545 | 35207 | 31043 | 29295 | 95545 | - - - | - - - | - - - | - - -
5/7/2026 | 9:15:00 PM | 284.29 | 282.12 | 281.66 | 492.82 | 486.54 | 489.52 | 135.0451 | 121.4228 | 119.4729 | 3.0585 | 1.437 | 1.434 | 1.43 | 1.796 | 1.862 | 1.934 | Over-range | 60.01 | 35781 | 31570 | 29945 | 97297 | - - - | - - - | - - - | - - - | 35781 | 31570 | 29945 | 97297 | 4392 | 1096 | 6027 | 11516 | - - - | - - - | - - - | - - - | 4392 | 1096 | 6027 | 11516 | 38374 | 34241 | 33636 | 106251 | # # # | # # # | # # # | # # # | 0.932 | 0.922 | 0.89 | 0.916 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.98 | 0.991 | - - - | 0.118 | 1.54 | 1.51 | 1.51 | 1.48 | 1.47 | 1.51 | 37.13 | 42.1 | 46.66 | 0 | - - - | - - - | - - - | - - - | 38374 | 34241 | 33636 | 106251 | Over-range | 13858 | 13254 | 15316 | 42680 | 13144 | 13209 | 14080 | 41097 | 35685 | 31509 | 29861 | 97055 | 35685 | 31509 | 29861 | 97055 | - - - | - - - | - - - | - - -
5/7/2026 | 9:30:00 PM | 284.79 | 282.65 | 282.11 | 493.76 | 487.36 | 490.31 | 136.3452 | 122.0802 | 120.0396 | 3.0588 | 1.437 | 1.435 | 1.43 | 1.791 | 1.858 | 1.938 | Over-range | 60.02 | 36244 | 31836 | 30128 | 98208 | - - - | - - - | - - - | - - - | 36244 | 31836 | 30128 | 98208 | 4415 | 961 | 6126 | 11501 | - - - | - - - | - - - | - - - | 4415 | 961 | 6126 | 11501 | 38809 | 34490 | 33848 | 107146 | # # # | # # # | # # # | # # # | 0.934 | 0.923 | 0.89 | 0.917 | # # # | # # # | # # # | - - - | 0.993 | 1 | 0.98 | 0.991 | - - - | 0.117 | 1.57 | 1.53 | 1.53 | 1.51 | 1.48 | 1.53 | 36.64 | 41.78 | 46.58 | 0 | - - - | - - - | - - - | - - - | 38809 | 34490 | 33848 | 107146 | Over-range | 13867 | 13265 | 15423 | 42832 | 13145 | 13230 | 14154 | 41259 | 36151 | 31784 | 30042 | 97976 | 36151 | 31784 | 30042 | 97976 | - - - | - - - | - - - | - - -
5/7/2026 | 9:45:00 PM | 285.14 | 282.93 | 282.46 | 494.29 | 487.9 | 490.96 | 136.4677 | 121.9241 | 120.5488 | 3.0869 | 1.437 | 1.435 | 1.43 | 1.798 | 1.853 | 1.939 | Over-range | 60.01 | 36348 | 31808 | 30285 | 98442 | - - - | - - - | - - - | - - - | 36348 | 31808 | 30285 | 98442 | 4328 | 1003 | 6216 | 11546 | - - - | - - - | - - - | - - - | 4328 | 1003 | 6216 | 11546 | 38895 | 34482 | 34035 | 107412 | # # # | # # # | # # # | # # # | 0.935 | 0.923 | 0.89 | 0.917 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.979 | 0.991 | - - - | 0.117 | 1.58 | 1.54 | 1.55 | 1.52 | 1.5 | 1.55 | 36.57 | 41.95 | 46.57 | 0 | - - - | - - - | - - - | - - - | 38895 | 34482 | 34035 | 107412 | Over-range | 13837 | 13310 | 15527 | 42961 | 13143 | 13272 | 14228 | 41380 | 36239 | 31761 | 30206 | 98206 | 36239 | 31761 | 30206 | 98206 | - - - | - - - | - - - | - - -
5/7/2026 | 10:00:00 PM | 285.11 | 282.9 | 282.38 | 494.25 | 487.79 | 490.86 | 138.2235 | 124.718 | 122.2656 | 3.131 | 1.437 | 1.435 | 1.43 | 1.784 | 1.848 | 1.921 | Over-range | 60.02 | 36799 | 32613 | 30835 | 100246 | - - - | - - - | - - - | - - - | 36799 | 32613 | 30835 | 100246 | 4538 | 1123 | 6069 | 11729 | - - - | - - - | - - - | - - - | 4538 | 1123 | 6069 | 11729 | 39390 | 35267 | 34510 | 109167 | # # # | # # # | # # # | # # # | 0.934 | 0.925 | 0.893 | 0.918 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.981 | 0.991 | - - - | 0.117 | 1.6 | 1.56 | 1.56 | 1.54 | 1.52 | 1.57 | 36.48 | 41.22 | 45.88 | 0 | - - - | - - - | - - - | - - - | 39390 | 35267 | 34510 | 109167 | Over-range | 14043 | 13418 | 15491 | 43204 | 13289 | 13370 | 14252 | 41581 | 36705 | 32557 | 30747 | 100008 | 36705 | 32557 | 30747 | 100008 | - - - | - - - | - - - | - - -
5/7/2026 | 10:15:00 PM | 284.39 | 282.02 | 281.59 | 492.86 | 486.28 | 489.62 | 139.338 | 125.4637 | 123.7934 | 3.1725 | 1.436 | 1.433 | 1.429 | 1.792 | 1.845 | 1.923 | Over-range | 60 | 37010 | 32693 | 31134 | 100837 | - - - | - - - | - - - | - - - | 37010 | 32693 | 31134 | 100837 | 4450 | 1200 | 6156 | 11806 | - - - | - - - | - - - | - - - | 4450 | 1200 | 6156 | 11806 | 39606 | 35367 | 34844 | 109817 | # # # | # # # | # # # | # # # | 0.935 | 0.924 | 0.893 | 0.918 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.981 | 0.991 | - - - | 0.117 | 1.58 | 1.55 | 1.54 | 1.52 | 1.5 | 1.55 | 36.49 | 41.28 | 45.8 | 0 | - - - | - - - | - - - | - - - | 39606 | 35367 | 34844 | 109817 | Over-range | 14095 | 13489 | 15641 | 43481 | 13374 | 13435 | 14379 | 41848 | 36903 | 32648 | 31053 | 100604 | 36903 | 32648 | 31053 | 100604 | - - - | - - - | - - - | - - -
5/7/2026 | 10:30:00 PM | 284.38 | 282.05 | 281.6 | 492.88 | 486.33 | 489.6 | 137.3451 | 123.4876 | 121.4413 | 3.1053 | 1.435 | 1.432 | 1.428 | 1.792 | 1.855 | 1.933 | Over-range | 60.01 | 36443 | 32154 | 30475 | 99072 | - - - | - - - | - - - | - - - | 36443 | 32154 | 30475 | 99072 | 4484 | 1084 | 6096 | 11664 | - - - | - - - | - - - | - - - | 4484 | 1084 | 6096 | 11664 | 39038 | 34815 | 34183 | 108036 | # # # | # # # | # # # | # # # | 0.934 | 0.924 | 0.891 | 0.917 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.98 | 0.991 | - - - | 0.118 | 1.57 | 1.54 | 1.55 | 1.51 | 1.51 | 1.55 | 36.68 | 41.55 | 46.27 | 0 | - - - | - - - | - - - | - - - | 39038 | 34815 | 34183 | 108036 | Over-range | 13988 | 13346 | 15478 | 43071 | 13250 | 13302 | 14226 | 41462 | 36358 | 32104 | 30387 | 98850 | 36358 | 32104 | 30387 | 98850 | - - - | - - - | - - - | - - -
5/7/2026 | 10:45:00 PM | 284.78 | 282.41 | 282.05 | 493.5 | 487.03 | 490.38 | 134.7056 | 120.44 | 119.051 | 3.1113 | 1.436 | 1.432 | 1.428 | 1.797 | 1.848 | 1.937 | Over-range | 60.01 | 35826 | 31350 | 29851 | 97027 | - - - | - - - | - - - | - - - | 35826 | 31350 | 29851 | 97027 | 4311 | 988 | 6149 | 11449 | - - - | - - - | - - - | - - - | 4311 | 988 | 6149 | 11449 | 38328 | 33984 | 33552 | 105865 | # # # | # # # | # # # | # # # | 0.935 | 0.923 | 0.89 | 0.917 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.979 | 0.991 | - - - | 0.118 | 1.6 | 1.55 | 1.56 | 1.53 | 1.53 | 1.57 | 36.39 | 41.89 | 46.52 | 0 | - - - | - - - | - - - | - - - | 38328 | 33984 | 33552 | 105865 | Over-range | 13611 | 13116 | 15314 | 42328 | 12910 | 13078 | 14025 | 40750 | 35712 | 31312 | 29776 | 96800 | 35712 | 31312 | 29776 | 96800 | - - - | - - - | - - - | - - -
5/7/2026 | 11:00:00 PM | 285.38 | 283.02 | 282.62 | 494.57 | 488.04 | 491.37 | 132.6467 | 117.5586 | 117.2396 | 3.0059 | 1.436 | 1.432 | 1.429 | 1.822 | 1.873 | 1.963 | Over-range | 60.01 | 35275 | 30542 | 29293 | 95110 | - - - | - - - | - - - | - - - | 35275 | 30542 | 29293 | 95110 | 4177 | 985 | 6294 | 11456 | - - - | - - - | - - - | - - - | 4177 | 985 | 6294 | 11456 | 37829 | 33251 | 33116 | 104196 | # # # | # # # | # # # | # # # | 0.933 | 0.919 | 0.885 | 0.913 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.978 | 0.99 | - - - | 0.12 | 1.59 | 1.55 | 1.57 | 1.53 | 1.53 | 1.57 | 37.27 | 43.14 | 47.62 | 0 | - - - | - - - | - - - | - - - | 37829 | 33251 | 33116 | 104196 | Over-range | 13658 | 13143 | 15441 | 42541 | 13004 | 13105 | 14100 | 40969 | 35182 | 30489 | 29202 | 94873 | 35182 | 30489 | 29202 | 94873 | - - - | - - - | - - - | - - -
5/7/2026 | 11:15:00 PM | 285.26 | 282.76 | 282.37 | 494.27 | 487.52 | 491.08 | 128.6085 | 113.72 | 114.9013 | 2.9828 | 1.435 | 1.432 | 1.428 | 1.844 | 1.876 | 1.965 | Over-range | 59.98 | 34126 | 29448 | 28656 | 92230 | - - - | - - - | - - - | - - - | 34126 | 29448 | 28656 | 92230 | 3848 | 1200 | 6202 | 11249 | - - - | - - - | - - - | - - - | 3848 | 1200 | 6202 | 11249 | 36662 | 32136 | 32427 | 101224 | # # # | # # # | # # # | # # # | 0.931 | 0.916 | 0.884 | 0.911 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.977 | 0.99 | - - - | 0.122 | 1.59 | 1.56 | 1.56 | 1.53 | 1.53 | 1.56 | 38.02 | 43.74 | 47.8 | 0 | - - - | - - - | - - - | - - - | 36662 | 32136 | 32427 | 101224 | Over-range | 13391 | 12863 | 15172 | 41700 | 12826 | 12806 | 13847 | 40154 | 34033 | 29393 | 28570 | 91996 | 34033 | 29393 | 28570 | 91996 | - - - | - - - | - - - | - - -
5/7/2026 | 11:30:00 PM | 285.57 | 283.13 | 282.7 | 494.87 | 488.16 | 491.62 | 126.8709 | 112.5677 | 113.7791 | 2.9535 | 1.436 | 1.432 | 1.429 | 1.847 | 1.88 | 1.961 | Over-range | 60.01 | 33663 | 29167 | 28434 | 91264 | - - - | - - - | - - - | - - - | 33663 | 29167 | 28434 | 91264 | 3794 | 1311 | 6093 | 11199 | - - - | - - - | - - - | - - - | 3794 | 1311 | 6093 | 11199 | 36207 | 31854 | 32149 | 100210 | # # # | # # # | # # # | # # # | 0.93 | 0.916 | 0.884 | 0.911 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.978 | 0.99 | - - - | 0.123 | 1.61 | 1.58 | 1.57 | 1.54 | 1.54 | 1.58 | 38.38 | 43.93 | 47.71 | 0 | - - - | - - - | - - - | - - - | 36207 | 31854 | 32149 | 100210 | Over-range | 13326 | 12802 | 14997 | 41374 | 12774 | 12735 | 13703 | 39830 | 33566 | 29118 | 28343 | 91026 | 33566 | 29118 | 28343 | 91026 | - - - | - - - | - - - | - - -
5/7/2026 | 11:45:00 PM | 285.98 | 283.46 | 282.98 | 495.57 | 488.62 | 492.22 | 125.1586 | 110.588 | 112.2712 | 2.9205 | 1.435 | 1.432 | 1.428 | 1.859 | 1.888 | 1.973 | Over-range | 60.01 | 33226 | 28638 | 28023 | 89887 | - - - | - - - | - - - | - - - | 33226 | 28638 | 28023 | 89887 | 3686 | 1303 | 6100 | 11090 | - - - | - - - | - - - | - - - | 3686 | 1303 | 6100 | 11090 | 35768 | 31329 | 31753 | 98850 | # # # | # # # | # # # | # # # | 0.929 | 0.914 | 0.882 | 0.909 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.977 | 0.99 | - - - | 0.123 | 1.6 | 1.57 | 1.55 | 1.53 | 1.53 | 1.56 | 38.72 | 44.4 | 48.11 | 0 | - - - | - - - | - - - | - - - | 35768 | 31329 | 31753 | 98850 | Over-range | 13236 | 12699 | 14928 | 41116 | 12712 | 12632 | 13624 | 39592 | 33127 | 28594 | 27923 | 89644 | 33127 | 28594 | 27923 | 89644 | - - - | - - - | - - - | - - -
5/8/2026 | 12:00:00 AM | 285.82 | 283.39 | 282.95 | 495.31 | 488.6 | 492.04 | 122.4566 | 108.8533 | 110.7587 | 2.8643 | 1.435 | 1.432 | 1.428 | 1.854 | 1.868 | 1.948 | Over-range | 60 | 32519 | 28214 | 27764 | 88498 | - - - | - - - | - - - | - - - | 32519 | 28214 | 27764 | 88498 | 3511 | 1453 | 5870 | 10834 | - - - | - - - | - - - | - - - | 3511 | 1453 | 5870 | 10834 | 34967 | 30822 | 31316 | 97105 | # # # | # # # | # # # | # # # | 0.93 | 0.915 | 0.887 | 0.911 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.978 | 0.991 | - - - | 0.122 | 1.6 | 1.55 | 1.55 | 1.53 | 1.52 | 1.56 | 38.42 | 43.92 | 47.2 | 0 | - - - | - - - | - - - | - - - | 34967 | 30822 | 31316 | 97105 | Over-range | 12841 | 12404 | 14479 | 39948 | 12351 | 12318 | 13235 | 38451 | 32422 | 28169 | 27673 | 88264 | 32422 | 28169 | 27673 | 88264 | - - - | - - - | - - - | - - -
5/8/2026 | 12:15:00 AM | 284.18 | 281.84 | 281.39 | 492.52 | 485.96 | 489.25 | 123.4169 | 110.0055 | 112.0756 | 2.8936 | 1.435 | 1.431 | 1.428 | 1.865 | 1.885 | 1.954 | Over-range | 59.99 | 32491 | 28316 | 27920 | 88726 | - - - | - - - | - - - | - - - | 32491 | 28316 | 27920 | 88726 | 3542 | 1619 | 5873 | 11034 | - - - | - - - | - - - | - - - | 3542 | 1619 | 5873 | 11034 | 35046 | 30983 | 31516 | 97545 | # # # | # # # | # # # | # # # | 0.927 | 0.914 | 0.886 | 0.91 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.978 | 0.99 | - - - | 0.124 | 1.6 | 1.55 | 1.57 | 1.53 | 1.52 | 1.57 | 39.37 | 44.34 | 47.51 | 0 | - - - | - - - | - - - | - - - | 35046 | 30983 | 31516 | 97545 | Over-range | 13127 | 12574 | 14614 | 40513 | 12640 | 12469 | 13382 | 38982 | 32387 | 28256 | 27833 | 88476 | 32387 | 28256 | 27833 | 88476 | - - - | - - - | - - - | - - -
5/8/2026 | 12:30:00 AM | 284.05 | 281.49 | 281.17 | 492.1 | 485.38 | 489.05 | 120.912 | 107.346 | 111.2667 | 2.8578 | 1.434 | 1.429 | 1.426 | 1.887 | 1.876 | 1.951 | Over-range | 60 | 31795 | 27556 | 27730 | 87081 | - - - | - - - | - - - | - - - | 31795 | 27556 | 27730 | 87081 | 3158 | 1855 | 5824 | 10838 | - - - | - - - | - - - | - - - | 3158 | 1855 | 5824 | 10838 | 34321 | 30198 | 31269 | 95788 | # # # | # # # | # # # | # # # | 0.926 | 0.913 | 0.887 | 0.909 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.979 | 0.991 | - - - | 0.125 | 1.57 | 1.53 | 1.53 | 1.5 | 1.5 | 1.53 | 39.9 | 44.65 | 47.27 | 0 | - - - | - - - | - - - | - - - | 34321 | 30198 | 31269 | 95788 | Over-range | 12917 | 12351 | 14444 | 39891 | 12525 | 12211 | 13218 | 38391 | 31704 | 27491 | 27635 | 86829 | 31704 | 27491 | 27635 | 86829 | - - - | - - - | - - - | - - -
5/8/2026 | 12:45:00 AM | 284.4 | 281.87 | 281.45 | 492.78 | 485.93 | 489.55 | 118.1308 | 104.9171 | 109.0369 | 2.7285 | 1.434 | 1.43 | 1.426 | 1.891 | 1.879 | 1.947 | Over-range | 60 | 31072 | 26944 | 27222 | 85238 | - - - | - - - | - - - | - - - | 31072 | 26944 | 27222 | 85238 | 3029 | 1906 | 5684 | 10620 | - - - | - - - | - - - | - - - | 3029 | 1906 | 5684 | 10620 | 33565 | 29550 | 30666 | 93781 | # # # | # # # | # # # | # # # | 0.926 | 0.912 | 0.888 | 0.909 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.979 | 0.991 | - - - | 0.125 | 1.59 | 1.55 | 1.55 | 1.53 | 1.52 | 1.55 | 40.18 | 44.81 | 47.07 | 0 | - - - | - - - | - - - | - - - | 33565 | 29550 | 30666 | 93781 | Over-range | 12686 | 12131 | 14113 | 39090 | 12319 | 11980 | 12917 | 37620 | 30971 | 26872 | 27144 | 84986 | 30971 | 26872 | 27144 | 84986 | - - - | - - - | - - - | - - -
5/8/2026 | 1:00:00 AM | 284.51 | 281.94 | 281.55 | 492.93 | 486.07 | 489.76 | 115.0283 | 102.2466 | 106.5633 | 2.6784 | 1.435 | 1.43 | 1.427 | 1.903 | 1.885 | 1.95 | Over-range | 60.01 | 30210 | 26212 | 26583 | 83006 | - - - | - - - | - - - | - - - | 30210 | 26212 | 26583 | 83006 | 2903 | 1947 | 5537 | 10388 | - - - | - - - | - - - | - - - | 2903 | 1947 | 5537 | 10388 | 32690 | 28801 | 29976 | 91467 | # # # | # # # | # # # | # # # | 0.924 | 0.91 | 0.887 | 0.908 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.979 | 0.991 | - - - | 0.125 | 1.6 | 1.55 | 1.55 | 1.53 | 1.52 | 1.56 | 40.7 | 45.25 | 47.34 | 0 | - - - | - - - | - - - | - - - | 32690 | 28801 | 29976 | 91467 | Over-range | 12477 | 11930 | 13844 | 38400 | 12135 | 11770 | 12689 | 36969 | 30107 | 26141 | 26504 | 82751 | 30107 | 26141 | 26504 | 82751 | - - - | - - - | - - - | - - -
5/8/2026 | 1:15:00 AM | 284.48 | 281.77 | 281.44 | 492.76 | 485.76 | 489.68 | 112.8649 | 99.6075 | 104.4732 | 2.5776 | 1.433 | 1.429 | 1.426 | 1.923 | 1.907 | 1.974 | Over-range | 60 | 29577 | 25445 | 25955 | 80977 | - - - | - - - | - - - | - - - | 29577 | 25445 | 25955 | 80977 | 2788 | 1881 | 5540 | 10209 | - - - | - - - | - - - | - - - | 2788 | 1881 | 5540 | 10209 | 32080 | 28044 | 29382 | 89505 | # # # | # # # | # # # | # # # | 0.922 | 0.907 | 0.883 | 0.905 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.978 | 0.99 | - - - | 0.126 | 1.57 | 1.53 | 1.52 | 1.51 | 1.5 | 1.53 | 41.45 | 46.11 | 48.13 | 0 | - - - | - - - | - - - | - - - | 32080 | 28044 | 29382 | 89505 | Over-range | 12415 | 11788 | 13764 | 38115 | 12097 | 11636 | 12600 | 36722 | 29479 | 25382 | 25860 | 80722 | 29479 | 25382 | 25860 | 80722 | - - - | - - - | - - - | - - -
5/8/2026 | 1:30:00 AM | 284.52 | 281.65 | 281.39 | 492.71 | 485.55 | 489.74 | 108.7965 | 95.4248 | 100.8435 | 2.5041 | 1.434 | 1.429 | 1.426 | 1.933 | 1.903 | 1.978 | Over-range | 60 | 28527 | 24340 | 25018 | 77885 | - - - | - - - | - - - | - - - | 28527 | 24340 | 25018 | 77885 | 2564 | 1783 | 5421 | 9768 | - - - | - - - | - - - | - - - | 2564 | 1783 | 5421 | 9768 | 30910 | 26844 | 28343 | 86098 | # # # | # # # | # # # | # # # | 0.923 | 0.907 | 0.883 | 0.905 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.977 | 0.99 | - - - | 0.125 | 1.59 | 1.54 | 1.53 | 1.51 | 1.51 | 1.55 | 41.24 | 46.31 | 48.12 | 0 | - - - | - - - | - - - | - - - | 30910 | 26844 | 28343 | 86098 | Over-range | 11889 | 11317 | 13311 | 36673 | 11609 | 11175 | 12157 | 35348 | 28436 | 24268 | 24931 | 77634 | 28436 | 24268 | 24931 | 77634 | - - - | - - - | - - - | - - -
5/8/2026 | 1:45:00 AM | 284.48 | 281.81 | 281.51 | 492.76 | 485.89 | 489.75 | 106.0437 | 93.5561 | 98.0366 | 2.4003 | 1.434 | 1.429 | 1.426 | 1.935 | 1.921 | 1.983 | Over-range | 60.02 | 27719 | 23822 | 24282 | 75823 | - - - | - - - | - - - | - - - | 27719 | 23822 | 24282 | 75823 | 2641 | 1728 | 5216 | 9585 | - - - | - - - | - - - | - - - | 2641 | 1728 | 5216 | 9585 | 30123 | 26331 | 27563 | 84017 | # # # | # # # | # # # | # # # | 0.92 | 0.905 | 0.881 | 0.903 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.126 | 1.57 | 1.52 | 1.51 | 1.5 | 1.49 | 1.52 | 41.98 | 46.9 | 48.73 | 0 | - - - | - - - | - - - | - - - | 30123 | 26331 | 27563 | 84017 | Over-range | 11782 | 11212 | 13035 | 36169 | 11482 | 11078 | 11946 | 34876 | 27617 | 23755 | 24203 | 75576 | 27617 | 23755 | 24203 | 75576 | - - - | - - - | - - - | - - -
5/8/2026 | 2:00:00 AM | 284.84 | 281.95 | 281.69 | 493.24 | 486.05 | 490.29 | 103.0083 | 89.6237 | 94.853 | 2.3811 | 1.434 | 1.429 | 1.426 | 1.963 | 1.948 | 2.021 | Over-range | 60.01 | 26889 | 22719 | 23320 | 72928 | - - - | - - - | - - - | - - - | 26889 | 22719 | 23320 | 72928 | 2492 | 1581 | 5292 | 9366 | - - - | - - - | - - - | - - - | 2492 | 1581 | 5292 | 9366 | 29304 | 25241 | 26691 | 81237 | # # # | # # # | # # # | # # # | 0.918 | 0.9 | 0.874 | 0.898 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.975 | 0.99 | - - - | 0.128 | 1.57 | 1.52 | 1.53 | 1.5 | 1.5 | 1.53 | 42.89 | 48.31 | 50.22 | 0 | - - - | - - - | - - - | - - - | 29304 | 25241 | 26691 | 81237 | Over-range | 11642 | 10995 | 12980 | 35775 | 11372 | 10880 | 11852 | 34527 | 26798 | 22642 | 23241 | 72681 | 26798 | 22642 | 23241 | 72681 | - - - | - - - | - - - | - - -
5/8/2026 | 2:15:00 AM | 284.86 | 281.92 | 281.7 | 493.23 | 486.01 | 490.35 | 99.2356 | 86.1271 | 91.5114 | 2.329 | 1.432 | 1.428 | 1.424 | 1.968 | 1.94 | 2.019 | Over-range | 60.01 | 25920 | 21806 | 22491 | 70217 | - - - | - - - | - - - | - - - | 25920 | 21806 | 22491 | 70217 | 2305 | 1513 | 5127 | 8945 | - - - | - - - | - - - | - - - | 2305 | 1513 | 5127 | 8945 | 28213 | 24239 | 25739 | 78192 | # # # | # # # | # # # | # # # | 0.919 | 0.9 | 0.874 | 0.898 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.975 | 0.99 | - - - | 0.127 | 1.55 | 1.52 | 1.5 | 1.48 | 1.48 | 1.5 | 42.54 | 48.43 | 50.08 | 0 | - - - | - - - | - - - | - - - | 28213 | 24239 | 25739 | 78192 | Over-range | 11129 | 10582 | 12508 | 34380 | 10887 | 10473 | 11408 | 33196 | 25838 | 21735 | 22408 | 69982 | 25838 | 21735 | 22408 | 69982 | - - - | - - - | - - - | - - -
5/8/2026 | 2:30:00 AM | 284.91 | 282.07 | 281.8 | 493.41 | 486.27 | 490.43 | 98.9262 | 85.6478 | 90.6973 | 2.313 | 1.433 | 1.428 | 1.425 | 1.988 | 1.982 | 2.053 | Over-range | 60 | 25706 | 21582 | 22120 | 69409 | - - - | - - - | - - - | - - - | 25706 | 21582 | 22120 | 69409 | 2432 | 1447 | 5196 | 9076 | - - - | - - - | - - - | - - - | 2432 | 1447 | 5196 | 9076 | 28152 | 24135 | 25534 | 77821 | # # # | # # # | # # # | # # # | 0.913 | 0.894 | 0.866 | 0.892 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.973 | 0.989 | - - - | 0.131 | 1.54 | 1.52 | 1.51 | 1.49 | 1.48 | 1.5 | 44.21 | 50 | 51.91 | 0 | - - - | - - - | - - - | - - - | 28152 | 24135 | 25534 | 77821 | Over-range | 11469 | 10798 | 12748 | 35174 | 11207 | 10701 | 11641 | 33983 | 25591 | 21521 | 22053 | 69165 | 25591 | 21521 | 22053 | 69165 | - - - | - - - | - - - | - - -
5/8/2026 | 2:45:00 AM | 285.01 | 282 | 281.82 | 493.42 | 486.17 | 490.6 | 95.1164 | 81.7817 | 87.6026 | 2.2674 | 1.432 | 1.427 | 1.424 | 1.998 | 1.966 | 2.051 | Over-range | 60.01 | 24755 | 20565 | 21350 | 66670 | - - - | - - - | - - - | - - - | 24755 | 20565 | 21350 | 66670 | 2162 | 1409 | 5089 | 8661 | - - - | - - - | - - - | - - - | 2162 | 1409 | 5089 | 8661 | 27052 | 23021 | 24648 | 74722 | # # # | # # # | # # # | # # # | 0.915 | 0.893 | 0.866 | 0.892 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.972 | 0.989 | - - - | 0.13 | 1.54 | 1.51 | 1.49 | 1.48 | 1.48 | 1.49 | 43.7 | 50.26 | 51.68 | 0 | - - - | - - - | - - - | - - - | 27052 | 23021 | 24648 | 74722 | Over-range | 10895 | 10341 | 12307 | 33713 | 10678 | 10245 | 11205 | 32582 | 24674 | 20488 | 21273 | 66436 | 24674 | 20488 | 21273 | 66436 | - - - | - - - | - - - | - - -
5/8/2026 | 3:00:00 AM | 285.21 | 282.22 | 281.98 | 493.82 | 486.49 | 490.9 | 94.7548 | 80.9931 | 86.8152 | 2.2672 | 1.432 | 1.427 | 1.424 | 2.011 | 1.994 | 2.077 | Over-range | 60.01 | 24616 | 20320 | 21050 | 65985 | - - - | - - - | - - - | - - - | 24616 | 20320 | 21050 | 65985 | 2194 | 1331 | 5171 | 8696 | - - - | - - - | - - - | - - - | 2194 | 1331 | 5171 | 8696 | 26980 | 22825 | 24448 | 74255 | # # # | # # # | # # # | # # # | 0.912 | 0.89 | 0.861 | 0.889 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.971 | 0.988 | - - - | 0.132 | 1.54 | 1.52 | 1.49 | 1.48 | 1.48 | 1.49 | 44.57 | 51.19 | 52.8 | 0 | - - - | - - - | - - - | - - - | 26980 | 22825 | 24448 | 74255 | Over-range | 11037 | 10395 | 12428 | 34036 | 10816 | 10309 | 11302 | 32907 | 24508 | 20257 | 20978 | 65743 | 24508 | 20257 | 20978 | 65743 | - - - | - - - | - - - | - - -
5/8/2026 | 3:15:00 AM | 285.48 | 282.6 | 282.42 | 494.32 | 487.28 | 491.5 | 92.5447 | 79.5675 | 85.145 | 2.2233 | 1.433 | 1.427 | 1.424 | 2.011 | 1.985 | 2.065 | Over-range | 60 | 24046 | 19962 | 20699 | 64708 | - - - | - - - | - - - | - - - | 24046 | 19962 | 20699 | 64708 | 2141 | 1374 | 5002 | 8517 | - - - | - - - | - - - | - - - | 2141 | 1374 | 5002 | 8517 | 26366 | 22446 | 24010 | 72822 | # # # | # # # | # # # | # # # | 0.912 | 0.889 | 0.862 | 0.889 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.972 | 0.989 | - - - | 0.132 | 1.54 | 1.51 | 1.49 | 1.48 | 1.47 | 1.49 | 44.6 | 51.33 | 52.7 | 0 | - - - | - - - | - - - | - - - | 26366 | 22446 | 24010 | 72822 | Over-range | 10801 | 10260 | 12157 | 33382 | 10586 | 10167 | 11080 | 32277 | 23962 | 19903 | 20609 | 64474 | 23962 | 19903 | 20609 | 64474 | - - - | - - - | - - - | - - -
5/8/2026 | 3:30:00 AM | 285.67 | 282.81 | 282.54 | 494.7 | 487.55 | 491.73 | 91.7828 | 78.646 | 84.0343 | 2.2003 | 1.432 | 1.427 | 1.424 | 2.011 | 1.995 | 2.075 | Over-range | 60 | 23861 | 19737 | 20397 | 63995 | - - - | - - - | - - - | - - - | 23861 | 19737 | 20397 | 63995 | 2158 | 1278 | 4999 | 8435 | - - - | - - - | - - - | - - - | 2158 | 1278 | 4999 | 8435 | 26164 | 22201 | 23703 | 72069 | # # # | # # # | # # # | # # # | 0.912 | 0.889 | 0.861 | 0.888 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.971 | 0.988 | - - - | 0.132 | 1.54 | 1.5 | 1.5 | 1.48 | 1.48 | 1.49 | 44.61 | 51.53 | 52.93 | 0 | - - - | - - - | - - - | - - - | 26164 | 22201 | 23703 | 72069 | Over-range | 10721 | 10162 | 12068 | 33123 | 10502 | 10081 | 10984 | 32031 | 23773 | 19657 | 20331 | 63760 | 23773 | 19657 | 20331 | 63760 | - - - | - - - | - - - | - - -
5/8/2026 | 3:45:00 AM | 285.61 | 282.69 | 282.51 | 494.52 | 487.41 | 491.7 | 91.6702 | 78.39 | 84.101 | 2.2275 | 1.433 | 1.428 | 1.425 | 2.022 | 2.001 | 2.083 | Over-range | 60.01 | 23791 | 19618 | 20364 | 63773 | - - - | - - - | - - - | - - - | 23791 | 19618 | 20364 | 63773 | 2124 | 1317 | 5052 | 8493 | - - - | - - - | - - - | - - - | 2124 | 1317 | 5052 | 8493 | 26134 | 22124 | 23727 | 71986 | # # # | # # # | # # # | # # # | 0.91 | 0.887 | 0.858 | 0.886 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.97 | 0.988 | - - - | 0.133 | 1.54 | 1.53 | 1.49 | 1.49 | 1.48 | 1.5 | 45.13 | 52.15 | 53.49 | 0 | - - - | - - - | - - - | - - - | 26134 | 22124 | 23727 | 71986 | Over-range | 10806 | 10225 | 12171 | 33373 | 10594 | 10139 | 11073 | 32275 | 23695 | 19561 | 20278 | 63533 | 23695 | 19561 | 20278 | 63533 | - - - | - - - | - - - | - - -
5/8/2026 | 4:00:00 AM | 285.71 | 282.92 | 282.67 | 494.8 | 487.81 | 491.86 | 88.1929 | 75.8133 | 80.8668 | 2.1231 | 1.432 | 1.427 | 1.424 | 2.012 | 1.99 | 2.069 | Over-range | 60.02 | 22925 | 19004 | 19640 | 61570 | - - - | - - - | - - - | - - - | 22925 | 19004 | 19640 | 61570 | 2064 | 1243 | 4782 | 8089 | - - - | - - - | - - - | - - - | 2064 | 1243 | 4782 | 8089 | 25132 | 21402 | 22813 | 69347 | # # # | # # # | # # # | # # # | 0.912 | 0.888 | 0.861 | 0.888 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.971 | 0.989 | - - - | 0.131 | 1.53 | 1.5 | 1.48 | 1.47 | 1.46 | 1.48 | 44.5 | 51.77 | 52.88 | 0 | - - - | - - - | - - - | - - - | 25132 | 21402 | 22813 | 69347 | Over-range | 10281 | 9837 | 11595 | 31878 | 10071 | 9758 | 10563 | 30835 | 22834 | 18933 | 19573 | 61341 | 22834 | 18933 | 19573 | 61341 | - - - | - - - | - - - | - - -
5/8/2026 | 4:15:00 AM | 285.5 | 282.61 | 282.38 | 494.37 | 487.23 | 491.47 | 90.1653 | 77.0667 | 82.4785 | 2.1982 | 1.433 | 1.428 | 1.425 | 2.029 | 2.016 | 2.096 | Over-range | 60 | 23334 | 19235 | 19887 | 62456 | - - - | - - - | - - - | - - - | 23334 | 19235 | 19887 | 62456 | 2141 | 1266 | 4979 | 8386 | - - - | - - - | - - - | - - - | 2141 | 1266 | 4979 | 8386 | 25695 | 21742 | 23256 | 70693 | # # # | # # # | # # # | # # # | 0.908 | 0.885 | 0.855 | 0.883 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.97 | 0.988 | - - - | 0.134 | 1.54 | 1.52 | 1.51 | 1.49 | 1.49 | 1.5 | 45.74 | 52.7 | 54.24 | 0 | - - - | - - - | - - - | - - - | 25695 | 21742 | 23256 | 70693 | Over-range | 10750 | 10132 | 12052 | 33102 | 10533 | 10052 | 10975 | 32022 | 23243 | 19176 | 19803 | 62222 | 23243 | 19176 | 19803 | 62222 | - - - | - - - | - - - | - - -
5/8/2026 | 4:30:00 AM | 285.61 | 282.79 | 282.54 | 494.61 | 487.56 | 491.67 | 86.2735 | 73.9622 | 79.0525 | 2.095 | 1.432 | 1.427 | 1.424 | 2.02 | 1.997 | 2.078 | Over-range | 60.01 | 22388 | 18492 | 19129 | 60009 | - - - | - - - | - - - | - - - | 22388 | 18492 | 19129 | 60009 | 2010 | 1205 | 4715 | 7930 | - - - | - - - | - - - | - - - | 2010 | 1205 | 4715 | 7930 | 24574 | 20867 | 22287 | 67728 | # # # | # # # | # # # | # # # | 0.911 | 0.886 | 0.858 | 0.886 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.971 | 0.988 | - - - | 0.132 | 1.54 | 1.5 | 1.5 | 1.48 | 1.47 | 1.49 | 44.82 | 52.24 | 53.46 | 0 | - - - | - - - | - - - | - - - | 24574 | 20867 | 22287 | 67728 | Over-range | 10117 | 9662 | 11427 | 31373 | 9916 | 9587 | 10409 | 30355 | 22328 | 18430 | 19034 | 59792 | 22328 | 18430 | 19034 | 59792 | - - - | - - - | - - - | - - -
5/8/2026 | 4:45:00 AM | 285.24 | 282.43 | 282.23 | 493.94 | 487 | 491.1 | 86.4665 | 74.1725 | 79.2846 | 2.0992 | 1.432 | 1.427 | 1.425 | 2.034 | 2.017 | 2.092 | Over-range | 59.99 | 22315 | 18441 | 19083 | 59839 | - - - | - - - | - - - | - - - | 22315 | 18441 | 19083 | 59839 | 2056 | 1245 | 4755 | 8056 | - - - | - - - | - - - | - - - | 2056 | 1245 | 4755 | 8056 | 24603 | 20903 | 22333 | 67839 | # # # | # # # | # # # | # # # | 0.907 | 0.882 | 0.855 | 0.882 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.97 | 0.988 | - - - | 0.135 | 1.53 | 1.51 | 1.49 | 1.48 | 1.48 | 1.49 | 46.01 | 53.35 | 54.4 | 0 | - - - | - - - | - - - | - - - | 24603 | 20903 | 22333 | 67839 | Over-range | 10349 | 9838 | 11593 | 31936 | 10142 | 9758 | 10573 | 30904 | 22221 | 18369 | 19022 | 59612 | 22221 | 18369 | 19022 | 59612 | - - - | - - - | - - - | - - -
5/8/2026 | 5:00:00 AM | 285.39 | 282.5 | 282.26 | 494.19 | 487.04 | 491.26 | 84.0833 | 71.7622 | 77.007 | 2.0497 | 1.431 | 1.427 | 1.424 | 2.032 | 2.008 | 2.091 | Over-range | 60.03 | 21755 | 17842 | 18522 | 58119 | - - - | - - - | - - - | - - - | 21755 | 17842 | 18522 | 58119 | 1932 | 1141 | 4684 | 7757 | - - - | - - - | - - - | - - - | 1932 | 1141 | 4684 | 7757 | 23928 | 20219 | 21686 | 65832 | # # # | # # # | # # # | # # # | 0.909 | 0.882 | 0.854 | 0.883 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.969 | 0.988 | - - - | 0.134 | 1.54 | 1.51 | 1.51 | 1.48 | 1.48 | 1.5 | 45.44 | 53.23 | 54.27 | 0 | - - - | - - - | - - - | - - - | 23928 | 20219 | 21686 | 65832 | Over-range | 9949 | 9507 | 11272 | 30898 | 9759 | 9438 | 10252 | 29909 | 21651 | 17802 | 18454 | 57906 | 21651 | 17802 | 18454 | 57906 | - - - | - - - | - - - | - - -
5/8/2026 | 5:15:00 AM | 284.93 | 282.08 | 281.83 | 493.42 | 486.31 | 490.48 | 84.2637 | 72.456 | 77.0561 | 2.0707 | 1.433 | 1.429 | 1.426 | 2.019 | 2.005 | 2.079 | Over-range | 60.01 | 21749 | 18031 | 18544 | 58324 | - - - | - - - | - - - | - - - | 21749 | 18031 | 18544 | 58324 | 2038 | 1155 | 4578 | 7771 | - - - | - - - | - - - | - - - | 2038 | 1155 | 4578 | 7771 | 23942 | 20388 | 21666 | 65997 | # # # | # # # | # # # | # # # | 0.908 | 0.884 | 0.856 | 0.884 | # # # | # # # | # # # | - - - | 0.996 | 0.998 | 0.971 | 0.988 | - - - | 0.133 | 1.58 | 1.54 | 1.57 | 1.52 | 1.53 | 1.56 | 45.46 | 52.67 | 53.97 | 0 | - - - | - - - | - - - | - - - | 23942 | 20388 | 21666 | 65997 | Over-range | 9994 | 9511 | 11196 | 30857 | 9784 | 9441 | 10217 | 29862 | 21655 | 17969 | 18505 | 58129 | 21655 | 17969 | 18505 | 58129 | - - - | - - - | - - - | - - -
5/8/2026 | 5:30:00 AM | 284.83 | 282.11 | 281.85 | 493.33 | 486.44 | 490.37 | 81.5434 | 70.7832 | 74.6236 | 1.9946 | 1.433 | 1.429 | 1.426 | 2.01 | 1.999 | 2.065 | Over-range | 60 | 21040 | 17627 | 18012 | 56679 | - - - | - - - | - - - | - - - | 21040 | 17627 | 18012 | 56679 | 2032 | 1149 | 4325 | 7506 | - - - | - - - | - - - | - - - | 2032 | 1149 | 4325 | 7506 | 23155 | 19908 | 20981 | 64045 | # # # | # # # | # # # | # # # | 0.909 | 0.885 | 0.859 | 0.885 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.972 | 0.989 | - - - | 0.132 | 1.59 | 1.56 | 1.57 | 1.53 | 1.54 | 1.57 | 45.25 | 52.38 | 53.59 | 0 | - - - | - - - | - - - | - - - | 23155 | 19908 | 20981 | 64045 | Over-range | 9652 | 9250 | 10752 | 29795 | 9435 | 9178 | 9844 | 28834 | 20960 | 17564 | 17977 | 56500 | 20960 | 17564 | 17977 | 56500 | - - - | - - - | - - - | - - -
5/8/2026 | 5:45:00 AM | 284.72 | 281.95 | 281.66 | 493.13 | 486.08 | 490.12 | 80.4076 | 69.434 | 73.3857 | 1.9746 | 1.432 | 1.429 | 1.426 | 2.017 | 2.007 | 2.076 | Over-range | 60 | 20713 | 17245 | 17630 | 55589 | - - - | - - - | - - - | - - - | 20713 | 17245 | 17630 | 55589 | 1995 | 1078 | 4318 | 7390 | - - - | - - - | - - - | - - - | 1995 | 1078 | 4318 | 7390 | 22818 | 19519 | 20616 | 62953 | # # # | # # # | # # # | # # # | 0.908 | 0.883 | 0.855 | 0.883 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.971 | 0.988 | - - - | 0.133 | 1.59 | 1.58 | 1.57 | 1.53 | 1.55 | 1.58 | 45.49 | 52.88 | 54.26 | 0 | - - - | - - - | - - - | - - - | 22818 | 19519 | 20616 | 62953 | Over-range | 9559 | 9138 | 10678 | 29521 | 9348 | 9074 | 9766 | 28582 | 20631 | 17192 | 17590 | 55413 | 20631 | 17192 | 17590 | 55413 | - - - | - - - | - - - | - - -
5/8/2026 | 6:00:00 AM | 284.32 | 281.48 | 281.27 | 492.33 | 485.32 | 489.48 | 79.1818 | 68.5205 | 72.577 | 1.9275 | 1.433 | 1.429 | 1.427 | 2.018 | 2.002 | 2.068 | Over-range | 60 | 20349 | 16980 | 17417 | 54746 | - - - | - - - | - - - | - - - | 20349 | 16980 | 17417 | 54746 | 1935 | 1115 | 4214 | 7264 | - - - | - - - | - - - | - - - | 1935 | 1115 | 4214 | 7264 | 22430 | 19227 | 20349 | 62006 | # # # | # # # | # # # | # # # | 0.907 | 0.883 | 0.856 | 0.883 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.972 | 0.988 | - - - | 0.133 | 1.61 | 1.6 | 1.6 | 1.55 | 1.57 | 1.61 | 45.63 | 52.88 | 54.16 | 0 | - - - | - - - | - - - | - - - | 22430 | 19227 | 20349 | 62006 | Over-range | 9422 | 9015 | 10514 | 29089 | 9221 | 8946 | 9633 | 28168 | 20280 | 16937 | 17366 | 54584 | 20280 | 16937 | 17366 | 54584 | - - - | - - - | - - - | - - -
5/8/2026 | 6:15:00 AM | 283.59 | 280.83 | 280.48 | 491.21 | 484.09 | 488.11 | 78.4595 | 68.4718 | 71.4883 | 1.8691 | 1.432 | 1.43 | 1.427 | 2.003 | 2.005 | 2.062 | Over-range | 59.98 | 20101 | 16946 | 17136 | 54182 | - - - | - - - | - - - | - - - | 20101 | 16946 | 17136 | 54182 | 2043 | 1061 | 4058 | 7162 | - - - | - - - | - - - | - - - | 2043 | 1061 | 4058 | 7162 | 22180 | 19171 | 20000 | 61352 | # # # | # # # | # # # | # # # | 0.906 | 0.884 | 0.857 | 0.883 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.973 | 0.989 | - - - | 0.132 | 1.65 | 1.64 | 1.65 | 1.58 | 1.61 | 1.65 | 45.64 | 52.61 | 54.15 | 0 | - - - | - - - | - - - | - - - | 22180 | 19171 | 20000 | 61352 | Over-range | 9364 | 8960 | 10307 | 28757 | 9137 | 8897 | 9475 | 27851 | 20036 | 16915 | 17091 | 54042 | 20036 | 16915 | 17091 | 54042 | - - - | - - - | - - - | - - -
5/8/2026 | 6:30:00 AM | 283.77 | 281.06 | 280.69 | 491.56 | 484.49 | 488.41 | 78.6786 | 68.6837 | 71.7179 | 1.8836 | 1.432 | 1.43 | 1.427 | 2.004 | 2.006 | 2.064 | Over-range | 60 | 20151 | 17007 | 17185 | 54344 | - - - | - - - | - - - | - - - | 20151 | 17007 | 17185 | 54344 | 2052 | 1065 | 4045 | 7162 | - - - | - - - | - - - | - - - | 2052 | 1065 | 4045 | 7162 | 22249 | 19241 | 20072 | 61562 | # # # | # # # | # # # | # # # | 0.906 | 0.884 | 0.856 | 0.883 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.973 | 0.989 | - - - | 0.132 | 1.63 | 1.6 | 1.62 | 1.56 | 1.58 | 1.63 | 45.73 | 52.63 | 54.31 | 0 | - - - | - - - | - - - | - - - | 22249 | 19241 | 20072 | 61562 | Over-range | 9418 | 8994 | 10364 | 28902 | 9192 | 8930 | 9541 | 28001 | 20127 | 16943 | 17144 | 54213 | 20127 | 16943 | 17144 | 54213 | - - - | - - - | - - - | - - -
5/8/2026 | 6:45:00 AM | 283.73 | 281.07 | 280.71 | 491.51 | 484.56 | 488.39 | 76.992 | 67.1588 | 70.1208 | 1.813 | 1.432 | 1.43 | 1.427 | 2.011 | 2.017 | 2.073 | Over-range | 59.99 | 19680 | 16581 | 16741 | 53002 | - - - | - - - | - - - | - - - | 19680 | 16581 | 16741 | 53002 | 2034 | 1016 | 4000 | 7050 | - - - | - - - | - - - | - - - | 2034 | 1016 | 4000 | 7050 | 21772 | 18816 | 19627 | 60215 | # # # | # # # | # # # | # # # | 0.904 | 0.881 | 0.853 | 0.88 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.972 | 0.989 | - - - | 0.133 | 1.62 | 1.58 | 1.6 | 1.54 | 1.57 | 1.61 | 46.26 | 53.32 | 55.03 | 0 | - - - | - - - | - - - | - - - | 21772 | 18816 | 19627 | 60215 | Over-range | 9298 | 8889 | 10238 | 28552 | 9072 | 8830 | 9424 | 27668 | 19616 | 16556 | 16700 | 52871 | 19616 | 16556 | 16700 | 52871 | - - - | - - - | - - - | - - -
5/8/2026 | 7:00:00 AM | 283.43 | 280.73 | 280.43 | 490.94 | 484 | 487.91 | 76.8983 | 67.0169 | 70.2194 | 1.8018 | 1.432 | 1.43 | 1.426 | 2.016 | 2.012 | 2.072 | Over-range | 60 | 19625 | 16519 | 16748 | 52892 | - - - | - - - | - - - | - - - | 19625 | 16519 | 16748 | 52892 | 1995 | 1051 | 3992 | 7038 | - - - | - - - | - - - | - - - | 1995 | 1051 | 3992 | 7038 | 21719 | 18751 | 19638 | 60109 | # # # | # # # | # # # | # # # | 0.904 | 0.881 | 0.853 | 0.88 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.973 | 0.989 | - - - | 0.133 | 1.62 | 1.58 | 1.58 | 1.53 | 1.55 | 1.6 | 46.36 | 53.39 | 55.12 | 0 | - - - | - - - | - - - | - - - | 21719 | 18751 | 19638 | 60109 | Over-range | 9291 | 8870 | 10247 | 28534 | 9074 | 8807 | 9438 | 27653 | 19580 | 16486 | 16696 | 52761 | 19580 | 16486 | 16696 | 52761 | - - - | - - - | - - - | - - -
5/8/2026 | 7:15:00 AM | 283.32 | 280.65 | 280.28 | 490.79 | 483.8 | 487.66 | 74.6426 | 65.0707 | 67.9326 | 1.7542 | 1.431 | 1.429 | 1.426 | 2.007 | 2.008 | 2.069 | Over-range | 60 | 19088 | 16079 | 16211 | 51378 | - - - | - - - | - - - | - - - | 19088 | 16079 | 16211 | 51378 | 1966 | 945 | 3852 | 6762 | - - - | - - - | - - - | - - - | 1966 | 945 | 3852 | 6762 | 21082 | 18210 | 18992 | 58284 | # # # | # # # | # # # | # # # | 0.905 | 0.883 | 0.854 | 0.881 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.973 | 0.989 | - - - | 0.132 | 1.62 | 1.58 | 1.6 | 1.54 | 1.56 | 1.61 | 45.78 | 52.89 | 54.84 | 0 | - - - | - - - | - - - | - - - | 21082 | 18210 | 18992 | 58284 | Over-range | 8935 | 8543 | 9886 | 27493 | 8716 | 8491 | 9104 | 26649 | 19039 | 16036 | 16187 | 51262 | 19039 | 16036 | 16187 | 51262 | - - - | - - - | - - - | - - -
5/8/2026 | 7:30:00 AM | 283.45 | 280.79 | 280.64 | 490.91 | 484.3 | 488.14 | 73.5388 | 64.4488 | 67.6858 | 1.723 | 1.432 | 1.43 | 1.426 | 2.014 | 1.988 | 2.05 | Over-range | 60.02 | 18819 | 15931 | 16233 | 50982 | - - - | - - - | - - - | - - - | 18819 | 15931 | 16233 | 50982 | 1873 | 1078 | 3756 | 6707 | - - - | - - - | - - - | - - - | 1873 | 1078 | 3756 | 6707 | 20780 | 18041 | 18949 | 57770 | # # # | # # # | # # # | # # # | 0.906 | 0.883 | 0.857 | 0.882 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.974 | 0.989 | - - - | 0.132 | 1.67 | 1.59 | 1.62 | 1.57 | 1.59 | 1.64 | 45.77 | 52.86 | 54.29 | 0 | - - - | - - - | - - - | - - - | 20780 | 18041 | 18949 | 57770 | Over-range | 8799 | 8463 | 9769 | 27148 | 8597 | 8394 | 9018 | 26306 | 18805 | 15857 | 16208 | 50869 | 18805 | 15857 | 16208 | 50869 | - - - | - - - | - - - | - - -
5/8/2026 | 7:45:00 AM | 283.23 | 280.62 | 280.45 | 490.56 | 484.02 | 487.77 | 73.2876 | 64.3819 | 67.2565 | 1.7186 | 1.432 | 1.43 | 1.426 | 2.014 | 2 | 2.057 | Over-range | 60.01 | 18696 | 15885 | 16071 | 50652 | - - - | - - - | - - - | - - - | 18696 | 15885 | 16071 | 50652 | 1933 | 1060 | 3719 | 6711 | - - - | - - - | - - - | - - - | 1933 | 1060 | 3719 | 6711 | 20688 | 18008 | 18808 | 57504 | # # # | # # # | # # # | # # # | 0.904 | 0.882 | 0.855 | 0.881 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.974 | 0.989 | - - - | 0.133 | 1.65 | 1.59 | 1.61 | 1.55 | 1.58 | 1.63 | 46.29 | 53.09 | 54.99 | 0 | - - - | - - - | - - - | - - - | 20688 | 18008 | 18808 | 57504 | Over-range | 8848 | 8479 | 9765 | 27205 | 8634 | 8412 | 9029 | 26364 | 18683 | 15842 | 16007 | 50532 | 18683 | 15842 | 16007 | 50532 | - - - | - - - | - - - | - - -
5/8/2026 | 8:00:00 AM | 282.98 | 280.24 | 280.16 | 490.01 | 483.39 | 487.36 | 74.0839 | 64.7038 | 68.1906 | 1.7819 | 1.433 | 1.431 | 1.427 | 2.028 | 2.005 | 2.067 | Over-range | 60.02 | 18834 | 15890 | 16223 | 50946 | - - - | - - - | - - - | - - - | 18834 | 15890 | 16223 | 50946 | 1879 | 1092 | 3855 | 6826 | - - - | - - - | - - - | - - - | 1879 | 1092 | 3855 | 6826 | 20891 | 18073 | 19052 | 58016 | # # # | # # # | # # # | # # # | 0.902 | 0.879 | 0.852 | 0.878 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.973 | 0.989 | - - - | 0.134 | 1.67 | 1.6 | 1.63 | 1.57 | 1.6 | 1.65 | 47.06 | 53.72 | 55.49 | 0 | - - - | - - - | - - - | - - - | 20891 | 18073 | 19052 | 58016 | Over-range | 9029 | 8605 | 9983 | 27732 | 8830 | 8535 | 9208 | 26879 | 18765 | 15884 | 16176 | 50825 | 18765 | 15884 | 16176 | 50825 | - - - | - - - | - - - | - - -
5/8/2026 | 8:15:00 AM | 282.44 | 279.7 | 279.54 | 489.1 | 482.35 | 486.33 | 76.2691 | 66.5081 | 69.87 | 1.8341 | 1.434 | 1.432 | 1.428 | 2.023 | 2.019 | 2.076 | Over-range | 60.01 | 19317 | 16280 | 16542 | 52139 | - - - | - - - | - - - | - - - | 19317 | 16280 | 16542 | 52139 | 1990 | 1099 | 3969 | 7058 | - - - | - - - | - - - | - - - | 1990 | 1099 | 3969 | 7058 | 21467 | 18540 | 19473 | 59481 | # # # | # # # | # # # | # # # | 0.9 | 0.878 | 0.85 | 0.877 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.972 | 0.988 | - - - | 0.135 | 1.66 | 1.62 | 1.64 | 1.57 | 1.61 | 1.65 | 47.41 | 54.13 | 55.98 | 0 | - - - | - - - | - - - | - - - | 21467 | 18540 | 19473 | 59481 | Over-range | 9349 | 8865 | 10266 | 28599 | 9134 | 8797 | 9468 | 27714 | 19276 | 16253 | 16470 | 51999 | 19276 | 16253 | 16470 | 51999 | - - - | - - - | - - - | - - -
5/8/2026 | 8:30:00 AM | 282.55 | 279.73 | 279.65 | 489.21 | 482.45 | 486.59 | 79.8209 | 69.3491 | 73.2393 | 1.905 | 1.435 | 1.433 | 1.428 | 2.032 | 2.033 | 2.088 | Over-range | 60.01 | 20183 | 16956 | 17307 | 54446 | - - - | - - - | - - - | - - - | 20183 | 16956 | 17307 | 54446 | 2097 | 1190 | 4220 | 7507 | - - - | - - - | - - - | - - - | 2097 | 1190 | 4220 | 7507 | 22507 | 19363 | 20444 | 62313 | # # # | # # # | # # # | # # # | 0.897 | 0.876 | 0.847 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.971 | 0.988 | - - - | 0.138 | 1.68 | 1.64 | 1.66 | 1.59 | 1.62 | 1.67 | 48.45 | 54.86 | 56.62 | 0 | - - - | - - - | - - - | - - - | 22507 | 19363 | 20444 | 62313 | Over-range | 9952 | 9345 | 10876 | 30290 | 9728 | 9268 | 10024 | 29345 | 20117 | 16911 | 17268 | 54295 | 20117 | 16911 | 17268 | 54295 | - - - | - - - | - - - | - - -
5/8/2026 | 8:45:00 AM | 282.46 | 279.7 | 279.57 | 489.12 | 482.38 | 486.4 | 76.0518 | 66.3562 | 69.8808 | 1.8391 | 1.434 | 1.433 | 1.428 | 2.015 | 2.001 | 2.061 | Over-range | 60.01 | 19334 | 16297 | 16622 | 52253 | - - - | - - - | - - - | - - - | 19334 | 16297 | 16622 | 52253 | 1943 | 1109 | 3950 | 7002 | - - - | - - - | - - - | - - - | 1943 | 1109 | 3950 | 7002 | 21410 | 18498 | 19481 | 59389 | # # # | # # # | # # # | # # # | 0.903 | 0.881 | 0.853 | 0.88 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.973 | 0.989 | - - - | 0.134 | 1.67 | 1.63 | 1.65 | 1.59 | 1.62 | 1.67 | 46.61 | 53.44 | 55.04 | 0 | - - - | - - - | - - - | - - - | 21410 | 18498 | 19481 | 59389 | Over-range | 9184 | 8747 | 10152 | 28202 | 8976 | 8676 | 9351 | 27319 | 19289 | 16243 | 16581 | 52113 | 19289 | 16243 | 16581 | 52113 | - - - | - - - | - - - | - - -
5/8/2026 | 9:00:00 AM | 282.13 | 279.26 | 279.13 | 488.48 | 481.56 | 485.77 | 78.038 | 67.5301 | 71.4842 | 1.8398 | 1.435 | 1.433 | 1.428 | 2.026 | 2.017 | 2.083 | Over-range | 60.01 | 19764 | 16514 | 16883 | 53161 | - - - | - - - | - - - | - - - | 19764 | 16514 | 16883 | 53161 | 1991 | 1089 | 4137 | 7217 | - - - | - - - | - - - | - - - | 1991 | 1089 | 4137 | 7217 | 21948 | 18805 | 19901 | 60655 | # # # | # # # | # # # | # # # | 0.901 | 0.878 | 0.848 | 0.876 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.971 | 0.988 | - - - | 0.136 | 1.68 | 1.63 | 1.66 | 1.59 | 1.61 | 1.67 | 47.42 | 54.22 | 56.05 | 0 | - - - | - - - | - - - | - - - | 21948 | 18805 | 19901 | 60655 | Over-range | 9534 | 8990 | 10530 | 29182 | 9323 | 8923 | 9683 | 28276 | 19688 | 16484 | 16837 | 53009 | 19688 | 16484 | 16837 | 53009 | - - - | - - - | - - - | - - -
5/8/2026 | 9:15:00 AM | 281.68 | 278.72 | 278.67 | 487.6 | 480.66 | 485.03 | 80.3697 | 69.4721 | 73.6667 | 1.893 | 1.436 | 1.434 | 1.429 | 2.033 | 2.03 | 2.092 | Over-range | 60 | 20273 | 16925 | 17329 | 54528 | - - - | - - - | - - - | - - - | 20273 | 16925 | 17329 | 54528 | 2071 | 1169 | 4288 | 7528 | - - - | - - - | - - - | - - - | 2071 | 1169 | 4288 | 7528 | 22585 | 19322 | 20487 | 62394 | # # # | # # # | # # # | # # # | 0.898 | 0.876 | 0.846 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.971 | 0.988 | - - - | 0.138 | 1.69 | 1.62 | 1.66 | 1.58 | 1.62 | 1.67 | 48.31 | 54.84 | 56.66 | 0 | - - - | - - - | - - - | - - - | 22585 | 19322 | 20487 | 62394 | Over-range | 9944 | 9317 | 10922 | 30310 | 9726 | 9243 | 10045 | 29360 | 20193 | 16897 | 17280 | 54369 | 20193 | 16897 | 17280 | 54369 | - - - | - - - | - - - | - - -
5/8/2026 | 9:30:00 AM | 281.79 | 278.76 | 278.78 | 487.71 | 480.76 | 485.26 | 77.4327 | 67.031 | 71.4323 | 1.8308 | 1.435 | 1.434 | 1.429 | 2.024 | 1.996 | 2.064 | Over-range | 60 | 19637 | 16395 | 16927 | 52959 | - - - | - - - | - - - | - - - | 19637 | 16395 | 16927 | 52959 | 1884 | 1172 | 4097 | 7152 | - - - | - - - | - - - | - - - | 1884 | 1172 | 4097 | 7152 | 21747 | 18626 | 19857 | 60230 | # # # | # # # | # # # | # # # | 0.903 | 0.88 | 0.852 | 0.879 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.972 | 0.988 | - - - | 0.135 | 1.69 | 1.67 | 1.68 | 1.61 | 1.65 | 1.69 | 46.84 | 53.65 | 55.09 | 0 | - - - | - - - | - - - | - - - | 21747 | 18626 | 19857 | 60230 | Over-range | 9331 | 8834 | 10376 | 28666 | 9139 | 8756 | 9533 | 27760 | 19573 | 16353 | 16872 | 52797 | 19573 | 16353 | 16872 | 52797 | - - - | - - - | - - - | - - -
5/8/2026 | 9:45:00 AM | 282.57 | 279.48 | 279.57 | 488.99 | 482.05 | 486.65 | 81.7799 | 70.4186 | 75.3567 | 1.918 | 1.436 | 1.435 | 1.43 | 2.048 | 2.035 | 2.097 | Over-range | 60.01 | 20668 | 17156 | 17762 | 55586 | - - - | - - - | - - - | - - - | 20668 | 17156 | 17762 | 55586 | 2048 | 1271 | 4450 | 7770 | - - - | - - - | - - - | - - - | 2048 | 1271 | 4450 | 7770 | 23064 | 19647 | 21031 | 63742 | # # # | # # # | # # # | # # # | 0.896 | 0.873 | 0.845 | 0.872 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.988 | - - - | 0.14 | 1.69 | 1.66 | 1.7 | 1.61 | 1.66 | 1.69 | 48.86 | 55.55 | 56.92 | 0 | - - - | - - - | - - - | - - - | 23064 | 19647 | 21031 | 63742 | Over-range | 10226 | 9570 | 11257 | 31180 | 10019 | 9485 | 10340 | 30196 | 20588 | 17117 | 17705 | 55409 | 20588 | 17117 | 17705 | 55409 | - - - | - - - | - - - | - - -
5/8/2026 | 10:00:00 AM | 282.4 | 279.37 | 279.39 | 488.77 | 481.83 | 486.31 | 80.1126 | 69.3737 | 73.8282 | 1.8781 | 1.436 | 1.434 | 1.43 | 2.034 | 2.016 | 2.078 | Over-range | 60.01 | 20282 | 16941 | 17462 | 54685 | - - - | - - - | - - - | - - - | 20282 | 16941 | 17462 | 54685 | 2023 | 1237 | 4282 | 7542 | - - - | - - - | - - - | - - - | 2023 | 1237 | 4282 | 7542 | 22558 | 19327 | 20576 | 62461 | # # # | # # # | # # # | # # # | 0.899 | 0.877 | 0.849 | 0.875 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.138 | 1.68 | 1.64 | 1.68 | 1.59 | 1.64 | 1.67 | 47.95 | 54.63 | 55.96 | 0 | - - - | - - - | - - - | - - - | 22558 | 19327 | 20576 | 62461 | Over-range | 9863 | 9298 | 10878 | 30162 | 9653 | 9215 | 10000 | 29204 | 20197 | 16890 | 17435 | 54522 | 20197 | 16890 | 17435 | 54522 | - - - | - - - | - - - | - - -
5/8/2026 | 10:15:00 AM | 282.04 | 278.83 | 278.94 | 487.99 | 480.89 | 485.68 | 82.9749 | 71.2135 | 76.6357 | 1.9378 | 1.437 | 1.435 | 1.43 | 2.046 | 2.022 | 2.091 | Over-range | 60.01 | 20971 | 17346 | 18063 | 56381 | - - - | - - - | - - - | - - - | 20971 | 17346 | 18063 | 56381 | 2008 | 1306 | 4522 | 7837 | - - - | - - - | - - - | - - - | 2008 | 1306 | 4522 | 7837 | 23347 | 19816 | 21335 | 64499 | # # # | # # # | # # # | # # # | 0.898 | 0.875 | 0.847 | 0.874 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.97 | 0.988 | - - - | 0.139 | 1.69 | 1.66 | 1.68 | 1.6 | 1.65 | 1.68 | 48.31 | 54.95 | 56.31 | 0 | - - - | - - - | - - - | - - - | 23347 | 19816 | 21335 | 64499 | Over-range | 10253 | 9577 | 11347 | 31307 | 10054 | 9488 | 10406 | 30311 | 20896 | 17307 | 17999 | 56203 | 20896 | 17307 | 17999 | 56203 | - - - | - - - | - - - | - - -
5/8/2026 | 10:30:00 AM | 282.03 | 278.93 | 278.94 | 488.08 | 481.01 | 485.62 | 82.9475 | 71.558 | 76.3038 | 1.9693 | 1.436 | 1.435 | 1.431 | 2.03 | 2.018 | 2.08 | Over-range | 60.01 | 20997 | 17488 | 18032 | 56517 | - - - | - - - | - - - | - - - | 20997 | 17488 | 18032 | 56517 | 2088 | 1266 | 4456 | 7810 | - - - | - - - | - - - | - - - | 2088 | 1266 | 4456 | 7810 | 23337 | 19915 | 21239 | 64491 | # # # | # # # | # # # | # # # | 0.9 | 0.878 | 0.849 | 0.876 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.138 | 1.69 | 1.67 | 1.71 | 1.61 | 1.66 | 1.7 | 47.76 | 54.21 | 55.8 | 0 | - - - | - - - | - - - | - - - | 23337 | 19915 | 21239 | 64491 | Over-range | 10173 | 9524 | 11215 | 31041 | 9957 | 9439 | 10291 | 30043 | 20924 | 17439 | 17986 | 56348 | 20924 | 17439 | 17986 | 56348 | - - - | - - - | - - - | - - -
5/8/2026 | 10:45:00 AM | 281.58 | 278.39 | 278.52 | 487.19 | 480.16 | 484.94 | 85.1473 | 73.4939 | 78.7847 | 1.9779 | 1.437 | 1.436 | 1.431 | 2.028 | 2.002 | 2.068 | Over-range | 60 | 21557 | 17967 | 18659 | 58183 | - - - | - - - | - - - | - - - | 21557 | 17967 | 18659 | 58183 | 2086 | 1375 | 4556 | 8017 | - - - | - - - | - - - | - - - | 2086 | 1375 | 4556 | 8017 | 23925 | 20420 | 21904 | 66248 | # # # | # # # | # # # | # # # | 0.901 | 0.88 | 0.852 | 0.878 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.138 | 1.72 | 1.69 | 1.72 | 1.63 | 1.68 | 1.72 | 47.52 | 53.7 | 55.18 | 0 | - - - | - - - | - - - | - - - | 23925 | 20420 | 21904 | 66248 | Over-range | 10369 | 9699 | 11466 | 31661 | 10156 | 9601 | 10522 | 30630 | 21469 | 17920 | 18614 | 58003 | 21469 | 17920 | 18614 | 58003 | - - - | - - - | - - - | - - -
5/8/2026 | 11:00:00 AM | 281.57 | 278.37 | 278.53 | 487.16 | 480.16 | 484.94 | 87.1655 | 75.3016 | 80.6858 | 2.0369 | 1.438 | 1.436 | 1.432 | 2.025 | 2.004 | 2.067 | Over-range | 60 | 22076 | 18432 | 19130 | 59638 | - - - | - - - | - - - | - - - | 22076 | 18432 | 19130 | 59638 | 2157 | 1431 | 4658 | 8247 | - - - | - - - | - - - | - - - | 2157 | 1431 | 4658 | 8247 | 24506 | 20933 | 22444 | 67883 | # # # | # # # | # # # | # # # | 0.901 | 0.88 | 0.852 | 0.878 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.971 | 0.988 | - - - | 0.138 | 1.72 | 1.69 | 1.72 | 1.63 | 1.69 | 1.72 | 47.56 | 53.57 | 55.16 | 0 | - - - | - - - | - - - | - - - | 24506 | 20933 | 22444 | 67883 | Over-range | 10631 | 9921 | 11733 | 32411 | 10409 | 9817 | 10768 | 31345 | 22007 | 18381 | 19064 | 59452 | 22007 | 18381 | 19064 | 59452 | - - - | - - - | - - - | - - -
5/8/2026 | 11:15:00 AM | 281.49 | 278.28 | 278.41 | 487.02 | 479.96 | 484.77 | 85.8633 | 74.369 | 79.6239 | 1.9916 | 1.437 | 1.436 | 1.431 | 2.011 | 1.979 | 2.047 | Over-range | 60 | 21817 | 18262 | 18963 | 59042 | - - - | - - - | - - - | - - - | 21817 | 18262 | 18963 | 59042 | 2075 | 1404 | 4519 | 7998 | - - - | - - - | - - - | - - - | 2075 | 1404 | 4519 | 7998 | 24109 | 20649 | 22121 | 66879 | # # # | # # # | # # # | # # # | 0.905 | 0.884 | 0.857 | 0.883 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.988 | - - - | 0.136 | 1.7 | 1.69 | 1.72 | 1.63 | 1.68 | 1.71 | 46.35 | 52.46 | 54 | 0 | - - - | - - - | - - - | - - - | 24109 | 20649 | 22121 | 66879 | Over-range | 10248 | 9633 | 11382 | 31390 | 10036 | 9529 | 10446 | 30354 | 21756 | 18204 | 18903 | 58863 | 21756 | 18204 | 18903 | 58863 | - - - | - - - | - - - | - - -
5/8/2026 | 11:30:00 AM | 281.3 | 278.19 | 278.29 | 486.76 | 479.83 | 484.47 | 88.6149 | 77.1366 | 82.0174 | 2.0772 | 1.438 | 1.436 | 1.432 | 2.01 | 1.995 | 2.053 | Over-range | 60 | 22437 | 18915 | 19493 | 60845 | - - - | - - - | - - - | - - - | 22437 | 18915 | 19493 | 60845 | 2259 | 1488 | 4639 | 8386 | - - - | - - - | - - - | - - - | 2259 | 1488 | 4639 | 8386 | 24889 | 21430 | 22795 | 69114 | # # # | # # # | # # # | # # # | 0.902 | 0.883 | 0.855 | 0.88 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.988 | - - - | 0.138 | 1.71 | 1.69 | 1.73 | 1.63 | 1.69 | 1.72 | 47.34 | 52.91 | 54.67 | 0 | - - - | - - - | - - - | - - - | 24889 | 21430 | 22795 | 69114 | Over-range | 10767 | 10070 | 11811 | 32768 | 10527 | 9959 | 10862 | 31677 | 22351 | 18876 | 19433 | 60659 | 22351 | 18876 | 19433 | 60659 | - - - | - - - | - - - | - - -
5/8/2026 | 11:45:00 AM | 281.18 | 277.98 | 278.19 | 486.45 | 479.53 | 484.33 | 88.273 | 76.5564 | 82.0072 | 2.0673 | 1.438 | 1.436 | 1.432 | 2.014 | 1.986 | 2.05 | Over-range | 60 | 22370 | 18765 | 19507 | 60641 | - - - | - - - | - - - | - - - | 22370 | 18765 | 19507 | 60641 | 2154 | 1506 | 4655 | 8315 | - - - | - - - | - - - | - - - | 2154 | 1506 | 4655 | 8315 | 24780 | 21249 | 22780 | 68809 | # # # | # # # | # # # | # # # | 0.903 | 0.883 | 0.856 | 0.881 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.988 | - - - | 0.137 | 1.72 | 1.69 | 1.73 | 1.63 | 1.69 | 1.73 | 47.02 | 52.79 | 54.3 | 0 | - - - | - - - | - - - | - - - | 24780 | 21249 | 22780 | 68809 | Over-range | 10652 | 9968 | 11761 | 32503 | 10431 | 9853 | 10801 | 31421 | 22296 | 18712 | 19454 | 60462 | 22296 | 18712 | 19454 | 60462 | - - - | - - - | - - - | - - -
5/8/2026 | 12:00:00 PM | 280.82 | 277.59 | 277.9 | 485.75 | 478.96 | 483.81 | 87.7555 | 76.1243 | 81.9192 | 2.0174 | 1.437 | 1.435 | 1.432 | 2.014 | 1.97 | 2.039 | Over-range | 60 | 22229 | 18645 | 19507 | 60381 | - - - | - - - | - - - | - - - | 22229 | 18645 | 19507 | 60381 | 2059 | 1544 | 4602 | 8204 | - - - | - - - | - - - | - - - | 2059 | 1544 | 4602 | 8204 | 24585 | 21088 | 22719 | 68393 | # # # | # # # | # # # | # # # | 0.904 | 0.884 | 0.859 | 0.883 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.989 | - - - | 0.136 | 1.7 | 1.68 | 1.74 | 1.62 | 1.69 | 1.72 | 46.62 | 52.33 | 53.69 | 0 | - - - | - - - | - - - | - - - | 24585 | 21088 | 22719 | 68393 | Over-range | 10490 | 9848 | 11638 | 32095 | 10286 | 9726 | 10689 | 31029 | 22151 | 18603 | 19454 | 60208 | 22151 | 18603 | 19454 | 60208 | - - - | - - - | - - - | - - -
5/8/2026 | 12:15:00 PM | 280.74 | 277.59 | 277.83 | 485.69 | 478.92 | 483.64 | 89.0094 | 77.3625 | 82.8346 | 2.0603 | 1.438 | 1.436 | 1.432 | 2.014 | 1.983 | 2.047 | Over-range | 59.99 | 22517 | 18938 | 19687 | 61142 | - - - | - - - | - - - | - - - | 22517 | 18938 | 19687 | 61142 | 2178 | 1550 | 4663 | 8391 | - - - | - - - | - - - | - - - | 2178 | 1550 | 4663 | 8391 | 24952 | 21447 | 22985 | 69384 | # # # | # # # | # # # | # # # | 0.902 | 0.883 | 0.857 | 0.881 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.988 | - - - | 0.137 | 1.71 | 1.69 | 1.73 | 1.63 | 1.69 | 1.73 | 47.11 | 52.74 | 54.31 | 0 | - - - | - - - | - - - | - - - | 24952 | 21447 | 22985 | 69384 | Over-range | 10744 | 10062 | 11859 | 32785 | 10521 | 9942 | 10903 | 31693 | 22444 | 18893 | 19630 | 60966 | 22444 | 18893 | 19630 | 60966 | - - - | - - - | - - - | - - -
5/8/2026 | 12:30:00 PM | 280.9 | 277.66 | 277.91 | 485.91 | 479.01 | 483.86 | 88.0596 | 76.2796 | 82.0357 | 2.0368 | 1.438 | 1.436 | 1.432 | 2.015 | 1.976 | 2.046 | Over-range | 59.98 | 22311 | 18683 | 19510 | 60503 | - - - | - - - | - - - | - - - | 22311 | 18683 | 19510 | 60503 | 2085 | 1510 | 4640 | 8236 | - - - | - - - | - - - | - - - | 2085 | 1510 | 4640 | 8236 | 24687 | 21143 | 22760 | 68591 | # # # | # # # | # # # | # # # | 0.904 | 0.884 | 0.857 | 0.882 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.973 | 0.988 | - - - | 0.136 | 1.71 | 1.69 | 1.73 | 1.62 | 1.69 | 1.72 | 46.74 | 52.56 | 54.02 | 0 | - - - | - - - | - - - | - - - | 24687 | 21143 | 22760 | 68591 | Over-range | 10557 | 9895 | 11716 | 32293 | 10349 | 9779 | 10758 | 31225 | 22232 | 18638 | 19466 | 60336 | 22232 | 18638 | 19466 | 60336 | - - - | - - - | - - - | - - -
5/8/2026 | 12:45:00 PM | 281.02 | 277.9 | 278.06 | 486.24 | 479.38 | 484.04 | 88.8786 | 77.2652 | 82.5318 | 2.124 | 1.438 | 1.436 | 1.432 | 2.009 | 1.981 | 2.047 | Over-range | 59.99 | 22511 | 18947 | 19628 | 61087 | - - - | - - - | - - - | - - - | 22511 | 18947 | 19628 | 61087 | 2186 | 1519 | 4654 | 8359 | - - - | - - - | - - - | - - - | 2186 | 1519 | 4654 | 8359 | 24931 | 21439 | 22913 | 69284 | # # # | # # # | # # # | # # # | 0.903 | 0.884 | 0.857 | 0.882 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.973 | 0.988 | - - - | 0.137 | 1.72 | 1.69 | 1.73 | 1.63 | 1.69 | 1.73 | 46.87 | 52.53 | 54.21 | 0 | - - - | - - - | - - - | - - - | 24931 | 21439 | 22913 | 69284 | Over-range | 10705 | 10027 | 11814 | 32668 | 10479 | 9911 | 10858 | 31581 | 22443 | 18898 | 19568 | 60909 | 22443 | 18898 | 19568 | 60909 | - - - | - - - | - - - | - - -
5/8/2026 | 1:00:00 PM | 280.89 | 277.88 | 278.09 | 486.04 | 479.46 | 483.93 | 90.4417 | 79.2948 | 84.4242 | 2.1376 | 1.438 | 1.436 | 1.433 | 2.007 | 1.975 | 2.035 | Over-range | 59.98 | 22894 | 19467 | 20148 | 62510 | - - - | - - - | - - - | - - - | 22894 | 19467 | 20148 | 62510 | 2262 | 1667 | 4646 | 8574 | - - - | - - - | - - - | - - - | 2262 | 1667 | 4646 | 8574 | 25370 | 22008 | 23448 | 70826 | # # # | # # # | # # # | # # # | 0.902 | 0.884 | 0.859 | 0.883 | # # # | # # # | # # # | - - - | 0.995 | 0.996 | 0.974 | 0.989 | - - - | 0.137 | 1.7 | 1.7 | 1.74 | 1.64 | 1.69 | 1.73 | 47.05 | 52.26 | 53.9 | 0 | - - - | - - - | - - - | - - - | 25370 | 22008 | 23448 | 70826 | Over-range | 10925 | 10263 | 11989 | 33287 | 10688 | 10127 | 11052 | 32163 | 22828 | 19412 | 20090 | 62330 | 22828 | 19412 | 20090 | 62330 | - - - | - - - | - - - | - - -
5/8/2026 | 1:15:00 PM | 280.84 | 277.82 | 277.94 | 486.01 | 479.27 | 483.73 | 89.4676 | 78.312 | 83.2319 | 2.1623 | 1.438 | 1.436 | 1.432 | 1.997 | 1.967 | 2.03 | Over-range | 59.97 | 22696 | 19264 | 19881 | 61842 | - - - | - - - | - - - | - - - | 22696 | 19264 | 19881 | 61842 | 2222 | 1566 | 4593 | 8381 | - - - | - - - | - - - | - - - | 2222 | 1566 | 4593 | 8381 | 25076 | 21719 | 23094 | 69890 | # # # | # # # | # # # | # # # | 0.905 | 0.887 | 0.861 | 0.885 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.974 | 0.989 | - - - | 0.136 | 1.7 | 1.69 | 1.72 | 1.63 | 1.68 | 1.71 | 46.22 | 51.62 | 53.35 | 0 | - - - | - - - | - - - | - - - | 25076 | 21719 | 23094 | 69890 | Over-range | 10651 | 10026 | 11743 | 32537 | 10416 | 9903 | 10807 | 31439 | 22634 | 19207 | 19828 | 61669 | 22634 | 19207 | 19828 | 61669 | - - - | - - - | - - - | - - -
5/8/2026 | 1:30:00 PM | 280.53 | 277.43 | 277.52 | 485.44 | 478.51 | 483.13 | 92.5824 | 80.8617 | 85.9189 | 2.2336 | 1.438 | 1.437 | 1.433 | 1.994 | 1.971 | 2.034 | Over-range | 59.98 | 23476 | 19894 | 20490 | 63861 | - - - | - - - | - - - | - - - | 23476 | 19894 | 20490 | 63861 | 2325 | 1582 | 4765 | 8672 | - - - | - - - | - - - | - - - | 2325 | 1582 | 4765 | 8672 | 25937 | 22406 | 23816 | 72160 | # # # | # # # | # # # | # # # | 0.905 | 0.888 | 0.86 | 0.885 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.974 | 0.989 | - - - | 0.136 | 1.71 | 1.68 | 1.73 | 1.63 | 1.68 | 1.72 | 46.25 | 51.41 | 53.45 | 0 | - - - | - - - | - - - | - - - | 25937 | 22406 | 23816 | 72160 | Over-range | 11020 | 10306 | 12136 | 33586 | 10772 | 10183 | 11161 | 32447 | 23403 | 19842 | 20440 | 63685 | 23403 | 19842 | 20440 | 63685 | - - - | - - - | - - - | - - -
5/8/2026 | 1:45:00 PM | 280.23 | 277.1 | 277.24 | 484.87 | 477.97 | 482.64 | 93.0161 | 81.1306 | 86.4543 | 2.1604 | 1.439 | 1.437 | 1.433 | 1.996 | 1.97 | 2.034 | Over-range | 59.98 | 23561 | 19932 | 20599 | 64092 | - - - | - - - | - - - | - - - | 23561 | 19932 | 20599 | 64092 | 2311 | 1599 | 4788 | 8698 | - - - | - - - | - - - | - - - | 2311 | 1599 | 4788 | 8698 | 26034 | 22458 | 23943 | 72435 | # # # | # # # | # # # | # # # | 0.905 | 0.888 | 0.86 | 0.885 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.974 | 0.989 | - - - | 0.136 | 1.71 | 1.68 | 1.72 | 1.62 | 1.68 | 1.72 | 46.29 | 51.48 | 53.46 | 0 | - - - | - - - | - - - | - - - | 26034 | 22458 | 23943 | 72435 | Over-range | 11069 | 10343 | 12199 | 33735 | 10824 | 10219 | 11221 | 32594 | 23485 | 19890 | 20543 | 63917 | 23485 | 19890 | 20543 | 63917 | - - - | - - - | - - - | - - -
5/8/2026 | 2:00:00 PM | 280.11 | 276.97 | 277.03 | 484.71 | 477.65 | 482.34 | 95.0902 | 83.4679 | 88.2535 | 2.3123 | 1.438 | 1.437 | 1.433 | 1.964 | 1.942 | 2.004 | Over-range | 59.99 | 24218 | 20664 | 21210 | 66092 | - - - | - - - | - - - | - - - | 24218 | 20664 | 21210 | 66092 | 2349 | 1615 | 4748 | 8712 | - - - | - - - | - - - | - - - | 2349 | 1615 | 4748 | 8712 | 26586 | 23082 | 24412 | 74080 | # # # | # # # | # # # | # # # | 0.911 | 0.895 | 0.869 | 0.892 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.989 | - - - | 0.132 | 1.71 | 1.69 | 1.72 | 1.62 | 1.68 | 1.72 | 44.47 | 49.32 | 51.44 | 0 | - - - | - - - | - - - | - - - | 26586 | 23082 | 24412 | 74080 | Over-range | 10959 | 10281 | 12078 | 33441 | 10704 | 10153 | 11106 | 32286 | 24162 | 20615 | 21151 | 65928 | 24162 | 20615 | 21151 | 65928 | - - - | - - - | - - - | - - -
5/8/2026 | 2:15:00 PM | 280.25 | 277.18 | 277.28 | 484.95 | 478.1 | 482.67 | 96.3 | 84.8587 | 89.6757 | 2.3625 | 1.438 | 1.437 | 1.433 | 1.967 | 1.938 | 2 | Over-range | 59.97 | 24530 | 21023 | 21588 | 67141 | - - - | - - - | - - - | - - - | 24530 | 21023 | 21588 | 67141 | 2396 | 1708 | 4789 | 8893 | - - - | - - - | - - - | - - - | 2396 | 1708 | 4789 | 8893 | 26951 | 23493 | 24838 | 75283 | # # # | # # # | # # # | # # # | 0.91 | 0.895 | 0.869 | 0.892 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.989 | - - - | 0.133 | 1.72 | 1.7 | 1.72 | 1.63 | 1.68 | 1.73 | 44.74 | 49.38 | 51.51 | 0 | - - - | - - - | - - - | - - - | 26951 | 23493 | 24838 | 75283 | Over-range | 11156 | 10483 | 12279 | 34037 | 10896 | 10343 | 11306 | 32855 | 24464 | 20980 | 21526 | 66969 | 24464 | 20980 | 21526 | 66969 | - - - | - - - | - - - | - - -
5/8/2026 | 2:30:00 PM | 280.13 | 277.13 | 277.22 | 484.79 | 478.04 | 482.49 | 97.1761 | 85.8035 | 90.3703 | 2.3439 | 1.439 | 1.437 | 1.434 | 1.964 | 1.942 | 2 | Over-range | 59.98 | 24732 | 21256 | 21750 | 67739 | - - - | - - - | - - - | - - - | 24732 | 21256 | 21750 | 67739 | 2488 | 1709 | 4811 | 9008 | - - - | - - - | - - - | - - - | 2488 | 1709 | 4811 | 9008 | 27190 | 23755 | 25029 | 75974 | # # # | # # # | # # # | # # # | 0.91 | 0.895 | 0.869 | 0.892 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.989 | - - - | 0.133 | 1.72 | 1.7 | 1.75 | 1.64 | 1.69 | 1.74 | 44.86 | 49.42 | 51.61 | 0 | - - - | - - - | - - - | - - - | 27190 | 23755 | 25029 | 75974 | Over-range | 11289 | 10603 | 12380 | 34389 | 11012 | 10464 | 11407 | 33188 | 24660 | 21211 | 21692 | 67563 | 24660 | 21211 | 21692 | 67563 | - - - | - - - | - - - | - - -
5/8/2026 | 2:45:00 PM | 279.82 | 276.71 | 276.82 | 484.19 | 477.27 | 481.92 | 97.8939 | 86.0783 | 91.1473 | 2.3732 | 1.438 | 1.437 | 1.433 | 1.97 | 1.941 | 2.005 | Over-range | 59.97 | 24882 | 21274 | 21868 | 68024 | - - - | - - - | - - - | - - - | 24882 | 21274 | 21868 | 68024 | 2450 | 1723 | 4902 | 9075 | - - - | - - - | - - - | - - - | 2450 | 1723 | 4902 | 9075 | 27364 | 23796 | 25208 | 76369 | # # # | # # # | # # # | # # # | 0.909 | 0.894 | 0.868 | 0.891 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.989 | - - - | 0.133 | 1.72 | 1.69 | 1.73 | 1.63 | 1.69 | 1.73 | 45.01 | 49.66 | 51.85 | 0 | - - - | - - - | - - - | - - - | 27364 | 23796 | 25208 | 76369 | Over-range | 11381 | 10660 | 12536 | 34700 | 11113 | 10520 | 11538 | 33492 | 24807 | 21228 | 21815 | 67851 | 24807 | 21228 | 21815 | 67851 | - - - | - - - | - - - | - - -
5/8/2026 | 3:00:00 PM | 279.93 | 276.86 | 276.96 | 484.41 | 477.55 | 482.12 | 97.3843 | 85.817 | 90.704 | 2.3607 | 1.438 | 1.437 | 1.434 | 1.964 | 1.934 | 1.997 | Over-range | 59.98 | 24782 | 21237 | 21802 | 67821 | - - - | - - - | - - - | - - - | 24782 | 21237 | 21802 | 67821 | 2450 | 1719 | 4850 | 9020 | - - - | - - - | - - - | - - - | 2450 | 1719 | 4850 | 9020 | 27220 | 23728 | 25090 | 76039 | # # # | # # # | # # # | # # # | 0.91 | 0.895 | 0.869 | 0.892 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.989 | - - - | 0.133 | 1.72 | 1.72 | 1.75 | 1.65 | 1.71 | 1.75 | 44.64 | 49.32 | 51.53 | 0 | - - - | - - - | - - - | - - - | 27220 | 23728 | 25090 | 76039 | Over-range | 11253 | 10580 | 12411 | 34366 | 10982 | 10439 | 11423 | 33162 | 24709 | 21192 | 21750 | 67650 | 24709 | 21192 | 21750 | 67650 | - - - | - - - | - - - | - - -
5/8/2026 | 3:15:00 PM | 280.15 | 277.2 | 277.24 | 484.88 | 478.14 | 482.5 | 97.6075 | 86.2485 | 90.8365 | 2.3179 | 1.439 | 1.438 | 1.434 | 1.958 | 1.932 | 1.992 | Over-range | 59.99 | 24854 | 21377 | 21867 | 68098 | - - - | - - - | - - - | - - - | 24854 | 21377 | 21867 | 68098 | 2506 | 1725 | 4822 | 9053 | - - - | - - - | - - - | - - - | 2506 | 1725 | 4822 | 9053 | 27294 | 23871 | 25145 | 76310 | # # # | # # # | # # # | # # # | 0.911 | 0.896 | 0.87 | 0.892 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.989 | - - - | 0.133 | 1.74 | 1.72 | 1.76 | 1.66 | 1.71 | 1.76 | 44.5 | 49.17 | 51.37 | 0 | - - - | - - - | - - - | - - - | 27294 | 23871 | 25145 | 76310 | Over-range | 11271 | 10618 | 12405 | 34414 | 10988 | 10477 | 11430 | 33203 | 24788 | 21320 | 21816 | 67924 | 24788 | 21320 | 21816 | 67924 | - - - | - - - | - - - | - - -
5/8/2026 | 3:30:00 PM | 279.95 | 276.89 | 276.95 | 484.46 | 477.56 | 482.12 | 98.401 | 86.6844 | 91.5886 | 2.3511 | 1.438 | 1.437 | 1.434 | 1.963 | 1.933 | 1.998 | Over-range | 59.99 | 25055 | 21463 | 22016 | 68534 | - - - | - - - | - - - | - - - | 25055 | 21463 | 22016 | 68534 | 2487 | 1723 | 4900 | 9110 | - - - | - - - | - - - | - - - | 2487 | 1723 | 4900 | 9110 | 27517 | 23979 | 25344 | 76839 | # # # | # # # | # # # | # # # | 0.911 | 0.895 | 0.869 | 0.892 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.989 | - - - | 0.133 | 1.74 | 1.72 | 1.77 | 1.66 | 1.72 | 1.76 | 44.61 | 49.34 | 51.59 | 0 | - - - | - - - | - - - | - - - | 27517 | 23979 | 25344 | 76839 | Over-range | 11370 | 10690 | 12550 | 34736 | 11095 | 10550 | 11554 | 33520 | 24983 | 21412 | 21967 | 68362 | 24983 | 21412 | 21967 | 68362 | - - - | - - - | - - - | - - -
5/8/2026 | 3:45:00 PM | 280.08 | 277.07 | 277.07 | 484.76 | 477.83 | 482.31 | 99.8237 | 88.0005 | 92.5741 | 2.4129 | 1.439 | 1.438 | 1.434 | 1.956 | 1.936 | 1.998 | Over-range | 59.98 | 25444 | 21836 | 22273 | 69553 | - - - | - - - | - - - | - - - | 25444 | 21836 | 22273 | 69553 | 2582 | 1706 | 4959 | 9248 | - - - | - - - | - - - | - - - | 2582 | 1706 | 4959 | 9248 | 27929 | 24360 | 25627 | 77916 | # # # | # # # | # # # | # # # | 0.911 | 0.896 | 0.869 | 0.893 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.976 | 0.989 | - - - | 0.133 | 1.76 | 1.72 | 1.78 | 1.67 | 1.73 | 1.77 | 44.41 | 49.01 | 51.46 | 0 | - - - | - - - | - - - | - - - | 27929 | 24360 | 25627 | 77916 | Over-range | 11510 | 10796 | 12671 | 35106 | 11216 | 10660 | 11660 | 33866 | 25374 | 21790 | 22216 | 69380 | 25374 | 21790 | 22216 | 69380 | - - - | - - - | - - - | - - -
5/8/2026 | 4:00:00 PM | 280.24 | 277.27 | 277.28 | 485.06 | 478.22 | 482.61 | 99.8873 | 88.3599 | 92.8426 | 2.4365 | 1.438 | 1.437 | 1.434 | 1.956 | 1.933 | 1.994 | Over-range | 59.99 | 25462 | 21938 | 22372 | 69772 | - - - | - - - | - - - | - - - | 25462 | 21938 | 22372 | 69772 | 2587 | 1758 | 4926 | 9270 | - - - | - - - | - - - | - - - | 2587 | 1758 | 4926 | 9270 | 27964 | 24478 | 25721 | 78163 | # # # | # # # | # # # | # # # | 0.911 | 0.896 | 0.87 | 0.893 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.977 | 0.989 | - - - | 0.133 | 1.74 | 1.72 | 1.75 | 1.66 | 1.71 | 1.75 | 44.55 | 49 | 51.42 | 0 | - - - | - - - | - - - | - - - | 27964 | 24478 | 25721 | 78163 | Over-range | 11556 | 10855 | 12688 | 35221 | 11262 | 10711 | 11692 | 33979 | 25388 | 21896 | 22317 | 69600 | 25388 | 21896 | 22317 | 69600 | - - - | - - - | - - - | - - -
5/8/2026 | 4:15:00 PM | 280.35 | 277.53 | 277.49 | 485.36 | 478.68 | 482.83 | 99.9674 | 89.1733 | 92.946 | 2.3948 | 1.439 | 1.438 | 1.434 | 1.933 | 1.913 | 1.967 | Over-range | 59.99 | 25562 | 22248 | 22550 | 70360 | - - - | - - - | - - - | - - - | 25562 | 22248 | 22550 | 70360 | 2637 | 1765 | 4778 | 9180 | - - - | - - - | - - - | - - - | 2637 | 1765 | 4778 | 9180 | 27977 | 24711 | 25756 | 78443 | # # # | # # # | # # # | # # # | 0.914 | 0.9 | 0.875 | 0.897 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.131 | 1.76 | 1.73 | 1.77 | 1.68 | 1.72 | 1.78 | 43.48 | 47.79 | 50.12 | 0 | - - - | - - - | - - - | - - - | 27977 | 24711 | 25756 | 78443 | Over-range | 11361 | 10750 | 12437 | 34663 | 11051 | 10604 | 11482 | 33425 | 25492 | 22201 | 22509 | 70201 | 25492 | 22201 | 22509 | 70201 | - - - | - - - | - - - | - - -
5/8/2026 | 4:30:00 PM | 280.33 | 277.57 | 277.49 | 485.38 | 478.75 | 482.78 | 100.8011 | 89.9507 | 93.5468 | 2.478 | 1.439 | 1.437 | 1.434 | 1.932 | 1.915 | 1.969 | Over-range | 59.98 | 25798 | 22480 | 22710 | 70988 | - - - | - - - | - - - | - - - | 25798 | 22480 | 22710 | 70988 | 2679 | 1747 | 4810 | 9236 | - - - | - - - | - - - | - - - | 2679 | 1747 | 4810 | 9236 | 28224 | 24942 | 25933 | 79098 | # # # | # # # | # # # | # # # | 0.914 | 0.901 | 0.876 | 0.898 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.13 | 1.76 | 1.72 | 1.77 | 1.68 | 1.71 | 1.78 | 43.35 | 47.53 | 50.1 | 0 | - - - | - - - | - - - | - - - | 28224 | 24942 | 25933 | 79098 | Over-range | 11440 | 10800 | 12515 | 34873 | 11121 | 10658 | 11554 | 33627 | 25743 | 22431 | 22654 | 70828 | 25743 | 22431 | 22654 | 70828 | - - - | - - - | - - - | - - -
5/8/2026 | 4:45:00 PM | 280.2 | 277.42 | 277.39 | 485.11 | 478.53 | 482.62 | 102.3736 | 91.3398 | 95.2595 | 2.5105 | 1.44 | 1.438 | 1.434 | 1.931 | 1.91 | 1.965 | Over-range | 59.98 | 26207 | 22829 | 23149 | 72185 | - - - | - - - | - - - | - - - | 26207 | 22829 | 23149 | 72185 | 2678 | 1815 | 4893 | 9386 | - - - | - - - | - - - | - - - | 2678 | 1815 | 4893 | 9386 | 28658 | 25319 | 26402 | 80380 | # # # | # # # | # # # | # # # | 0.915 | 0.902 | 0.877 | 0.898 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.13 | 1.76 | 1.72 | 1.77 | 1.67 | 1.71 | 1.78 | 43.29 | 47.42 | 49.83 | 0 | - - - | - - - | - - - | - - - | 28658 | 25319 | 26402 | 80380 | Over-range | 11590 | 10947 | 12692 | 35345 | 11276 | 10795 | 11710 | 34076 | 26137 | 22784 | 23105 | 72025 | 26137 | 22784 | 23105 | 72025 | - - - | - - - | - - - | - - -
5/8/2026 | 5:00:00 PM | 280.19 | 277.51 | 277.35 | 485.23 | 478.59 | 482.5 | 103.4979 | 92.7581 | 96.0386 | 2.4507 | 1.439 | 1.437 | 1.434 | 1.922 | 1.917 | 1.962 | Over-range | 60 | 26468 | 23191 | 23349 | 73007 | - - - | - - - | - - - | - - - | 26468 | 23191 | 23349 | 73007 | 2818 | 1829 | 4869 | 9516 | - - - | - - - | - - - | - - - | 2818 | 1829 | 4869 | 9516 | 28973 | 25720 | 26616 | 81309 | # # # | # # # | # # # | # # # | 0.914 | 0.902 | 0.877 | 0.898 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.979 | 0.99 | - - - | 0.13 | 1.72 | 1.69 | 1.74 | 1.64 | 1.68 | 1.74 | 43.45 | 47.46 | 49.86 | 0 | - - - | - - - | - - - | - - - | 28973 | 25720 | 26616 | 81309 | Over-range | 11778 | 11121 | 12772 | 35780 | 11436 | 10969 | 11807 | 34491 | 26413 | 23140 | 23288 | 72840 | 26413 | 23140 | 23288 | 72840 | - - - | - - - | - - - | - - -
5/8/2026 | 5:15:00 PM | 280.78 | 278.16 | 278 | 486.29 | 479.76 | 483.55 | 104.1929 | 93.7475 | 96.9183 | 2.5351 | 1.439 | 1.437 | 1.433 | 1.916 | 1.906 | 1.95 | Over-range | 59.99 | 26736 | 23533 | 23685 | 73954 | - - - | - - - | - - - | - - - | 26736 | 23533 | 23685 | 73954 | 2831 | 1897 | 4867 | 9595 | - - - | - - - | - - - | - - - | 2831 | 1897 | 4867 | 9595 | 29225 | 26054 | 26920 | 82198 | # # # | # # # | # # # | # # # | 0.915 | 0.903 | 0.88 | 0.9 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.979 | 0.99 | - - - | 0.13 | 1.72 | 1.68 | 1.71 | 1.64 | 1.67 | 1.72 | 43.1 | 46.99 | 49.3 | 0 | - - - | - - - | - - - | - - - | 29225 | 26054 | 26920 | 82198 | Over-range | 11796 | 11178 | 12789 | 35867 | 11451 | 11015 | 11827 | 34560 | 26672 | 23482 | 23624 | 73779 | 26672 | 23482 | 23624 | 73779 | - - - | - - - | - - - | - - -
5/8/2026 | 5:30:00 PM | 280.88 | 278.31 | 278.04 | 486.55 | 479.92 | 483.62 | 106.7996 | 96.3165 | 98.9314 | 2.6468 | 1.439 | 1.437 | 1.434 | 1.9 | 1.901 | 1.943 | Over-range | 59.98 | 27479 | 24264 | 24242 | 75984 | - - - | - - - | - - - | - - - | 27479 | 24264 | 24242 | 75984 | 2965 | 1866 | 4939 | 9769 | - - - | - - - | - - - | - - - | 2965 | 1866 | 4939 | 9769 | 29968 | 26784 | 27484 | 84236 | # # # | # # # | # # # | # # # | 0.917 | 0.906 | 0.882 | 0.902 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.98 | 0.99 | - - - | 0.129 | 1.73 | 1.7 | 1.73 | 1.66 | 1.68 | 1.74 | 42.39 | 46.28 | 48.76 | 0 | - - - | - - - | - - - | - - - | 29968 | 26784 | 27484 | 84236 | Over-range | 11952 | 11339 | 12945 | 36347 | 11579 | 11184 | 11966 | 35009 | 27411 | 24212 | 24187 | 75809 | 27411 | 24212 | 24187 | 75809 | - - - | - - - | - - - | - - -
5/8/2026 | 5:45:00 PM | 280.92 | 278.4 | 278.21 | 486.61 | 480.2 | 483.8 | 108.2236 | 97.9531 | 100.4892 | 2.6223 | 1.438 | 1.436 | 1.433 | 1.896 | 1.895 | 1.934 | Over-range | 59.99 | 27864 | 24698 | 24684 | 77246 | - - - | - - - | - - - | - - - | 27864 | 24698 | 24684 | 77246 | 3024 | 1941 | 4955 | 9919 | - - - | - - - | - - - | - - - | 3024 | 1941 | 4955 | 9919 | 30376 | 27251 | 27938 | 85565 | # # # | # # # | # # # | # # # | 0.917 | 0.906 | 0.883 | 0.903 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.98 | 0.991 | - - - | 0.128 | 1.7 | 1.67 | 1.71 | 1.63 | 1.66 | 1.7 | 42.29 | 46.11 | 48.47 | 0 | - - - | - - - | - - - | - - - | 30376 | 27251 | 27938 | 85565 | Over-range | 12090 | 11513 | 13080 | 36789 | 11705 | 11348 | 12105 | 35426 | 27783 | 24655 | 24629 | 77067 | 27783 | 24655 | 24629 | 77067 | - - - | - - - | - - - | - - -
5/8/2026 | 6:00:00 PM | 281.21 | 278.73 | 278.55 | 487.13 | 480.81 | 484.36 | 109.2792 | 98.7445 | 101.3875 | 2.639 | 1.438 | 1.436 | 1.433 | 1.894 | 1.891 | 1.935 | Over-range | 59.99 | 28189 | 24935 | 24933 | 78057 | - - - | - - - | - - - | - - - | 28189 | 24935 | 24933 | 78057 | 3056 | 1943 | 5045 | 10044 | - - - | - - - | - - - | - - - | 3056 | 1943 | 5045 | 10044 | 30701 | 27500 | 28221 | 86422 | # # # | # # # | # # # | # # # | 0.918 | 0.907 | 0.883 | 0.903 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.98 | 0.99 | - - - | 0.129 | 1.68 | 1.65 | 1.67 | 1.61 | 1.63 | 1.67 | 42.05 | 46.06 | 48.46 | 0 | - - - | - - - | - - - | - - - | 30701 | 27500 | 28221 | 86422 | Over-range | 12156 | 11595 | 13215 | 37080 | 11765 | 11430 | 12214 | 35694 | 28121 | 24878 | 24866 | 77865 | 28121 | 24878 | 24866 | 77865 | - - - | - - - | - - - | - - -
5/8/2026 | 6:15:00 PM | 281.15 | 278.73 | 278.53 | 487.07 | 480.82 | 484.26 | 115.7144 | 104.5014 | 107.5627 | 2.8788 | 1.436 | 1.433 | 1.43 | 1.882 | 1.871 | 1.923 | Over-range | 59.99 | 29968 | 26488 | 26560 | 83016 | - - - | - - - | - - - | - - - | 29968 | 26488 | 26560 | 83016 | 3135 | 2032 | 5340 | 10506 | - - - | - - - | - - - | - - - | 3135 | 2032 | 5340 | 10506 | 32498 | 29100 | 29933 | 91531 | # # # | # # # | # # # | # # # | 0.922 | 0.91 | 0.887 | 0.907 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.98 | 0.991 | - - - | 0.127 | 1.57 | 1.54 | 1.56 | 1.51 | 1.52 | 1.55 | 41.01 | 45.06 | 47.48 | 0 | - - - | - - - | - - - | - - - | 32498 | 29100 | 29933 | 91531 | Over-range | 12566 | 12045 | 13799 | 38539 | 12169 | 11872 | 12724 | 37079 | 29873 | 26434 | 26492 | 82799 | 29873 | 26434 | 26492 | 82799 | - - - | - - - | - - - | - - -
5/8/2026 | 6:30:00 PM | 280.95 | 278.44 | 278.29 | 486.63 | 480.32 | 483.92 | 118.0354 | 106.1462 | 109.3742 | 2.8879 | 1.435 | 1.433 | 1.43 | 1.878 | 1.868 | 1.927 | Over-range | 59.97 | 30610 | 26912 | 26981 | 84503 | - - - | - - - | - - - | - - - | 30610 | 26912 | 26981 | 84503 | 3192 | 1957 | 5491 | 10639 | - - - | - - - | - - - | - - - | 3192 | 1957 | 5491 | 10639 | 33136 | 29537 | 30419 | 93093 | # # # | # # # | # # # | # # # | 0.924 | 0.911 | 0.887 | 0.908 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.98 | 0.991 | - - - | 0.126 | 1.56 | 1.54 | 1.55 | 1.5 | 1.52 | 1.54 | 40.51 | 44.87 | 47.45 | 0 | - - - | - - - | - - - | - - - | 33136 | 29537 | 30419 | 93093 | Over-range | 12686 | 12170 | 14043 | 39045 | 12277 | 12011 | 12924 | 37567 | 30516 | 26864 | 26909 | 84289 | 30516 | 26864 | 26909 | 84289 | - - - | - - - | - - - | - - -
5/8/2026 | 6:45:00 PM | 280.98 | 278.56 | 278.31 | 486.8 | 480.46 | 483.91 | 119.5062 | 107.29 | 109.5473 | 2.9098 | 1.435 | 1.433 | 1.43 | 1.865 | 1.874 | 1.934 | Over-range | 59.97 | 31027 | 27248 | 26992 | 85267 | - - - | - - - | - - - | - - - | 31027 | 27248 | 26992 | 85267 | 3389 | 1743 | 5557 | 10690 | - - - | - - - | - - - | - - - | 3389 | 1743 | 5557 | 10690 | 33550 | 29865 | 30468 | 93884 | # # # | # # # | # # # | # # # | 0.925 | 0.912 | 0.886 | 0.908 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.979 | 0.991 | - - - | 0.125 | 1.56 | 1.54 | 1.56 | 1.5 | 1.52 | 1.55 | 40.01 | 44.63 | 47.64 | 0 | - - - | - - - | - - - | - - - | 33550 | 29865 | 30468 | 93884 | Over-range | 12758 | 12223 | 14130 | 39278 | 12299 | 12097 | 12991 | 37795 | 30949 | 27195 | 26913 | 85057 | 30949 | 27195 | 26913 | 85057 | - - - | - - - | - - - | - - -
5/8/2026 | 7:00:00 PM | 281.22 | 278.67 | 278.52 | 487.09 | 480.69 | 484.36 | 121.3172 | 107.9462 | 111.0034 | 2.9042 | 1.436 | 1.433 | 1.429 | 1.873 | 1.874 | 1.95 | Over-range | 59.98 | 31578 | 27417 | 27294 | 86290 | - - - | - - - | - - - | - - - | 31578 | 27417 | 27294 | 86290 | 3374 | 1644 | 5796 | 10815 | - - - | - - - | - - - | - - - | 3374 | 1644 | 5796 | 10815 | 34091 | 30063 | 30897 | 95051 | # # # | # # # | # # # | # # # | 0.926 | 0.912 | 0.883 | 0.908 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.978 | 0.99 | - - - | 0.125 | 1.54 | 1.52 | 1.52 | 1.48 | 1.49 | 1.51 | 39.67 | 44.84 | 48.09 | 0 | - - - | - - - | - - - | - - - | 34091 | 30063 | 30897 | 95051 | Over-range | 12840 | 12331 | 14475 | 39849 | 12389 | 12220 | 13263 | 38353 | 31491 | 27361 | 27210 | 86062 | 31491 | 27361 | 27210 | 86062 | - - - | - - - | - - - | - - -
5/8/2026 | 7:15:00 PM | 280.96 | 278.32 | 278.13 | 486.61 | 480 | 483.82 | 123.9817 | 109.5095 | 112.2132 | 2.828 | 1.435 | 1.433 | 1.429 | 1.866 | 1.882 | 1.965 | Over-range | 59.99 | 32282 | 27790 | 27482 | 87554 | - - - | - - - | - - - | - - - | 32282 | 27790 | 27482 | 87554 | 3538 | 1428 | 5989 | 10955 | - - - | - - - | - - - | - - - | 3538 | 1428 | 5989 | 10955 | 34805 | 30456 | 31190 | 96452 | # # # | # # # | # # # | # # # | 0.928 | 0.912 | 0.881 | 0.908 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.977 | 0.99 | - - - | 0.125 | 1.51 | 1.51 | 1.5 | 1.46 | 1.48 | 1.48 | 39.22 | 44.83 | 48.49 | 0 | - - - | - - - | - - - | - - - | 34805 | 30456 | 31190 | 96452 | Over-range | 13005 | 12461 | 14747 | 40453 | 12513 | 12378 | 13476 | 38942 | 32195 | 27731 | 27392 | 87318 | 32195 | 27731 | 27392 | 87318 | - - - | - - - | - - - | - - -
5/8/2026 | 7:30:00 PM | 281 | 278.47 | 278.21 | 486.78 | 480.23 | 483.87 | 127.3034 | 112.4163 | 113.9154 | 2.8553 | 1.435 | 1.433 | 1.429 | 1.848 | 1.883 | 1.969 | Over-range | 59.99 | 33210 | 28600 | 27891 | 89701 | - - - | - - - | - - - | - - - | 33210 | 28600 | 27891 | 89701 | 3822 | 1196 | 6112 | 11130 | - - - | - - - | - - - | - - - | 3822 | 1196 | 6112 | 11130 | 35748 | 31286 | 31675 | 98710 | # # # | # # # | # # # | # # # | 0.929 | 0.914 | 0.88 | 0.909 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.977 | 0.99 | - - - | 0.124 | 1.51 | 1.51 | 1.51 | 1.46 | 1.49 | 1.49 | 38.56 | 44.4 | 48.57 | 0 | - - - | - - - | - - - | - - - | 35748 | 31286 | 31675 | 98710 | Over-range | 13223 | 12683 | 15011 | 41190 | 12658 | 12625 | 13710 | 39658 | 33100 | 28557 | 27812 | 89468 | 33100 | 28557 | 27812 | 89468 | - - - | - - - | - - - | - - -
5/8/2026 | 7:45:00 PM | 281.16 | 278.54 | 278.33 | 486.98 | 480.36 | 484.14 | 129.614 | 114.0321 | 115.5558 | 2.9026 | 1.435 | 1.433 | 1.429 | 1.845 | 1.88 | 1.975 | Over-range | 59.98 | 33874 | 29029 | 28275 | 91178 | - - - | - - - | - - - | - - - | 33874 | 29029 | 28275 | 91178 | 3883 | 1095 | 6269 | 11247 | - - - | - - - | - - - | - - - | 3883 | 1095 | 6269 | 11247 | 36418 | 31743 | 32144 | 100305 | # # # | # # # | # # # | # # # | 0.93 | 0.915 | 0.88 | 0.909 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.976 | 0.99 | - - - | 0.123 | 1.5 | 1.52 | 1.52 | 1.46 | 1.49 | 1.49 | 38.18 | 44.3 | 48.7 | 0 | - - - | - - - | - - - | - - - | 36418 | 31743 | 32144 | 100305 | Over-range | 13365 | 12841 | 15286 | 41794 | 12788 | 12794 | 13941 | 40252 | 33775 | 28988 | 28186 | 90949 | 33775 | 28988 | 28186 | 90949 | - - - | - - - | - - - | - - -
5/8/2026 | 8:00:00 PM | 281.46 | 278.89 | 278.62 | 487.56 | 480.92 | 484.63 | 131.5773 | 115.789 | 116.8281 | 2.9322 | 1.435 | 1.433 | 1.429 | 1.837 | 1.878 | 1.976 | Over-range | 59.98 | 34458 | 29549 | 28633 | 92641 | - - - | - - - | - - - | - - - | 34458 | 29549 | 28633 | 92641 | 4012 | 1015 | 6346 | 11372 | - - - | - - - | - - - | - - - | 4012 | 1015 | 6346 | 11372 | 37012 | 32276 | 32535 | 101824 | # # # | # # # | # # # | # # # | 0.931 | 0.916 | 0.88 | 0.91 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.976 | 0.99 | - - - | 0.123 | 1.51 | 1.52 | 1.52 | 1.47 | 1.5 | 1.5 | 37.86 | 44.03 | 48.58 | 0 | - - - | - - - | - - - | - - - | 37012 | 32276 | 32535 | 101824 | Over-range | 13504 | 12983 | 15445 | 42248 | 12894 | 12943 | 14081 | 40688 | 34352 | 29507 | 28548 | 92406 | 34352 | 29507 | 28548 | 92406 | - - - | - - - | - - - | - - -
5/8/2026 | 8:15:00 PM | 281.5 | 278.93 | 278.67 | 487.61 | 481.01 | 484.71 | 131.5573 | 115.7695 | 116.9637 | 2.9314 | 1.435 | 1.432 | 1.428 | 1.837 | 1.876 | 1.973 | Over-range | 59.98 | 34466 | 29548 | 28691 | 92706 | - - - | - - - | - - - | - - - | 34466 | 29548 | 28691 | 92706 | 3966 | 1027 | 6340 | 11333 | - - - | - - - | - - - | - - - | 3966 | 1027 | 6340 | 11333 | 37011 | 32274 | 32578 | 101863 | # # # | # # # | # # # | # # # | 0.931 | 0.916 | 0.881 | 0.91 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.976 | 0.99 | - - - | 0.122 | 1.49 | 1.5 | 1.5 | 1.44 | 1.48 | 1.48 | 37.81 | 44.03 | 48.43 | 0 | - - - | - - - | - - - | - - - | 37011 | 32274 | 32578 | 101863 | Over-range | 13481 | 12980 | 15427 | 42200 | 12884 | 12939 | 14064 | 40649 | 34373 | 29495 | 28606 | 92474 | 34373 | 29495 | 28606 | 92474 | - - - | - - - | - - - | - - -
5/8/2026 | 8:30:00 PM | 281.48 | 278.86 | 278.54 | 487.59 | 480.78 | 484.57 | 131.9125 | 115.6807 | 116.5607 | 2.9148 | 1.435 | 1.433 | 1.428 | 1.834 | 1.884 | 1.983 | Over-range | 59.98 | 34560 | 29517 | 28524 | 92601 | - - - | - - - | - - - | - - - | 34560 | 29517 | 28524 | 92601 | 4038 | 894 | 6394 | 11326 | - - - | - - - | - - - | - - - | 4038 | 894 | 6394 | 11326 | 37108 | 32241 | 32450 | 101799 | # # # | # # # | # # # | # # # | 0.931 | 0.916 | 0.879 | 0.91 | # # # | # # # | # # # | - - - | 0.993 | 1 | 0.976 | 0.99 | - - - | 0.122 | 1.5 | 1.5 | 1.5 | 1.45 | 1.48 | 1.48 | 37.72 | 44.06 | 48.74 | 0 | - - - | - - - | - - - | - - - | 37108 | 32241 | 32450 | 101799 | Over-range | 13507 | 12968 | 15468 | 42274 | 12889 | 12937 | 14084 | 40729 | 34468 | 29468 | 28434 | 92369 | 34468 | 29468 | 28434 | 92369 | - - - | - - - | - - - | - - -
5/8/2026 | 8:45:00 PM | 281.47 | 278.84 | 278.49 | 487.58 | 480.71 | 484.51 | 131.7469 | 115.4362 | 116.2055 | 2.9601 | 1.435 | 1.433 | 1.428 | 1.835 | 1.884 | 1.986 | Over-range | 59.98 | 34522 | 29461 | 28426 | 92409 | - - - | - - - | - - - | - - - | 34522 | 29461 | 28426 | 92409 | 4010 | 856 | 6385 | 11251 | - - - | - - - | - - - | - - - | 4010 | 856 | 6385 | 11251 | 37058 | 32170 | 32345 | 101572 | # # # | # # # | # # # | # # # | 0.932 | 0.916 | 0.879 | 0.91 | # # # | # # # | # # # | - - - | 0.993 | 1 | 0.976 | 0.99 | - - - | 0.122 | 1.51 | 1.52 | 1.51 | 1.46 | 1.49 | 1.49 | 37.68 | 44 | 48.77 | 0 | - - - | - - - | - - - | - - - | 37058 | 32170 | 32345 | 101572 | Over-range | 13467 | 12919 | 15427 | 42150 | 12856 | 12890 | 14044 | 40620 | 34422 | 29412 | 28342 | 92176 | 34422 | 29412 | 28342 | 92176 | - - - | - - - | - - - | - - -
5/8/2026 | 9:00:00 PM | 281.41 | 278.8 | 278.43 | 487.5 | 480.65 | 484.41 | 130.3696 | 114.3207 | 114.5889 | 2.9757 | 1.435 | 1.433 | 1.428 | 1.831 | 1.882 | 1.984 | Over-range | 59.98 | 34167 | 29184 | 28025 | 91376 | - - - | - - - | - - - | - - - | 34167 | 29184 | 28025 | 91376 | 4003 | 779 | 6289 | 11071 | - - - | - - - | - - - | - - - | 4003 | 779 | 6289 | 11071 | 36661 | 31852 | 31888 | 100401 | # # # | # # # | # # # | # # # | 0.932 | 0.916 | 0.879 | 0.91 | # # # | # # # | # # # | - - - | 0.993 | 1 | 0.976 | 0.99 | - - - | 0.121 | 1.53 | 1.53 | 1.53 | 1.48 | 1.5 | 1.51 | 37.5 | 43.85 | 48.77 | 0 | - - - | - - - | - - - | - - - | 36661 | 31852 | 31888 | 100401 | Over-range | 13281 | 12759 | 15210 | 41590 | 12664 | 12735 | 13848 | 40089 | 34063 | 29143 | 27944 | 91150 | 34063 | 29143 | 27944 | 91150 | - - - | - - - | - - - | - - -
5/8/2026 | 9:15:00 PM | 281.72 | 279.22 | 278.84 | 488.11 | 481.41 | 485 | 129.9654 | 114.3715 | 114.5642 | 2.9246 | 1.436 | 1.434 | 1.429 | 1.829 | 1.878 | 1.976 | Over-range | 59.97 | 34093 | 29258 | 28118 | 91469 | - - - | - - - | - - - | - - - | 34093 | 29258 | 28118 | 91469 | 3998 | 872 | 6210 | 11081 | - - - | - - - | - - - | - - - | 3998 | 872 | 6210 | 11081 | 36586 | 31913 | 31925 | 100424 | # # # | # # # | # # # | # # # | 0.932 | 0.917 | 0.881 | 0.911 | # # # | # # # | # # # | - - - | 0.993 | 1 | 0.976 | 0.99 | - - - | 0.121 | 1.55 | 1.54 | 1.55 | 1.5 | 1.52 | 1.53 | 37.52 | 43.67 | 48.41 | 0 | - - - | - - - | - - - | - - - | 36586 | 31913 | 31925 | 100424 | Over-range | 13265 | 12741 | 15115 | 41439 | 12648 | 12711 | 13780 | 39930 | 33996 | 29223 | 28022 | 91240 | 33996 | 29223 | 28022 | 91240 | - - - | - - - | - - - | - - -
5/8/2026 | 9:30:00 PM | 282.09 | 279.59 | 279.27 | 488.72 | 482.12 | 485.71 | 129.1251 | 113.6115 | 114.1466 | 2.9384 | 1.436 | 1.433 | 1.429 | 1.835 | 1.876 | 1.976 | Over-range | 59.98 | 33923 | 29090 | 28052 | 91065 | - - - | - - - | - - - | - - - | 33923 | 29090 | 28052 | 91065 | 3931 | 900 | 6204 | 11035 | - - - | - - - | - - - | - - - | 3931 | 900 | 6204 | 11035 | 36395 | 31741 | 31855 | 99991 | # # # | # # # | # # # | # # # | 0.932 | 0.917 | 0.881 | 0.911 | # # # | # # # | # # # | - - - | 0.993 | 1 | 0.976 | 0.99 | - - - | 0.121 | 1.55 | 1.54 | 1.54 | 1.5 | 1.5 | 1.53 | 37.52 | 43.78 | 48.47 | 0 | - - - | - - - | - - - | - - - | 36395 | 31741 | 31855 | 99991 | Over-range | 13178 | 12696 | 15089 | 41284 | 12578 | 12664 | 13755 | 39782 | 33819 | 29045 | 27964 | 90827 | 33819 | 29045 | 27964 | 90827 | - - - | - - - | - - - | - - -
5/8/2026 | 9:45:00 PM | 282.16 | 279.78 | 279.37 | 488.96 | 482.42 | 485.78 | 128.7849 | 113.7934 | 113.7816 | 2.9226 | 1.436 | 1.433 | 1.429 | 1.834 | 1.885 | 1.975 | Over-range | 59.99 | 33785 | 29145 | 27979 | 90909 | - - - | - - - | - - - | - - - | 33785 | 29145 | 27979 | 90909 | 4013 | 951 | 6124 | 11089 | - - - | - - - | - - - | - - - | 4013 | 951 | 6124 | 11089 | 36310 | 31817 | 31769 | 99897 | # # # | # # # | # # # | # # # | 0.931 | 0.916 | 0.881 | 0.91 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.977 | 0.99 | - - - | 0.122 | 1.55 | 1.52 | 1.52 | 1.49 | 1.49 | 1.52 | 37.99 | 43.94 | 48.59 | 0 | - - - | - - - | - - - | - - - | 36310 | 31817 | 31769 | 99897 | Over-range | 13298 | 12762 | 15043 | 41399 | 12678 | 12725 | 13740 | 39887 | 33678 | 29104 | 27884 | 90666 | 33678 | 29104 | 27884 | 90666 | - - - | - - - | - - - | - - -
5/8/2026 | 10:00:00 PM | 282.13 | 279.67 | 279.33 | 488.82 | 482.26 | 485.76 | 128.1289 | 113.1429 | 113.7173 | 2.9139 | 1.436 | 1.433 | 1.429 | 1.841 | 1.882 | 1.972 | Over-range | 59.99 | 33606 | 28953 | 27975 | 90534 | - - - | - - - | - - - | - - - | 33606 | 28953 | 27975 | 90534 | 3903 | 1028 | 6115 | 11046 | - - - | - - - | - - - | - - - | 3903 | 1028 | 6115 | 11046 | 36118 | 31618 | 31746 | 99482 | # # # | # # # | # # # | # # # | 0.931 | 0.916 | 0.881 | 0.91 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.977 | 0.99 | - - - | 0.122 | 1.54 | 1.52 | 1.52 | 1.48 | 1.49 | 1.51 | 38.07 | 44.02 | 48.43 | 0 | - - - | - - - | - - - | - - - | 36118 | 31618 | 31746 | 99482 | Over-range | 13226 | 12705 | 15001 | 41222 | 12637 | 12662 | 13698 | 39715 | 33492 | 28904 | 27893 | 90289 | 33492 | 28904 | 27893 | 90289 | - - - | - - - | - - - | - - -
5/8/2026 | 10:15:00 PM | 282.24 | 279.69 | 279.31 | 488.99 | 482.2 | 485.87 | 128.1269 | 112.7014 | 113.6909 | 2.8881 | 1.435 | 1.433 | 1.428 | 1.847 | 1.888 | 1.982 | Over-range | 59.97 | 33616 | 28822 | 27925 | 90363 | - - - | - - - | - - - | - - - | 33616 | 28822 | 27925 | 90363 | 3876 | 1016 | 6193 | 11085 | - - - | - - - | - - - | - - - | 3876 | 1016 | 6193 | 11085 | 36140 | 31503 | 31738 | 99381 | # # # | # # # | # # # | # # # | 0.93 | 0.915 | 0.88 | 0.909 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.976 | 0.99 | - - - | 0.123 | 1.55 | 1.54 | 1.53 | 1.5 | 1.5 | 1.53 | 38.2 | 44.27 | 48.68 | 0 | - - - | - - - | - - - | - - - | 36140 | 31503 | 31738 | 99381 | Over-range | 13263 | 12715 | 15079 | 41354 | 12684 | 12673 | 13748 | 39841 | 33512 | 28773 | 27832 | 90117 | 33512 | 28773 | 27832 | 90117 | - - - | - - - | - - - | - - -
5/8/2026 | 10:30:00 PM | 282.5 | 279.99 | 279.64 | 489.45 | 482.77 | 486.36 | 130.8834 | 116.7756 | 117.0506 | 2.9777 | 1.436 | 1.432 | 1.429 | 1.829 | 1.868 | 1.947 | Over-range | 59.98 | 34401 | 30027 | 29031 | 93460 | - - - | - - - | - - - | - - - | 34401 | 30027 | 29031 | 93460 | 4010 | 1283 | 6039 | 11333 | - - - | - - - | - - - | - - - | 4010 | 1283 | 6039 | 11333 | 36948 | 32675 | 32713 | 102336 | # # # | # # # | # # # | # # # | 0.931 | 0.919 | 0.887 | 0.913 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.979 | 0.991 | - - - | 0.121 | 1.58 | 1.55 | 1.55 | 1.52 | 1.52 | 1.55 | 37.85 | 42.97 | 47.16 | 0 | - - - | - - - | - - - | - - - | 36948 | 32675 | 32713 | 102336 | Over-range | 13475 | 12882 | 15073 | 41678 | 12863 | 12817 | 13810 | 40108 | 34292 | 29973 | 28948 | 93212 | 34292 | 29973 | 28948 | 93212 | - - - | - - - | - - - | - - -
5/8/2026 | 10:45:00 PM | 282.67 | 280.23 | 279.86 | 489.79 | 483.21 | 486.69 | 127.9583 | 113.9437 | 114.4937 | 2.875 | 1.436 | 1.432 | 1.429 | 1.823 | 1.855 | 1.938 | Over-range | 59.98 | 33708 | 29323 | 28441 | 91472 | - - - | - - - | - - - | - - - | 33708 | 29323 | 28441 | 91472 | 3854 | 1222 | 5950 | 11026 | - - - | - - - | - - - | - - - | 3854 | 1222 | 5950 | 11026 | 36131 | 31902 | 32017 | 100050 | # # # | # # # | # # # | # # # | 0.933 | 0.919 | 0.888 | 0.914 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.979 | 0.991 | - - - | 0.121 | 1.59 | 1.54 | 1.56 | 1.52 | 1.52 | 1.56 | 37.29 | 42.92 | 46.84 | 0 | - - - | - - - | - - - | - - - | 36131 | 31902 | 32017 | 100050 | Over-range | 12999 | 12561 | 14696 | 40512 | 12414 | 12500 | 13437 | 38983 | 33613 | 29258 | 28354 | 91225 | 33613 | 29258 | 28354 | 91225 | - - - | - - - | - - - | - - -
5/8/2026 | 11:00:00 PM | 282.97 | 280.59 | 280.25 | 490.34 | 483.9 | 487.26 | 128.74 | 114.5071 | 115.298 | 2.8828 | 1.437 | 1.433 | 1.429 | 1.834 | 1.869 | 1.95 | Over-range | 59.99 | 33892 | 29467 | 28618 | 91978 | - - - | - - - | - - - | - - - | 33892 | 29467 | 28618 | 91978 | 3910 | 1279 | 6054 | 11242 | - - - | - - - | - - - | - - - | 3910 | 1279 | 6054 | 11242 | 36405 | 32111 | 32293 | 100810 | # # # | # # # | # # # | # # # | 0.931 | 0.918 | 0.886 | 0.912 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.978 | 0.99 | - - - | 0.122 | 1.61 | 1.57 | 1.58 | 1.55 | 1.54 | 1.59 | 37.94 | 43.38 | 47.37 | 0 | - - - | - - - | - - - | - - - | 36405 | 32111 | 32293 | 100810 | Over-range | 13284 | 12756 | 14957 | 41249 | 12695 | 12691 | 13677 | 39687 | 33778 | 29416 | 28528 | 91721 | 33778 | 29416 | 28528 | 91721 | - - - | - - - | - - - | - - -
5/8/2026 | 11:15:00 PM | 283.09 | 280.47 | 280.16 | 490.39 | 483.59 | 487.36 | 127.7982 | 112.7824 | 114.4113 | 2.8929 | 1.436 | 1.433 | 1.429 | 1.848 | 1.876 | 1.966 | Over-range | 59.97 | 33650 | 28957 | 28296 | 90903 | - - - | - - - | - - - | - - - | 33650 | 28957 | 28296 | 90903 | 3778 | 1224 | 6164 | 11166 | - - - | - - - | - - - | - - - | 3778 | 1224 | 6164 | 11166 | 36152 | 31613 | 32036 | 99801 | # # # | # # # | # # # | # # # | 0.931 | 0.916 | 0.883 | 0.911 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.977 | 0.99 | - - - | 0.123 | 1.63 | 1.58 | 1.6 | 1.56 | 1.56 | 1.6 | 38.14 | 43.91 | 47.91 | 0 | - - - | - - - | - - - | - - - | 36152 | 31613 | 32036 | 99801 | Over-range | 13208 | 12683 | 15016 | 41182 | 12656 | 12623 | 13693 | 39640 | 33542 | 28904 | 28201 | 90647 | 33542 | 28904 | 28201 | 90647 | - - - | - - - | - - - | - - -
5/8/2026 | 11:30:00 PM | 283.12 | 280.55 | 280.15 | 490.52 | 483.64 | 487.36 | 126.7116 | 111.7562 | 113.3204 | 2.8602 | 1.438 | 1.434 | 1.43 | 1.851 | 1.884 | 1.97 | Over-range | 59.98 | 33333 | 28667 | 27985 | 89986 | - - - | - - - | - - - | - - - | 33333 | 28667 | 27985 | 89986 | 3775 | 1211 | 6142 | 11128 | - - - | - - - | - - - | - - - | 3775 | 1211 | 6142 | 11128 | 35847 | 31331 | 31725 | 98904 | # # # | # # # | # # # | # # # | 0.93 | 0.915 | 0.882 | 0.91 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.977 | 0.99 | - - - | 0.124 | 1.63 | 1.6 | 1.61 | 1.57 | 1.57 | 1.61 | 38.39 | 44.22 | 48.17 | 0 | - - - | - - - | - - - | - - - | 35847 | 31331 | 31725 | 98904 | Over-range | 13178 | 12640 | 14939 | 41027 | 12626 | 12582 | 13617 | 39489 | 33227 | 28611 | 27888 | 89725 | 33227 | 28611 | 27888 | 89725 | - - - | - - - | - - - | - - -
5/8/2026 | 11:45:00 PM | 283.56 | 280.97 | 280.69 | 491.2 | 484.52 | 488.23 | 122.6701 | 108.5282 | 110.7892 | 2.7562 | 1.437 | 1.433 | 1.429 | 1.853 | 1.866 | 1.951 | Over-range | 59.99 | 32353 | 27892 | 27521 | 87766 | - - - | - - - | - - - | - - - | 32353 | 27892 | 27521 | 87766 | 3490 | 1355 | 5903 | 10748 | - - - | - - - | - - - | - - - | 3490 | 1355 | 5903 | 10748 | 34745 | 30465 | 31070 | 96281 | # # # | # # # | # # # | # # # | 0.931 | 0.916 | 0.886 | 0.912 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.978 | 0.99 | - - - | 0.123 | 1.64 | 1.6 | 1.6 | 1.57 | 1.57 | 1.61 | 38.11 | 43.99 | 47.34 | 0 | - - - | - - - | - - - | - - - | 34745 | 30465 | 31070 | 96281 | Over-range | 12657 | 12252 | 14415 | 39568 | 12165 | 12176 | 13151 | 38080 | 32255 | 27827 | 27430 | 87512 | 32255 | 27827 | 27430 | 87512 | - - - | - - - | - - - | - - -
5/9/2026 | 12:00:00 AM | 283.65 | 281.13 | 280.76 | 491.45 | 484.71 | 488.33 | 122.8783 | 108.9556 | 111.1509 | 2.7673 | 1.437 | 1.433 | 1.429 | 1.862 | 1.883 | 1.958 | Over-range | 59.99 | 32330 | 27975 | 27586 | 87892 | - - - | - - - | - - - | - - - | 32330 | 27975 | 27586 | 87892 | 3544 | 1479 | 5903 | 10926 | - - - | - - - | - - - | - - - | 3544 | 1479 | 5903 | 10926 | 34827 | 30611 | 31188 | 96626 | # # # | # # # | # # # | # # # | 0.928 | 0.914 | 0.884 | 0.91 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.978 | 0.99 | - - - | 0.124 | 1.65 | 1.61 | 1.62 | 1.58 | 1.58 | 1.63 | 39.03 | 44.46 | 47.78 | 0 | - - - | - - - | - - - | - - - | 34827 | 30611 | 31188 | 96626 | Over-range | 12942 | 12425 | 14544 | 40132 | 12447 | 12336 | 13292 | 38616 | 32230 | 27913 | 27484 | 87626 | 32230 | 27913 | 27484 | 87626 | - - - | - - - | - - - | - - -
5/9/2026 | 12:15:00 AM | 283.65 | 281.01 | 280.72 | 491.34 | 484.54 | 488.35 | 121.4539 | 107.4832 | 111.0312 | 2.7675 | 1.436 | 1.432 | 1.428 | 1.884 | 1.884 | 1.96 | Over-range | 59.98 | 31905 | 27539 | 27557 | 87001 | - - - | - - - | - - - | - - - | 31905 | 27539 | 27557 | 87001 | 3305 | 1699 | 5902 | 10906 | - - - | - - - | - - - | - - - | 3305 | 1699 | 5902 | 10906 | 34425 | 30185 | 31152 | 95761 | # # # | # # # | # # # | # # # | 0.927 | 0.912 | 0.885 | 0.909 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.978 | 0.99 | - - - | 0.125 | 1.65 | 1.61 | 1.62 | 1.59 | 1.58 | 1.62 | 39.74 | 44.84 | 47.78 | 0 | - - - | - - - | - - - | - - - | 34425 | 30185 | 31152 | 95761 | Over-range | 12920 | 12355 | 14522 | 39999 | 12489 | 12237 | 13269 | 38484 | 31789 | 27474 | 27461 | 86724 | 31789 | 27474 | 27461 | 86724 | - - - | - - - | - - - | - - -
5/9/2026 | 12:30:00 AM | 284.13 | 281.51 | 281.17 | 492.21 | 485.36 | 489.12 | 120.2727 | 106.1914 | 110.1623 | 2.7307 | 1.436 | 1.432 | 1.428 | 1.891 | 1.888 | 1.963 | Over-range | 59.99 | 31631 | 27244 | 27386 | 86262 | - - - | - - - | - - - | - - - | 31631 | 27244 | 27386 | 86262 | 3198 | 1741 | 5884 | 10822 | - - - | - - - | - - - | - - - | 3198 | 1741 | 5884 | 10822 | 34148 | 29877 | 30957 | 94983 | # # # | # # # | # # # | # # # | 0.926 | 0.912 | 0.885 | 0.908 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.978 | 0.99 | - - - | 0.126 | 1.65 | 1.59 | 1.6 | 1.58 | 1.57 | 1.61 | 39.98 | 44.98 | 47.73 | 0 | - - - | - - - | - - - | - - - | 34148 | 29877 | 30957 | 94983 | Over-range | 12860 | 12260 | 14431 | 39744 | 12456 | 12135 | 13177 | 38242 | 31534 | 27165 | 27286 | 85984 | 31534 | 27165 | 27286 | 85984 | - - - | - - - | - - - | - - -
5/9/2026 | 12:45:00 AM | 284.48 | 281.87 | 281.6 | 492.77 | 486.07 | 489.82 | 117.2293 | 103.9201 | 108.3935 | 2.6915 | 1.436 | 1.432 | 1.428 | 1.889 | 1.863 | 1.94 | Over-range | 59.98 | 30906 | 26715 | 27092 | 84713 | - - - | - - - | - - - | - - - | 30906 | 26715 | 27092 | 84713 | 2965 | 1865 | 5680 | 10510 | - - - | - - - | - - - | - - - | 2965 | 1865 | 5680 | 10510 | 33305 | 29261 | 30494 | 93060 | # # # | # # # | # # # | # # # | 0.928 | 0.913 | 0.888 | 0.91 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.979 | 0.991 | - - - | 0.124 | 1.66 | 1.61 | 1.6 | 1.59 | 1.57 | 1.62 | 39.55 | 44.51 | 46.84 | 0 | - - - | - - - | - - - | - - - | 33305 | 29261 | 30494 | 93060 | Over-range | 12400 | 11935 | 13987 | 38499 | 12040 | 11787 | 12782 | 37037 | 30798 | 26652 | 26995 | 84445 | 30798 | 26652 | 26995 | 84445 | - - - | - - - | - - - | - - -
5/9/2026 | 1:00:00 AM | 284.77 | 282.17 | 281.78 | 493.35 | 486.46 | 490.19 | 118.9085 | 105.1058 | 109.377 | 2.6974 | 1.437 | 1.432 | 1.428 | 1.898 | 1.89 | 1.96 | Over-range | 59.99 | 31308 | 27003 | 27269 | 85580 | - - - | - - - | - - - | - - - | 31308 | 27003 | 27269 | 85580 | 3104 | 1841 | 5825 | 10770 | - - - | - - - | - - - | - - - | 3104 | 1841 | 5825 | 10770 | 33835 | 29638 | 30803 | 94276 | # # # | # # # | # # # | # # # | 0.925 | 0.911 | 0.885 | 0.908 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.978 | 0.99 | - - - | 0.126 | 1.66 | 1.61 | 1.62 | 1.59 | 1.58 | 1.63 | 40.37 | 45.14 | 47.63 | 0 | - - - | - - - | - - - | - - - | 33835 | 29638 | 30803 | 94276 | Over-range | 12822 | 12215 | 14320 | 39534 | 12440 | 12075 | 13082 | 38039 | 31188 | 26939 | 27169 | 85295 | 31188 | 26939 | 27169 | 85295 | - - - | - - - | - - - | - - -
5/9/2026 | 1:15:00 AM | 284.74 | 282.08 | 281.86 | 493.18 | 486.46 | 490.31 | 117.9759 | 104.4078 | 109.3403 | 2.6929 | 1.437 | 1.432 | 1.428 | 1.905 | 1.882 | 1.952 | Over-range | 59.97 | 31052 | 26802 | 27303 | 85158 | - - - | - - - | - - - | - - - | 31052 | 26802 | 27303 | 85158 | 2966 | 1993 | 5772 | 10732 | - - - | - - - | - - - | - - - | 2966 | 1993 | 5772 | 10732 | 33566 | 29433 | 30800 | 93799 | # # # | # # # | # # # | # # # | 0.925 | 0.911 | 0.886 | 0.908 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.126 | 1.66 | 1.62 | 1.61 | 1.6 | 1.58 | 1.63 | 40.54 | 45.2 | 47.41 | 0 | - - - | - - - | - - - | - - - | 33566 | 29433 | 30800 | 93799 | Over-range | 12739 | 12160 | 14248 | 39310 | 12388 | 11995 | 13026 | 37817 | 30946 | 26734 | 27191 | 84871 | 30946 | 26734 | 27191 | 84871 | - - - | - - - | - - - | - - -
5/9/2026 | 1:30:00 AM | 284.78 | 282.14 | 281.91 | 493.27 | 486.55 | 490.37 | 118.0796 | 104.579 | 109.3345 | 2.666 | 1.437 | 1.432 | 1.429 | 1.902 | 1.883 | 1.95 | Over-range | 59.99 | 31083 | 26854 | 27316 | 85253 | - - - | - - - | - - - | - - - | 31083 | 26854 | 27316 | 85253 | 3001 | 1985 | 5769 | 10755 | - - - | - - - | - - - | - - - | 3001 | 1985 | 5769 | 10755 | 33603 | 29488 | 30805 | 93896 | # # # | # # # | # # # | # # # | 0.925 | 0.911 | 0.887 | 0.908 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.126 | 1.66 | 1.63 | 1.63 | 1.6 | 1.59 | 1.64 | 40.53 | 45.19 | 47.33 | 0 | - - - | - - - | - - - | - - - | 33603 | 29488 | 30805 | 93896 | Over-range | 12760 | 12179 | 14235 | 39334 | 12401 | 12016 | 13013 | 37835 | 30970 | 26784 | 27216 | 84969 | 30970 | 26784 | 27216 | 84969 | - - - | - - - | - - - | - - -
5/9/2026 | 1:45:00 AM | 284.97 | 282.39 | 282.1 | 493.65 | 486.95 | 490.66 | 115.5913 | 102.6937 | 107.2082 | 2.6112 | 1.436 | 1.431 | 1.428 | 1.894 | 1.871 | 1.937 | Over-range | 59.99 | 30481 | 26423 | 26872 | 83776 | - - - | - - - | - - - | - - - | 30481 | 26423 | 26872 | 83776 | 2903 | 1963 | 5577 | 10443 | - - - | - - - | - - - | - - - | 2903 | 1963 | 5577 | 10443 | 32900 | 28970 | 30214 | 92085 | # # # | # # # | # # # | # # # | 0.926 | 0.912 | 0.889 | 0.91 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.979 | 0.991 | - - - | 0.125 | 1.66 | 1.61 | 1.62 | 1.6 | 1.58 | 1.62 | 40.05 | 44.71 | 46.67 | 0 | - - - | - - - | - - - | - - - | 32900 | 28970 | 30214 | 92085 | Over-range | 12373 | 11875 | 13804 | 38204 | 12027 | 11711 | 12627 | 36749 | 30369 | 26351 | 26783 | 83502 | 30369 | 26351 | 26783 | 83502 | - - - | - - - | - - - | - - -
5/9/2026 | 2:00:00 AM | 285.12 | 282.47 | 282.2 | 493.87 | 487.09 | 490.9 | 117.5027 | 104.0124 | 108.6817 | 2.6797 | 1.437 | 1.432 | 1.428 | 1.903 | 1.885 | 1.954 | Over-range | 59.99 | 30965 | 26746 | 27173 | 84884 | - - - | - - - | - - - | - - - | 30965 | 26746 | 27173 | 84884 | 2991 | 1956 | 5744 | 10690 | - - - | - - - | - - - | - - - | 2991 | 1956 | 5744 | 10690 | 33477 | 29362 | 30653 | 93492 | # # # | # # # | # # # | # # # | 0.925 | 0.911 | 0.886 | 0.908 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.126 | 1.67 | 1.63 | 1.62 | 1.6 | 1.59 | 1.63 | 40.54 | 45.14 | 47.38 | 0 | - - - | - - - | - - - | - - - | 33477 | 29362 | 30653 | 93492 | Over-range | 12716 | 12115 | 14180 | 39174 | 12359 | 11956 | 12965 | 37687 | 30866 | 26665 | 27075 | 84605 | 30866 | 26665 | 27075 | 84605 | - - - | - - - | - - - | - - -
5/9/2026 | 2:15:00 AM | 284.94 | 282.29 | 282.05 | 493.54 | 486.81 | 490.63 | 118.0262 | 104.5267 | 109.2278 | 2.6618 | 1.438 | 1.432 | 1.429 | 1.901 | 1.884 | 1.952 | Over-range | 59.98 | 31085 | 26853 | 27295 | 85233 | - - - | - - - | - - - | - - - | 31085 | 26853 | 27295 | 85233 | 3027 | 1980 | 5780 | 10787 | - - - | - - - | - - - | - - - | 3027 | 1980 | 5780 | 10787 | 33605 | 29489 | 30791 | 93886 | # # # | # # # | # # # | # # # | 0.925 | 0.911 | 0.886 | 0.908 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.127 | 1.69 | 1.65 | 1.65 | 1.63 | 1.61 | 1.65 | 40.51 | 45.21 | 47.38 | 0 | - - - | - - - | - - - | - - - | 33605 | 29489 | 30791 | 93886 | Over-range | 12760 | 12185 | 14245 | 39353 | 12395 | 12023 | 13020 | 37846 | 30977 | 26776 | 27194 | 84947 | 30977 | 26776 | 27194 | 84947 | - - - | - - - | - - - | - - -
5/9/2026 | 2:30:00 AM | 285.17 | 282.49 | 282.28 | 493.91 | 487.17 | 491.04 | 118.5893 | 105.0537 | 109.8522 | 2.7113 | 1.437 | 1.432 | 1.429 | 1.902 | 1.877 | 1.949 | Over-range | 60.01 | 31276 | 27018 | 27493 | 85787 | - - - | - - - | - - - | - - - | 31276 | 27018 | 27493 | 85787 | 3002 | 2000 | 5799 | 10801 | - - - | - - - | - - - | - - - | 3002 | 2000 | 5799 | 10801 | 33786 | 29653 | 30987 | 94426 | # # # | # # # | # # # | # # # | 0.926 | 0.911 | 0.887 | 0.909 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.126 | 1.7 | 1.65 | 1.65 | 1.63 | 1.62 | 1.66 | 40.32 | 45.04 | 47.19 | 0 | - - - | - - - | - - - | - - - | 33786 | 29653 | 30987 | 94426 | Over-range | 12771 | 12217 | 14288 | 39441 | 12412 | 12052 | 13058 | 37934 | 31169 | 26946 | 27387 | 85502 | 31169 | 26946 | 27387 | 85502 | - - - | - - - | - - - | - - -
5/9/2026 | 2:45:00 AM | 285.22 | 282.59 | 282.24 | 494.1 | 487.2 | 491 | 119.0676 | 105.5316 | 109.9597 | 2.6823 | 1.437 | 1.433 | 1.428 | 1.885 | 1.866 | 1.937 | Over-range | 59.99 | 31482 | 27222 | 27586 | 86291 | - - - | - - - | - - - | - - - | 31482 | 27222 | 27586 | 86291 | 3042 | 1930 | 5779 | 10751 | - - - | - - - | - - - | - - - | 3042 | 1930 | 5779 | 10751 | 33923 | 29794 | 31008 | 94726 | # # # | # # # | # # # | # # # | 0.928 | 0.914 | 0.89 | 0.911 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.979 | 0.991 | - - - | 0.125 | 1.71 | 1.66 | 1.66 | 1.64 | 1.63 | 1.67 | 39.52 | 44.31 | 46.52 | 0 | - - - | - - - | - - - | - - - | 33923 | 29794 | 31008 | 94726 | Over-range | 12624 | 12106 | 14154 | 39055 | 12252 | 11950 | 12920 | 37546 | 31377 | 27153 | 27483 | 86013 | 31377 | 27153 | 27483 | 86013 | - - - | - - - | - - - | - - -
5/9/2026 | 3:00:00 AM | 285.14 | 282.43 | 282.12 | 493.9 | 486.92 | 490.85 | 119.235 | 105.2072 | 110.1676 | 2.7044 | 1.437 | 1.432 | 1.428 | 1.898 | 1.877 | 1.951 | Over-range | 59.98 | 31488 | 27077 | 27556 | 86121 | - - - | - - - | - - - | - - - | 31488 | 27077 | 27556 | 86121 | 2992 | 1924 | 5879 | 10796 | - - - | - - - | - - - | - - - | 2992 | 1924 | 5879 | 10796 | 33969 | 29694 | 31059 | 94723 | # # # | # # # | # # # | # # # | 0.927 | 0.912 | 0.887 | 0.909 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.125 | 1.69 | 1.65 | 1.65 | 1.62 | 1.62 | 1.66 | 39.94 | 44.85 | 47.03 | 0 | - - - | - - - | - - - | - - - | 33969 | 29694 | 31059 | 94723 | Over-range | 12737 | 12186 | 14322 | 39423 | 12380 | 12032 | 13059 | 37916 | 31370 | 27003 | 27468 | 85841 | 31370 | 27003 | 27468 | 85841 | - - - | - - - | - - - | - - -
5/9/2026 | 3:15:00 AM | 285.18 | 282.54 | 282.16 | 494.04 | 487.09 | 490.89 | 119.5032 | 105.7796 | 110.121 | 2.7344 | 1.436 | 1.432 | 1.428 | 1.895 | 1.883 | 1.953 | Over-range | 59.99 | 31535 | 27231 | 27538 | 86304 | - - - | - - - | - - - | - - - | 31535 | 27231 | 27538 | 86304 | 3101 | 1917 | 5846 | 10865 | - - - | - - - | - - - | - - - | 3101 | 1917 | 5846 | 10865 | 34054 | 29869 | 31055 | 94978 | # # # | # # # | # # # | # # # | 0.926 | 0.912 | 0.887 | 0.909 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.978 | 0.99 | - - - | 0.126 | 1.69 | 1.65 | 1.64 | 1.62 | 1.61 | 1.65 | 40.15 | 44.94 | 47.25 | 0 | - - - | - - - | - - - | - - - | 34054 | 29869 | 31055 | 94978 | Over-range | 12848 | 12269 | 14350 | 39641 | 12468 | 12117 | 13106 | 38123 | 31431 | 27151 | 27441 | 86023 | 31431 | 27151 | 27441 | 86023 | - - - | - - - | - - - | - - -
5/9/2026 | 3:30:00 AM | 285.51 | 282.82 | 282.49 | 494.56 | 487.59 | 491.5 | 119.381 | 105.2843 | 110.4197 | 2.7017 | 1.437 | 1.432 | 1.428 | 1.903 | 1.881 | 1.955 | Over-range | 59.98 | 31543 | 27112 | 27635 | 86290 | - - - | - - - | - - - | - - - | 31543 | 27112 | 27635 | 86290 | 2990 | 1958 | 5913 | 10861 | - - - | - - - | - - - | - - - | 2990 | 1958 | 5913 | 10861 | 34062 | 29760 | 31176 | 94999 | # # # | # # # | # # # | # # # | 0.926 | 0.911 | 0.886 | 0.908 | # # # | # # # | # # # | - - - | 0.996 | 0.997 | 0.978 | 0.99 | - - - | 0.126 | 1.69 | 1.65 | 1.64 | 1.62 | 1.61 | 1.66 | 40.24 | 45.09 | 47.24 | 0 | - - - | - - - | - - - | - - - | 34062 | 29760 | 31176 | 94999 | Over-range | 12851 | 12270 | 14426 | 39721 | 12498 | 12112 | 13158 | 38208 | 31431 | 27031 | 27548 | 86010 | 31431 | 27031 | 27548 | 86010 | - - - | - - - | - - - | - - -
5/9/2026 | 3:45:00 AM | 285.42 | 282.85 | 282.47 | 494.5 | 487.66 | 491.34 | 116.4836 | 103.4234 | 107.7371 | 2.6643 | 1.435 | 1.43 | 1.427 | 1.891 | 1.871 | 1.939 | Over-range | 59.98 | 30780 | 26662 | 27039 | 84481 | - - - | - - - | - - - | - - - | 30780 | 26662 | 27039 | 84481 | 2949 | 1934 | 5638 | 10520 | - - - | - - - | - - - | - - - | 2949 | 1934 | 5638 | 10520 | 33204 | 29223 | 30402 | 92829 | # # # | # # # | # # # | # # # | 0.927 | 0.912 | 0.889 | 0.91 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.979 | 0.991 | - - - | 0.125 | 1.67 | 1.62 | 1.62 | 1.6 | 1.59 | 1.63 | 39.82 | 44.65 | 46.6 | 0 | - - - | - - - | - - - | - - - | 33204 | 29223 | 30402 | 92829 | Over-range | 12440 | 11959 | 13890 | 38449 | 12085 | 11801 | 12695 | 36982 | 30678 | 26583 | 26955 | 84216 | 30678 | 26583 | 26955 | 84216 | - - - | - - - | - - - | - - -
5/9/2026 | 4:00:00 AM | 285.52 | 282.93 | 282.59 | 494.65 | 487.82 | 491.55 | 117.5385 | 104.011 | 108.6801 | 2.6772 | 1.436 | 1.431 | 1.428 | 1.904 | 1.886 | 1.956 | Over-range | 59.99 | 31014 | 26762 | 27193 | 84969 | - - - | - - - | - - - | - - - | 31014 | 26762 | 27193 | 84969 | 2992 | 1954 | 5781 | 10727 | - - - | - - - | - - - | - - - | 2992 | 1954 | 5781 | 10727 | 33533 | 29407 | 30693 | 93633 | # # # | # # # | # # # | # # # | 0.925 | 0.91 | 0.886 | 0.908 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.126 | 1.68 | 1.63 | 1.63 | 1.61 | 1.6 | 1.64 | 40.57 | 45.38 | 47.47 | 0 | - - - | - - - | - - - | - - - | 33533 | 29407 | 30693 | 93633 | Over-range | 12743 | 12188 | 14229 | 39325 | 12386 | 12030 | 13002 | 37834 | 30895 | 26688 | 27105 | 84688 | 30895 | 26688 | 27105 | 84688 | - - - | - - - | - - - | - - -
5/9/2026 | 4:15:00 AM | 285.65 | 283.07 | 282.67 | 494.92 | 488.01 | 491.71 | 117.5243 | 103.9118 | 108.6186 | 2.6847 | 1.437 | 1.431 | 1.428 | 1.905 | 1.891 | 1.959 | Over-range | 59.99 | 31014 | 26751 | 27170 | 84935 | - - - | - - - | - - - | - - - | 31014 | 26751 | 27170 | 84935 | 3004 | 1954 | 5798 | 10756 | - - - | - - - | - - - | - - - | 3004 | 1954 | 5798 | 10756 | 33548 | 29398 | 30685 | 93632 | # # # | # # # | # # # | # # # | 0.925 | 0.91 | 0.885 | 0.907 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.127 | 1.68 | 1.63 | 1.64 | 1.62 | 1.6 | 1.65 | 40.67 | 45.39 | 47.58 | 0 | - - - | - - - | - - - | - - - | 33548 | 29398 | 30685 | 93632 | Over-range | 12783 | 12189 | 14256 | 39392 | 12425 | 12031 | 13024 | 37896 | 30916 | 26679 | 27064 | 84658 | 30916 | 26679 | 27064 | 84658 | - - - | - - - | - - - | - - -
5/9/2026 | 4:30:00 AM | 285.79 | 283.27 | 282.9 | 495.16 | 488.42 | 492.02 | 116.5185 | 103.2981 | 107.8525 | 2.6503 | 1.436 | 1.43 | 1.428 | 1.904 | 1.885 | 1.952 | Over-range | 59.99 | 30772 | 26614 | 27040 | 84426 | - - - | - - - | - - - | - - - | 30772 | 26614 | 27040 | 84426 | 2965 | 1966 | 5703 | 10634 | - - - | - - - | - - - | - - - | 2965 | 1966 | 5703 | 10634 | 33270 | 29240 | 30491 | 93001 | # # # | # # # | # # # | # # # | 0.925 | 0.91 | 0.887 | 0.908 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.126 | 1.68 | 1.63 | 1.63 | 1.62 | 1.6 | 1.64 | 40.52 | 45.3 | 47.29 | 0 | - - - | - - - | - - - | - - - | 33270 | 29240 | 30491 | 93001 | Over-range | 12638 | 12107 | 14084 | 38987 | 12285 | 11946 | 12878 | 37509 | 30676 | 26538 | 26940 | 84154 | 30676 | 26538 | 26940 | 84154 | - - - | - - - | - - - | - - -
5/9/2026 | 4:45:00 AM | 285.61 | 283.13 | 282.83 | 494.84 | 488.28 | 491.82 | 115.2686 | 102.8107 | 107.1672 | 2.6369 | 1.437 | 1.432 | 1.428 | 1.895 | 1.87 | 1.933 | Over-range | 60 | 30442 | 26499 | 26939 | 83880 | - - - | - - - | - - - | - - - | 30442 | 26499 | 26939 | 83880 | 2922 | 2041 | 5548 | 10512 | - - - | - - - | - - - | - - - | 2922 | 2041 | 5548 | 10512 | 32881 | 29078 | 30281 | 92241 | # # # | # # # | # # # | # # # | 0.926 | 0.911 | 0.89 | 0.909 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.979 | 0.991 | - - - | 0.125 | 1.68 | 1.64 | 1.63 | 1.62 | 1.6 | 1.64 | 40.22 | 44.91 | 46.68 | 0 | - - - | - - - | - - - | - - - | 32881 | 29078 | 30281 | 92241 | Over-range | 12418 | 11969 | 13819 | 38350 | 12069 | 11793 | 12656 | 36881 | 30341 | 26415 | 26850 | 83606 | 30341 | 26415 | 26850 | 83606 | - - - | - - - | - - - | - - -
5/9/2026 | 5:00:00 AM | 285.43 | 282.85 | 282.52 | 494.48 | 487.71 | 491.41 | 117.0081 | 103.7587 | 108.3149 | 2.6508 | 1.437 | 1.431 | 1.428 | 1.904 | 1.89 | 1.952 | Over-range | 59.99 | 30833 | 26687 | 27111 | 84631 | - - - | - - - | - - - | - - - | 30833 | 26687 | 27111 | 84631 | 3006 | 2017 | 5722 | 10745 | - - - | - - - | - - - | - - - | 3006 | 2017 | 5722 | 10745 | 33373 | 29331 | 30584 | 93288 | # # # | # # # | # # # | # # # | 0.924 | 0.91 | 0.886 | 0.907 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.978 | 0.99 | - - - | 0.127 | 1.69 | 1.65 | 1.66 | 1.63 | 1.62 | 1.67 | 40.83 | 45.38 | 47.39 | 0 | - - - | - - - | - - - | - - - | 33373 | 29331 | 30584 | 93288 | Over-range | 12765 | 12168 | 14149 | 39233 | 12406 | 12000 | 12940 | 37733 | 30734 | 26613 | 27011 | 84358 | 30734 | 26613 | 27011 | 84358 | - - - | - - - | - - - | - - -
5/9/2026 | 5:15:00 AM | 285.33 | 282.73 | 282.47 | 494.27 | 487.57 | 491.3 | 116.956 | 103.9244 | 108.3609 | 2.682 | 1.437 | 1.432 | 1.429 | 1.899 | 1.882 | 1.946 | Over-range | 60 | 30827 | 26735 | 27146 | 84708 | - - - | - - - | - - - | - - - | 30827 | 26735 | 27146 | 84708 | 3003 | 2018 | 5687 | 10708 | - - - | - - - | - - - | - - - | 3003 | 2018 | 5687 | 10708 | 33345 | 29363 | 30591 | 93299 | # # # | # # # | # # # | # # # | 0.925 | 0.911 | 0.887 | 0.908 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.979 | 0.99 | - - - | 0.126 | 1.72 | 1.68 | 1.69 | 1.65 | 1.65 | 1.7 | 40.61 | 45.15 | 47.17 | 0 | - - - | - - - | - - - | - - - | 33345 | 29363 | 30591 | 93299 | Over-range | 12703 | 12139 | 14099 | 39091 | 12342 | 11969 | 12900 | 37596 | 30720 | 26669 | 27056 | 84444 | 30720 | 26669 | 27056 | 84444 | - - - | - - - | - - - | - - -
5/9/2026 | 5:30:00 AM | 285.2 | 282.72 | 282.36 | 494.15 | 487.5 | 491.03 | 116.4402 | 104.0573 | 107.6038 | 2.6765 | 1.437 | 1.432 | 1.429 | 1.886 | 1.882 | 1.936 | Over-range | 60.01 | 30682 | 26800 | 26990 | 84472 | - - - | - - - | - - - | - - - | 30682 | 26800 | 26990 | 84472 | 3099 | 1992 | 5557 | 10648 | - - - | - - - | - - - | - - - | 3099 | 1992 | 5557 | 10648 | 33180 | 29399 | 30364 | 92943 | # # # | # # # | # # # | # # # | 0.925 | 0.912 | 0.889 | 0.909 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.979 | 0.991 | - - - | 0.126 | 1.73 | 1.68 | 1.69 | 1.66 | 1.66 | 1.71 | 40.4 | 44.83 | 46.88 | 0 | - - - | - - - | - - - | - - - | 33180 | 29399 | 30364 | 92943 | Over-range | 12623 | 12082 | 13904 | 38750 | 12236 | 11917 | 12745 | 37259 | 30579 | 26741 | 26896 | 84216 | 30579 | 26741 | 26896 | 84216 | - - - | - - - | - - - | - - -
5/9/2026 | 5:45:00 AM | 285.11 | 282.49 | 282.22 | 493.86 | 487.14 | 490.9 | 114.8499 | 102.3891 | 106.76 | 2.6369 | 1.436 | 1.431 | 1.428 | 1.89 | 1.867 | 1.928 | Over-range | 60.01 | 30293 | 26358 | 26803 | 83455 | - - - | - - - | - - - | - - - | 30293 | 26358 | 26803 | 83455 | 2891 | 2029 | 5500 | 10420 | - - - | - - - | - - - | - - - | 2891 | 2029 | 5500 | 10420 | 32707 | 28897 | 30101 | 91706 | # # # | # # # | # # # | # # # | 0.926 | 0.912 | 0.89 | 0.91 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.979 | 0.991 | - - - | 0.125 | 1.71 | 1.64 | 1.68 | 1.63 | 1.63 | 1.68 | 40.06 | 44.58 | 46.39 | 0 | - - - | - - - | - - - | - - - | 32707 | 28897 | 30101 | 91706 | Over-range | 12321 | 11840 | 13691 | 37994 | 11977 | 11665 | 12538 | 36537 | 30194 | 26297 | 26714 | 83205 | 30194 | 26297 | 26714 | 83205 | - - - | - - - | - - - | - - -
5/9/2026 | 6:00:00 AM | 285 | 282.51 | 282.2 | 493.79 | 487.19 | 490.74 | 116.3217 | 104.0307 | 107.8738 | 2.6734 | 1.437 | 1.432 | 1.429 | 1.89 | 1.879 | 1.931 | Over-range | 60 | 30621 | 26767 | 27062 | 84450 | - - - | - - - | - - - | - - - | 30621 | 26767 | 27062 | 84450 | 3042 | 2064 | 5537 | 10642 | - - - | - - - | - - - | - - - | 3042 | 2064 | 5537 | 10642 | 33128 | 29373 | 30424 | 92925 | # # # | # # # | # # # | # # # | 0.924 | 0.911 | 0.889 | 0.909 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.98 | 0.991 | - - - | 0.126 | 1.71 | 1.65 | 1.67 | 1.64 | 1.63 | 1.68 | 40.56 | 44.88 | 46.76 | 0 | - - - | - - - | - - - | - - - | 33128 | 29373 | 30424 | 92925 | Over-range | 12636 | 12091 | 13898 | 38758 | 12264 | 11913 | 12748 | 37269 | 30527 | 26693 | 26978 | 84197 | 30527 | 26693 | 26978 | 84197 | - - - | - - - | - - - | - - -
5/9/2026 | 6:15:00 AM | 284.77 | 282.31 | 282.02 | 493.38 | 486.89 | 490.38 | 116.4268 | 104.4553 | 108.1901 | 2.7029 | 1.437 | 1.432 | 1.429 | 1.886 | 1.872 | 1.925 | Over-range | 60 | 30634 | 26873 | 27153 | 84660 | - - - | - - - | - - - | - - - | 30634 | 26873 | 27153 | 84660 | 3046 | 2101 | 5494 | 10641 | - - - | - - - | - - - | - - - | 3046 | 2101 | 5494 | 10641 | 33129 | 29471 | 30493 | 93093 | # # # | # # # | # # # | # # # | 0.925 | 0.912 | 0.89 | 0.909 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.98 | 0.991 | - - - | 0.126 | 1.71 | 1.65 | 1.67 | 1.63 | 1.63 | 1.68 | 40.45 | 44.67 | 46.58 | 0 | - - - | - - - | - - - | - - - | 33129 | 29471 | 30493 | 93093 | Over-range | 12604 | 12096 | 13871 | 38701 | 12230 | 11911 | 12736 | 37209 | 30526 | 26817 | 27065 | 84408 | 30526 | 26817 | 27065 | 84408 | - - - | - - - | - - - | - - -
5/9/2026 | 6:30:00 AM | 284.65 | 282.26 | 281.91 | 493.26 | 486.77 | 490.14 | 116.4996 | 104.6824 | 107.8236 | 2.684 | 1.436 | 1.432 | 1.429 | 1.88 | 1.876 | 1.926 | Over-range | 60.01 | 30632 | 26936 | 27047 | 84615 | - - - | - - - | - - - | - - - | 30632 | 26936 | 27047 | 84615 | 3137 | 2044 | 5453 | 10634 | - - - | - - - | - - - | - - - | 3137 | 2044 | 5453 | 10634 | 33137 | 29529 | 30379 | 93044 | # # # | # # # | # # # | # # # | 0.924 | 0.912 | 0.89 | 0.909 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.98 | 0.991 | - - - | 0.126 | 1.7 | 1.65 | 1.66 | 1.63 | 1.62 | 1.67 | 40.43 | 44.63 | 46.65 | 0 | - - - | - - - | - - - | - - - | 33137 | 29529 | 30379 | 93044 | Over-range | 12632 | 12098 | 13826 | 38685 | 12236 | 11923 | 12706 | 37195 | 30542 | 26860 | 26966 | 84368 | 30542 | 26860 | 26966 | 84368 | - - - | - - - | - - - | - - -
5/9/2026 | 6:45:00 AM | 284.71 | 282.32 | 282.05 | 493.31 | 486.98 | 490.35 | 115.179 | 104.0707 | 107.3947 | 2.7013 | 1.435 | 1.431 | 1.428 | 1.873 | 1.853 | 1.903 | Over-range | 60.01 | 30338 | 26815 | 27055 | 84208 | - - - | - - - | - - - | - - - | 30338 | 26815 | 27055 | 84208 | 3017 | 2152 | 5316 | 10485 | - - - | - - - | - - - | - - - | 3017 | 2152 | 5316 | 10485 | 32754 | 29353 | 30262 | 92369 | # # # | # # # | # # # | # # # | 0.926 | 0.914 | 0.894 | 0.912 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.981 | 0.991 | - - - | 0.125 | 1.68 | 1.64 | 1.64 | 1.62 | 1.61 | 1.65 | 39.89 | 44.08 | 45.76 | 0 | - - - | - - - | - - - | - - - | 32754 | 29353 | 30262 | 92369 | Over-range | 12336 | 11933 | 13548 | 37935 | 11961 | 11737 | 12461 | 36457 | 30234 | 26759 | 26971 | 83964 | 30234 | 26759 | 26971 | 83964 | - - - | - - - | - - - | - - -
5/9/2026 | 7:00:00 AM | 284.62 | 282.26 | 282.02 | 493.16 | 486.92 | 490.23 | 118.0074 | 106.6883 | 109.8272 | 2.7405 | 1.437 | 1.432 | 1.43 | 1.869 | 1.863 | 1.906 | Over-range | 60.01 | 31052 | 27487 | 27647 | 86187 | - - - | - - - | - - - | - - - | 31052 | 27487 | 27647 | 86187 | 3192 | 2163 | 5453 | 10808 | - - - | - - - | - - - | - - - | 3192 | 2163 | 5453 | 10808 | 33562 | 30095 | 30955 | 94613 | # # # | # # # | # # # | # # # | 0.925 | 0.913 | 0.893 | 0.911 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.981 | 0.991 | - - - | 0.125 | 1.73 | 1.67 | 1.72 | 1.65 | 1.66 | 1.72 | 40.11 | 44.17 | 46 | 0 | - - - | - - - | - - - | - - - | 33562 | 30095 | 30955 | 94613 | Over-range | 12729 | 12252 | 13918 | 39018 | 12322 | 12059 | 12805 | 37491 | 30962 | 27429 | 27561 | 85951 | 30962 | 27429 | 27561 | 85951 | - - - | - - - | - - - | - - -
5/9/2026 | 7:15:00 AM | 284.28 | 281.9 | 281.62 | 492.57 | 486.24 | 489.6 | 118.1469 | 106.9365 | 109.7896 | 2.7837 | 1.436 | 1.433 | 1.43 | 1.865 | 1.864 | 1.905 | Over-range | 60 | 31046 | 27527 | 27600 | 86173 | - - - | - - - | - - - | - - - | 31046 | 27527 | 27600 | 86173 | 3225 | 2138 | 5421 | 10784 | - - - | - - - | - - - | - - - | 3225 | 2138 | 5421 | 10784 | 33563 | 30127 | 30902 | 94592 | # # # | # # # | # # # | # # # | 0.925 | 0.914 | 0.893 | 0.911 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.981 | 0.991 | - - - | 0.125 | 1.78 | 1.72 | 1.75 | 1.7 | 1.71 | 1.77 | 40.08 | 44.04 | 45.97 | 0 | - - - | - - - | - - - | - - - | 33563 | 30127 | 30902 | 94592 | Over-range | 12744 | 12241 | 13895 | 38997 | 12329 | 12052 | 12794 | 37477 | 30964 | 27469 | 27524 | 85958 | 30964 | 27469 | 27524 | 85958 | - - - | - - - | - - - | - - -
5/9/2026 | 7:30:00 AM | 283.98 | 281.58 | 281.29 | 492.04 | 485.66 | 489.06 | 119.1804 | 107.8599 | 110.2778 | 2.8314 | 1.436 | 1.433 | 1.43 | 1.86 | 1.865 | 1.909 | Over-range | 60.01 | 31302 | 27755 | 27670 | 86727 | - - - | - - - | - - - | - - - | 31302 | 27755 | 27670 | 86727 | 3335 | 2065 | 5462 | 10862 | - - - | - - - | - - - | - - - | 3335 | 2065 | 5462 | 10862 | 33822 | 30353 | 31004 | 95180 | # # # | # # # | # # # | # # # | 0.926 | 0.914 | 0.892 | 0.911 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.981 | 0.991 | - - - | 0.125 | 1.79 | 1.74 | 1.77 | 1.71 | 1.73 | 1.78 | 39.88 | 43.89 | 46.13 | 0 | - - - | - - - | - - - | - - - | 33822 | 30353 | 31004 | 95180 | Over-range | 12806 | 12285 | 13983 | 39201 | 12364 | 12109 | 12872 | 37666 | 31213 | 27702 | 27593 | 86507 | 31213 | 27702 | 27593 | 86507 | - - - | - - - | - - - | - - -
5/9/2026 | 7:45:00 AM | 283.59 | 281.23 | 280.89 | 491.42 | 485.02 | 488.35 | 120.7449 | 109.2274 | 110.7492 | 2.8435 | 1.436 | 1.433 | 1.431 | 1.847 | 1.869 | 1.913 | Over-range | 60 | 31687 | 28102 | 27720 | 87509 | - - - | - - - | - - - | - - - | 31687 | 28102 | 27720 | 87509 | 3534 | 1912 | 5510 | 10956 | - - - | - - - | - - - | - - - | 3534 | 1912 | 5510 | 10956 | 34218 | 30700 | 31092 | 96011 | # # # | # # # | # # # | # # # | 0.926 | 0.915 | 0.891 | 0.911 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.981 | 0.991 | - - - | 0.125 | 1.82 | 1.77 | 1.81 | 1.74 | 1.77 | 1.82 | 39.53 | 43.68 | 46.31 | 0 | - - - | - - - | - - - | - - - | 34218 | 30700 | 31092 | 96011 | Over-range | 12910 | 12358 | 14078 | 39487 | 12417 | 12209 | 12955 | 37937 | 31606 | 28050 | 27639 | 87295 | 31606 | 28050 | 27639 | 87295 | - - - | - - - | - - - | - - -
5/9/2026 | 8:00:00 AM | 283.29 | 280.83 | 280.59 | 490.78 | 484.39 | 487.88 | 122.6479 | 110.6604 | 111.9382 | 2.9179 | 1.436 | 1.434 | 1.431 | 1.842 | 1.865 | 1.918 | Over-range | 60.01 | 32194 | 28452 | 27955 | 88601 | - - - | - - - | - - - | - - - | 32194 | 28452 | 27955 | 88601 | 3634 | 1788 | 5623 | 11045 | - - - | - - - | - - - | - - - | 3634 | 1788 | 5623 | 11045 | 34717 | 31055 | 31391 | 97164 | # # # | # # # | # # # | # # # | 0.927 | 0.916 | 0.89 | 0.912 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.98 | 0.991 | - - - | 0.125 | 1.83 | 1.78 | 1.83 | 1.75 | 1.79 | 1.83 | 39.08 | 43.51 | 46.47 | 0 | - - - | - - - | - - - | - - - | 34717 | 31055 | 31391 | 97164 | Over-range | 12987 | 12443 | 14276 | 39871 | 12467 | 12313 | 13122 | 38310 | 32102 | 28397 | 27890 | 88388 | 32102 | 28397 | 27890 | 88388 | - - - | - - - | - - - | - - -
5/9/2026 | 8:15:00 AM | 282.86 | 280.48 | 280.22 | 490.1 | 483.8 | 487.18 | 126.0863 | 113.9541 | 113.9318 | 2.9205 | 1.437 | 1.435 | 1.431 | 1.818 | 1.859 | 1.912 | Over-range | 59.99 | 33110 | 29349 | 28443 | 90902 | - - - | - - - | - - - | - - - | 33110 | 29349 | 28443 | 90902 | 3938 | 1598 | 5684 | 11220 | - - - | - - - | - - - | - - - | 3938 | 1598 | 5684 | 11220 | 35638 | 31940 | 31909 | 99487 | # # # | # # # | # # # | # # # | 0.929 | 0.919 | 0.891 | 0.914 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.981 | 0.991 | - - - | 0.123 | 1.88 | 1.83 | 1.89 | 1.79 | 1.84 | 1.89 | 38.25 | 42.77 | 46.23 | 0 | - - - | - - - | - - - | - - - | 35638 | 31940 | 31909 | 99487 | Over-range | 13177 | 12599 | 14458 | 40417 | 12574 | 12496 | 13294 | 38828 | 33027 | 29299 | 28379 | 90705 | 33027 | 29299 | 28379 | 90705 | - - - | - - - | - - - | - - -
5/9/2026 | 8:30:00 AM | 282.66 | 280.34 | 280.13 | 489.75 | 483.66 | 486.91 | 129.5331 | 117.0035 | 116.1452 | 2.9326 | 1.437 | 1.435 | 1.431 | 1.804 | 1.854 | 1.913 | Over-range | 60.01 | 34041 | 30165 | 28976 | 93182 | - - - | - - - | - - - | - - - | 34041 | 30165 | 28976 | 93182 | 4172 | 1411 | 5802 | 11385 | - - - | - - - | - - - | - - - | 4172 | 1411 | 5802 | 11385 | 36586 | 32777 | 32515 | 101878 | # # # | # # # | # # # | # # # | 0.931 | 0.92 | 0.891 | 0.915 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.98 | 0.991 | - - - | 0.122 | 1.87 | 1.84 | 1.89 | 1.79 | 1.84 | 1.89 | 37.64 | 42.39 | 46.26 | 0 | - - - | - - - | - - - | - - - | 36586 | 32777 | 32515 | 101878 | Over-range | 13399 | 12821 | 14749 | 41175 | 12733 | 12743 | 13560 | 39570 | 33955 | 30127 | 28913 | 92994 | 33955 | 30127 | 28913 | 92994 | - - - | - - - | - - - | - - -
5/9/2026 | 8:45:00 AM | 282.23 | 279.81 | 279.54 | 488.99 | 482.61 | 486.04 | 133.9237 | 121.028 | 119.6772 | 2.998 | 1.437 | 1.436 | 1.432 | 1.788 | 1.847 | 1.907 | Over-range | 60 | 35210 | 31235 | 29868 | 96313 | - - - | - - - | - - - | - - - | 35210 | 31235 | 29868 | 96313 | 4354 | 1369 | 5915 | 11638 | - - - | - - - | - - - | - - - | 4354 | 1369 | 5915 | 11638 | 37771 | 33841 | 33432 | 105044 | # # # | # # # | # # # | # # # | 0.932 | 0.923 | 0.893 | 0.917 | # # # | # # # | # # # | - - - | 0.992 | 0.999 | 0.981 | 0.991 | - - - | 0.121 | 1.87 | 1.84 | 1.9 | 1.79 | 1.85 | 1.89 | 37 | 41.59 | 45.7 | 0 | - - - | - - - | - - - | - - - | 37771 | 33841 | 33432 | 105044 | Over-range | 13665 | 13022 | 15016 | 41919 | 12953 | 12949 | 13802 | 40271 | 35125 | 31198 | 29804 | 96127 | 35125 | 31198 | 29804 | 96127 | - - - | - - - | - - - | - - -
5/9/2026 | 9:00:00 AM | 282.17 | 279.71 | 279.55 | 488.79 | 482.54 | 486.04 | 137.5506 | 125.0108 | 124.2546 | 3.0636 | 1.438 | 1.437 | 1.432 | 1.779 | 1.82 | 1.878 | Over-range | 60.01 | 36255 | 32355 | 31221 | 99832 | - - - | - - - | - - - | - - - | 36255 | 32355 | 31221 | 99832 | 4301 | 1640 | 5934 | 11875 | - - - | - - - | - - - | - - - | 4301 | 1640 | 5934 | 11875 | 38794 | 34951 | 34719 | 108464 | # # # | # # # | # # # | # # # | 0.935 | 0.926 | 0.899 | 0.92 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.982 | 0.991 | - - - | 0.119 | 1.91 | 1.86 | 1.93 | 1.82 | 1.87 | 1.92 | 36.38 | 40.65 | 44.31 | 0 | - - - | - - - | - - - | - - - | 38794 | 34951 | 34719 | 108464 | Over-range | 13798 | 13215 | 15182 | 42392 | 13110 | 13112 | 13974 | 40695 | 36181 | 32306 | 31151 | 99638 | 36181 | 32306 | 31151 | 99638 | - - - | - - - | - - - | - - -
5/9/2026 | 9:15:00 AM | 282.63 | 280.41 | 280.16 | 489.79 | 483.78 | 486.88 | 139.1801 | 127.5322 | 125.7816 | 3.055 | 1.438 | 1.437 | 1.433 | 1.765 | 1.815 | 1.862 | Over-range | 60.01 | 36743 | 33144 | 31773 | 101660 | - - - | - - - | - - - | - - - | 36743 | 33144 | 31773 | 101660 | 4487 | 1722 | 5839 | 12049 | - - - | - - - | - - - | - - - | 4487 | 1722 | 5839 | 12049 | 39319 | 35747 | 35225 | 110291 | # # # | # # # | # # # | # # # | 0.935 | 0.927 | 0.902 | 0.922 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.983 | 0.992 | - - - | 0.118 | 1.91 | 1.85 | 1.91 | 1.82 | 1.86 | 1.92 | 36.25 | 40.18 | 43.79 | 0 | - - - | - - - | - - - | - - - | 39319 | 35747 | 35225 | 110291 | Over-range | 13993 | 13387 | 15204 | 42760 | 13253 | 13275 | 14038 | 41027 | 36664 | 33094 | 31713 | 101471 | 36664 | 33094 | 31713 | 101471 | - - - | - - - | - - - | - - -
5/9/2026 | 9:30:00 AM | 282.44 | 280 | 279.9 | 489.24 | 483.12 | 486.58 | 140.5278 | 128.011 | 127.5194 | 3.0889 | 1.439 | 1.437 | 1.433 | 1.772 | 1.806 | 1.862 | Over-range | 60.01 | 37140 | 33221 | 32194 | 102555 | - - - | - - - | - - - | - - - | 37140 | 33221 | 32194 | 102555 | 4320 | 1773 | 6012 | 12106 | - - - | - - - | - - - | - - - | 4320 | 1773 | 6012 | 12106 | 39675 | 35830 | 35681 | 111185 | # # # | # # # | # # # | # # # | 0.936 | 0.927 | 0.902 | 0.922 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.983 | 0.992 | - - - | 0.118 | 1.88 | 1.84 | 1.91 | 1.8 | 1.85 | 1.9 | 35.95 | 40.16 | 43.59 | 0 | - - - | - - - | - - - | - - - | 39675 | 35830 | 35681 | 111185 | Over-range | 13948 | 13419 | 15380 | 42939 | 13262 | 13301 | 14156 | 41197 | 37053 | 33179 | 32121 | 102353 | 37053 | 33179 | 32121 | 102353 | - - - | - - - | - - - | - - -
5/9/2026 | 9:45:00 AM | 282.11 | 279.61 | 279.48 | 488.65 | 482.37 | 485.95 | 144.1084 | 131.0874 | 130.5313 | 3.1375 | 1.44 | 1.438 | 1.434 | 1.772 | 1.813 | 1.868 | Over-range | 60.01 | 38039 | 33988 | 32894 | 104921 | - - - | - - - | - - - | - - - | 38039 | 33988 | 32894 | 104921 | 4469 | 1794 | 6181 | 12444 | - - - | - - - | - - - | - - - | 4469 | 1794 | 6181 | 12444 | 40653 | 36652 | 36479 | 113784 | # # # | # # # | # # # | # # # | 0.936 | 0.927 | 0.902 | 0.922 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.983 | 0.992 | - - - | 0.119 | 1.89 | 1.84 | 1.92 | 1.8 | 1.85 | 1.91 | 36.1 | 40.17 | 43.74 | 0 | - - - | - - - | - - - | - - - | 40653 | 36652 | 36479 | 113784 | Over-range | 14343 | 13717 | 15770 | 44028 | 13629 | 13599 | 14508 | 42233 | 37953 | 33941 | 32821 | 104715 | 37953 | 33941 | 32821 | 104715 | - - - | - - - | - - - | - - -
5/9/2026 | 10:00:00 AM | 281.9 | 279.64 | 279.49 | 488.44 | 482.54 | 485.69 | 142.5173 | 131.0086 | 129.7316 | 3.1209 | 1.44 | 1.438 | 1.434 | 1.755 | 1.794 | 1.838 | Over-range | 60.01 | 37612 | 34033 | 32844 | 104489 | - - - | - - - | - - - | - - - | 37612 | 34033 | 32844 | 104489 | 4440 | 1905 | 5871 | 12216 | - - - | - - - | - - - | - - - | 4440 | 1905 | 5871 | 12216 | 40159 | 36622 | 36245 | 113026 | # # # | # # # | # # # | # # # | 0.937 | 0.929 | 0.906 | 0.925 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.984 | 0.992 | - - - | 0.117 | 1.89 | 1.82 | 1.88 | 1.79 | 1.82 | 1.89 | 35.71 | 39.46 | 42.78 | 0 | - - - | - - - | - - - | - - - | 40159 | 36622 | 36245 | 113026 | Over-range | 14071 | 13522 | 15324 | 43082 | 13351 | 13387 | 14154 | 41314 | 37533 | 33983 | 32779 | 104295 | 37533 | 33983 | 32779 | 104295 | - - - | - - - | - - - | - - -
5/9/2026 | 10:15:00 AM | 281.8 | 279.46 | 279.31 | 488.22 | 482.18 | 485.48 | 142.8216 | 130.7795 | 129.8868 | 3.1214 | 1.439 | 1.437 | 1.433 | 1.759 | 1.795 | 1.845 | Over-range | 60 | 37693 | 33940 | 32826 | 104459 | - - - | - - - | - - - | - - - | 37693 | 33940 | 32826 | 104459 | 4398 | 1867 | 5958 | 12223 | - - - | - - - | - - - | - - - | 4398 | 1867 | 5958 | 12223 | 40232 | 36536 | 36265 | 113033 | # # # | # # # | # # # | # # # | 0.937 | 0.929 | 0.905 | 0.924 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.984 | 0.992 | - - - | 0.117 | 1.88 | 1.82 | 1.88 | 1.79 | 1.82 | 1.89 | 35.66 | 39.57 | 42.97 | 0 | - - - | - - - | - - - | - - - | 40232 | 36536 | 36265 | 113033 | Over-range | 14062 | 13522 | 15412 | 43173 | 13355 | 13392 | 14213 | 41407 | 37613 | 33896 | 32755 | 104264 | 37613 | 33896 | 32755 | 104264 | - - - | - - - | - - - | - - -
5/9/2026 | 10:30:00 AM | 281.64 | 279.25 | 279.1 | 487.92 | 481.8 | 485.17 | 144.6371 | 132.18 | 131.3914 | 3.1377 | 1.44 | 1.438 | 1.434 | 1.766 | 1.808 | 1.856 | Over-range | 60 | 38111 | 34247 | 33132 | 105490 | - - - | - - - | - - - | - - - | 38111 | 34247 | 33132 | 105490 | 4481 | 1891 | 6092 | 12463 | - - - | - - - | - - - | - - - | 4481 | 1891 | 6092 | 12463 | 40735 | 36911 | 36671 | 114317 | # # # | # # # | # # # | # # # | 0.936 | 0.928 | 0.904 | 0.923 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.983 | 0.992 | - - - | 0.118 | 1.86 | 1.81 | 1.88 | 1.77 | 1.82 | 1.88 | 36.12 | 39.97 | 43.39 | 0 | - - - | - - - | - - - | - - - | 40735 | 36911 | 36671 | 114317 | Over-range | 14384 | 13768 | 15716 | 44048 | 13668 | 13638 | 14487 | 42248 | 38026 | 34198 | 33065 | 105289 | 38026 | 34198 | 33065 | 105289 | - - - | - - - | - - - | - - -
5/9/2026 | 10:45:00 AM | 281.37 | 278.97 | 278.85 | 487.42 | 481.34 | 484.74 | 143.0084 | 130.8902 | 130.1482 | 3.122 | 1.439 | 1.437 | 1.433 | 1.761 | 1.796 | 1.845 | Over-range | 60.02 | 37678 | 33897 | 32837 | 104412 | - - - | - - - | - - - | - - - | 37678 | 33897 | 32837 | 104412 | 4372 | 1880 | 5965 | 12217 | - - - | - - - | - - - | - - - | 4372 | 1880 | 5965 | 12217 | 40222 | 36502 | 36280 | 113004 | # # # | # # # | # # # | # # # | 0.937 | 0.929 | 0.905 | 0.924 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.984 | 0.992 | - - - | 0.117 | 1.85 | 1.81 | 1.88 | 1.77 | 1.82 | 1.87 | 35.72 | 39.66 | 42.96 | 0 | - - - | - - - | - - - | - - - | 40222 | 36502 | 36280 | 113004 | Over-range | 14074 | 13538 | 15422 | 43210 | 13377 | 13407 | 14222 | 41448 | 37596 | 33858 | 32767 | 104221 | 37596 | 33858 | 32767 | 104221 | - - - | - - - | - - - | - - -
5/9/2026 | 11:00:00 AM | 281.39 | 278.9 | 278.76 | 487.41 | 481.14 | 484.7 | 143.4192 | 130.5998 | 130.1556 | 3.0831 | 1.439 | 1.437 | 1.433 | 1.764 | 1.798 | 1.854 | Over-range | 60.01 | 37808 | 33811 | 32784 | 104403 | - - - | - - - | - - - | - - - | 37808 | 33811 | 32784 | 104403 | 4359 | 1787 | 6070 | 12216 | - - - | - - - | - - - | - - - | 4359 | 1787 | 6070 | 12216 | 40341 | 36412 | 36271 | 113024 | # # # | # # # | # # # | # # # | 0.937 | 0.929 | 0.904 | 0.924 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.983 | 0.992 | - - - | 0.117 | 1.85 | 1.8 | 1.88 | 1.76 | 1.82 | 1.87 | 35.58 | 39.72 | 43.15 | 0 | - - - | - - - | - - - | - - - | 40341 | 36412 | 36271 | 113024 | Over-range | 14064 | 13514 | 15513 | 43284 | 13371 | 13395 | 14276 | 41525 | 37734 | 33765 | 32720 | 104218 | 37734 | 33765 | 32720 | 104218 | - - - | - - - | - - - | - - -
5/9/2026 | 11:15:00 AM | 281.25 | 278.77 | 278.67 | 487.16 | 480.97 | 484.51 | 145.441 | 132.5693 | 132.3576 | 3.1386 | 1.44 | 1.438 | 1.434 | 1.767 | 1.802 | 1.853 | Over-range | 60.01 | 38305 | 34304 | 33343 | 105951 | - - - | - - - | - - - | - - - | 38305 | 34304 | 33343 | 105951 | 4398 | 1908 | 6152 | 12459 | - - - | - - - | - - - | - - - | 4398 | 1908 | 6152 | 12459 | 40905 | 36956 | 36883 | 114745 | # # # | # # # | # # # | # # # | 0.936 | 0.928 | 0.904 | 0.923 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.983 | 0.992 | - - - | 0.118 | 1.87 | 1.81 | 1.88 | 1.77 | 1.82 | 1.88 | 35.91 | 39.82 | 43.19 | 0 | - - - | - - - | - - - | - - - | 40905 | 36956 | 36883 | 114745 | Over-range | 14352 | 13748 | 15769 | 44054 | 13661 | 13615 | 14519 | 42256 | 38225 | 34257 | 33273 | 105755 | 38225 | 34257 | 33273 | 105755 | - - - | - - - | - - - | - - -
5/9/2026 | 11:30:00 AM | 281.14 | 278.79 | 278.62 | 487.08 | 481.01 | 484.31 | 144.394 | 132.5321 | 131.4512 | 3.1654 | 1.44 | 1.438 | 1.434 | 1.753 | 1.791 | 1.836 | Over-range | 60.02 | 38024 | 34339 | 33189 | 105551 | - - - | - - - | - - - | - - - | 38024 | 34339 | 33189 | 105551 | 4457 | 1897 | 5953 | 12308 | - - - | - - - | - - - | - - - | 4457 | 1897 | 5953 | 12308 | 40579 | 36937 | 36614 | 114130 | # # # | # # # | # # # | # # # | 0.937 | 0.93 | 0.907 | 0.925 | # # # | # # # | # # # | - - - | 0.993 | 0.998 | 0.984 | 0.992 | - - - | 0.117 | 1.87 | 1.81 | 1.88 | 1.78 | 1.81 | 1.88 | 35.59 | 39.34 | 42.66 | 0 | - - - | - - - | - - - | - - - | 40579 | 36937 | 36614 | 114130 | Over-range | 14169 | 13606 | 15458 | 43403 | 13449 | 13473 | 14265 | 41621 | 37938 | 34303 | 33118 | 105359 | 37938 | 34303 | 33118 | 105359 | - - - | - - - | - - - | - - -
5/9/2026 | 11:45:00 AM | 280.99 | 278.51 | 278.39 | 486.71 | 480.49 | 484.02 | 147.3243 | 134.6004 | 134.0846 | 3.354 | 1.44 | 1.439 | 1.435 | 1.763 | 1.797 | 1.848 | Over-range | 60.01 | 38770 | 34814 | 33764 | 107348 | - - - | - - - | - - - | - - - | 38770 | 34814 | 33764 | 107348 | 4487 | 1895 | 6214 | 12596 | - - - | - - - | - - - | - - - | 4487 | 1895 | 6214 | 12596 | 41396 | 37487 | 37326 | 116209 | # # # | # # # | # # # | # # # | 0.937 | 0.929 | 0.905 | 0.924 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.983 | 0.992 | - - - | 0.117 | 1.87 | 1.83 | 1.89 | 1.78 | 1.83 | 1.89 | 35.83 | 39.69 | 43.06 | 0 | - - - | - - - | - - - | - - - | 41396 | 37487 | 37326 | 116209 | Over-range | 14508 | 13901 | 15914 | 44508 | 13796 | 13771 | 14651 | 42688 | 38690 | 34771 | 33690 | 107151 | 38690 | 34771 | 33690 | 107151 | - - - | - - - | - - - | - - -
5/9/2026 | 12:00:00 PM | 280.79 | 278.36 | 278.25 | 486.4 | 480.28 | 483.72 | 146.1995 | 133.9918 | 133.2325 | 3.384 | 1.44 | 1.438 | 1.435 | 1.754 | 1.786 | 1.834 | Over-range | 60.02 | 38480 | 34675 | 33610 | 106765 | - - - | - - - | - - - | - - - | 38480 | 34675 | 33610 | 106765 | 4416 | 1894 | 6077 | 12387 | - - - | - - - | - - - | - - - | 4416 | 1894 | 6077 | 12387 | 41037 | 37287 | 37060 | 115384 | # # # | # # # | # # # | # # # | 0.938 | 0.93 | 0.907 | 0.925 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.984 | 0.992 | - - - | 0.116 | 1.86 | 1.82 | 1.89 | 1.77 | 1.83 | 1.88 | 35.43 | 39.27 | 42.45 | 0 | - - - | - - - | - - - | - - - | 41037 | 37287 | 37060 | 115384 | Over-range | 14254 | 13710 | 15610 | 43748 | 13552 | 13578 | 14379 | 41958 | 38405 | 34631 | 33537 | 106573 | 38405 | 34631 | 33537 | 106573 | - - - | - - - | - - - | - - -
5/9/2026 | 12:15:00 PM | 280.86 | 278.39 | 278.33 | 486.47 | 480.35 | 483.88 | 149.3533 | 136.4826 | 136.3952 | 3.3886 | 1.441 | 1.439 | 1.435 | 1.76 | 1.788 | 1.84 | Over-range | 60.01 | 39331 | 35312 | 34400 | 109043 | - - - | - - - | - - - | - - - | 39331 | 35312 | 34400 | 109043 | 4461 | 1985 | 6296 | 12741 | - - - | - - - | - - - | - - - | 4461 | 1985 | 6296 | 12741 | 41947 | 37994 | 37961 | 117902 | # # # | # # # | # # # | # # # | 0.938 | 0.929 | 0.906 | 0.925 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.984 | 0.992 | - - - | 0.117 | 1.85 | 1.81 | 1.88 | 1.76 | 1.82 | 1.87 | 35.57 | 39.47 | 42.64 | 0 | - - - | - - - | - - - | - - - | 41947 | 37994 | 37961 | 117902 | Over-range | 14579 | 14023 | 16051 | 44838 | 13879 | 13882 | 14765 | 42989 | 39245 | 35263 | 34326 | 108834 | 39245 | 35263 | 34326 | 108834 | - - - | - - - | - - - | - - -
5/9/2026 | 12:30:00 PM | 280.98 | 278.43 | 278.31 | 486.66 | 480.31 | 483.97 | 150.4477 | 136.8091 | 136.8456 | 3.4898 | 1.44 | 1.438 | 1.434 | 1.764 | 1.793 | 1.853 | Over-range | 60 | 39648 | 35396 | 34447 | 109490 | - - - | - - - | - - - | - - - | 39648 | 35396 | 34447 | 109490 | 4479 | 1866 | 6448 | 12793 | - - - | - - - | - - - | - - - | 4479 | 1866 | 6448 | 12793 | 42272 | 38091 | 38085 | 118448 | # # # | # # # | # # # | # # # | 0.938 | 0.929 | 0.905 | 0.924 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.117 | 1.84 | 1.8 | 1.86 | 1.75 | 1.81 | 1.86 | 35.51 | 39.57 | 42.96 | 0 | - - - | - - - | - - - | - - - | 42272 | 38091 | 38085 | 118448 | Over-range | 14663 | 14074 | 16243 | 45187 | 13962 | 13949 | 14908 | 43338 | 39557 | 35350 | 34371 | 109278 | 39557 | 35350 | 34371 | 109278 | - - - | - - - | - - - | - - -
5/9/2026 | 12:45:00 PM | 280.91 | 278.42 | 278.31 | 486.57 | 480.34 | 483.9 | 148.9295 | 135.8014 | 135.7526 | 3.4772 | 1.441 | 1.438 | 1.435 | 1.755 | 1.78 | 1.839 | Over-range | 60 | 39280 | 35169 | 34249 | 108697 | - - - | - - - | - - - | - - - | 39280 | 35169 | 34249 | 108697 | 4385 | 1877 | 6307 | 12569 | - - - | - - - | - - - | - - - | 4385 | 1877 | 6307 | 12569 | 41822 | 37799 | 37770 | 117391 | # # # | # # # | # # # | # # # | 0.939 | 0.93 | 0.907 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.116 | 1.84 | 1.79 | 1.86 | 1.75 | 1.8 | 1.85 | 35.07 | 39.15 | 42.38 | 0 | - - - | - - - | - - - | - - - | 41822 | 37799 | 37770 | 117391 | Over-range | 14356 | 13852 | 15921 | 44326 | 13669 | 13723 | 14618 | 42507 | 39193 | 35117 | 34180 | 108489 | 39193 | 35117 | 34180 | 108489 | - - - | - - - | - - - | - - -
5/9/2026 | 1:00:00 PM | 280.9 | 278.41 | 278.33 | 486.54 | 480.36 | 483.92 | 150.2433 | 136.9289 | 136.9801 | 3.4413 | 1.441 | 1.439 | 1.435 | 1.762 | 1.789 | 1.845 | Over-range | 60.01 | 39590 | 35432 | 34531 | 109553 | - - - | - - - | - - - | - - - | 39590 | 35432 | 34531 | 109553 | 4461 | 1934 | 6392 | 12787 | - - - | - - - | - - - | - - - | 4461 | 1934 | 6392 | 12787 | 42204 | 38122 | 38125 | 118451 | # # # | # # # | # # # | # # # | 0.938 | 0.929 | 0.906 | 0.925 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.117 | 1.82 | 1.78 | 1.84 | 1.73 | 1.79 | 1.84 | 35.49 | 39.49 | 42.72 | 0 | - - - | - - - | - - - | - - - | 42204 | 38122 | 38125 | 118451 | Over-range | 14622 | 14066 | 16159 | 45043 | 13924 | 13932 | 14841 | 43190 | 39503 | 35381 | 34448 | 109332 | 39503 | 35381 | 34448 | 109332 | - - - | - - - | - - - | - - -
5/9/2026 | 1:15:00 PM | 281.17 | 278.65 | 278.52 | 487.01 | 480.7 | 484.31 | 151.5194 | 137.5434 | 137.7629 | 3.556 | 1.441 | 1.438 | 1.435 | 1.767 | 1.795 | 1.857 | Over-range | 60 | 39971 | 35610 | 34698 | 110279 | - - - | - - - | - - - | - - - | 39971 | 35610 | 34698 | 110279 | 4490 | 1867 | 6562 | 12919 | - - - | - - - | - - - | - - - | 4490 | 1867 | 6562 | 12919 | 42602 | 38326 | 38369 | 119297 | # # # | # # # | # # # | # # # | 0.938 | 0.929 | 0.904 | 0.924 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.982 | 0.992 | - - - | 0.117 | 1.78 | 1.75 | 1.81 | 1.71 | 1.76 | 1.8 | 35.5 | 39.67 | 43.01 | 0 | - - - | - - - | - - - | - - - | 42602 | 38326 | 38369 | 119297 | Over-range | 14737 | 14171 | 16377 | 45499 | 14036 | 14047 | 15005 | 43626 | 39873 | 35555 | 34609 | 110037 | 39873 | 35555 | 34609 | 110037 | - - - | - - - | - - - | - - -
5/9/2026 | 1:30:00 PM | 281.12 | 278.5 | 278.43 | 486.83 | 480.45 | 484.24 | 152.0637 | 137.5897 | 138.3868 | 3.5559 | 1.44 | 1.437 | 1.434 | 1.771 | 1.791 | 1.859 | Over-range | 60.01 | 40133 | 35596 | 34835 | 110564 | - - - | - - - | - - - | - - - | 40133 | 35596 | 34835 | 110564 | 4414 | 1873 | 6648 | 12936 | - - - | - - - | - - - | - - - | 4414 | 1873 | 6648 | 12936 | 42748 | 38318 | 38531 | 119597 | # # # | # # # | # # # | # # # | 0.939 | 0.929 | 0.904 | 0.925 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.982 | 0.992 | - - - | 0.117 | 1.78 | 1.75 | 1.81 | 1.7 | 1.76 | 1.8 | 35.39 | 39.71 | 43 | 0 | - - - | - - - | - - - | - - - | 42748 | 38318 | 38531 | 119597 | Over-range | 14721 | 14183 | 16468 | 45597 | 14043 | 14058 | 15066 | 43723 | 40037 | 35542 | 34744 | 110322 | 40037 | 35542 | 34744 | 110322 | - - - | - - - | - - - | - - -
5/9/2026 | 1:45:00 PM | 281.15 | 278.73 | 278.62 | 487.03 | 480.92 | 484.35 | 150.3565 | 137.1942 | 137.028 | 3.446 | 1.44 | 1.437 | 1.434 | 1.758 | 1.783 | 1.841 | Over-range | 60 | 39681 | 35563 | 34615 | 109858 | - - - | - - - | - - - | - - - | 39681 | 35563 | 34615 | 109858 | 4455 | 1899 | 6353 | 12708 | - - - | - - - | - - - | - - - | 4455 | 1899 | 6353 | 12708 | 42262 | 38232 | 38170 | 118664 | # # # | # # # | # # # | # # # | 0.939 | 0.93 | 0.907 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.116 | 1.78 | 1.74 | 1.79 | 1.7 | 1.74 | 1.78 | 35.23 | 39.3 | 42.46 | 0 | - - - | - - - | - - - | - - - | 42262 | 38232 | 38170 | 118664 | Over-range | 14540 | 14034 | 16083 | 44852 | 13840 | 13905 | 14774 | 43014 | 39583 | 35509 | 34535 | 109626 | 39583 | 35509 | 34535 | 109626 | - - - | - - - | - - - | - - -
5/9/2026 | 2:00:00 PM | 281.26 | 278.74 | 278.71 | 487.12 | 480.97 | 484.58 | 151.416 | 137.3308 | 138.2957 | 3.5376 | 1.44 | 1.437 | 1.434 | 1.771 | 1.783 | 1.852 | Over-range | 60.01 | 40003 | 35569 | 34901 | 110473 | - - - | - - - | - - - | - - - | 40003 | 35569 | 34901 | 110473 | 4309 | 1911 | 6553 | 12772 | - - - | - - - | - - - | - - - | 4309 | 1911 | 6553 | 12772 | 42582 | 38276 | 38539 | 119398 | # # # | # # # | # # # | # # # | 0.939 | 0.929 | 0.906 | 0.925 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.116 | 1.72 | 1.69 | 1.72 | 1.65 | 1.68 | 1.72 | 35.27 | 39.62 | 42.71 | 0 | - - - | - - - | - - - | - - - | 42582 | 38276 | 38539 | 119398 | Over-range | 14591 | 14138 | 16346 | 45290 | 13939 | 14008 | 14975 | 43452 | 39901 | 35506 | 34810 | 110217 | 39901 | 35506 | 34810 | 110217 | - - - | - - - | - - - | - - -
5/9/2026 | 2:15:00 PM | 281.18 | 278.69 | 278.62 | 487 | 480.86 | 484.42 | 152.9059 | 138.8322 | 139.5957 | 3.6337 | 1.44 | 1.437 | 1.434 | 1.768 | 1.784 | 1.852 | Over-range | 60.01 | 40389 | 35965 | 35230 | 111584 | - - - | - - - | - - - | - - - | 40389 | 35965 | 35230 | 111584 | 4368 | 1916 | 6592 | 12876 | - - - | - - - | - - - | - - - | 4368 | 1916 | 6592 | 12876 | 42990 | 38687 | 38890 | 120567 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.906 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.115 | 1.71 | 1.67 | 1.71 | 1.64 | 1.66 | 1.7 | 35.26 | 39.52 | 42.67 | 0 | - - - | - - - | - - - | - - - | 42990 | 38687 | 38890 | 120567 | Over-range | 14725 | 14255 | 16471 | 45667 | 14062 | 14126 | 15094 | 43814 | 40283 | 35909 | 35134 | 111326 | 40283 | 35909 | 35134 | 111326 | - - - | - - - | - - - | - - -
5/9/2026 | 2:30:00 PM | 280.92 | 278.48 | 278.47 | 486.56 | 480.59 | 484.06 | 154.2674 | 140.4209 | 141.3978 | 3.6527 | 1.441 | 1.438 | 1.435 | 1.764 | 1.774 | 1.84 | Over-range | 60 | 40739 | 36378 | 35739 | 112856 | - - - | - - - | - - - | - - - | 40739 | 36378 | 35739 | 112856 | 4349 | 2045 | 6598 | 12993 | - - - | - - - | - - - | - - - | 4349 | 2045 | 6598 | 12993 | 43337 | 39104 | 39374 | 121815 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.908 | 0.927 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.115 | 1.72 | 1.69 | 1.72 | 1.65 | 1.67 | 1.71 | 35.11 | 39.27 | 42.25 | 0 | - - - | - - - | - - - | - - - | 43337 | 39104 | 39374 | 121815 | Over-range | 14777 | 14345 | 16524 | 45852 | 14122 | 14198 | 15149 | 43973 | 40632 | 36320 | 35645 | 112597 | 40632 | 36320 | 35645 | 112597 | - - - | - - - | - - - | - - -
5/9/2026 | 2:45:00 PM | 280.73 | 278.21 | 278.19 | 486.18 | 480.06 | 483.67 | 153.4041 | 139.3372 | 140.3831 | 3.6592 | 1.441 | 1.437 | 1.435 | 1.759 | 1.768 | 1.837 | Over-range | 60.01 | 40519 | 36080 | 35456 | 112055 | - - - | - - - | - - - | - - - | 40519 | 36080 | 35456 | 112055 | 4278 | 1960 | 6577 | 12814 | - - - | - - - | - - - | - - - | 4278 | 1960 | 6577 | 12814 | 43052 | 38756 | 39043 | 120850 | # # # | # # # | # # # | # # # | 0.941 | 0.931 | 0.908 | 0.927 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.114 | 1.71 | 1.68 | 1.71 | 1.64 | 1.67 | 1.71 | 34.73 | 39.06 | 42.02 | 0 | - - - | - - - | - - - | - - - | 43052 | 38756 | 39043 | 120850 | Over-range | 14546 | 14149 | 16343 | 45252 | 13902 | 14012 | 14961 | 43400 | 40418 | 36023 | 35361 | 111801 | 40418 | 36023 | 35361 | 111801 | - - - | - - - | - - - | - - -
5/9/2026 | 3:00:00 PM | 280.61 | 278.13 | 278.11 | 486.01 | 479.95 | 483.5 | 154.6026 | 140.4036 | 141.5093 | 3.7247 | 1.442 | 1.438 | 1.436 | 1.764 | 1.776 | 1.843 | Over-range | 60 | 40794 | 36325 | 35701 | 112820 | - - - | - - - | - - - | - - - | 40794 | 36325 | 35701 | 112820 | 4334 | 2000 | 6667 | 13001 | - - - | - - - | - - - | - - - | 4334 | 2000 | 6667 | 13001 | 43384 | 39050 | 39355 | 121789 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.907 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.115 | 1.71 | 1.68 | 1.71 | 1.64 | 1.67 | 1.71 | 35.04 | 39.3 | 42.29 | 0 | - - - | - - - | - - - | - - - | 43384 | 39050 | 39355 | 121789 | Over-range | 14766 | 14332 | 16559 | 45871 | 14114 | 14191 | 15158 | 43990 | 40690 | 36270 | 35604 | 112563 | 40690 | 36270 | 35604 | 112563 | - - - | - - - | - - - | - - -
5/9/2026 | 3:15:00 PM | 280.5 | 278.07 | 278.08 | 485.82 | 479.92 | 483.37 | 154.2009 | 140.3648 | 141.6156 | 3.641 | 1.442 | 1.438 | 1.436 | 1.763 | 1.772 | 1.836 | Over-range | 60 | 40664 | 36305 | 35763 | 112733 | - - - | - - - | - - - | - - - | 40664 | 36305 | 35763 | 112733 | 4293 | 2085 | 6594 | 12973 | - - - | - - - | - - - | - - - | 4293 | 2085 | 6594 | 12973 | 43253 | 39031 | 39381 | 121665 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.908 | 0.927 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.115 | 1.71 | 1.68 | 1.71 | 1.64 | 1.67 | 1.71 | 35.08 | 39.28 | 42.09 | 0 | - - - | - - - | - - - | - - - | 43253 | 39031 | 39381 | 121665 | Over-range | 14739 | 14330 | 16487 | 45757 | 14098 | 14177 | 15111 | 43879 | 40561 | 36247 | 35673 | 112481 | 40561 | 36247 | 35673 | 112481 | - - - | - - - | - - - | - - -
5/9/2026 | 3:30:00 PM | 280.29 | 277.82 | 277.74 | 485.48 | 479.36 | 482.88 | 154.7365 | 140.5623 | 141.462 | 3.6372 | 1.441 | 1.438 | 1.436 | 1.761 | 1.777 | 1.843 | Over-range | 60.01 | 40772 | 36332 | 35642 | 112746 | - - - | - - - | - - - | - - - | 40772 | 36332 | 35642 | 112746 | 4375 | 1974 | 6633 | 12982 | - - - | - - - | - - - | - - - | 4375 | 1974 | 6633 | 12982 | 43371 | 39051 | 39290 | 121712 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.907 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.115 | 1.7 | 1.68 | 1.71 | 1.63 | 1.67 | 1.7 | 35.04 | 39.25 | 42.29 | 0 | - - - | - - - | - - - | - - - | 43371 | 39051 | 39290 | 121712 | Over-range | 14788 | 14318 | 16534 | 45851 | 14125 | 14181 | 15144 | 43975 | 40675 | 36277 | 35553 | 112504 | 40675 | 36277 | 35553 | 112504 | - - - | - - - | - - - | - - -
5/9/2026 | 3:45:00 PM | 280.37 | 277.8 | 277.78 | 485.52 | 479.32 | 483.03 | 154.9247 | 140.294 | 141.8136 | 3.6582 | 1.441 | 1.438 | 1.436 | 1.768 | 1.778 | 1.847 | Over-range | 60 | 40833 | 36237 | 35704 | 112775 | - - - | - - - | - - - | - - - | 40833 | 36237 | 35704 | 112775 | 4303 | 2005 | 6727 | 13036 | - - - | - - - | - - - | - - - | 4303 | 2005 | 6727 | 13036 | 43435 | 38973 | 39393 | 121801 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.906 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.116 | 1.69 | 1.68 | 1.7 | 1.63 | 1.66 | 1.69 | 35.11 | 39.41 | 42.41 | 0 | - - - | - - - | - - - | - - - | 43435 | 38973 | 39393 | 121801 | Over-range | 14809 | 14343 | 16642 | 46014 | 14169 | 14202 | 15221 | 44129 | 40733 | 36181 | 35616 | 112531 | 40733 | 36181 | 35616 | 112531 | - - - | - - - | - - - | - - -
5/9/2026 | 4:00:00 PM | 280.37 | 277.81 | 277.72 | 485.57 | 479.27 | 482.96 | 155.2293 | 140.4394 | 141.5845 | 3.6894 | 1.442 | 1.438 | 1.436 | 1.765 | 1.781 | 1.852 | Over-range | 60.01 | 40921 | 36284 | 35618 | 112823 | - - - | - - - | - - - | - - - | 40921 | 36284 | 35618 | 112823 | 4360 | 1905 | 6746 | 13011 | - - - | - - - | - - - | - - - | 4360 | 1905 | 6746 | 13011 | 43521 | 39015 | 39321 | 121857 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.906 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.982 | 0.992 | - - - | 0.115 | 1.69 | 1.66 | 1.69 | 1.62 | 1.65 | 1.68 | 35 | 39.38 | 42.53 | 0 | - - - | - - - | - - - | - - - | 43521 | 39015 | 39321 | 121857 | Over-range | 14817 | 14340 | 16657 | 46044 | 14160 | 14213 | 15230 | 44168 | 40821 | 36232 | 35525 | 112578 | 40821 | 36232 | 35525 | 112578 | - - - | - - - | - - - | - - -
5/9/2026 | 4:15:00 PM | 280.25 | 277.79 | 277.71 | 485.41 | 479.3 | 482.82 | 154.8453 | 140.6175 | 141.6531 | 3.6189 | 1.442 | 1.438 | 1.436 | 1.763 | 1.776 | 1.843 | Over-range | 60.01 | 40802 | 36339 | 35688 | 112829 | - - - | - - - | - - - | - - - | 40802 | 36339 | 35688 | 112829 | 4348 | 1976 | 6633 | 12957 | - - - | - - - | - - - | - - - | 4348 | 1976 | 6633 | 12957 | 43395 | 39061 | 39338 | 121795 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.907 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.115 | 1.69 | 1.65 | 1.68 | 1.62 | 1.63 | 1.68 | 35.02 | 39.26 | 42.31 | 0 | - - - | - - - | - - - | - - - | 43395 | 39061 | 39338 | 121795 | Over-range | 14776 | 14326 | 16550 | 45865 | 14121 | 14189 | 15162 | 43997 | 40701 | 36287 | 35592 | 112580 | 40701 | 36287 | 35592 | 112580 | - - - | - - - | - - - | - - -
5/9/2026 | 4:30:00 PM | 280.24 | 277.75 | 277.68 | 485.37 | 479.23 | 482.79 | 155.0517 | 140.5242 | 141.8787 | 3.6914 | 1.441 | 1.438 | 1.436 | 1.768 | 1.778 | 1.847 | Over-range | 60 | 40846 | 36293 | 35711 | 112850 | - - - | - - - | - - - | - - - | 40846 | 36293 | 35711 | 112850 | 4308 | 1990 | 6712 | 13010 | - - - | - - - | - - - | - - - | 4308 | 1990 | 6712 | 13010 | 43451 | 39030 | 39397 | 121878 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.906 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.115 | 1.67 | 1.65 | 1.67 | 1.61 | 1.63 | 1.67 | 35.11 | 39.4 | 42.43 | 0 | - - - | - - - | - - - | - - - | 43451 | 39030 | 39397 | 121878 | Over-range | 14818 | 14359 | 16638 | 46033 | 14177 | 14220 | 15224 | 44157 | 40747 | 36234 | 35622 | 112602 | 40747 | 36234 | 35622 | 112602 | - - - | - - - | - - - | - - -
5/9/2026 | 4:45:00 PM | 280.14 | 277.63 | 277.55 | 485.2 | 478.99 | 482.6 | 155.8431 | 141.1654 | 142.3984 | 3.7384 | 1.442 | 1.438 | 1.436 | 1.767 | 1.78 | 1.849 | Over-range | 60 | 41033 | 36434 | 35801 | 113268 | - - - | - - - | - - - | - - - | 41033 | 36434 | 35801 | 113268 | 4379 | 1987 | 6784 | 13150 | - - - | - - - | - - - | - - - | 4379 | 1987 | 6784 | 13150 | 43658 | 39192 | 39522 | 122372 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.906 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.982 | 0.992 | - - - | 0.116 | 1.69 | 1.67 | 1.7 | 1.62 | 1.66 | 1.69 | 35.14 | 39.49 | 42.54 | 0 | - - - | - - - | - - - | - - - | 43658 | 39192 | 39522 | 122372 | Over-range | 14911 | 14441 | 16741 | 46316 | 14253 | 14303 | 15304 | 44410 | 40935 | 36376 | 35708 | 113019 | 40935 | 36376 | 35708 | 113019 | - - - | - - - | - - - | - - -
5/9/2026 | 5:00:00 PM | 280.08 | 277.52 | 277.48 | 485.05 | 478.82 | 482.52 | 156.2036 | 141.2187 | 142.9129 | 3.6651 | 1.441 | 1.438 | 1.436 | 1.769 | 1.777 | 1.849 | Over-range | 60.01 | 41124 | 36426 | 35910 | 113460 | - - - | - - - | - - - | - - - | 41124 | 36426 | 35910 | 113460 | 4338 | 2002 | 6825 | 13166 | - - - | - - - | - - - | - - - | 4338 | 2002 | 6825 | 13166 | 43750 | 39191 | 39655 | 122596 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.906 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.982 | 0.992 | - - - | 0.116 | 1.69 | 1.66 | 1.7 | 1.62 | 1.65 | 1.69 | 35.14 | 39.53 | 42.6 | 0 | - - - | - - - | - - - | - - - | 43750 | 39191 | 39655 | 122596 | Over-range | 14929 | 14458 | 16823 | 46438 | 14284 | 14319 | 15376 | 44533 | 41027 | 36370 | 35813 | 113209 | 41027 | 36370 | 35813 | 113209 | - - - | - - - | - - - | - - -
5/9/2026 | 5:15:00 PM | 280.34 | 277.89 | 277.76 | 485.61 | 479.42 | 482.92 | 155.6619 | 141.1461 | 142.0779 | 3.7172 | 1.441 | 1.438 | 1.435 | 1.766 | 1.783 | 1.851 | Over-range | 60.01 | 40999 | 36469 | 35738 | 113206 | - - - | - - - | - - - | - - - | 40999 | 36469 | 35738 | 113206 | 4420 | 1935 | 6730 | 13086 | - - - | - - - | - - - | - - - | 4420 | 1935 | 6730 | 13086 | 43638 | 39223 | 39464 | 122324 | # # # | # # # | # # # | # # # | 0.94 | 0.93 | 0.906 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.983 | 0.992 | - - - | 0.116 | 1.67 | 1.64 | 1.67 | 1.6 | 1.63 | 1.66 | 35.21 | 39.44 | 42.67 | 0 | - - - | - - - | - - - | - - - | 43638 | 39223 | 39464 | 122324 | Over-range | 14945 | 14438 | 16738 | 46343 | 14275 | 14307 | 15325 | 44457 | 40900 | 36417 | 35644 | 112962 | 40900 | 36417 | 35644 | 112962 | - - - | - - - | - - - | - - -
5/9/2026 | 5:30:00 PM | 280.26 | 277.85 | 277.77 | 485.47 | 479.44 | 482.86 | 156.1471 | 141.8301 | 142.8261 | 3.7328 | 1.442 | 1.438 | 1.436 | 1.766 | 1.779 | 1.845 | Over-range | 60.01 | 41108 | 36635 | 35943 | 113686 | - - - | - - - | - - - | - - - | 41108 | 36635 | 35943 | 113686 | 4429 | 2049 | 6742 | 13220 | - - - | - - - | - - - | - - - | 4429 | 2049 | 6742 | 13220 | 43762 | 39408 | 39673 | 122842 | # # # | # # # | # # # | # # # | 0.939 | 0.93 | 0.906 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.116 | 1.69 | 1.66 | 1.69 | 1.62 | 1.65 | 1.69 | 35.28 | 39.44 | 42.59 | 0 | - - - | - - - | - - - | - - - | 43762 | 39408 | 39673 | 122842 | Over-range | 15008 | 14519 | 16792 | 46536 | 14339 | 14374 | 15379 | 44619 | 41007 | 36582 | 35846 | 113435 | 41007 | 36582 | 35846 | 113435 | - - - | - - - | - - - | - - -
5/9/2026 | 5:45:00 PM | 280.45 | 278.19 | 278.1 | 485.89 | 480.11 | 483.26 | 155.5902 | 142.0658 | 142.6816 | 3.6683 | 1.441 | 1.438 | 1.436 | 1.762 | 1.779 | 1.837 | Over-range | 60.01 | 40960 | 36743 | 35995 | 113698 | - - - | - - - | - - - | - - - | 40960 | 36743 | 35995 | 113698 | 4474 | 2135 | 6615 | 13223 | - - - | - - - | - - - | - - - | 4474 | 2135 | 6615 | 13223 | 43634 | 39522 | 39680 | 122836 | # # # | # # # | # # # | # # # | 0.939 | 0.93 | 0.907 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.116 | 1.69 | 1.65 | 1.69 | 1.62 | 1.64 | 1.68 | 35.44 | 39.39 | 42.42 | 0 | - - - | - - - | - - - | - - - | 43634 | 39522 | 39680 | 122836 | Over-range | 15042 | 14556 | 16698 | 46490 | 14361 | 14398 | 15332 | 44570 | 40861 | 36689 | 35905 | 113455 | 40861 | 36689 | 35905 | 113455 | - - - | - - - | - - - | - - -
5/9/2026 | 6:00:00 PM | 280.42 | 278.12 | 278.02 | 485.82 | 479.94 | 483.17 | 155.1506 | 141.5124 | 142.0542 | 3.6766 | 1.441 | 1.438 | 1.436 | 1.762 | 1.78 | 1.84 | Over-range | 60.02 | 40855 | 36604 | 35825 | 113285 | - - - | - - - | - - - | - - - | 40855 | 36604 | 35825 | 113285 | 4454 | 2057 | 6593 | 13104 | - - - | - - - | - - - | - - - | 4454 | 2057 | 6593 | 13104 | 43506 | 39358 | 39493 | 122357 | # # # | # # # | # # # | # # # | 0.939 | 0.93 | 0.907 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.116 | 1.67 | 1.64 | 1.66 | 1.61 | 1.62 | 1.66 | 35.31 | 39.29 | 42.39 | 0 | - - - | - - - | - - - | - - - | 43506 | 39358 | 39493 | 122357 | Over-range | 14956 | 14462 | 16620 | 46236 | 14277 | 14314 | 15256 | 44341 | 40759 | 36555 | 35735 | 113049 | 40759 | 36555 | 35735 | 113049 | - - - | - - - | - - - | - - -
5/9/2026 | 6:15:00 PM | 280.6 | 278.34 | 278.19 | 486.18 | 480.28 | 483.47 | 154.7948 | 141.2989 | 141.4909 | 3.6927 | 1.441 | 1.438 | 1.435 | 1.759 | 1.78 | 1.839 | Over-range | 60.02 | 40796 | 36594 | 35717 | 113107 | - - - | - - - | - - - | - - - | 40796 | 36594 | 35717 | 113107 | 4477 | 2017 | 6550 | 13044 | - - - | - - - | - - - | - - - | 4477 | 2017 | 6550 | 13044 | 43436 | 39328 | 39361 | 122126 | # # # | # # # | # # # | # # # | 0.939 | 0.931 | 0.907 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.115 | 1.66 | 1.64 | 1.66 | 1.6 | 1.62 | 1.66 | 35.21 | 39.15 | 42.33 | 0 | - - - | - - - | - - - | - - - | 43436 | 39328 | 39361 | 122126 | Over-range | 14911 | 14407 | 16542 | 46059 | 14223 | 14265 | 15189 | 44174 | 40707 | 36541 | 35626 | 112875 | 40707 | 36541 | 35626 | 112875 | - - - | - - - | - - - | - - -
5/9/2026 | 6:30:00 PM | 280.6 | 278.36 | 278.18 | 486.21 | 480.31 | 483.43 | 157.3926 | 143.6911 | 143.7028 | 3.7451 | 1.44 | 1.437 | 1.435 | 1.755 | 1.78 | 1.837 | Over-range | 60.01 | 41473 | 37220 | 36278 | 114971 | - - - | - - - | - - - | - - - | 41473 | 37220 | 36278 | 114971 | 4586 | 2045 | 6663 | 13294 | - - - | - - - | - - - | - - - | 4586 | 2045 | 6663 | 13294 | 44159 | 39993 | 39971 | 124123 | # # # | # # # | # # # | # # # | 0.939 | 0.931 | 0.908 | 0.926 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.983 | 0.992 | - - - | 0.116 | 1.66 | 1.63 | 1.66 | 1.59 | 1.62 | 1.65 | 35.19 | 39.1 | 42.24 | 0 | - - - | - - - | - - - | - - - | 44159 | 39993 | 39971 | 124123 | Over-range | 15165 | 14634 | 16779 | 46778 | 14454 | 14490 | 15399 | 44849 | 41379 | 37170 | 36192 | 114741 | 41379 | 37170 | 36192 | 114741 | - - - | - - - | - - - | - - -
5/9/2026 | 6:45:00 PM | 280.62 | 278.42 | 278.28 | 486.24 | 480.47 | 483.54 | 159.3838 | 145.6914 | 145.9924 | 3.7002 | 1.44 | 1.437 | 1.435 | 1.754 | 1.774 | 1.831 | Over-range | 60.01 | 42023 | 37762 | 36917 | 116702 | - - - | - - - | - - - | - - - | 42023 | 37762 | 36917 | 116702 | 4601 | 2143 | 6710 | 13454 | - - - | - - - | - - - | - - - | 4601 | 2143 | 6710 | 13454 | 44726 | 40562 | 40627 | 125915 | # # # | # # # | # # # | # # # | 0.94 | 0.931 | 0.909 | 0.927 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.984 | 0.992 | - - - | 0.115 | 1.66 | 1.64 | 1.66 | 1.6 | 1.62 | 1.65 | 35.09 | 38.96 | 42 | 0 | - - - | - - - | - - - | - - - | 44726 | 40562 | 40627 | 125915 | Over-range | 15312 | 14810 | 16961 | 47280 | 14604 | 14654 | 15577 | 45325 | 41930 | 37710 | 36830 | 116470 | 41930 | 37710 | 36830 | 116470 | - - - | - - - | - - - | - - -
5/9/2026 | 7:00:00 PM | 280.86 | 278.65 | 278.49 | 486.66 | 480.84 | 483.92 | 159.352 | 145.5696 | 145.5687 | 3.825 | 1.441 | 1.437 | 1.435 | 1.751 | 1.774 | 1.833 | Over-range | 60.02 | 42073 | 37783 | 36835 | 116691 | - - - | - - - | - - - | - - - | 42073 | 37783 | 36835 | 116691 | 4622 | 2069 | 6736 | 13427 | - - - | - - - | - - - | - - - | 4622 | 2069 | 6736 | 13427 | 44755 | 40562 | 40539 | 125856 | # # # | # # # | # # # | # # # | 0.94 | 0.932 | 0.909 | 0.927 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.984 | 0.992 | - - - | 0.115 | 1.68 | 1.65 | 1.68 | 1.61 | 1.63 | 1.68 | 34.9 | 38.83 | 41.96 | 0 | - - - | - - - | - - - | - - - | 44755 | 40562 | 40539 | 125856 | Over-range | 15259 | 14757 | 16927 | 47147 | 14542 | 14611 | 15529 | 45195 | 41980 | 37732 | 36747 | 116458 | 41980 | 37732 | 36747 | 116458 | - - - | - - - | - - - | - - -
5/9/2026 | 7:15:00 PM | 280.59 | 278.35 | 278.24 | 486.15 | 480.37 | 483.49 | 158.7568 | 144.9318 | 145.2878 | 3.7747 | 1.441 | 1.437 | 1.435 | 1.752 | 1.769 | 1.831 | Over-range | 60 | 41900 | 37587 | 36753 | 116241 | - - - | - - - | - - - | - - - | 41900 | 37587 | 36753 | 116241 | 4528 | 2063 | 6695 | 13286 | - - - | - - - | - - - | - - - | 4528 | 2063 | 6695 | 13286 | 44545 | 40342 | 40424 | 125311 | # # # | # # # | # # # | # # # | 0.941 | 0.932 | 0.909 | 0.928 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.984 | 0.992 | - - - | 0.114 | 1.68 | 1.65 | 1.68 | 1.61 | 1.62 | 1.67 | 34.77 | 38.74 | 41.83 | 0 | - - - | - - - | - - - | - - - | 44545 | 40342 | 40424 | 125311 | Over-range | 15122 | 14651 | 16832 | 46808 | 14427 | 14504 | 15443 | 44883 | 41806 | 37540 | 36669 | 116015 | 41806 | 37540 | 36669 | 116015 | - - - | - - - | - - - | - - -
5/9/2026 | 7:30:00 PM | 280.51 | 278.35 | 278.16 | 486.1 | 480.32 | 483.32 | 158.7341 | 145.187 | 145.1308 | 3.6147 | 1.44 | 1.437 | 1.435 | 1.747 | 1.774 | 1.828 | Over-range | 60.01 | 41861 | 37656 | 36718 | 116235 | - - - | - - - | - - - | - - - | 41861 | 37656 | 36718 | 116235 | 4608 | 2091 | 6618 | 13316 | - - - | - - - | - - - | - - - | 4608 | 2091 | 6618 | 13316 | 44527 | 40412 | 40370 | 125309 | # # # | # # # | # # # | # # # | 0.94 | 0.932 | 0.91 | 0.928 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.984 | 0.992 | - - - | 0.115 | 1.67 | 1.64 | 1.66 | 1.61 | 1.62 | 1.66 | 34.87 | 38.72 | 41.81 | 0 | - - - | - - - | - - - | - - - | 44527 | 40412 | 40370 | 125309 | Over-range | 15175 | 14668 | 16778 | 46816 | 14458 | 14518 | 15418 | 44882 | 41770 | 37604 | 36631 | 116004 | 41770 | 37604 | 36631 | 116004 | - - - | - - - | - - - | - - -
5/9/2026 | 7:45:00 PM | 280.65 | 278.48 | 278.28 | 486.35 | 480.52 | 483.54 | 158.93 | 145.1316 | 145.1198 | 3.5178 | 1.44 | 1.437 | 1.434 | 1.75 | 1.779 | 1.835 | Over-range | 59.99 | 41916 | 37643 | 36692 | 116250 | - - - | - - - | - - - | - - - | 41916 | 37643 | 36692 | 116250 | 4637 | 2087 | 6649 | 13373 | - - - | - - - | - - - | - - - | 4637 | 2087 | 6649 | 13373 | 44604 | 40415 | 40383 | 125402 | # # # | # # # | # # # | # # # | 0.94 | 0.931 | 0.909 | 0.927 | # # # | # # # | # # # | - - - | 0.994 | 0.998 | 0.984 | 0.992 | - - - | 0.115 | 1.65 | 1.63 | 1.64 | 1.59 | 1.61 | 1.64 | 34.99 | 38.84 | 42.05 | 0 | - - - | - - - | - - - | - - - | 44604 | 40415 | 40383 | 125402 | Over-range | 15250 | 14711 | 16867 | 47028 | 14527 | 14562 | 15501 | 45086 | 41821 | 37593 | 36607 | 116020 | 41821 | 37593 | 36607 | 116020 | - - - | - - - | - - - | - - -
5/9/2026 | 8:00:00 PM | 279.97 | 277.83 | 277.68 | 485.16 | 479.47 | 482.44 | 235.6289 | 225.3781 | 219.8275 | 7.7689 | 1.44 | 1.436 | 1.435 | 1.631 | 1.608 | 1.727 | Over-range | 60 | 59498 | 56616 | 53982 | 170096 | - - - | - - - | - - - | - - - | 59498 | 56616 | 53982 | 170096 | 18570 | 15273 | 18853 | 52696 | - - - | - - - | - - - | - - - | 18570 | 15273 | 18853 | 52696 | 64362 | 60811 | 59456 | 184630 | # # # | # # # | # # # | # # # | 0.924 | 0.931 | 0.908 | 0.921 | # # # | # # # | # # # | - - - | 0.948 | 0.959 | 0.94 | 0.949 | - - - | 0.31 | 1.69 | 1.66 | 1.7 | 1.62 | 1.65 | 1.69 | 24.72 | 26.59 | 28.77 | 0 | - - - | - - - | - - - | - - - | 64362 | 60811 | 59456 | 184630 | Over-range | 24457 | 22140 | 24879 | 71651 | 13950 | 14010 | 14805 | 43195 | 59311 | 56518 | 53838 | 169666 | 59311 | 56518 | 53838 | 169666 | - - - | - - - | - - - | - - -
5/9/2026 | 8:15:00 PM | 280.24 | 278.21 | 278.05 | 485.68 | 480.19 | 482.96 | 280.908 | 269.052 | 260.5414 | 9.4842 | 1.438 | 1.435 | 1.435 | 1.554 | 1.516 | 1.686 | Over-range | 60 | 72649 | 69900 | 65607 | 208156 | - - - | - - - | - - - | - - - | 72649 | 69900 | 65607 | 208156 | 26569 | 22033 | 26390 | 74991 | - - - | - - - | - - - | - - - | 26569 | 22033 | 26390 | 74991 | 78719 | 74851 | 72443 | 226013 | # # # | # # # | # # # | # # # | 0.923 | 0.934 | 0.906 | 0.921 | # # # | # # # | # # # | - - - | 0.939 | 0.954 | 0.928 | 0.94 | - - - | 0.36 | 1.8 | 1.79 | 1.84 | 1.72 | 1.8 | 1.83 | 19.71 | 21.5 | 23.07 | 0 | - - - | - - - | - - - | - - - | 78719 | 74851 | 72443 | 226013 | Over-range | 30312 | 26770 | 30718 | 88049 | 14592 | 15204 | 15721 | 46141 | 72376 | 69759 | 65509 | 207645 | 72376 | 69759 | 65509 | 207645 | - - - | - - - | - - - | - - -
5/9/2026 | 8:30:00 PM | 280.6 | 278.4 | 278.3 | 486.19 | 480.48 | 483.55 | 270.0052 | 255.8761 | 248.3668 | 8.2794 | 1.438 | 1.435 | 1.434 | 1.56 | 1.524 | 1.709 | Over-range | 60 | 69643 | 66345 | 62142 | 198130 | - - - | - - - | - - - | - - - | 69643 | 66345 | 62142 | 198130 | 26247 | 21376 | 26079 | 73701 | - - - | - - - | - - - | - - - | 26247 | 21376 | 26079 | 73701 | 75724 | 71193 | 69077 | 215994 | # # # | # # # | # # # | # # # | 0.92 | 0.932 | 0.9 | 0.917 | # # # | # # # | # # # | - - - | 0.935 | 0.952 | 0.922 | 0.936 | - - - | 0.372 | 1.67 | 1.67 | 1.73 | 1.6 | 1.68 | 1.7 | 19.7 | 21.54 | 23.39 | 0 | - - - | - - - | - - - | - - - | 75724 | 71193 | 69077 | 215994 | Over-range | 29729 | 25818 | 30162 | 86001 | 13959 | 14472 | 15151 | 44310 | 69389 | 66206 | 62028 | 197623 | 69389 | 66206 | 62028 | 197623 | - - - | - - - | - - - | - - -
5/9/2026 | 8:45:00 PM | 280.82 | 278.56 | 278.41 | 486.57 | 480.68 | 483.84 | 246.4801 | 236.2445 | 229.4224 | 6.7118 | 1.438 | 1.434 | 1.434 | 1.583 | 1.553 | 1.704 | Over-range | 60 | 63136 | 60837 | 57339 | 181312 | - - - | - - - | - - - | - - - | 63136 | 60837 | 57339 | 181312 | 25300 | 21588 | 24649 | 71537 | - - - | - - - | - - - | - - - | 25300 | 21588 | 24649 | 71537 | 69206 | 65803 | 63868 | 198877 | # # # | # # # | # # # | # # # | 0.912 | 0.925 | 0.898 | 0.912 | # # # | # # # | # # # | - - - | 0.928 | 0.942 | 0.918 | 0.93 | - - - | 0.395 | 1.56 | 1.53 | 1.58 | 1.49 | 1.52 | 1.56 | 19.85 | 20.69 | 22.68 | 0 | - - - | - - - | - - - | - - - | 69206 | 65803 | 63868 | 198877 | Over-range | 28343 | 25076 | 28130 | 81718 | 12775 | 12754 | 13554 | 39494 | 62902 | 60708 | 57193 | 180803 | 62902 | 60708 | 57193 | 180803 | - - - | - - - | - - - | - - -
5/9/2026 | 9:00:00 PM | 280.66 | 278.38 | 278.25 | 486.27 | 480.38 | 483.58 | 238.7717 | 229.0374 | 223.3455 | 6.3511 | 1.438 | 1.434 | 1.434 | 1.58 | 1.558 | 1.704 | Over-range | 60.02 | 61033 | 58775 | 55697 | 175505 | - - - | - - - | - - - | - - - | 61033 | 58775 | 55697 | 175505 | 24845 | 21518 | 24340 | 70703 | - - - | - - - | - - - | - - - | 24845 | 21518 | 24340 | 70703 | 67013 | 63758 | 62145 | 192916 | # # # | # # # | # # # | # # # | 0.911 | 0.922 | 0.896 | 0.91 | # # # | # # # | # # # | - - - | 0.926 | 0.939 | 0.916 | 0.927 | - - - | 0.403 | 1.55 | 1.51 | 1.55 | 1.48 | 1.49 | 1.54 | 19.64 | 20.36 | 22.32 | 0 | - - - | - - - | - - - | - - - | 67013 | 63758 | 62145 | 192916 | Over-range | 27672 | 24710 | 27565 | 80091 | 12182 | 12146 | 12939 | 37625 | 60845 | 58631 | 55523 | 174999 | 60845 | 58631 | 55523 | 174999 | - - - | - - - | - - - | - - -
5/9/2026 | 9:15:00 PM | 280.7 | 278.41 | 278.18 | 486.38 | 480.31 | 483.52 | 238.1651 | 226.7644 | 221.3432 | 6.2497 | 1.438 | 1.434 | 1.434 | 1.577 | 1.553 | 1.716 | Over-range | 59.97 | 60856 | 58214 | 54988 | 174058 | - - - | - - - | - - - | - - - | 60856 | 58214 | 54988 | 174058 | 24886 | 21214 | 24496 | 70596 | - - - | - - - | - - - | - - - | 24886 | 21214 | 24496 | 70596 | 66851 | 63133 | 61573 | 191558 | # # # | # # # | # # # | # # # | 0.91 | 0.922 | 0.893 | 0.909 | # # # | # # # | # # # | - - - | 0.925 | 0.939 | 0.913 | 0.926 | - - - | 0.406 | 1.56 | 1.52 | 1.55 | 1.48 | 1.51 | 1.55 | 19.57 | 20.5 | 22.55 | 0 | - - - | - - - | - - - | - - - | 66851 | 63133 | 61573 | 191558 | Over-range | 27670 | 24432 | 27705 | 79988 | 12095 | 12119 | 12942 | 37606 | 60676 | 58064 | 54810 | 173549 | 60676 | 58064 | 54810 | 173549 | - - - | - - - | - - - | - - -
5/9/2026 | 9:30:00 PM | 281.01 | 278.74 | 278.55 | 486.91 | 480.94 | 484.12 | 237.9636 | 226.0505 | 220.6709 | 6.4599 | 1.438 | 1.434 | 1.434 | 1.577 | 1.553 | 1.72 | Over-range | 60 | 60851 | 58077 | 54789 | 173717 | - - - | - - - | - - - | - - - | 60851 | 58077 | 54789 | 173717 | 24935 | 21190 | 24652 | 70778 | - - - | - - - | - - - | - - - | 24935 | 21190 | 24652 | 70778 | 66870 | 63010 | 61468 | 191348 | # # # | # # # | # # # | # # # | 0.91 | 0.922 | 0.891 | 0.908 | # # # | # # # | # # # | - - - | 0.925 | 0.939 | 0.911 | 0.925 | - - - | 0.407 | 1.55 | 1.51 | 1.56 | 1.48 | 1.51 | 1.55 | 19.62 | 20.65 | 22.68 | 0 | - - - | - - - | - - - | - - - | 66870 | 63010 | 61468 | 191348 | Over-range | 27727 | 24438 | 27867 | 80227 | 12123 | 12174 | 12993 | 37775 | 60653 | 57936 | 54613 | 173202 | 60653 | 57936 | 54613 | 173202 | - - - | - - - | - - - | - - -
5/9/2026 | 9:45:00 PM | 281.49 | 279.18 | 279.03 | 487.69 | 481.72 | 484.97 | 231.9028 | 221.0137 | 216.4327 | 6.6294 | 1.436 | 1.432 | 1.432 | 1.583 | 1.572 | 1.729 | Over-range | 60 | 59161 | 56588 | 53605 | 169355 | - - - | - - - | - - - | - - - | 59161 | 56588 | 53605 | 169355 | 24802 | 21430 | 24621 | 70853 | - - - | - - - | - - - | - - - | 24802 | 21430 | 24621 | 70853 | 65261 | 61696 | 60385 | 187342 | # # # | # # # | # # # | # # # | 0.907 | 0.917 | 0.888 | 0.904 | # # # | # # # | # # # | - - - | 0.922 | 0.935 | 0.908 | 0.922 | - - - | 0.418 | 1.46 | 1.43 | 1.44 | 1.39 | 1.4 | 1.43 | 20.05 | 20.97 | 23.01 | 0 | - - - | - - - | - - - | - - - | 65261 | 61696 | 60385 | 187342 | Over-range | 27546 | 24574 | 27798 | 80094 | 11984 | 12020 | 12904 | 37343 | 58940 | 56462 | 53388 | 168790 | 58940 | 56462 | 53388 | 168790 | - - - | - - - | - - - | - - -
5/9/2026 | 10:00:00 PM | 281.88 | 279.59 | 279.43 | 488.39 | 482.43 | 485.64 | 217.0397 | 210.4161 | 206.5599 | 5.647 | 1.436 | 1.432 | 1.43 | 1.599 | 1.599 | 1.712 | Over-range | 60.03 | 55055 | 53452 | 51288 | 159795 | - - - | - - - | - - - | - - - | 55055 | 53452 | 51288 | 159795 | 24159 | 21975 | 23730 | 69864 | - - - | - - - | - - - | - - - | 24159 | 21975 | 23730 | 69864 | 61171 | 58825 | 57712 | 177707 | # # # | # # # | # # # | # # # | 0.9 | 0.909 | 0.889 | 0.899 | # # # | # # # | # # # | - - - | 0.915 | 0.924 | 0.907 | 0.916 | - - - | 0.437 | 1.44 | 1.39 | 1.4 | 1.38 | 1.35 | 1.4 | 20.11 | 20.2 | 21.95 | 0 | - - - | - - - | - - - | - - - | 61171 | 58825 | 57712 | 177707 | Over-range | 26661 | 24560 | 26461 | 77752 | 11274 | 10964 | 11703 | 34112 | 54859 | 53274 | 51108 | 159241 | 54859 | 53274 | 51108 | 159241 | - - - | - - - | - - - | - - -
5/9/2026 | 10:15:00 PM | 281.63 | 279.19 | 279.01 | 487.88 | 481.61 | 485.1 | 220.01 | 210.7394 | 206.5911 | 5.7256 | 1.438 | 1.433 | 1.432 | 1.59 | 1.583 | 1.723 | Over-range | 60.01 | 55845 | 53666 | 51069 | 160580 | - - - | - - - | - - - | - - - | 55845 | 53666 | 51069 | 160580 | 24357 | 21449 | 23953 | 69759 | - - - | - - - | - - - | - - - | 24357 | 21449 | 23953 | 69759 | 61958 | 58834 | 57639 | 178431 | # # # | # # # | # # # | # # # | 0.901 | 0.912 | 0.886 | 0.9 | # # # | # # # | # # # | - - - | 0.916 | 0.928 | 0.905 | 0.916 | - - - | 0.434 | 1.54 | 1.49 | 1.51 | 1.46 | 1.47 | 1.51 | 19.78 | 20.18 | 22.17 | 0 | - - - | - - - | - - - | - - - | 61958 | 58834 | 57639 | 178431 | Over-range | 26834 | 24110 | 26725 | 77791 | 11260 | 11007 | 11852 | 34424 | 55651 | 53507 | 50896 | 160053 | 55651 | 53507 | 50896 | 160053 | - - - | - - - | - - - | - - -
5/9/2026 | 10:30:00 PM | 281.88 | 279.5 | 279.25 | 488.39 | 482.11 | 485.49 | 225.0963 | 213.9957 | 208.9759 | 6.0576 | 1.438 | 1.434 | 1.433 | 1.588 | 1.568 | 1.734 | Over-range | 60.01 | 57293 | 54761 | 51624 | 163678 | - - - | - - - | - - - | - - - | 57293 | 54761 | 51624 | 163678 | 24721 | 21181 | 24295 | 70196 | - - - | - - - | - - - | - - - | 24721 | 21181 | 24295 | 70196 | 63450 | 59811 | 58356 | 181617 | # # # | # # # | # # # | # # # | 0.903 | 0.916 | 0.885 | 0.901 | # # # | # # # | # # # | - - - | 0.918 | 0.932 | 0.904 | 0.918 | - - - | 0.429 | 1.57 | 1.53 | 1.56 | 1.49 | 1.51 | 1.56 | 19.7 | 20.46 | 22.6 | 0 | - - - | - - - | - - - | - - - | 63450 | 59811 | 58356 | 181617 | Over-range | 27266 | 24053 | 27211 | 78704 | 11502 | 11398 | 12255 | 35592 | 57102 | 54610 | 51443 | 163156 | 57102 | 54610 | 51443 | 163156 | - - - | - - - | - - - | - - -
5/9/2026 | 10:45:00 PM | 281.98 | 279.52 | 279.33 | 488.47 | 482.17 | 485.69 | 230.4568 | 218.7498 | 213.7439 | 6.3558 | 1.438 | 1.434 | 1.434 | 1.58 | 1.56 | 1.73 | Over-range | 60.02 | 58863 | 56140 | 52934 | 167937 | - - - | - - - | - - - | - - - | 58863 | 56140 | 52934 | 167937 | 24905 | 21203 | 24578 | 70686 | - - - | - - - | - - - | - - - | 24905 | 21203 | 24578 | 70686 | 64976 | 61140 | 59699 | 185816 | # # # | # # # | # # # | # # # | 0.906 | 0.918 | 0.887 | 0.904 | # # # | # # # | # # # | - - - | 0.92 | 0.935 | 0.906 | 0.921 | - - - | 0.421 | 1.6 | 1.57 | 1.6 | 1.52 | 1.56 | 1.6 | 19.53 | 20.5 | 22.63 | 0 | - - - | - - - | - - - | - - - | 64976 | 61140 | 59699 | 185816 | Over-range | 27512 | 24214 | 27604 | 79523 | 11688 | 11693 | 12566 | 36433 | 58670 | 55992 | 52753 | 167414 | 58670 | 55992 | 52753 | 167414 | - - - | - - - | - - - | - - -
5/9/2026 | 11:00:00 PM | 282.37 | 279.95 | 279.68 | 489.22 | 482.84 | 486.29 | 234.3854 | 221.8708 | 216.4319 | 6.4262 | 1.439 | 1.435 | 1.434 | 1.577 | 1.55 | 1.731 | Over-range | 60.01 | 60047 | 57168 | 53710 | 170925 | - - - | - - - | - - - | - - - | 60047 | 57168 | 53710 | 170925 | 25179 | 21149 | 24822 | 71149 | - - - | - - - | - - - | - - - | 25179 | 21149 | 24822 | 71149 | 66183 | 62113 | 60531 | 188827 | # # # | # # # | # # # | # # # | 0.907 | 0.92 | 0.887 | 0.905 | # # # | # # # | # # # | - - - | 0.922 | 0.938 | 0.907 | 0.922 | - - - | 0.416 | 1.64 | 1.59 | 1.64 | 1.55 | 1.59 | 1.64 | 19.42 | 20.55 | 22.69 | 0 | - - - | - - - | - - - | - - - | 66183 | 62113 | 60531 | 188827 | Over-range | 27830 | 24286 | 27916 | 80251 | 11855 | 11939 | 12774 | 37123 | 59864 | 57009 | 53533 | 170406 | 59864 | 57009 | 53533 | 170406 | - - - | - - - | - - - | - - -
5/9/2026 | 11:15:00 PM | 282.75 | 280.32 | 280.14 | 489.82 | 483.59 | 487.04 | 234.7365 | 221.9337 | 216.7256 | 6.6337 | 1.44 | 1.435 | 1.434 | 1.574 | 1.551 | 1.731 | Over-range | 60.01 | 60252 | 57250 | 53835 | 171337 | - - - | - - - | - - - | - - - | 60252 | 57250 | 53835 | 171337 | 25187 | 21209 | 24967 | 71363 | - - - | - - - | - - - | - - - | 25187 | 21209 | 24967 | 71363 | 66371 | 62212 | 60714 | 189297 | # # # | # # # | # # # | # # # | 0.908 | 0.92 | 0.887 | 0.905 | # # # | # # # | # # # | - - - | 0.922 | 0.937 | 0.907 | 0.922 | - - - | 0.417 | 1.66 | 1.62 | 1.65 | 1.58 | 1.61 | 1.66 | 19.37 | 20.58 | 22.69 | 0 | - - - | - - - | - - - | - - - | 66371 | 62212 | 60714 | 189297 | Over-range | 27835 | 24347 | 28070 | 80479 | 11849 | 11955 | 12829 | 37203 | 60043 | 57112 | 53657 | 170812 | 60043 | 57112 | 53657 | 170812 | - - - | - - - | - - - | - - -
5/9/2026 | 11:30:00 PM | 282.97 | 280.62 | 280.33 | 490.33 | 484.02 | 487.34 | 234.8718 | 222.2155 | 216.3344 | 6.5687 | 1.44 | 1.435 | 1.434 | 1.577 | 1.548 | 1.731 | Over-range | 60.02 | 60292 | 57408 | 53778 | 171478 | - - - | - - - | - - - | - - - | 60292 | 57408 | 53778 | 171478 | 25326 | 21172 | 24947 | 71445 | - - - | - - - | - - - | - - - | 25326 | 21172 | 24947 | 71445 | 66461 | 62359 | 60644 | 189464 | # # # | # # # | # # # | # # # | 0.907 | 0.921 | 0.887 | 0.905 | # # # | # # # | # # # | - - - | 0.922 | 0.938 | 0.907 | 0.922 | - - - | 0.417 | 1.66 | 1.61 | 1.66 | 1.58 | 1.61 | 1.66 | 19.36 | 20.59 | 22.69 | 0 | - - - | - - - | - - - | - - - | 66461 | 62359 | 60644 | 189464 | Over-range | 27963 | 24350 | 28029 | 80571 | 11853 | 12027 | 12778 | 37247 | 60143 | 57219 | 53586 | 170949 | 60143 | 57219 | 53586 | 170949 | - - - | - - - | - - - | - - -
5/9/2026 | 11:45:00 PM | 283.21 | 280.73 | 280.47 | 490.64 | 484.17 | 487.72 | 234.5314 | 221.248 | 216.111 | 6.4539 | 1.44 | 1.435 | 1.434 | 1.574 | 1.551 | 1.735 | Over-range | 60.02 | 60269 | 57149 | 53690 | 171108 | - - - | - - - | - - - | - - - | 60269 | 57149 | 53690 | 171108 | 25276 | 21182 | 25041 | 71499 | - - - | - - - | - - - | - - - | 25276 | 21182 | 25041 | 71499 | 66421 | 62110 | 60613 | 189143 | # # # | # # # | # # # | # # # | 0.907 | 0.92 | 0.886 | 0.905 | # # # | # # # | # # # | - - - | 0.922 | 0.937 | 0.906 | 0.922 | - - - | 0.418 | 1.66 | 1.61 | 1.66 | 1.58 | 1.61 | 1.66 | 19.39 | 20.62 | 22.76 | 0 | - - - | - - - | - - - | - - - | 66421 | 62110 | 60613 | 189143 | Over-range | 27917 | 24324 | 28129 | 80604 | 11852 | 11956 | 12814 | 37215 | 60075 | 56982 | 53514 | 170570 | 60075 | 56982 | 53514 | 170570 | - - - | - - - | - - - | - - -
5/10/2026 | 12:00:00 AM | 283.54 | 281.04 | 280.79 | 491.2 | 484.72 | 488.29 | 233.8747 | 220.6313 | 215.6974 | 6.3771 | 1.44 | 1.435 | 1.435 | 1.573 | 1.552 | 1.734 | Over-range | 60.01 | 60156 | 57032 | 53639 | 170826 | - - - | - - - | - - - | - - - | 60156 | 57032 | 53639 | 170826 | 25287 | 21238 | 25062 | 71587 | - - - | - - - | - - - | - - - | 25287 | 21238 | 25062 | 71587 | 66311 | 62006 | 60566 | 188883 | # # # | # # # | # # # | # # # | 0.907 | 0.92 | 0.886 | 0.904 | # # # | # # # | # # # | - - - | 0.921 | 0.937 | 0.905 | 0.921 | - - - | 0.419 | 1.69 | 1.64 | 1.68 | 1.61 | 1.64 | 1.69 | 19.34 | 20.55 | 22.69 | 0 | - - - | - - - | - - - | - - - | 66311 | 62006 | 60566 | 188883 | Over-range | 27899 | 24334 | 28127 | 80592 | 11787 | 11879 | 12766 | 37019 | 59953 | 56879 | 53453 | 170285 | 59953 | 56879 | 53453 | 170285 | - - - | - - - | - - - | - - -
5/10/2026 | 12:15:00 AM | 283.62 | 281.17 | 280.87 | 491.39 | 484.9 | 488.4 | 232.0331 | 219.5326 | 214.7279 | 6.116 | 1.44 | 1.435 | 1.434 | 1.577 | 1.556 | 1.731 | Over-range | 60 | 59631 | 56712 | 53443 | 169785 | - - - | - - - | - - - | - - - | 59631 | 56712 | 53443 | 169785 | 25245 | 21338 | 24934 | 71517 | - - - | - - - | - - - | - - - | 25245 | 21338 | 24934 | 71517 | 65809 | 61725 | 60310 | 187844 | # # # | # # # | # # # | # # # | 0.906 | 0.919 | 0.886 | 0.904 | # # # | # # # | # # # | - - - | 0.92 | 0.936 | 0.906 | 0.921 | - - - | 0.421 | 1.68 | 1.63 | 1.67 | 1.6 | 1.62 | 1.68 | 19.41 | 20.48 | 22.56 | 0 | - - - | - - - | - - - | - - - | 65809 | 61725 | 60310 | 187844 | Over-range | 27838 | 24367 | 27948 | 80362 | 11733 | 11766 | 12626 | 36653 | 59433 | 56552 | 53255 | 169239 | 59433 | 56552 | 53255 | 169239 | - - - | - - - | - - - | - - -
5/10/2026 | 12:30:00 AM | 284.17 | 281.58 | 281.34 | 492.23 | 485.6 | 489.35 | 230.666 | 218.094 | 214.3045 | 6.0736 | 1.44 | 1.435 | 1.433 | 1.575 | 1.564 | 1.734 | Over-range | 60 | 59372 | 56333 | 53368 | 169073 | - - - | - - - | - - - | - - - | 59372 | 56333 | 53368 | 169073 | 25177 | 21471 | 25055 | 71703 | - - - | - - - | - - - | - - - | 25177 | 21471 | 25055 | 71703 | 65548 | 61410 | 60292 | 187250 | # # # | # # # | # # # | # # # | 0.906 | 0.917 | 0.885 | 0.903 | # # # | # # # | # # # | - - - | 0.92 | 0.934 | 0.905 | 0.92 | - - - | 0.424 | 1.67 | 1.62 | 1.66 | 1.59 | 1.62 | 1.66 | 19.49 | 20.47 | 22.57 | 0 | - - - | - - - | - - - | - - - | 65548 | 61410 | 60292 | 187250 | Over-range | 27776 | 24448 | 28054 | 80478 | 11730 | 11690 | 12620 | 36543 | 59177 | 56165 | 53182 | 168525 | 59177 | 56165 | 53182 | 168525 | - - - | - - - | - - - | - - -
5/10/2026 | 12:45:00 AM | 284.46 | 282.05 | 281.75 | 492.88 | 486.44 | 489.88 | 228.4899 | 217.2296 | 212.9982 | 6.0115 | 1.44 | 1.434 | 1.434 | 1.584 | 1.569 | 1.73 | Over-range | 60 | 58761 | 56092 | 53138 | 167990 | - - - | - - - | - - - | - - - | 58761 | 56092 | 53138 | 167990 | 25182 | 21698 | 24916 | 71795 | - - - | - - - | - - - | - - - | 25182 | 21698 | 24916 | 71795 | 64996 | 61268 | 60011 | 186276 | # # # | # # # | # # # | # # # | 0.904 | 0.916 | 0.885 | 0.902 | # # # | # # # | # # # | - - - | 0.919 | 0.932 | 0.905 | 0.919 | - - - | 0.427 | 1.67 | 1.61 | 1.65 | 1.59 | 1.6 | 1.66 | 19.64 | 20.53 | 22.51 | 0 | - - - | - - - | - - - | - - - | 64996 | 61268 | 60011 | 186276 | Over-range | 27779 | 24648 | 27887 | 80485 | 11728 | 11693 | 12525 | 36376 | 58560 | 55924 | 52955 | 167439 | 58560 | 55924 | 52955 | 167439 | - - - | - - - | - - - | - - -
5/10/2026 | 1:00:00 AM | 284.42 | 282.03 | 281.75 | 492.8 | 486.45 | 489.84 | 227.9764 | 217.2985 | 212.9476 | 6.1061 | 1.44 | 1.434 | 1.433 | 1.586 | 1.573 | 1.729 | Over-range | 60.01 | 58593 | 56064 | 53142 | 167799 | - - - | - - - | - - - | - - - | 58593 | 56064 | 53142 | 167799 | 25157 | 21792 | 24864 | 71813 | - - - | - - - | - - - | - - - | 25157 | 21792 | 24864 | 71813 | 64839 | 61284 | 59997 | 186120 | # # # | # # # | # # # | # # # | 0.904 | 0.915 | 0.886 | 0.902 | # # # | # # # | # # # | - - - | 0.918 | 0.932 | 0.905 | 0.919 | - - - | 0.428 | 1.65 | 1.6 | 1.63 | 1.58 | 1.59 | 1.63 | 19.74 | 20.6 | 22.54 | 0 | - - - | - - - | - - - | - - - | 64839 | 61284 | 59997 | 186120 | Over-range | 27767 | 24749 | 27849 | 80524 | 11753 | 11730 | 12544 | 36428 | 58393 | 55900 | 52952 | 167245 | 58393 | 55900 | 52952 | 167245 | - - - | - - - | - - - | - - -
5/10/2026 | 1:15:00 AM | 284.41 | 281.87 | 281.63 | 492.68 | 486.13 | 489.78 | 228.3822 | 216.8377 | 213.0145 | 6.0503 | 1.44 | 1.434 | 1.433 | 1.583 | 1.572 | 1.733 | Over-range | 60 | 58720 | 55928 | 53077 | 167725 | - - - | - - - | - - - | - - - | 58720 | 55928 | 53077 | 167725 | 25154 | 21701 | 24977 | 71832 | - - - | - - - | - - - | - - - | 25154 | 21701 | 24977 | 71832 | 64954 | 61120 | 59991 | 186064 | # # # | # # # | # # # | # # # | 0.904 | 0.915 | 0.885 | 0.901 | # # # | # # # | # # # | - - - | 0.919 | 0.932 | 0.904 | 0.918 | - - - | 0.428 | 1.66 | 1.62 | 1.65 | 1.58 | 1.61 | 1.65 | 19.72 | 20.6 | 22.59 | 0 | - - - | - - - | - - - | - - - | 64954 | 61120 | 59991 | 186064 | Over-range | 27766 | 24652 | 27959 | 80550 | 11755 | 11695 | 12563 | 36445 | 58525 | 55761 | 52883 | 167168 | 58525 | 55761 | 52883 | 167168 | - - - | - - - | - - - | - - -
5/10/2026 | 1:30:00 AM | 284.46 | 281.82 | 281.67 | 492.66 | 486.09 | 489.9 | 227.8935 | 215.9921 | 212.8671 | 5.9934 | 1.44 | 1.434 | 1.433 | 1.578 | 1.575 | 1.733 | Over-range | 60.01 | 58640 | 55689 | 53027 | 167356 | - - - | - - - | - - - | - - - | 58640 | 55689 | 53027 | 167356 | 25048 | 21672 | 25021 | 71741 | - - - | - - - | - - - | - - - | 25048 | 21672 | 25021 | 71741 | 64825 | 60871 | 59957 | 185654 | # # # | # # # | # # # | # # # | 0.905 | 0.915 | 0.884 | 0.901 | # # # | # # # | # # # | - - - | 0.919 | 0.932 | 0.904 | 0.918 | - - - | 0.429 | 1.67 | 1.62 | 1.65 | 1.59 | 1.61 | 1.66 | 19.63 | 20.51 | 22.53 | 0 | - - - | - - - | - - - | - - - | 64825 | 60871 | 59957 | 185654 | Over-range | 27634 | 24578 | 27981 | 80368 | 11672 | 11593 | 12524 | 36226 | 58441 | 55519 | 52837 | 166797 | 58441 | 55519 | 52837 | 166797 | - - - | - - - | - - - | - - -
5/10/2026 | 1:45:00 AM | 284.69 | 282.21 | 281.97 | 493.2 | 486.76 | 490.3 | 227.2352 | 215.6431 | 211.8631 | 5.9894 | 1.44 | 1.434 | 1.434 | 1.583 | 1.572 | 1.733 | Over-range | 60 | 58448 | 55662 | 52811 | 166921 | - - - | - - - | - - - | - - - | 58448 | 55662 | 52811 | 166921 | 25153 | 21690 | 24989 | 71831 | - - - | - - - | - - - | - - - | 25153 | 21690 | 24989 | 71831 | 64691 | 60856 | 59739 | 185286 | # # # | # # # | # # # | # # # | 0.904 | 0.915 | 0.884 | 0.901 | # # # | # # # | # # # | - - - | 0.918 | 0.931 | 0.903 | 0.918 | - - - | 0.43 | 1.67 | 1.62 | 1.65 | 1.59 | 1.6 | 1.66 | 19.64 | 20.55 | 22.51 | 0 | - - - | - - - | - - - | - - - | 64691 | 60856 | 59739 | 185286 | Over-range | 27724 | 24602 | 27924 | 80424 | 11661 | 11609 | 12462 | 36171 | 58246 | 55494 | 52624 | 166364 | 58246 | 55494 | 52624 | 166364 | - - - | - - - | - - - | - - -
5/10/2026 | 2:00:00 AM | 284.96 | 282.43 | 282.16 | 493.66 | 487.07 | 490.7 | 225.263 | 213.7889 | 210.0573 | 5.8988 | 1.44 | 1.434 | 1.433 | 1.584 | 1.572 | 1.736 | Over-range | 60 | 57912 | 55161 | 52325 | 165397 | - - - | - - - | - - - | - - - | 57912 | 55161 | 52325 | 165397 | 25155 | 21716 | 24950 | 71821 | - - - | - - - | - - - | - - - | 25155 | 21716 | 24950 | 71821 | 64190 | 60380 | 59269 | 183839 | # # # | # # # | # # # | # # # | 0.902 | 0.914 | 0.883 | 0.9 | # # # | # # # | # # # | - - - | 0.917 | 0.93 | 0.902 | 0.916 | - - - | 0.434 | 1.65 | 1.59 | 1.63 | 1.57 | 1.58 | 1.63 | 19.65 | 20.48 | 22.5 | 0 | - - - | - - - | - - - | - - - | 64190 | 60380 | 59269 | 183839 | Over-range | 27688 | 24555 | 27838 | 80251 | 11567 | 11460 | 12347 | 35805 | 57704 | 54989 | 52145 | 164838 | 57704 | 54989 | 52145 | 164838 | - - - | - - - | - - - | - - -
5/10/2026 | 2:15:00 AM | 284.74 | 282.1 | 281.96 | 493.15 | 486.59 | 490.41 | 223.499 | 212.0128 | 209.1282 | 5.8546 | 1.44 | 1.434 | 1.433 | 1.582 | 1.58 | 1.736 | Over-range | 60 | 57398 | 54558 | 52008 | 163964 | - - - | - - - | - - - | - - - | 57398 | 54558 | 52008 | 163964 | 24971 | 21726 | 24929 | 71626 | - - - | - - - | - - - | - - - | 24971 | 21726 | 24929 | 71626 | 63638 | 59809 | 58965 | 182412 | # # # | # # # | # # # | # # # | 0.902 | 0.912 | 0.882 | 0.899 | # # # | # # # | # # # | - - - | 0.916 | 0.929 | 0.901 | 0.916 | - - - | 0.437 | 1.64 | 1.59 | 1.62 | 1.56 | 1.57 | 1.63 | 19.69 | 20.47 | 22.48 | 0 | - - - | - - - | - - - | - - - | 63638 | 59809 | 58965 | 182412 | Over-range | 27482 | 24506 | 27785 | 79936 | 11475 | 11336 | 12270 | 35490 | 57195 | 54388 | 51818 | 163400 | 57195 | 54388 | 51818 | 163400 | - - - | - - - | - - - | - - -
5/10/2026 | 2:30:00 AM | 284.7 | 282.09 | 281.91 | 493.11 | 486.53 | 490.31 | 221.5774 | 210.6601 | 207.4871 | 5.7517 | 1.44 | 1.434 | 1.433 | 1.586 | 1.583 | 1.734 | Over-range | 60.01 | 56816 | 54143 | 51580 | 162539 | - - - | - - - | - - - | - - - | 56816 | 54143 | 51580 | 162539 | 24939 | 21768 | 24785 | 71492 | - - - | - - - | - - - | - - - | 24939 | 21768 | 24785 | 71492 | 63082 | 59423 | 58491 | 180996 | # # # | # # # | # # # | # # # | 0.901 | 0.911 | 0.882 | 0.898 | # # # | # # # | # # # | - - - | 0.915 | 0.927 | 0.901 | 0.915 | - - - | 0.44 | 1.65 | 1.6 | 1.63 | 1.57 | 1.58 | 1.63 | 19.71 | 20.42 | 22.38 | 0 | - - - | - - - | - - - | - - - | 63082 | 59423 | 58491 | 180996 | Over-range | 27410 | 24488 | 27580 | 79628 | 11373 | 11216 | 12097 | 35064 | 56609 | 53966 | 51389 | 161964 | 56609 | 53966 | 51389 | 161964 | - - - | - - - | - - - | - - -
5/10/2026 | 2:45:00 AM | 285.13 | 282.41 | 282.14 | 493.84 | 486.93 | 490.9 | 134.1856 | 121.7588 | 124.3491 | 3.3148 | 1.44 | 1.434 | 1.432 | 1.886 | 1.879 | 1.968 | Over-range | 60.01 | 33368 | 29333 | 29260 | 91961 | - - - | - - - | - - - | - - - | 33368 | 29333 | 29260 | 91961 | 6682 | 5208 | 9001 | 20890 | - - - | - - - | - - - | - - - | 6682 | 5208 | 9001 | 20890 | 36567 | 32435 | 33451 | 102454 | # # # | # # # | # # # | # # # | 0.913 | 0.904 | 0.875 | 0.898 | # # # | # # # | # # # | - - - | 0.971 | 0.975 | 0.951 | 0.965 | - - - | 0.227 | 1.67 | 1.61 | 1.62 | 1.59 | 1.58 | 1.63 | 38.87 | 43.25 | 45.57 | 0 | - - - | - - - | - - - | - - - | 36567 | 32435 | 33451 | 102454 | Over-range | 14944 | 13833 | 16209 | 45161 | 12000 | 11560 | 12595 | 36590 | 33249 | 29251 | 29152 | 91652 | 33249 | 29251 | 29152 | 91652 | - - - | - - - | - - - | - - -
5/10/2026 | 3:00:00 AM | 285.26 | 282.61 | 282.26 | 494.16 | 487.23 | 491.07 | 119.1974 | 104.9905 | 109.5172 | 2.7295 | 1.44 | 1.434 | 1.431 | 1.909 | 1.906 | 1.976 | Over-range | 60 | 31387 | 26949 | 27257 | 85593 | - - - | - - - | - - - | - - - | 31387 | 26949 | 27257 | 85593 | 3139 | 1844 | 5954 | 10937 | - - - | - - - | - - - | - - - | 3139 | 1844 | 5954 | 10937 | 33978 | 29648 | 30893 | 94520 | # # # | # # # | # # # | # # # | 0.924 | 0.909 | 0.882 | 0.906 | # # # | # # # | # # # | - - - | 0.995 | 0.998 | 0.977 | 0.99 | - - - | 0.128 | 1.69 | 1.63 | 1.64 | 1.61 | 1.6 | 1.66 | 40.89 | 45.82 | 48.3 | 0 | - - - | - - - | - - - | - - - | 33978 | 29648 | 30893 | 94520 | Over-range | 13011 | 12358 | 14540 | 40090 | 12626 | 12218 | 13264 | 38570 | 31278 | 26874 | 27160 | 85311 | 31278 | 26874 | 27160 | 85311 | - - - | - - - | - - - | - - -
5/10/2026 | 3:15:00 AM | 285.15 | 282.55 | 282.18 | 494.01 | 487.13 | 490.88 | 127.1622 | 111.6759 | 114.5705 | 2.9633 | 1.44 | 1.434 | 1.431 | 1.879 | 1.9 | 1.986 | Over-range | 60 | 33642 | 28779 | 28458 | 90879 | - - - | - - - | - - - | - - - | 33642 | 28779 | 28458 | 90879 | 3666 | 1436 | 6385 | 11487 | - - - | - - - | - - - | - - - | 3666 | 1436 | 6385 | 11487 | 36253 | 31550 | 32328 | 100131 | # # # | # # # | # # # | # # # | 0.928 | 0.912 | 0.88 | 0.908 | # # # | # # # | # # # | - - - | 0.994 | 0.999 | 0.976 | 0.99 | - - - | 0.126 | 1.71 | 1.66 | 1.68 | 1.63 | 1.64 | 1.68 | 39.27 | 45.05 | 48.53 | 0 | - - - | - - - | - - - | - - - | 36253 | 31550 | 32328 | 100131 | Over-range | 13511 | 12929 | 15336 | 42039 | 13002 | 12846 | 13944 | 40439 | 33526 | 28713 | 28358 | 90597 | 33526 | 28713 | 28358 | 90597 | - - - | - - - | - - - | - - -
5/10/2026 | 3:30:00 AM | 285.14 | 282.51 | 282.04 | 494.03 | 486.92 | 490.73 | 133.5083 | 116.1405 | 117.6089 | 3.0515 | 1.44 | 1.435 | 1.431 | 1.857 | 1.906 | 2.011 | Over-range | 60.01 | 35418 | 29956 | 29030 | 94404 | - - - | - - - | - - - | - - - | 35418 | 29956 | 29030 | 94404 | 4117 | 912 | 6820 | 11849 | - - - | - - - | - - - | - - - | 4117 | 912 | 6820 | 11849 | 38059 | 32803 | 33166 | 104028 | # # # | # # # | # # # | # # # | 0.931 | 0.913 | 0.875 | 0.908 | # # # | # # # | # # # | - - - | 0.993 | 1 | 0.973 | 0.989 | - - - | 0.126 | 1.71 | 1.69 | 1.7 | 1.65 | 1.67 | 1.7 | 38.16 | 44.89 | 49.4 | 0 | - - - | - - - | - - - | - - - | 38059 | 32803 | 33166 | 104028 | Over-range | 13928 | 13368 | 16038 | 43700 | 13305 | 13335 | 14516 | 42063 | 35302 | 29893 | 28925 | 94119 | 35302 | 29893 | 28925 | 94119 | - - - | - - - | - - - | - - -
5/10/2026 | 3:45:00 AM | 285.16 | 282.48 | 282.08 | 494 | 486.92 | 490.81 | 139.9133 | 121.4212 | 122.7672 | 3.2455 | 1.44 | 1.435 | 1.431 | 1.842 | 1.889 | 2.006 | Over-range | 60.01 | 37252 | 31398 | 30360 | 99010 | - - - | - - - | - - - | - - - | 37252 | 31398 | 30360 | 99010 | 4291 | 794 | 7166 | 12251 | - - - | - - - | - - - | - - - | 4291 | 794 | 7166 | 12251 | 39893 | 34296 | 34625 | 108813 | # # # | # # # | # # # | # # # | 0.934 | 0.916 | 0.877 | 0.91 | # # # | # # # | # # # | - - - | 0.993 | 1 | 0.973 | 0.989 | - - - | 0.124 | 1.73 | 1.71 | 1.72 | 1.67 | 1.69 | 1.72 | 37.13 | 44.21 | 48.87 | 0 | - - - | - - - | - - - | - - - | 39893 | 34296 | 34625 | 108813 | Over-range | 14272 | 13796 | 16647 | 45135 | 13612 | 13773 | 15026 | 43441 | 37129 | 31340 | 30254 | 98723 | 37129 | 31340 | 30254 | 98723 | - - - | - - - | - - - | - - -
5/10/2026 | 4:00:00 AM | 285.35 | 282.8 | 282.35 | 494.43 | 487.5 | 491.16 | 142.3732 | 124.4299 | 124.8934 | 3.2847 | 1.44 | 1.435 | 1.432 | 1.829 | 1.882 | 1.99 | Over-range | 59.99 | 37960 | 32291 | 31048 | 101299 | - - - | - - - | - - - | - - - | 37960 | 32291 | 31048 | 101299 | 4465 | 853 | 7134 | 12451 | - - - | - - - | - - - | - - - | 4465 | 853 | 7134 | 12451 | 40625 | 35188 | 35263 | 111076 | # # # | # # # | # # # | # # # | 0.934 | 0.918 | 0.88 | 0.912 | # # # | # # # | # # # | - - - | 0.993 | 1 | 0.974 | 0.989 | - - - | 0.123 | 1.75 | 1.72 | 1.75 | 1.68 | 1.71 | 1.74 | 36.84 | 43.55 | 48.17 | 0 | - - - | - - - | - - - | - - - | 40625 | 35188 | 35263 | 111076 | Over-range | 14473 | 13980 | 16716 | 45566 | 13767 | 13953 | 15117 | 43832 | 37837 | 32233 | 30936 | 101005 | 37837 | 32233 | 30936 | 101005 | - - - | - - - | - - - | - - -
5/10/2026 | 4:15:00 AM | 285.31 | 282.61 | 282.29 | 494.2 | 487.23 | 491.14 | 143.9501 | 125.9693 | 126.9492 | 3.3156 | 1.44 | 1.435 | 1.432 | 1.827 | 1.87 | 1.98 | Over-range | 60 | 38406 | 32718 | 31637 | 102762 | - - - | - - - | - - - | - - - | 38406 | 32718 | 31637 | 102762 | 4437 | 989 | 7170 | 12596 | - - - | - - - | - - - | - - - | 4437 | 989 | 7170 | 12596 | 41069 | 35599 | 35834 | 112503 | # # # | # # # | # # # | # # # | 0.935 | 0.919 | 0.883 | 0.913 | # # # | # # # | # # # | - - - | 0.993 | 1 | 0.975 | 0.99 | - - - | 0.123 | 1.75 | 1.72 | 1.74 | 1.68 | 1.71 | 1.74 | 36.65 | 43.11 | 47.62 | 0 | - - - | - - - | - - - | - - - | 41069 | 35599 | 35834 | 112503 | Over-range | 14547 | 14029 | 16827 | 45790 | 13853 | 13993 | 15222 | 44023 | 38283 | 32660 | 31526 | 102468 | 38283 | 32660 | 31526 | 102468 | - - - | - - - | - - - | - - -
5/10/2026 | 4:30:00 AM | 285.41 | 282.73 | 282.34 | 494.43 | 487.37 | 491.26 | 144.6965 | 127.1277 | 127.5429 | 3.3303 | 1.441 | 1.436 | 1.432 | 1.818 | 1.868 | 1.971 | Over-range | 60 | 38628 | 33079 | 31863 | 103570 | - - - | - - - | - - - | - - - | 38628 | 33079 | 31863 | 103570 | 4533 | 1041 | 7116 | 12690 | - - - | - - - | - - - | - - - | 4533 | 1041 | 7116 | 12690 | 41298 | 35943 | 36011 | 113252 | # # # | # # # | # # # | # # # | 0.935 | 0.92 | 0.885 | 0.915 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.976 | 0.99 | - - - | 0.123 | 1.77 | 1.74 | 1.77 | 1.7 | 1.73 | 1.77 | 36.5 | 42.72 | 47.22 | 0 | - - - | - - - | - - - | - - - | 41298 | 35943 | 36011 | 113252 | Over-range | 14608 | 14060 | 16779 | 45817 | 13886 | 14021 | 15195 | 44025 | 38510 | 33012 | 31754 | 103276 | 38510 | 33012 | 31754 | 103276 | - - - | - - - | - - - | - - -
5/10/2026 | 4:45:00 AM | 285.4 | 282.79 | 282.37 | 494.46 | 487.48 | 491.24 | 143.2378 | 126.1899 | 126.3609 | 3.2718 | 1.44 | 1.435 | 1.431 | 1.812 | 1.859 | 1.961 | Over-range | 60 | 38250 | 32852 | 31618 | 102721 | - - - | - - - | - - - | - - - | 38250 | 32852 | 31618 | 102721 | 4480 | 1037 | 6969 | 12486 | - - - | - - - | - - - | - - - | 4480 | 1037 | 6969 | 12486 | 40864 | 35673 | 35669 | 112206 | # # # | # # # | # # # | # # # | 0.936 | 0.921 | 0.886 | 0.916 | # # # | # # # | # # # | - - - | 0.993 | 0.999 | 0.976 | 0.99 | - - - | 0.122 | 1.76 | 1.73 | 1.75 | 1.69 | 1.72 | 1.75 | 36.23 | 42.51 | 46.87 | 0 | - - - | - - - | - - - | - - - | 40864 | 35673 | 35669 | 112206 | Over-range | 14374 | 13902 | 16505 | 45141 | 13657 | 13863 | 14962 | 43380 | 38132 | 32792 | 31506 | 102430 | 38132 | 32792 | 31506 | 102430 | - - - | - - - | - - - | - - -
5/10/2026 | 5:00:00 AM | 284.85 | 282.22 | 281.91 | 493.45 | 486.6 | 490.41 | 241.2675 | 227.041 | 220.7672 | 8.0123 | 1.441 | 1.436 | 1.434 | 1.602 | 1.568 | 1.756 | Over-range | 60.02 | 62160 | 58588 | 54866 | 175615 | - - - | - - - | - - - | - - - | 62160 | 58588 | 54866 | 175615 | 23689 | 19052 | 23527 | 66268 | - - - | - - - | - - - | - - - | 23689 | 19052 | 23527 | 66268 | 68002 | 63262 | 61514 | 192778 | # # # | # # # | # # # | # # # | 0.914 | 0.926 | 0.892 | 0.911 | # # # | # # # | # # # | - - - | 0.931 | 0.947 | 0.917 | 0.932 | - - - | 0.377 | 1.77 | 1.73 | 1.81 | 1.7 | 1.74 | 1.79 | 21.27 | 23.18 | 25.57 | 0 | - - - | - - - | - - - | - - - | 68002 | 63262 | 61514 | 192778 | Over-range | 27504 | 23797 | 27769 | 79358 | 12876 | 13095 | 13995 | 40693 | 61942 | 58461 | 54649 | 175052 | 61942 | 58461 | 54649 | 175052 | - - - | - - - | - - - | - - -
5/10/2026 | 5:15:00 AM | 285.36 | 282.79 | 282.49 | 494.36 | 487.64 | 491.34 | 242.8015 | 230.8813 | 224.9651 | 6.484 | 1.441 | 1.435 | 1.434 | 1.58 | 1.557 | 1.723 | Over-range | 60.01 | 62905 | 60094 | 56610 | 179609 | - - - | - - - | - - - | - - - | 62905 | 60094 | 56610 | 179609 | 25999 | 22042 | 25498 | 73539 | - - - | - - - | - - - | - - - | 25999 | 22042 | 25498 | 73539 | 69237 | 65263 | 63534 | 198034 | # # # | # # # | # # # | # # # | 0.909 | 0.921 | 0.891 | 0.907 | # # # | # # # | # # # | - - - | 0.924 | 0.938 | 0.911 | 0.925 | - - - | 0.409 | 1.76 | 1.71 | 1.77 | 1.68 | 1.71 | 1.77 | 19.88 | 20.83 | 22.87 | 0 | - - - | - - - | - - - | - - - | 69237 | 65263 | 63534 | 198034 | Over-range | 28924 | 25442 | 28841 | 83409 | 12674 | 12680 | 13473 | 39330 | 62723 | 59888 | 56419 | 179029 | 62723 | 59888 | 56419 | 179029 | - - - | - - - | - - - | - - -
5/10/2026 | 5:30:00 AM | 285.34 | 282.72 | 282.52 | 494.22 | 487.61 | 491.39 | 225.7582 | 217.4577 | 214.0398 | 5.8859 | 1.44 | 1.434 | 1.432 | 1.583 | 1.585 | 1.705 | Over-range | 60.01 | 58268 | 56099 | 53886 | 168252 | - - - | - - - | - - - | - - - | 58268 | 56099 | 53886 | 168252 | 24884 | 22475 | 24650 | 72009 | - - - | - - - | - - - | - - - | 24884 | 22475 | 24650 | 72009 | 64414 | 61477 | 60468 | 186359 | # # # | # # # | # # # | # # # | 0.905 | 0.913 | 0.891 | 0.903 | # # # | # # # | # # # | - - - | 0.919 | 0.928 | 0.909 | 0.919 | - - - | 0.428 | 1.7 | 1.64 | 1.66 | 1.62 | 1.61 | 1.68 | 19.65 | 19.88 | 21.54 | 0 | - - - | - - - | - - - | - - - | 64414 | 61477 | 60468 | 186359 | Over-range | 27459 | 25145 | 27436 | 80130 | 11609 | 11276 | 12045 | 35146 | 58062 | 55928 | 53698 | 167687 | 58062 | 55928 | 53698 | 167687 | - - - | - - - | - - - | - - -
5/10/2026 | 5:45:00 AM | 285.21 | 282.58 | 282.33 | 494.03 | 487.3 | 491.09 | 221.8008 | 213.5147 | 209.731 | 5.7243 | 1.44 | 1.433 | 1.432 | 1.587 | 1.583 | 1.708 | Over-range | 60 | 57097 | 55005 | 52668 | 164769 | - - - | - - - | - - - | - - - | 57097 | 55005 | 52668 | 164769 | 24787 | 22264 | 24416 | 71468 | - - - | - - - | - - - | - - - | 24787 | 22264 | 24416 | 71468 | 63258 | 60334 | 59212 | 182804 | # # # | # # # | # # # | # # # | 0.903 | 0.912 | 0.889 | 0.901 | # # # | # # # | # # # | - - - | 0.917 | 0.927 | 0.907 | 0.917 | - - - | 0.434 | 1.68 | 1.61 | 1.63 | 1.6 | 1.59 | 1.65 | 19.46 | 19.64 | 21.3 | 0 | - - - | - - - | - - - | - - - | 63258 | 60334 | 59212 | 182804 | Over-range | 27231 | 24793 | 27058 | 79172 | 11273 | 10909 | 11659 | 34067 | 56888 | 54840 | 52482 | 164209 | 56888 | 54840 | 52482 | 164209 | - - - | - - - | - - - | - - -
5/10/2026 | 6:00:00 AM | 285.36 | 282.75 | 282.56 | 494.26 | 487.68 | 491.44 | 220.1362 | 211.9736 | 208.6188 | 5.7306 | 1.44 | 1.433 | 1.432 | 1.587 | 1.59 | 1.711 | Over-range | 60.01 | 56627 | 54533 | 52334 | 163494 | - - - | - - - | - - - | - - - | 56627 | 54533 | 52334 | 163494 | 24754 | 22329 | 24482 | 71564 | - - - | - - - | - - - | - - - | 24754 | 22329 | 24482 | 71564 | 62817 | 59935 | 58947 | 181698 | # # # | # # # | # # # | # # # | 0.902 | 0.91 | 0.888 | 0.9 | # # # | # # # | # # # | - - - | 0.916 | 0.925 | 0.905 | 0.915 | - - - | 0.438 | 1.67 | 1.61 | 1.64 | 1.6 | 1.59 | 1.65 | 19.56 | 19.81 | 21.47 | 0 | - - - | - - - | - - - | - - - | 62817 | 59935 | 58947 | 181698 | Over-range | 27190 | 24865 | 27128 | 79271 | 11250 | 10940 | 11685 | 34095 | 56431 | 54352 | 52148 | 162930 | 56431 | 54352 | 52148 | 162930 | - - - | - - - | - - - | - - -
5/10/2026 | 6:15:00 AM | 285.33 | 282.84 | 282.57 | 494.32 | 487.8 | 491.36 | 219.6656 | 211.8313 | 207.9634 | 5.7041 | 1.44 | 1.434 | 1.432 | 1.591 | 1.59 | 1.712 | Over-range | 60 | 56428 | 54483 | 52136 | 163047 | - - - | - - - | - - - | - - - | 56428 | 54483 | 52136 | 163047 | 24838 | 22358 | 24433 | 71629 | - - - | - - - | - - - | - - - | 24838 | 22358 | 24433 | 71629 | 62676 | 59913 | 58763 | 181352 | # # # | # # # | # # # | # # # | 0.9 | 0.909 | 0.887 | 0.899 | # # # | # # # | # # # | - - - | 0.915 | 0.925 | 0.905 | 0.915 | - - - | 0.439 | 1.67 | 1.62 | 1.63 | 1.6 | 1.59 | 1.65 | 19.65 | 19.94 | 21.63 | 0 | - - - | - - - | - - - | - - - | 62676 | 59913 | 58763 | 181352 | Over-range | 27280 | 24923 | 27110 | 79400 | 11280 | 11013 | 11745 | 34258 | 56229 | 54307 | 51950 | 162486 | 56229 | 54307 | 51950 | 162486 | - - - | - - - | - - - | - - -
5/10/2026 | 6:30:00 AM | 285.04 | 282.47 | 282.24 | 493.76 | 487.17 | 490.86 | 221.5186 | 212.7273 | 209.0796 | 5.7313 | 1.44 | 1.434 | 1.432 | 1.586 | 1.586 | 1.718 | Over-range | 60.01 | 56903 | 54725 | 52311 | 163938 | - - - | - - - | - - - | - - - | 56903 | 54725 | 52311 | 163938 | 24895 | 22164 | 24552 | 71612 | - - - | - - - | - - - | - - - | 24895 | 22164 | 24552 | 71612 | 63140 | 60089 | 59011 | 182240 | # # # | # # # | # # # | # # # | 0.901 | 0.911 | 0.886 | 0.9 | # # # | # # # | # # # | - - - | 0.916 | 0.926 | 0.905 | 0.916 | - - - | 0.437 | 1.67 | 1.6 | 1.64 | 1.59 | 1.59 | 1.64 | 19.64 | 20.09 | 21.9 | 0 | - - - | - - - | - - - | - - - | 63140 | 60089 | 59011 | 182240 | Over-range | 27364 | 24818 | 27310 | 79598 | 11358 | 11165 | 11960 | 34751 | 56713 | 54548 | 52118 | 163378 | 56713 | 54548 | 52118 | 163378 | - - - | - - - | - - - | - - -
5/10/2026 | 6:45:00 AM | 285.16 | 282.6 | 282.35 | 493.98 | 487.38 | 491.05 | 224.3799 | 214.0601 | 210.2144 | 5.7937 | 1.44 | 1.434 | 1.433 | 1.584 | 1.576 | 1.726 | Over-range | 60.01 | 57704 | 55214 | 52514 | 165432 | - - - | - - - | - - - | - - - | 57704 | 55214 | 52514 | 165432 | 25141 | 21931 | 24820 | 71893 | - - - | - - - | - - - | - - - | 25141 | 21931 | 24820 | 71893 | 63983 | 60493 | 59354 | 183831 | # # # | # # # | # # # | # # # | 0.902 | 0.913 | 0.885 | 0.9 | # # # | # # # | # # # | - - - | 0.916 | 0.929 | 0.903 | 0.916 | - - - | 0.435 | 1.67 | 1.63 | 1.65 | 1.6 | 1.61 | 1.66 | 19.59 | 20.34 | 22.22 | 0 | - - - | - - - | - - - | - - - | 63983 | 60493 | 59354 | 183831 | Over-range | 27642 | 24714 | 27663 | 80161 | 11489 | 11392 | 12213 | 35457 | 57504 | 55039 | 52328 | 164872 | 57504 | 55039 | 52328 | 164872 | - - - | - - - | - - - | - - -
5/10/2026 | 7:00:00 AM | 285.16 | 282.71 | 282.51 | 494.02 | 487.68 | 491.18 | 221.7647 | 212.6494 | 208.9861 | 5.7006 | 1.44 | 1.434 | 1.433 | 1.586 | 1.583 | 1.718 | Over-range | 60 | 56976 | 54758 | 52285 | 164019 | - - - | - - - | - - - | - - - | 56976 | 54758 | 52285 | 164019 | 24987 | 22131 | 24658 | 71776 | - - - | - - - | - - - | - - - | 24987 | 22131 | 24658 | 71776 | 63238 | 60117 | 59041 | 182396 | # # # | # # # | # # # | # # # | 0.901 | 0.911 | 0.886 | 0.899 | # # # | # # # | # # # | - - - | 0.915 | 0.927 | 0.904 | 0.915 | - - - | 0.438 | 1.69 | 1.62 | 1.66 | 1.61 | 1.61 | 1.67 | 19.57 | 20.18 | 21.97 | 0 | - - - | - - - | - - - | - - - | 63238 | 60117 | 59041 | 182396 | Over-range | 27437 | 24812 | 27424 | 79788 | 11332 | 11217 | 12001 | 34845 | 56775 | 54587 | 52096 | 163458 | 56775 | 54587 | 52096 | 163458 | - - - | - - - | - - - | - - -
5/10/2026 | 7:15:00 AM | 285.15 | 282.77 | 282.5 | 494.07 | 487.76 | 491.12 | 221.0855 | 212.741 | 208.6069 | 5.7007 | 1.44 | 1.434 | 1.433 | 1.59 | 1.584 | 1.714 | Over-range | 60 | 56760 | 54769 | 52238 | 163768 | - - - | - - - | - - - | - - - | 56760 | 54769 | 52238 | 163768 | 24985 | 22220 | 24525 | 71731 | - - - | - - - | - - - | - - - | 24985 | 22220 | 24525 | 71731 | 63042 | 60157 | 58932 | 182130 | # # # | # # # | # # # | # # # | 0.9 | 0.91 | 0.886 | 0.899 | # # # | # # # | # # # | - - - | 0.915 | 0.926 | 0.905 | 0.915 | - - - | 0.438 | 1.68 | 1.61 | 1.64 | 1.6 | 1.59 | 1.65 | 19.6 | 20.11 | 21.88 | 0 | - - - | - - - | - - - | - - - | 63042 | 60157 | 58932 | 182130 | Over-range | 27432 | 24883 | 27279 | 79696 | 11324 | 11198 | 11944 | 34731 | 56567 | 54602 | 52048 | 163216 | 56567 | 54602 | 52048 | 163216 | - - - | - - - | - - - | - - -
5/10/2026 | 7:30:00 AM | 284.96 | 282.53 | 282.23 | 493.73 | 487.27 | 490.73 | 219.9401 | 211.4111 | 207.2384 | 5.6573 | 1.44 | 1.434 | 1.433 | 1.589 | 1.583 | 1.716 | Over-range | 60 | 56396 | 54372 | 51805 | 162572 | - - - | - - - | - - - | - - - | 56396 | 54372 | 51805 | 162572 | 24932 | 22119 | 24451 | 71502 | - - - | - - - | - - - | - - - | 24932 | 22119 | 24451 | 71502 | 62674 | 59729 | 58489 | 180892 | # # # | # # # | # # # | # # # | 0.9 | 0.91 | 0.886 | 0.899 | # # # | # # # | # # # | - - - | 0.914 | 0.926 | 0.904 | 0.915 | - - - | 0.44 | 1.68 | 1.61 | 1.64 | 1.61 | 1.59 | 1.66 | 19.55 | 20.01 | 21.83 | 0 | - - - | - - - | - - - | - - - | 62674 | 59729 | 58489 | 180892 | Over-range | 27340 | 24723 | 27152 | 79321 | 11220 | 11045 | 11804 | 34342 | 56196 | 54197 | 51624 | 162018 | 56196 | 54197 | 51624 | 162018 | - - - | - - - | - - - | - - -
5/10/2026 | 7:45:00 AM | 284.6 | 282.17 | 281.97 | 493.06 | 486.76 | 490.22 | 219.509 | 211.4768 | 207.4717 | 5.6473 | 1.44 | 1.434 | 1.433 | 1.59 | 1.588 | 1.712 | Over-range | 60 | 56223 | 54288 | 51864 | 162375 | - - - | - - - | - - - | - - - | 56223 | 54288 | 51864 | 162375 | 24818 | 22170 | 24364 | 71353 | - - - | - - - | - - - | - - - | 24818 | 22170 | 24364 | 71353 | 62472 | 59672 | 58500 | 180645 | # # # | # # # | # # # | # # # | 0.9 | 0.91 | 0.887 | 0.899 | # # # | # # # | # # # | - - - | 0.914 | 0.925 | 0.905 | 0.915 | - - - | 0.439 | 1.68 | 1.61 | 1.64 | 1.6 | 1.59 | 1.65 | 19.6 | 20.05 | 21.79 | 0 | - - - | - - - | - - - | - - - | 62472 | 59672 | 58500 | 180645 | Over-range | 27236 | 24770 | 27063 | 79164 | 11217 | 11047 | 11781 | 34289 | 56025 | 54110 | 51682 | 161816 | 56025 | 54110 | 51682 | 161816 | - - - | - - - | - - - | - - -
5/10/2026 | 8:00:00 AM | 284.5 | 282.09 | 281.9 | 492.88 | 486.64 | 490.07 | 219.127 | 211.4201 | 207.5816 | 5.659 | 1.44 | 1.434 | 1.434 | 1.59 | 1.59 | 1.711 | Over-range | 60.01 | 56113 | 54230 | 51904 | 162248 | - - - | - - - | - - - | - - - | 56113 | 54230 | 51904 | 162248 | 24742 | 22231 | 24320 | 71293 | - - - | - - - | - - - | - - - | 24742 | 22231 | 24320 | 71293 | 62341 | 59638 | 58517 | 180497 | # # # | # # # | # # # | # # # | 0.9 | 0.909 | 0.887 | 0.899 | # # # | # # # | # # # | - - - | 0.914 | 0.925 | 0.905 | 0.915 | - - - | 0.439 | 1.68 | 1.6 | 1.63 | 1.6 | 1.58 | 1.65 | 19.64 | 20.02 | 21.78 | 0 | - - - | - - - | - - - | - - - | 62341 | 59638 | 58517 | 180497 | Over-range | 27161 | 24815 | 27022 | 79086 | 11205 | 11026 | 11778 | 34234 | 55912 | 54059 | 51716 | 161687 | 55912 | 54059 | 51716 | 161687 | - - - | - - - | - - - | - - -
5/10/2026 | 8:15:00 AM | 284.36 | 281.91 | 281.71 | 492.63 | 486.3 | 489.8 | 217.6706 | 210.5763 | 206.6826 | 5.7488 | 1.44 | 1.434 | 1.434 | 1.589 | 1.593 | 1.707 | Over-range | 60 | 55695 | 53948 | 51676 | 161319 | - - - | - - - | - - - | - - - | 55695 | 53948 | 51676 | 161319 | 24615 | 22247 | 24169 | 71031 | - - - | - - - | - - - | - - - | 24615 | 22247 | 24169 | 71031 | 61897 | 59363 | 58224 | 179484 | # # # | # # # | # # # | # # # | 0.9 | 0.909 | 0.887 | 0.899 | # # # | # # # | # # # | - - - | 0.914 | 0.924 | 0.905 | 0.915 | - - - | 0.44 | 1.67 | 1.6 | 1.62 | 1.59 | 1.57 | 1.64 | 19.63 | 19.89 | 21.64 | 0 | - - - | - - - | - - - | - - - | 61897 | 59363 | 58224 | 179484 | Over-range | 27006 | 24770 | 26826 | 78681 | 11109 | 10891 | 11639 | 33841 | 55499 | 53778 | 51487 | 160763 | 55499 | 53778 | 51487 | 160763 | - - - | - - - | - - - | - - -
5/10/2026 | 8:30:00 AM | 284.02 | 281.6 | 281.41 | 492.05 | 485.79 | 489.23 | 217.794 | 210.9146 | 206.749 | 5.748 | 1.44 | 1.435 | 1.434 | 1.59 | 1.592 | 1.703 | Over-range | 60.01 | 55667 | 54003 | 51685 | 161356 | - - - | - - - | - - - | - - - | 55667 | 54003 | 51685 | 161356 | 24588 | 22209 | 24087 | 70884 | - - - | - - - | - - - | - - - | 24588 | 22209 | 24087 | 70884 | 61857 | 59394 | 58180 | 179432 | # # # | # # # | # # # | # # # | 0.9 | 0.909 | 0.888 | 0.899 | # # # | # # # | # # # | - - - | 0.914 | 0.924 | 0.906 | 0.915 | - - - | 0.439 | 1.65 | 1.6 | 1.62 | 1.58 | 1.57 | 1.63 | 19.58 | 19.84 | 21.51 | 0 | - - - | - - - | - - - | - - - | 61857 | 59394 | 58180 | 179432 | Over-range | 26970 | 24724 | 26713 | 78485 | 11082 | 10864 | 11550 | 33693 | 55475 | 53822 | 51499 | 160795 | 55475 | 53822 | 51499 | 160795 | - - - | - - - | - - - | - - -
5/10/2026 | 8:45:00 AM | 283.96 | 281.51 | 281.37 | 491.9 | 485.67 | 489.17 | 220.8977 | 212.4055 | 208.5383 | 5.8277 | 1.44 | 1.435 | 1.434 | 1.585 | 1.588 | 1.711 | Over-range | 60 | 56540 | 54484 | 52042 | 163066 | - - - | - - - | - - - | - - - | 56540 | 54484 | 52042 | 163066 | 24725 | 21990 | 24365 | 71080 | - - - | - - - | - - - | - - - | 24725 | 21990 | 24365 | 71080 | 62725 | 59794 | 58676 | 181195 | # # # | # # # | # # # | # # # | 0.901 | 0.911 | 0.887 | 0.9 | # # # | # # # | # # # | - - - | 0.916 | 0.927 | 0.905 | 0.916 | - - - | 0.436 | 1.67 | 1.6 | 1.63 | 1.59 | 1.58 | 1.64 | 19.57 | 20.09 | 21.88 | 0 | - - - | - - - | - - - | - - - | 62725 | 59794 | 58676 | 181195 | Over-range | 27160 | 24633 | 27101 | 79000 | 11239 | 11100 | 11866 | 34475 | 56344 | 54310 | 51854 | 162507 | 56344 | 54310 | 51854 | 162507 | - - - | - - - | - - - | - - -
5/10/2026 | 9:00:00 AM | 283.62 | 281.13 | 280.96 | 491.31 | 484.96 | 488.52 | 222.2798 | 213.0738 | 208.9063 | 5.9684 | 1.439 | 1.435 | 1.434 | 1.585 | 1.583 | 1.718 | Over-range | 60 | 56859 | 54671 | 52024 | 163554 | - - - | - - - | - - - | - - - | 56859 | 54671 | 52024 | 163554 | 24764 | 21770 | 24386 | 70920 | - - - | - - - | - - - | - - - | 24764 | 21770 | 24386 | 70920 | 63043 | 59902 | 58694 | 181639 | # # # | # # # | # # # | # # # | 0.902 | 0.913 | 0.886 | 0.9 | # # # | # # # | # # # | - - - | 0.916 | 0.929 | 0.905 | 0.917 | - - - | 0.434 | 1.64 | 1.58 | 1.61 | 1.56 | 1.56 | 1.62 | 19.62 | 20.21 | 22.1 | 0 | - - - | - - - | - - - | - - - | 63043 | 59902 | 58694 | 181639 | Over-range | 27229 | 24482 | 27175 | 79011 | 11321 | 11198 | 11990 | 34828 | 56663 | 54497 | 51834 | 162993 | 56663 | 54497 | 51834 | 162993 | - - - | - - - | - - - | - - -
5/10/2026 | 9:15:00 AM | 283.15 | 280.57 | 280.53 | 490.37 | 484.09 | 487.81 | 223.5442 | 213.4241 | 210.0289 | 5.8611 | 1.439 | 1.435 | 1.435 | 1.58 | 1.584 | 1.719 | Over-range | 59.99 | 57175 | 54696 | 52213 | 164084 | - - - | - - - | - - - | - - - | 57175 | 54696 | 52213 | 164084 | 24678 | 21630 | 24474 | 70782 | - - - | - - - | - - - | - - - | 24678 | 21630 | 24474 | 70782 | 63297 | 59881 | 58919 | 182097 | # # # | # # # | # # # | # # # | 0.903 | 0.913 | 0.886 | 0.901 | # # # | # # # | # # # | - - - | 0.918 | 0.93 | 0.905 | 0.917 | - - - | 0.431 | 1.63 | 1.6 | 1.61 | 1.57 | 1.57 | 1.62 | 19.59 | 20.27 | 22.2 | 0 | - - - | - - - | - - - | - - - | 63297 | 59881 | 58919 | 182097 | Over-range | 27158 | 24372 | 27299 | 78965 | 11336 | 11232 | 12092 | 35006 | 56975 | 54523 | 52022 | 163520 | 56975 | 54523 | 52022 | 163520 | - - - | - - - | - - - | - - -
5/10/2026 | 9:30:00 AM | 282.78 | 280.26 | 280.17 | 489.78 | 483.52 | 487.16 | 225.4002 | 214.5652 | 210.884 | 5.8185 | 1.439 | 1.435 | 1.435 | 1.579 | 1.576 | 1.72 | Over-range | 60 | 57620 | 55031 | 52363 | 165014 | - - - | - - - | - - - | - - - | 57620 | 55031 | 52363 | 165014 | 24770 | 21431 | 24515 | 70715 | - - - | - - - | - - - | - - - | 24770 | 21431 | 24515 | 70715 | 63739 | 60133 | 59083 | 182956 | # # # | # # # | # # # | # # # | 0.904 | 0.915 | 0.886 | 0.902 | # # # | # # # | # # # | - - - | 0.918 | 0.931 | 0.905 | 0.918 | - - - | 0.429 | 1.65 | 1.61 | 1.64 | 1.57 | 1.59 | 1.64 | 19.49 | 20.32 | 22.25 | 0 | - - - | - - - | - - - | - - - | 63739 | 60133 | 59083 | 182956 | Over-range | 27252 | 24239 | 27367 | 79013 | 11363 | 11323 | 12165 | 35248 | 57421 | 54866 | 52167 | 164454 | 57421 | 54866 | 52167 | 164454 | - - - | - - - | - - - | - - -
5/10/2026 | 9:45:00 AM | 282.62 | 279.99 | 279.9 | 489.44 | 482.99 | 486.8 | 227.5559 | 215.6119 | 211.6164 | 6.079 | 1.438 | 1.434 | 1.434 | 1.577 | 1.571 | 1.73 | Over-range | 60.01 | 58180 | 55340 | 52416 | 165935 | - - - | - - - | - - - | - - - | 58180 | 55340 | 52416 | 165935 | 24865 | 21203 | 24641 | 70709 | - - - | - - - | - - - | - - - | 24865 | 21203 | 24641 | 70709 | 64310 | 60368 | 59230 | 183909 | # # # | # # # | # # # | # # # | 0.905 | 0.917 | 0.885 | 0.902 | # # # | # # # | # # # | - - - | 0.919 | 0.933 | 0.904 | 0.919 | - - - | 0.426 | 1.63 | 1.59 | 1.63 | 1.56 | 1.59 | 1.62 | 19.55 | 20.52 | 22.59 | 0 | - - - | - - - | - - - | - - - | 64310 | 60368 | 59230 | 183909 | Over-range | 27402 | 24121 | 27583 | 79296 | 11514 | 11499 | 12396 | 35889 | 57975 | 55173 | 52231 | 165378 | 57975 | 55173 | 52231 | 165378 | - - - | - - - | - - - | - - -
5/10/2026 | 10:00:00 AM | 282.2 | 279.58 | 279.58 | 488.67 | 482.39 | 486.19 | 230.6739 | 218.0661 | 213.3127 | 6.8762 | 1.438 | 1.434 | 1.434 | 1.571 | 1.561 | 1.735 | Over-range | 60.02 | 59017 | 56007 | 52746 | 167770 | - - - | - - - | - - - | - - - | 59017 | 56007 | 52746 | 167770 | 24902 | 21070 | 24806 | 70778 | - - - | - - - | - - - | - - - | 24902 | 21070 | 24806 | 70778 | 65096 | 60966 | 59637 | 185700 | # # # | # # # | # # # | # # # | 0.907 | 0.919 | 0.884 | 0.903 | # # # | # # # | # # # | - - - | 0.921 | 0.936 | 0.904 | 0.92 | - - - | 0.422 | 1.64 | 1.59 | 1.62 | 1.55 | 1.58 | 1.62 | 19.39 | 20.61 | 22.78 | 0 | - - - | - - - | - - - | - - - | 65096 | 60966 | 59637 | 185700 | Over-range | 27469 | 24086 | 27829 | 79610 | 11593 | 11668 | 12614 | 36444 | 58766 | 55866 | 52589 | 167221 | 58766 | 55866 | 52589 | 167221 | - - - | - - - | - - - | - - -
5/10/2026 | 10:15:00 AM | 281.61 | 278.95 | 278.98 | 487.6 | 481.31 | 485.19 | 231.763 | 218.6538 | 213.906 | 6.9618 | 1.438 | 1.434 | 1.434 | 1.57 | 1.558 | 1.738 | Over-range | 60.01 | 59217 | 56089 | 52774 | 168080 | - - - | - - - | - - - | - - - | 59217 | 56089 | 52774 | 168080 | 24888 | 20857 | 24801 | 70546 | - - - | - - - | - - - | - - - | 24888 | 20857 | 24801 | 70546 | 65267 | 60993 | 59675 | 185935 | # # # | # # # | # # # | # # # | 0.907 | 0.92 | 0.884 | 0.904 | # # # | # # # | # # # | - - - | 0.922 | 0.937 | 0.904 | 0.921 | - - - | 0.42 | 1.61 | 1.57 | 1.61 | 1.53 | 1.57 | 1.59 | 19.39 | 20.69 | 22.92 | 0 | - - - | - - - | - - - | - - - | 65267 | 60993 | 59675 | 185935 | Over-range | 27444 | 23961 | 27857 | 79504 | 11564 | 11792 | 12685 | 36661 | 59071 | 55925 | 52539 | 167534 | 59071 | 55925 | 52539 | 167534 | - - - | - - - | - - - | - - -
5/10/2026 | 10:30:00 AM | 281.35 | 278.45 | 278.64 | 486.93 | 480.49 | 484.78 | 233.534 | 219.1301 | 215.1131 | 7.3475 | 1.438 | 1.434 | 1.434 | 1.562 | 1.558 | 1.745 | Over-range | 60.01 | 59711 | 56163 | 52918 | 168792 | - - - | - - - | - - - | - - - | 59711 | 56163 | 52918 | 168792 | 24773 | 20688 | 25059 | 70521 | - - - | - - - | - - - | - - - | 24773 | 20688 | 25059 | 70521 | 65706 | 61017 | 59938 | 186661 | # # # | # # # | # # # | # # # | 0.909 | 0.92 | 0.883 | 0.904 | # # # | # # # | # # # | - - - | 0.923 | 0.938 | 0.903 | 0.922 | - - - | 0.418 | 1.58 | 1.58 | 1.6 | 1.51 | 1.57 | 1.57 | 19.4 | 20.84 | 23.14 | 0 | - - - | - - - | - - - | - - - | 65706 | 61017 | 59938 | 186661 | Over-range | 27420 | 23850 | 28147 | 79697 | 11753 | 11866 | 12816 | 37126 | 59535 | 55911 | 52801 | 168247 | 59535 | 55911 | 52801 | 168247 | - - - | - - - | - - - | - - -
5/10/2026 | 10:45:00 AM | 280.98 | 278 | 278.23 | 486.2 | 479.71 | 484.16 | 233.2944 | 218.4324 | 214.9232 | 7.1259 | 1.437 | 1.434 | 1.433 | 1.562 | 1.559 | 1.746 | Over-range | 60.01 | 59576 | 55899 | 52779 | 168253 | - - - | - - - | - - - | - - - | 59576 | 55899 | 52779 | 168253 | 24710 | 20553 | 25021 | 70284 | - - - | - - - | - - - | - - - | 24710 | 20553 | 25021 | 70284 | 65551 | 60722 | 59798 | 186072 | # # # | # # # | # # # | # # # | 0.909 | 0.921 | 0.883 | 0.904 | # # # | # # # | # # # | - - - | 0.923 | 0.938 | 0.903 | 0.922 | - - - | 0.418 | 1.54 | 1.56 | 1.57 | 1.48 | 1.55 | 1.55 | 19.41 | 20.87 | 23.17 | 0 | - - - | - - - | - - - | - - - | 65551 | 60722 | 59798 | 186072 | Over-range | 27343 | 23718 | 28111 | 79457 | 11705 | 11837 | 12814 | 37062 | 59413 | 55671 | 52626 | 167710 | 59413 | 55671 | 52626 | 167710 | - - - | - - - | - - - | - - -
5/10/2026 | 11:00:00 AM | 280.61 | 277.62 | 277.89 | 485.54 | 479.1 | 483.55 | 230.8472 | 216.4474 | 213.4458 | 6.8617 | 1.438 | 1.435 | 1.434 | 1.562 | 1.562 | 1.743 | Over-range | 60 | 58833 | 55254 | 52360 | 166448 | - - - | - - - | - - - | - - - | 58833 | 55254 | 52360 | 166448 | 24555 | 20578 | 24806 | 69939 | - - - | - - - | - - - | - - - | 24555 | 20578 | 24806 | 69939 | 64778 | 60090 | 59314 | 184183 | # # # | # # # | # # # | # # # | 0.908 | 0.92 | 0.883 | 0.904 | # # # | # # # | # # # | - - - | 0.922 | 0.937 | 0.903 | 0.921 | - - - | 0.42 | 1.52 | 1.54 | 1.57 | 1.47 | 1.53 | 1.53 | 19.37 | 20.67 | 23.01 | 0 | - - - | - - - | - - - | - - - | 64778 | 60090 | 59314 | 184183 | Over-range | 27109 | 23617 | 27867 | 78857 | 11487 | 11588 | 12698 | 36427 | 58624 | 55138 | 52151 | 165913 | 58624 | 55138 | 52151 | 165913 | - - - | - - - | - - - | - - -
5/10/2026 | 11:15:00 AM | 280.35 | 277.31 | 277.57 | 485.05 | 478.52 | 483.06 | 231.6692 | 216.6944 | 213.4093 | 7.2429 | 1.438 | 1.435 | 1.434 | 1.557 | 1.557 | 1.748 | Over-range | 60 | 59027 | 55317 | 52233 | 166578 | - - - | - - - | - - - | - - - | 59027 | 55317 | 52233 | 166578 | 24566 | 20410 | 24842 | 69817 | - - - | - - - | - - - | - - - | 24566 | 20410 | 24842 | 69817 | 64947 | 60091 | 59236 | 184274 | # # # | # # # | # # # | # # # | 0.909 | 0.921 | 0.882 | 0.904 | # # # | # # # | # # # | - - - | 0.923 | 0.938 | 0.902 | 0.921 | - - - | 0.419 | 1.54 | 1.54 | 1.56 | 1.47 | 1.54 | 1.54 | 19.26 | 20.68 | 23.11 | 0 | - - - | - - - | - - - | - - - | 64947 | 60091 | 59236 | 184274 | Over-range | 27091 | 23471 | 27940 | 78796 | 11421 | 11589 | 12787 | 36528 | 58788 | 55258 | 52000 | 166046 | 58788 | 55258 | 52000 | 166046 | - - - | - - - | - - - | - - -
5/10/2026 | 11:30:00 AM | 280.23 | 277.11 | 277.33 | 484.83 | 478.07 | 482.77 | 230.6721 | 215.1768 | 212.069 | 6.9299 | 1.438 | 1.435 | 1.434 | 1.557 | 1.555 | 1.752 | Over-range | 59.99 | 58703 | 54897 | 51800 | 165401 | - - - | - - - | - - - | - - - | 58703 | 54897 | 51800 | 165401 | 24551 | 20248 | 24795 | 69594 | - - - | - - - | - - - | - - - | 24551 | 20248 | 24795 | 69594 | 64642 | 59626 | 58813 | 183081 | # # # | # # # | # # # | # # # | 0.908 | 0.921 | 0.881 | 0.903 | # # # | # # # | # # # | - - - | 0.922 | 0.938 | 0.901 | 0.921 | - - - | 0.421 | 1.53 | 1.54 | 1.55 | 1.46 | 1.53 | 1.53 | 19.25 | 20.62 | 23.17 | 0 | - - - | - - - | - - - | - - - | 64642 | 59626 | 58813 | 183081 | Over-range | 27063 | 23273 | 27851 | 78493 | 11386 | 11472 | 12684 | 36300 | 58495 | 54779 | 51598 | 164872 | 58495 | 54779 | 51598 | 164872 | - - - | - - - | - - - | - - -
5/10/2026 | 11:45:00 AM | 279.68 | 276.54 | 276.86 | 483.8 | 477.19 | 481.92 | 230.9787 | 215.7839 | 212.8872 | 7.1027 | 1.438 | 1.435 | 1.434 | 1.556 | 1.559 | 1.75 | Over-range | 60 | 58710 | 54924 | 51957 | 165591 | - - - | - - - | - - - | - - - | 58710 | 54924 | 51957 | 165591 | 24373 | 20299 | 24785 | 69457 | - - - | - - - | - - - | - - - | 24373 | 20299 | 24785 | 69457 | 64600 | 59672 | 58940 | 183212 | # # # | # # # | # # # | # # # | 0.909 | 0.92 | 0.881 | 0.904 | # # # | # # # | # # # | - - - | 0.923 | 0.938 | 0.902 | 0.921 | - - - | 0.419 | 1.5 | 1.52 | 1.55 | 1.45 | 1.52 | 1.51 | 19.3 | 20.7 | 23.15 | 0 | - - - | - - - | - - - | - - - | 64600 | 59672 | 58940 | 183212 | Over-range | 26950 | 23326 | 27828 | 78398 | 11498 | 11491 | 12652 | 36358 | 58466 | 54738 | 51857 | 165061 | 58466 | 54738 | 51857 | 165061 | - - - | - - - | - - - | - - -
5/10/2026 | 12:00:00 PM | 281.24 | 278.1 | 278.36 | 486.55 | 479.83 | 484.55 | 224.9482 | 210.5336 | 208.5231 | 6.3275 | 1.438 | 1.435 | 1.434 | 1.564 | 1.573 | 1.75 | Over-range | 60.01 | 57262 | 53668 | 51055 | 161985 | - - - | - - - | - - - | - - - | 57262 | 53668 | 51055 | 161985 | 24404 | 20539 | 24658 | 69601 | - - - | - - - | - - - | - - - | 24404 | 20539 | 24658 | 69601 | 63258 | 58544 | 58042 | 179843 | # # # | # # # | # # # | # # # | 0.905 | 0.917 | 0.88 | 0.901 | # # # | # # # | # # # | - - - | 0.919 | 0.934 | 0.9 | 0.918 | - - - | 0.43 | 1.49 | 1.5 | 1.51 | 1.44 | 1.48 | 1.48 | 19.46 | 20.53 | 23.02 | 0 | - - - | - - - | - - - | - - - | 63258 | 58544 | 58042 | 179843 | Over-range | 26881 | 23388 | 27608 | 78128 | 11269 | 11184 | 12415 | 35489 | 57052 | 53530 | 50872 | 161453 | 57052 | 53530 | 50872 | 161453 | - - - | - - - | - - - | - - -
5/10/2026 | 12:15:00 PM | 281.98 | 278.82 | 279.09 | 487.81 | 481.07 | 485.82 | 219.0947 | 205.6651 | 204.7146 | 5.6443 | 1.438 | 1.436 | 1.434 | 1.567 | 1.588 | 1.747 | Over-range | 60 | 55757 | 52336 | 50200 | 158294 | - - - | - - - | - - - | - - - | 55757 | 52336 | 50200 | 158294 | 24201 | 20790 | 24477 | 69468 | - - - | - - - | - - - | - - - | 24201 | 20790 | 24477 | 69468 | 61776 | 57340 | 57131 | 176247 | # # # | # # # | # # # | # # # | 0.903 | 0.913 | 0.879 | 0.898 | # # # | # # # | # # # | - - - | 0.917 | 0.929 | 0.898 | 0.915 | - - - | 0.439 | 1.49 | 1.49 | 1.49 | 1.44 | 1.47 | 1.47 | 19.54 | 20.31 | 22.72 | 0 | - - - | - - - | - - - | - - - | 61776 | 57340 | 57131 | 176247 | Over-range | 26596 | 23426 | 27273 | 77498 | 11030 | 10794 | 12030 | 34351 | 55560 | 52176 | 50018 | 157754 | 55560 | 52176 | 50018 | 157754 | - - - | - - - | - - - | - - -
5/10/2026 | 12:30:00 PM | 281.81 | 278.76 | 279.02 | 487.59 | 481.02 | 485.58 | 211.2552 | 200.9921 | 199.7517 | 5.5216 | 1.438 | 1.435 | 1.433 | 1.577 | 1.608 | 1.734 | Over-range | 59.99 | 53483 | 50800 | 49006 | 153289 | - - - | - - - | - - - | - - - | 53483 | 50800 | 49006 | 153289 | 23829 | 21241 | 23946 | 69016 | - - - | - - - | - - - | - - - | 23829 | 21241 | 23946 | 69016 | 59531 | 56027 | 55732 | 171290 | # # # | # # # | # # # | # # # | 0.898 | 0.907 | 0.879 | 0.895 | # # # | # # # | # # # | - - - | 0.913 | 0.922 | 0.898 | 0.911 | - - - | 0.45 | 1.47 | 1.46 | 1.45 | 1.42 | 1.42 | 1.44 | 19.77 | 20.05 | 22.23 | 0 | - - - | - - - | - - - | - - - | 59531 | 56027 | 55732 | 171290 | Over-range | 26142 | 23629 | 26541 | 76435 | 10750 | 10349 | 11446 | 32846 | 53277 | 50630 | 48838 | 152745 | 53277 | 50630 | 48838 | 152745 | - - - | - - - | - - - | - - -
5/10/2026 | 12:45:00 PM | 281.57 | 278.54 | 278.77 | 487.2 | 480.62 | 485.15 | 213.0408 | 201.5482 | 199.8324 | 5.914 | 1.439 | 1.436 | 1.435 | 1.575 | 1.596 | 1.742 | Over-range | 60 | 53914 | 51012 | 48860 | 153787 | - - - | - - - | - - - | - - - | 53914 | 51012 | 48860 | 153787 | 23992 | 20956 | 24120 | 69068 | - - - | - - - | - - - | - - - | 23992 | 20956 | 24120 | 69068 | 59979 | 56137 | 55706 | 171822 | # # # | # # # | # # # | # # # | 0.899 | 0.909 | 0.877 | 0.895 | # # # | # # # | # # # | - - - | 0.913 | 0.925 | 0.896 | 0.911 | - - - | 0.449 | 1.48 | 1.49 | 1.49 | 1.43 | 1.45 | 1.48 | 19.6 | 20.17 | 22.46 | 0 | - - - | - - - | - - - | - - - | 59979 | 56137 | 55706 | 171822 | Over-range | 26281 | 23431 | 26755 | 76632 | 10725 | 10476 | 11577 | 33191 | 53736 | 50850 | 48663 | 153248 | 53736 | 50850 | 48663 | 153248 | - - - | - - - | - - - | - - -
5/10/2026 | 1:00:00 PM | 281.33 | 278.29 | 278.54 | 486.76 | 480.2 | 484.74 | 217.2664 | 204.0024 | 201.6557 | 6.595 | 1.439 | 1.436 | 1.435 | 1.569 | 1.579 | 1.754 | Over-range | 60 | 55064 | 51803 | 49151 | 156019 | - - - | - - - | - - - | - - - | 55064 | 51803 | 49151 | 156019 | 24219 | 20584 | 24450 | 69253 | - - - | - - - | - - - | - - - | 24219 | 20584 | 24450 | 69253 | 61122 | 56771 | 56168 | 174061 | # # # | # # # | # # # | # # # | 0.901 | 0.913 | 0.875 | 0.896 | # # # | # # # | # # # | - - - | 0.915 | 0.929 | 0.895 | 0.913 | - - - | 0.444 | 1.51 | 1.51 | 1.53 | 1.45 | 1.49 | 1.5 | 19.4 | 20.36 | 22.84 | 0 | - - - | - - - | - - - | - - - | 61122 | 56771 | 56168 | 174061 | Over-range | 26529 | 23225 | 27185 | 77172 | 10827 | 10755 | 11882 | 34051 | 54907 | 51628 | 48953 | 155488 | 54907 | 51628 | 48953 | 155488 | - - - | - - - | - - - | - - -
5/10/2026 | 1:15:00 PM | 281.27 | 278.24 | 278.44 | 486.69 | 480.07 | 484.59 | 220.1107 | 205.9625 | 202.8428 | 7.1698 | 1.439 | 1.437 | 1.436 | 1.566 | 1.567 | 1.76 | Over-range | 60.01 | 55821 | 52421 | 49351 | 157593 | - - - | - - - | - - - | - - - | 55821 | 52421 | 49351 | 157593 | 24417 | 20379 | 24692 | 69488 | - - - | - - - | - - - | - - - | 24417 | 20379 | 24692 | 69488 | 61908 | 57306 | 56479 | 175693 | # # # | # # # | # # # | # # # | 0.902 | 0.915 | 0.874 | 0.897 | # # # | # # # | # # # | - - - | 0.916 | 0.931 | 0.894 | 0.914 | - - - | 0.441 | 1.53 | 1.51 | 1.54 | 1.46 | 1.5 | 1.51 | 19.32 | 20.55 | 23.05 | 0 | - - - | - - - | - - - | - - - | 61908 | 57306 | 56479 | 175693 | Over-range | 26770 | 23152 | 27464 | 77668 | 10974 | 10984 | 12023 | 34693 | 55677 | 52183 | 49210 | 157069 | 55677 | 52183 | 49210 | 157069 | - - - | - - - | - - - | - - -
5/10/2026 | 1:30:00 PM | 281.03 | 278.12 | 278.31 | 486.34 | 479.91 | 484.24 | 223.8637 | 208.4427 | 205.782 | 7.0733 | 1.439 | 1.437 | 1.436 | 1.562 | 1.563 | 1.76 | Over-range | 60 | 56864 | 53144 | 50069 | 160077 | - - - | - - - | - - - | - - - | 56864 | 53144 | 50069 | 160077 | 24500 | 20256 | 24897 | 69653 | - - - | - - - | - - - | - - - | 24500 | 20256 | 24897 | 69653 | 62908 | 57970 | 57267 | 178145 | # # # | # # # | # # # | # # # | 0.904 | 0.917 | 0.874 | 0.899 | # # # | # # # | # # # | - - - | 0.918 | 0.934 | 0.895 | 0.916 | - - - | 0.435 | 1.54 | 1.53 | 1.59 | 1.49 | 1.54 | 1.54 | 19.26 | 20.79 | 23.16 | 0 | - - - | - - - | - - - | - - - | 62908 | 57970 | 57267 | 178145 | Over-range | 26904 | 23156 | 27796 | 78173 | 11116 | 11218 | 12359 | 35486 | 56601 | 53043 | 49913 | 159556 | 56601 | 53043 | 49913 | 159556 | - - - | - - - | - - - | - - -
5/10/2026 | 1:45:00 PM | 280.62 | 277.66 | 277.81 | 485.63 | 479.03 | 483.46 | 225.8444 | 209.863 | 206.9046 | 7.3021 | 1.439 | 1.437 | 1.436 | 1.558 | 1.555 | 1.762 | Over-range | 59.99 | 57368 | 53520 | 50280 | 161168 | - - - | - - - | - - - | - - - | 57368 | 53520 | 50280 | 161168 | 24501 | 20082 | 24972 | 69555 | - - - | - - - | - - - | - - - | 24501 | 20082 | 24972 | 69555 | 63375 | 58269 | 57478 | 179122 | # # # | # # # | # # # | # # # | 0.905 | 0.919 | 0.875 | 0.9 | # # # | # # # | # # # | - - - | 0.919 | 0.936 | 0.895 | 0.917 | - - - | 0.432 | 1.56 | 1.57 | 1.57 | 1.5 | 1.55 | 1.56 | 19.13 | 20.75 | 23.17 | 0 | - - - | - - - | - - - | - - - | 63375 | 58269 | 57478 | 179122 | Over-range | 26929 | 23041 | 27851 | 78163 | 11173 | 11294 | 12331 | 35656 | 57184 | 53311 | 50161 | 160656 | 57184 | 53311 | 50161 | 160656 | - - - | - - - | - - - | - - -
5/10/2026 | 2:00:00 PM | 280.23 | 277.25 | 277.42 | 484.93 | 478.35 | 482.79 | 223.7368 | 208.7335 | 205.3667 | 7.071 | 1.44 | 1.438 | 1.436 | 1.56 | 1.554 | 1.759 | Over-range | 60 | 56682 | 53133 | 49895 | 159710 | - - - | - - - | - - - | - - - | 56682 | 53133 | 49895 | 159710 | 24448 | 20107 | 24622 | 69177 | - - - | - - - | - - - | - - - | 24448 | 20107 | 24622 | 69177 | 62696 | 57871 | 56971 | 177538 | # # # | # # # | # # # | # # # | 0.904 | 0.918 | 0.876 | 0.9 | # # # | # # # | # # # | - - - | 0.918 | 0.935 | 0.896 | 0.916 | - - - | 0.433 | 1.56 | 1.53 | 1.57 | 1.49 | 1.53 | 1.55 | 19.08 | 20.46 | 23.06 | 0 | - - - | - - - | - - - | - - - | 62696 | 57871 | 56971 | 177538 | Over-range | 26794 | 22932 | 27500 | 77540 | 10963 | 11027 | 12246 | 35026 | 56431 | 53037 | 49731 | 159198 | 56431 | 53037 | 49731 | 159198 | - - - | - - - | - - - | - - -
5/10/2026 | 2:15:00 PM | 280.33 | 277.32 | 277.62 | 485.02 | 478.6 | 483.1 | 223.3616 | 208.5118 | 205.7027 | 7.12 | 1.439 | 1.437 | 1.435 | 1.559 | 1.562 | 1.758 | Over-range | 60 | 56619 | 53028 | 50005 | 159651 | - - - | - - - | - - - | - - - | 56619 | 53028 | 50005 | 159651 | 24367 | 20199 | 24707 | 69273 | - - - | - - - | - - - | - - - | 24367 | 20199 | 24707 | 69273 | 62615 | 57825 | 57106 | 177546 | # # # | # # # | # # # | # # # | 0.904 | 0.917 | 0.876 | 0.899 | # # # | # # # | # # # | - - - | 0.918 | 0.934 | 0.896 | 0.916 | - - - | 0.434 | 1.5 | 1.54 | 1.52 | 1.45 | 1.5 | 1.51 | 19.16 | 20.55 | 23.12 | 0 | - - - | - - - | - - - | - - - | 62615 | 57825 | 57106 | 177546 | Over-range | 26738 | 23060 | 27580 | 77680 | 11008 | 11126 | 12256 | 35149 | 56483 | 52845 | 49821 | 159148 | 56483 | 52845 | 49821 | 159148 | - - - | - - - | - - - | - - -
5/10/2026 | 2:30:00 PM | 280.33 | 277.36 | 277.58 | 485.07 | 478.59 | 483.03 | 221.0433 | 206.9579 | 204.2732 | 6.4434 | 1.44 | 1.438 | 1.435 | 1.563 | 1.567 | 1.755 | Over-range | 59.99 | 55940 | 52565 | 49710 | 158216 | - - - | - - - | - - - | - - - | 55940 | 52565 | 49710 | 158216 | 24306 | 20308 | 24416 | 69031 | - - - | - - - | - - - | - - - | 24306 | 20308 | 24416 | 69031 | 61961 | 57398 | 56700 | 176059 | # # # | # # # | # # # | # # # | 0.903 | 0.916 | 0.877 | 0.899 | # # # | # # # | # # # | - - - | 0.917 | 0.932 | 0.897 | 0.916 | - - - | 0.436 | 1.51 | 1.51 | 1.53 | 1.46 | 1.49 | 1.5 | 19.26 | 20.37 | 23.01 | 0 | - - - | - - - | - - - | - - - | 61961 | 57398 | 56700 | 176059 | Over-range | 26643 | 23053 | 27272 | 77231 | 10911 | 10907 | 12149 | 34630 | 55762 | 52439 | 49509 | 157709 | 55762 | 52439 | 49509 | 157709 | - - - | - - - | - - - | - - -
5/10/2026 | 2:45:00 PM | 280.13 | 277.1 | 277.36 | 484.67 | 478.15 | 482.7 | 215.8194 | 203.2049 | 201.7554 | 5.6377 | 1.44 | 1.438 | 1.435 | 1.567 | 1.584 | 1.744 | Over-range | 59.99 | 54491 | 51366 | 49160 | 155017 | - - - | - - - | - - - | - - - | 54491 | 51366 | 49160 | 155017 | 23892 | 20553 | 24024 | 68469 | - - - | - - - | - - - | - - - | 23892 | 20553 | 24024 | 68469 | 60458 | 56307 | 55958 | 172722 | # # # | # # # | # # # | # # # | 0.901 | 0.912 | 0.878 | 0.898 | # # # | # # # | # # # | - - - | 0.915 | 0.928 | 0.898 | 0.914 | - - - | 0.442 | 1.48 | 1.48 | 1.48 | 1.43 | 1.45 | 1.46 | 19.38 | 20.02 | 22.56 | 0 | - - - | - - - | - - - | - - - | 60458 | 56307 | 55958 | 172722 | Over-range | 26189 | 23065 | 26731 | 76175 | 10725 | 10465 | 11721 | 33385 | 54313 | 51208 | 48989 | 154509 | 54313 | 51208 | 48989 | 154509 | - - - | - - - | - - - | - - -
5/10/2026 | 3:00:00 PM | 280.39 | 277.28 | 277.6 | 485.04 | 478.49 | 483.18 | 215.833 | 202.0402 | 200.7914 | 5.8553 | 1.44 | 1.438 | 1.436 | 1.56 | 1.578 | 1.751 | Over-range | 59.99 | 54550 | 51144 | 48818 | 154512 | - - - | - - - | - - - | - - - | 54550 | 51144 | 48818 | 154512 | 23959 | 20357 | 24214 | 68530 | - - - | - - - | - - - | - - - | 23959 | 20357 | 24214 | 68530 | 60513 | 56018 | 55737 | 172268 | # # # | # # # | # # # | # # # | 0.902 | 0.913 | 0.876 | 0.897 | # # # | # # # | # # # | - - - | 0.915 | 0.929 | 0.895 | 0.913 | - - - | 0.444 | 1.5 | 1.49 | 1.52 | 1.44 | 1.47 | 1.5 | 19.11 | 19.92 | 22.57 | 0 | - - - | - - - | - - - | - - - | 60513 | 56018 | 55737 | 172268 | Over-range | 26194 | 22852 | 26896 | 76171 | 10585 | 10381 | 11706 | 33247 | 54365 | 51009 | 48641 | 154015 | 54365 | 51009 | 48641 | 154015 | - - - | - - - | - - - | - - -
5/10/2026 | 3:15:00 PM | 280.39 | 277.35 | 277.59 | 485.13 | 478.56 | 483.12 | 215.3167 | 201.9117 | 199.5058 | 6.3381 | 1.44 | 1.438 | 1.436 | 1.564 | 1.573 | 1.754 | Over-range | 60.01 | 54348 | 51131 | 48440 | 153918 | - - - | - - - | - - - | - - - | 54348 | 51131 | 48440 | 153918 | 24077 | 20329 | 24179 | 68585 | - - - | - - - | - - - | - - - | 24077 | 20329 | 24179 | 68585 | 60370 | 55999 | 55380 | 171749 | # # # | # # # | # # # | # # # | 0.9 | 0.913 | 0.875 | 0.896 | # # # | # # # | # # # | - - - | 0.914 | 0.929 | 0.894 | 0.912 | - - - | 0.446 | 1.48 | 1.48 | 1.5 | 1.43 | 1.46 | 1.48 | 19.1 | 19.97 | 22.62 | 0 | - - - | - - - | - - - | - - - | 60370 | 55999 | 55380 | 171749 | Over-range | 26285 | 22836 | 26842 | 76203 | 10544 | 10402 | 11655 | 33210 | 54169 | 51001 | 48250 | 153420 | 54169 | 51001 | 48250 | 153420 | - - - | - - - | - - - | - - -
5/10/2026 | 3:30:00 PM | 280.23 | 277.11 | 277.47 | 484.74 | 478.24 | 482.93 | 218.4659 | 203.6129 | 201.4297 | 6.9445 | 1.44 | 1.438 | 1.436 | 1.558 | 1.567 | 1.76 | Over-range | 60 | 55227 | 51628 | 48783 | 155639 | - - - | - - - | - - - | - - - | 55227 | 51628 | 48783 | 155639 | 24138 | 20150 | 24535 | 68823 | - - - | - - - | - - - | - - - | 24138 | 20150 | 24535 | 68823 | 61220 | 56424 | 55889 | 173533 | # # # | # # # | # # # | # # # | 0.902 | 0.915 | 0.873 | 0.897 | # # # | # # # | # # # | - - - | 0.916 | 0.931 | 0.893 | 0.913 | - - - | 0.442 | 1.47 | 1.49 | 1.5 | 1.42 | 1.46 | 1.48 | 19.07 | 20.22 | 22.88 | 0 | - - - | - - - | - - - | - - - | 61220 | 56424 | 55889 | 173533 | Over-range | 26416 | 22763 | 27273 | 76748 | 10729 | 10588 | 11910 | 33963 | 54964 | 51519 | 48657 | 155139 | 54964 | 51519 | 48657 | 155139 | - - - | - - - | - - - | - - -
5/10/2026 | 3:45:00 PM | 279.9 | 276.76 | 277.07 | 484.17 | 477.56 | 482.29 | 221.2594 | 204.9918 | 202.7779 | 6.9018 | 1.439 | 1.438 | 1.436 | 1.557 | 1.559 | 1.766 | Over-range | 60.01 | 55933 | 52025 | 48997 | 156955 | - - - | - - - | - - - | - - - | 55933 | 52025 | 48997 | 156955 | 24295 | 19841 | 24686 | 68822 | - - - | - - - | - - - | - - - | 24295 | 19841 | 24686 | 68822 | 61929 | 56733 | 56183 | 174845 | # # # | # # # | # # # | # # # | 0.903 | 0.917 | 0.872 | 0.898 | # # # | # # # | # # # | - - - | 0.917 | 0.934 | 0.892 | 0.915 | - - - | 0.439 | 1.48 | 1.5 | 1.51 | 1.43 | 1.49 | 1.49 | 19.08 | 20.47 | 23.12 | 0 | - - - | - - - | - - - | - - - | 61929 | 56733 | 56183 | 174845 | Over-range | 26586 | 22627 | 27492 | 77045 | 10795 | 10877 | 12100 | 34634 | 55783 | 51894 | 48780 | 156457 | 55783 | 51894 | 48780 | 156457 | - - - | - - - | - - - | - - -
5/10/2026 | 4:00:00 PM | 280.16 | 277.09 | 277.41 | 484.66 | 478.19 | 482.8 | 220.4147 | 204.7576 | 202.456 | 6.741 | 1.44 | 1.438 | 1.436 | 1.556 | 1.56 | 1.762 | Over-range | 60 | 55752 | 52008 | 49027 | 156788 | - - - | - - - | - - - | - - - | 55752 | 52008 | 49027 | 156788 | 24288 | 19941 | 24622 | 68851 | - - - | - - - | - - - | - - - | 24288 | 19941 | 24622 | 68851 | 61751 | 56736 | 56163 | 174650 | # # # | # # # | # # # | # # # | 0.903 | 0.917 | 0.873 | 0.898 | # # # | # # # | # # # | - - - | 0.916 | 0.933 | 0.893 | 0.914 | - - - | 0.439 | 1.5 | 1.51 | 1.54 | 1.45 | 1.49 | 1.5 | 18.94 | 20.37 | 23 | 0 | - - - | - - - | - - - | - - - | 61751 | 56736 | 56163 | 174650 | Over-range | 26550 | 22675 | 27397 | 76944 | 10721 | 10793 | 12014 | 34347 | 55567 | 51863 | 48858 | 156288 | 55567 | 51863 | 48858 | 156288 | - - - | - - - | - - - | - - -
5/10/2026 | 4:15:00 PM | 280.23 | 277.21 | 277.56 | 484.8 | 478.45 | 482.99 | 218.5782 | 203.896 | 201.7838 | 6.5979 | 1.441 | 1.439 | 1.436 | 1.557 | 1.567 | 1.758 | Over-range | 60 | 55269 | 51722 | 48944 | 155936 | - - - | - - - | - - - | - - - | 55269 | 51722 | 48944 | 155936 | 24151 | 20138 | 24489 | 68778 | - - - | - - - | - - - | - - - | 24151 | 20138 | 24489 | 68778 | 61252 | 56521 | 56005 | 173778 | # # # | # # # | # # # | # # # | 0.902 | 0.915 | 0.874 | 0.897 | # # # | # # # | # # # | - - - | 0.916 | 0.931 | 0.894 | 0.914 | - - - | 0.441 | 1.51 | 1.51 | 1.53 | 1.46 | 1.49 | 1.51 | 18.99 | 20.21 | 22.87 | 0 | - - - | - - - | - - - | - - - | 61252 | 56521 | 56005 | 173778 | Over-range | 26402 | 22790 | 27223 | 76700 | 10667 | 10670 | 11891 | 33947 | 55106 | 51547 | 48785 | 155437 | 55106 | 51547 | 48785 | 155437 | - - - | - - - | - - - | - - -
5/10/2026 | 4:30:00 PM | 280.07 | 277.13 | 277.38 | 484.63 | 478.26 | 482.64 | 219.6605 | 204.9782 | 202.0057 | 6.8202 | 1.441 | 1.439 | 1.437 | 1.559 | 1.558 | 1.76 | Over-range | 60 | 55506 | 52055 | 48973 | 156534 | - - - | - - - | - - - | - - - | 55506 | 52055 | 48973 | 156534 | 24270 | 20086 | 24457 | 68814 | - - - | - - - | - - - | - - - | 24270 | 20086 | 24457 | 68814 | 61520 | 56806 | 56033 | 174359 | # # # | # # # | # # # | # # # | 0.902 | 0.916 | 0.874 | 0.898 | # # # | # # # | # # # | - - - | 0.915 | 0.933 | 0.894 | 0.914 | - - - | 0.44 | 1.52 | 1.52 | 1.54 | 1.47 | 1.51 | 1.52 | 18.96 | 20.21 | 22.88 | 0 | - - - | - - - | - - - | - - - | 61520 | 56806 | 56033 | 174359 | Over-range | 26530 | 22742 | 27228 | 76800 | 10713 | 10664 | 11965 | 34101 | 55228 | 51967 | 48843 | 156038 | 55228 | 51967 | 48843 | 156038 | - - - | - - - | - - - | - - -
5/10/2026 | 4:45:00 PM | 279.85 | 276.82 | 277.08 | 484.18 | 477.67 | 482.22 | 218.2372 | 203.7266 | 201.1033 | 6.6582 | 1.44 | 1.438 | 1.436 | 1.559 | 1.563 | 1.76 | Over-range | 59.99 | 55083 | 51633 | 48702 | 155419 | - - - | - - - | - - - | - - - | 55083 | 51633 | 48702 | 155419 | 24135 | 20056 | 24325 | 68515 | - - - | - - - | - - - | - - - | 24135 | 20056 | 24325 | 68515 | 61073 | 56395 | 55721 | 173188 | # # # | # # # | # # # | # # # | 0.902 | 0.916 | 0.874 | 0.897 | # # # | # # # | # # # | - - - | 0.915 | 0.932 | 0.894 | 0.914 | - - - | 0.441 | 1.49 | 1.5 | 1.52 | 1.44 | 1.47 | 1.49 | 19.02 | 20.13 | 22.88 | 0 | - - - | - - - | - - - | - - - | 61073 | 56395 | 55721 | 173188 | Over-range | 26376 | 22680 | 27073 | 76415 | 10640 | 10588 | 11883 | 33835 | 54878 | 51518 | 48532 | 154928 | 54878 | 51518 | 48532 | 154928 | - - - | - - - | - - - | - - -
5/10/2026 | 5:00:00 PM | 279.84 | 276.83 | 277.14 | 484.14 | 477.75 | 482.27 | 216.2171 | 202.5674 | 200.3415 | 6.4501 | 1.44 | 1.438 | 1.436 | 1.562 | 1.573 | 1.755 | Over-range | 59.99 | 54546 | 51248 | 48588 | 154382 | - - - | - - - | - - - | - - - | 54546 | 51248 | 48588 | 154382 | 23945 | 20218 | 24171 | 68333 | - - - | - - - | - - - | - - - | 23945 | 20218 | 24171 | 68333 | 60505 | 56076 | 55521 | 172102 | # # # | # # # | # # # | # # # | 0.902 | 0.914 | 0.875 | 0.897 | # # # | # # # | # # # | - - - | 0.915 | 0.93 | 0.895 | 0.913 | - - - | 0.443 | 1.47 | 1.46 | 1.48 | 1.42 | 1.44 | 1.46 | 19.1 | 20.05 | 22.7 | 0 | - - - | - - - | - - - | - - - | 60505 | 56076 | 55521 | 172102 | Over-range | 26184 | 22763 | 26867 | 76062 | 10594 | 10459 | 11729 | 33406 | 54350 | 51111 | 48428 | 153888 | 54350 | 51111 | 48428 | 153888 | - - - | - - - | - - - | - - -
5/10/2026 | 5:15:00 PM | 280.06 | 277.43 | 277.57 | 484.84 | 478.82 | 482.68 | 216.4049 | 203.6622 | 200.7172 | 6.14 | 1.44 | 1.438 | 1.436 | 1.572 | 1.572 | 1.752 | Over-range | 60.01 | 54568 | 51626 | 48833 | 155027 | - - - | - - - | - - - | - - - | 54568 | 51626 | 48833 | 155027 | 24101 | 20340 | 24089 | 68530 | - - - | - - - | - - - | - - - | 24101 | 20340 | 24089 | 68530 | 60606 | 56500 | 55713 | 172819 | # # # | # # # | # # # | # # # | 0.9 | 0.914 | 0.876 | 0.897 | # # # | # # # | # # # | - - - | 0.914 | 0.93 | 0.896 | 0.914 | - - - | 0.442 | 1.46 | 1.46 | 1.46 | 1.42 | 1.42 | 1.45 | 19.26 | 20.2 | 22.76 | 0 | - - - | - - - | - - - | - - - | 60606 | 56500 | 55713 | 172819 | Over-range | 26371 | 22956 | 26819 | 76374 | 10704 | 10641 | 11789 | 33713 | 54395 | 51478 | 48654 | 154528 | 54395 | 51478 | 48654 | 154528 | - - - | - - - | - - - | - - -
5/10/2026 | 5:30:00 PM | 279.79 | 277.06 | 277.25 | 484.29 | 478.18 | 482.21 | 217.5823 | 204.4655 | 201.2691 | 6.7371 | 1.44 | 1.438 | 1.436 | 1.567 | 1.568 | 1.755 | Over-range | 60 | 54867 | 51815 | 48867 | 155549 | - - - | - - - | - - - | - - - | 54867 | 51815 | 48867 | 155549 | 24100 | 20268 | 24213 | 68582 | - - - | - - - | - - - | - - - | 24100 | 20268 | 24213 | 68582 | 60876 | 56648 | 55802 | 173326 | # # # | # # # | # # # | # # # | 0.901 | 0.915 | 0.876 | 0.897 | # # # | # # # | # # # | - - - | 0.915 | 0.931 | 0.896 | 0.914 | - - - | 0.441 | 1.47 | 1.47 | 1.48 | 1.42 | 1.43 | 1.46 | 19.13 | 20.19 | 22.77 | 0 | - - - | - - - | - - - | - - - | 60876 | 56648 | 55802 | 173326 | Over-range | 26372 | 22897 | 26942 | 76463 | 10707 | 10652 | 11813 | 33809 | 54661 | 51673 | 48723 | 155057 | 54661 | 51673 | 48723 | 155057 | - - - | - - - | - - - | - - -
5/10/2026 | 5:45:00 PM | 279.68 | 277.04 | 277.21 | 484.17 | 478.18 | 482.05 | 216.8928 | 204.3788 | 201.0306 | 6.6111 | 1.44 | 1.438 | 1.436 | 1.57 | 1.569 | 1.75 | Over-range | 59.99 | 54652 | 51765 | 48861 | 155278 | - - - | - - - | - - - | - - - | 54652 | 51765 | 48861 | 155278 | 24057 | 20349 | 24102 | 68508 | - - - | - - - | - - - | - - - | 24057 | 20349 | 24102 | 68508 | 60660 | 56620 | 55727 | 173007 | # # # | # # # | # # # | # # # | 0.901 | 0.914 | 0.877 | 0.898 | # # # | # # # | # # # | - - - | 0.915 | 0.93 | 0.896 | 0.914 | - - - | 0.441 | 1.48 | 1.46 | 1.46 | 1.42 | 1.43 | 1.46 | 19.12 | 20.1 | 22.61 | 0 | - - - | - - - | - - - | - - - | 60660 | 56620 | 55727 | 173007 | Over-range | 26322 | 22939 | 26798 | 76291 | 10681 | 10586 | 11713 | 33571 | 54431 | 51623 | 48737 | 154791 | 54431 | 51623 | 48737 | 154791 | - - - | - - - | - - - | - - -
5/10/2026 | 6:00:00 PM | 279.67 | 277.15 | 277.27 | 484.25 | 478.39 | 482.03 | 214.0045 | 202.9967 | 199.7417 | 6.1016 | 1.44 | 1.438 | 1.436 | 1.576 | 1.576 | 1.74 | Over-range | 60.01 | 53840 | 51317 | 48677 | 153834 | - - - | - - - | - - - | - - - | 53840 | 51317 | 48677 | 153834 | 23906 | 20594 | 23790 | 68291 | - - - | - - - | - - - | - - - | 23906 | 20594 | 23790 | 68291 | 59848 | 56260 | 55382 | 171490 | # # # | # # # | # # # | # # # | 0.9 | 0.912 | 0.879 | 0.897 | # # # | # # # | # # # | - - - | 0.913 | 0.928 | 0.898 | 0.913 | - - - | 0.444 | 1.47 | 1.45 | 1.45 | 1.42 | 1.41 | 1.45 | 19.2 | 19.87 | 22.28 | 0 | - - - | - - - | - - - | - - - | 59848 | 56260 | 55382 | 171490 | Over-range | 26135 | 23059 | 26414 | 75789 | 10561 | 10371 | 11476 | 32868 | 53627 | 51184 | 48532 | 153342 | 53627 | 51184 | 48532 | 153342 | - - - | - - - | - - - | - - -
5/10/2026 | 6:15:00 PM | 279.92 | 277.5 | 277.65 | 484.71 | 479.09 | 482.57 | 217.2971 | 205.4708 | 201.6708 | 6.8213 | 1.44 | 1.438 | 1.437 | 1.573 | 1.567 | 1.744 | Over-range | 60.01 | 54793 | 52123 | 49139 | 156056 | - - - | - - - | - - - | - - - | 54793 | 52123 | 49139 | 156056 | 24138 | 20501 | 24167 | 68807 | - - - | - - - | - - - | - - - | 24138 | 20501 | 24167 | 68807 | 60825 | 57017 | 55994 | 173836 | # # # | # # # | # # # | # # # | 0.901 | 0.914 | 0.878 | 0.898 | # # # | # # # | # # # | - - - | 0.915 | 0.93 | 0.897 | 0.914 | - - - | 0.441 | 1.5 | 1.49 | 1.5 | 1.45 | 1.46 | 1.49 | 19.09 | 20.11 | 22.48 | 0 | - - - | - - - | - - - | - - - | 60825 | 57017 | 55994 | 173836 | Over-range | 26407 | 23112 | 26847 | 76589 | 10708 | 10669 | 11690 | 33636 | 54578 | 51965 | 49021 | 155563 | 54578 | 51965 | 49021 | 155563 | - - - | - - - | - - - | - - -
5/10/2026 | 6:30:00 PM | 279.96 | 277.52 | 277.69 | 484.77 | 479.12 | 482.64 | 216.3353 | 204.7775 | 200.9293 | 6.8221 | 1.44 | 1.438 | 1.437 | 1.576 | 1.57 | 1.745 | Over-range | 59.99 | 54520 | 51906 | 48950 | 155376 | - - - | - - - | - - - | - - - | 54520 | 51906 | 48950 | 155376 | 24109 | 20559 | 24084 | 68753 | - - - | - - - | - - - | - - - | 24109 | 20559 | 24084 | 68753 | 60566 | 56830 | 55795 | 173191 | # # # | # # # | # # # | # # # | 0.9 | 0.913 | 0.877 | 0.897 | # # # | # # # | # # # | - - - | 0.914 | 0.93 | 0.897 | 0.914 | - - - | 0.443 | 1.47 | 1.47 | 1.47 | 1.42 | 1.43 | 1.46 | 19.22 | 20.14 | 22.5 | 0 | - - - | - - - | - - - | - - - | 60566 | 56830 | 55795 | 173191 | Over-range | 26377 | 23138 | 26778 | 76507 | 10700 | 10614 | 11705 | 33562 | 54261 | 51820 | 48800 | 154881 | 54261 | 51820 | 48800 | 154881 | - - - | - - - | - - - | - - -
5/10/2026 | 6:45:00 PM | 280.21 | 277.86 | 277.96 | 485.29 | 479.68 | 483.05 | 215.8291 | 204.7237 | 200.5902 | 6.561 | 1.44 | 1.438 | 1.437 | 1.58 | 1.57 | 1.743 | Over-range | 59.99 | 54388 | 51931 | 48948 | 155267 | - - - | - - - | - - - | - - - | 54388 | 51931 | 48948 | 155267 | 24182 | 20610 | 24028 | 68820 | - - - | - - - | - - - | - - - | 24182 | 20610 | 24028 | 68820 | 60477 | 56883 | 55756 | 173116 | # # # | # # # | # # # | # # # | 0.899 | 0.913 | 0.878 | 0.897 | # # # | # # # | # # # | - - - | 0.913 | 0.929 | 0.897 | 0.913 | - - - | 0.443 | 1.49 | 1.47 | 1.47 | 1.43 | 1.44 | 1.47 | 19.25 | 20.13 | 22.48 | 0 | - - - | - - - | - - - | - - - | 60477 | 56883 | 55756 | 173116 | Over-range | 26446 | 23214 | 26698 | 76560 | 10706 | 10681 | 11638 | 33543 | 54227 | 51758 | 48791 | 154777 | 54227 | 51758 | 48791 | 154777 | - - - | - - - | - - - | - - -
5/10/2026 | 7:00:00 PM | 280.79 | 278.53 | 278.65 | 486.33 | 480.92 | 484.12 | 214.4069 | 203.8847 | 200.4529 | 5.9695 | 1.44 | 1.437 | 1.436 | 1.583 | 1.58 | 1.738 | Over-range | 60 | 54099 | 51740 | 49087 | 154925 | - - - | - - - | - - - | - - - | 54099 | 51740 | 49087 | 154925 | 24143 | 20855 | 23982 | 68980 | - - - | - - - | - - - | - - - | 24143 | 20855 | 23982 | 68980 | 60203 | 56787 | 55855 | 172845 | # # # | # # # | # # # | # # # | 0.899 | 0.911 | 0.879 | 0.896 | # # # | # # # | # # # | - - - | 0.913 | 0.927 | 0.898 | 0.913 | - - - | 0.445 | 1.49 | 1.47 | 1.47 | 1.44 | 1.43 | 1.46 | 19.37 | 20.1 | 22.39 | 0 | - - - | - - - | - - - | - - - | 60203 | 56787 | 55855 | 172845 | Over-range | 26414 | 23404 | 26651 | 76639 | 10713 | 10621 | 11626 | 33395 | 53910 | 51592 | 48927 | 154427 | 53910 | 51592 | 48927 | 154427 | - - - | - - - | - - - | - - -
5/10/2026 | 7:15:00 PM | 281.11 | 279 | 279.02 | 487.03 | 481.72 | 484.65 | 213.388 | 203.6633 | 199.7822 | 5.8964 | 1.44 | 1.438 | 1.436 | 1.589 | 1.58 | 1.735 | Over-range | 60 | 53830 | 51722 | 49014 | 154566 | - - - | - - - | - - - | - - - | 53830 | 51722 | 49014 | 154566 | 24214 | 21001 | 23914 | 69129 | - - - | - - - | - - - | - - - | 24214 | 21001 | 23914 | 69129 | 59985 | 56822 | 55743 | 172550 | # # # | # # # | # # # | # # # | 0.897 | 0.91 | 0.879 | 0.896 | # # # | # # # | # # # | - - - | 0.911 | 0.926 | 0.898 | 0.912 | - - - | 0.447 | 1.5 | 1.47 | 1.47 | 1.45 | 1.43 | 1.47 | 19.42 | 20.08 | 22.29 | 0 | - - - | - - - | - - - | - - - | 59985 | 56822 | 55743 | 172550 | Over-range | 26468 | 23528 | 26551 | 76701 | 10689 | 10607 | 11534 | 33229 | 53646 | 51568 | 48847 | 154060 | 53646 | 51568 | 48847 | 154060 | - - - | - - - | - - - | - - -
5/10/2026 | 7:30:00 PM | 281.31 | 279.16 | 279.2 | 487.35 | 481.99 | 484.99 | 214.5035 | 204.4911 | 200.2409 | 6.3933 | 1.44 | 1.438 | 1.437 | 1.587 | 1.578 | 1.74 | Over-range | 60 | 54166 | 52000 | 49096 | 155262 | - - - | - - - | - - - | - - - | 54166 | 52000 | 49096 | 155262 | 24322 | 20978 | 24069 | 69369 | - - - | - - - | - - - | - - - | 24322 | 20978 | 24069 | 69369 | 60342 | 57086 | 55907 | 173335 | # # # | # # # | # # # | # # # | 0.898 | 0.911 | 0.878 | 0.896 | # # # | # # # | # # # | - - - | 0.912 | 0.927 | 0.897 | 0.912 | - - - | 0.447 | 1.51 | 1.47 | 1.47 | 1.45 | 1.43 | 1.47 | 19.41 | 20.16 | 22.43 | 0 | - - - | - - - | - - - | - - - | 60342 | 57086 | 55907 | 173335 | Over-range | 26592 | 23554 | 26743 | 77062 | 10750 | 10710 | 11656 | 33562 | 53977 | 51858 | 48926 | 154760 | 53977 | 51858 | 48926 | 154760 | - - - | - - - | - - - | - - -
5/10/2026 | 7:45:00 PM | 281.77 | 279.82 | 279.72 | 488.34 | 483.07 | 485.74 | 213.4724 | 204.5026 | 199.7286 | 6.0135 | 1.44 | 1.438 | 1.437 | 1.597 | 1.58 | 1.735 | Over-range | 60 | 53894 | 52060 | 49131 | 155085 | - - - | - - - | - - - | - - - | 53894 | 52060 | 49131 | 155085 | 24436 | 21190 | 23940 | 69567 | - - - | - - - | - - - | - - - | 24436 | 21190 | 23940 | 69567 | 60150 | 57222 | 55867 | 173239 | # # # | # # # | # # # | # # # | 0.896 | 0.91 | 0.879 | 0.895 | # # # | # # # | # # # | - - - | 0.91 | 0.926 | 0.898 | 0.912 | - - - | 0.449 | 1.5 | 1.47 | 1.47 | 1.46 | 1.42 | 1.47 | 19.55 | 20.17 | 22.33 | 0 | - - - | - - - | - - - | - - - | 60150 | 57222 | 55867 | 173239 | Over-range | 26711 | 23753 | 26594 | 77205 | 10785 | 10730 | 11581 | 33482 | 53714 | 51906 | 48954 | 154573 | 53714 | 51906 | 48954 | 154573 | - - - | - - - | - - - | - - -
5/10/2026 | 8:00:00 PM | 282.23 | 280.14 | 280.07 | 489.04 | 483.59 | 486.49 | 212.4327 | 203.2521 | 199.4591 | 5.7315 | 1.44 | 1.437 | 1.436 | 1.595 | 1.586 | 1.736 | Over-range | 60.01 | 53726 | 51720 | 49109 | 154555 | - - - | - - - | - - - | - - - | 53726 | 51720 | 49109 | 154555 | 24327 | 21308 | 23987 | 69622 | - - - | - - - | - - - | - - - | 24327 | 21308 | 23987 | 69622 | 59954 | 56939 | 55862 | 172755 | # # # | # # # | # # # | # # # | 0.896 | 0.908 | 0.879 | 0.895 | # # # | # # # | # # # | - - - | 0.91 | 0.924 | 0.898 | 0.911 | - - - | 0.451 | 1.5 | 1.47 | 1.46 | 1.45 | 1.42 | 1.46 | 19.62 | 20.14 | 22.31 | 0 | - - - | - - - | - - - | - - - | 59954 | 56939 | 55862 | 172755 | Over-range | 26608 | 23814 | 26625 | 77182 | 10779 | 10632 | 11554 | 33314 | 53536 | 51565 | 48935 | 154036 | 53536 | 51565 | 48935 | 154036 | - - - | - - - | - - - | - - -
5/10/2026 | 8:15:00 PM | 282.11 | 279.95 | 279.93 | 488.77 | 483.29 | 486.3 | 211.854 | 202.6345 | 199.5347 | 5.6279 | 1.44 | 1.437 | 1.436 | 1.595 | 1.593 | 1.737 | Over-range | 60 | 53587 | 51479 | 49106 | 154172 | - - - | - - - | - - - | - - - | 53587 | 51479 | 49106 | 154172 | 24144 | 21324 | 23950 | 69419 | - - - | - - - | - - - | - - - | 24144 | 21324 | 23950 | 69419 | 59766 | 56728 | 55856 | 172350 | # # # | # # # | # # # | # # # | 0.897 | 0.908 | 0.879 | 0.895 | # # # | # # # | # # # | - - - | 0.911 | 0.923 | 0.898 | 0.911 | - - - | 0.45 | 1.48 | 1.46 | 1.44 | 1.44 | 1.4 | 1.43 | 19.75 | 20.21 | 22.4 | 0 | - - - | - - - | - - - | - - - | 59766 | 56728 | 55856 | 172350 | Over-range | 26465 | 23831 | 26618 | 77042 | 10838 | 10639 | 11614 | 33413 | 53398 | 51322 | 48940 | 153660 | 53398 | 51322 | 48940 | 153660 | - - - | - - - | - - - | - - -
5/10/2026 | 8:30:00 PM | 282.36 | 280.3 | 280.21 | 489.3 | 483.86 | 486.71 | 209.4621 | 201.8175 | 198.2583 | 5.5373 | 1.44 | 1.436 | 1.435 | 1.603 | 1.599 | 1.73 | Over-range | 60 | 52926 | 51210 | 48910 | 153046 | - - - | - - - | - - - | - - - | 52926 | 51210 | 48910 | 153046 | 24099 | 21598 | 23737 | 69434 | - - - | - - - | - - - | - - - | 24099 | 21598 | 23737 | 69434 | 59143 | 56569 | 55552 | 171265 | # # # | # # # | # # # | # # # | 0.895 | 0.905 | 0.88 | 0.894 | # # # | # # # | # # # | - - - | 0.91 | 0.921 | 0.899 | 0.91 | - - - | 0.454 | 1.47 | 1.44 | 1.41 | 1.43 | 1.38 | 1.42 | 19.87 | 20.13 | 22.16 | 0 | - - - | - - - | - - - | - - - | 59143 | 56569 | 55552 | 171265 | Over-range | 26396 | 24033 | 26342 | 76868 | 10769 | 10541 | 11421 | 32976 | 52740 | 51058 | 48729 | 152527 | 52740 | 51058 | 48729 | 152527 | - - - | - - - | - - - | - - -
5/10/2026 | 8:45:00 PM | 282.48 | 280.28 | 280.21 | 489.41 | 483.78 | 486.86 | 207.8776 | 200.3921 | 197.2158 | 5.5115 | 1.439 | 1.436 | 1.434 | 1.603 | 1.605 | 1.729 | Over-range | 60 | 52508 | 50755 | 48625 | 151889 | - - - | - - - | - - - | - - - | 52508 | 50755 | 48625 | 151889 | 23981 | 21679 | 23696 | 69356 | - - - | - - - | - - - | - - - | 23981 | 21679 | 23696 | 69356 | 58720 | 56166 | 55262 | 170149 | # # # | # # # | # # # | # # # | 0.894 | 0.904 | 0.88 | 0.893 | # # # | # # # | # # # | - - - | 0.909 | 0.919 | 0.898 | 0.909 | - - - | 0.457 | 1.46 | 1.43 | 1.41 | 1.42 | 1.37 | 1.41 | 20 | 20.08 | 22.08 | 0 | - - - | - - - | - - - | - - - | 58720 | 56166 | 55262 | 170149 | Over-range | 26287 | 24052 | 26258 | 76683 | 10766 | 10416 | 11313 | 32712 | 52313 | 50604 | 48451 | 151368 | 52313 | 50604 | 48451 | 151368 | - - - | - - - | - - - | - - -
5/10/2026 | 9:00:00 PM | 282.72 | 280.51 | 280.34 | 489.88 | 484.04 | 487.16 | 206.8667 | 199.5369 | 196.0073 | 5.5602 | 1.439 | 1.436 | 1.434 | 1.604 | 1.606 | 1.729 | Over-range | 60.01 | 52240 | 50542 | 48316 | 151097 | - - - | - - - | - - - | - - - | 52240 | 50542 | 48316 | 151097 | 24011 | 21715 | 23660 | 69385 | - - - | - - - | - - - | - - - | 24011 | 21715 | 23660 | 69385 | 58486 | 55971 | 54948 | 169405 | # # # | # # # | # # # | # # # | 0.893 | 0.903 | 0.879 | 0.892 | # # # | # # # | # # # | - - - | 0.908 | 0.918 | 0.897 | 0.908 | - - - | 0.459 | 1.47 | 1.44 | 1.41 | 1.43 | 1.37 | 1.42 | 20.02 | 19.99 | 21.99 | 0 | - - - | - - - | - - - | - - - | 58486 | 55971 | 54948 | 169405 | Over-range | 26298 | 24047 | 26171 | 76600 | 10727 | 10331 | 11184 | 32454 | 52060 | 50373 | 48142 | 150575 | 52060 | 50373 | 48142 | 150575 | - - - | - - - | - - - | - - -
5/10/2026 | 9:15:00 PM | 282.99 | 280.83 | 280.69 | 490.36 | 484.67 | 487.68 | 204.048 | 197.729 | 194.232 | 5.3114 | 1.44 | 1.436 | 1.434 | 1.61 | 1.613 | 1.721 | Over-range | 59.99 | 51478 | 50009 | 47969 | 149456 | - - - | - - - | - - - | - - - | 51478 | 50009 | 47969 | 149456 | 23927 | 21903 | 23507 | 69337 | - - - | - - - | - - - | - - - | 23927 | 21903 | 23507 | 69337 | 57743 | 55529 | 54518 | 167790 | # # # | # # # | # # # | # # # | 0.891 | 0.901 | 0.88 | 0.891 | # # # | # # # | # # # | - - - | 0.906 | 0.916 | 0.897 | 0.906 | - - - | 0.464 | 1.5 | 1.45 | 1.43 | 1.45 | 1.39 | 1.44 | 20.01 | 19.85 | 21.61 | 0 | - - - | - - - | - - - | - - - | 57743 | 55529 | 54518 | 167790 | Over-range | 26158 | 24137 | 25908 | 76266 | 10571 | 10139 | 10891 | 31760 | 51288 | 49849 | 47793 | 148929 | 51288 | 49849 | 47793 | 148929 | - - - | - - - | - - - | - - -
5/10/2026 | 9:30:00 PM | 283.34 | 281.15 | 281.05 | 490.93 | 485.25 | 488.32 | 200.9319 | 195.042 | 191.5192 | 5.2919 | 1.439 | 1.435 | 1.433 | 1.611 | 1.614 | 1.72 | Over-range | 60.02 | 50655 | 49309 | 47310 | 147274 | - - - | - - - | - - - | - - - | 50655 | 49309 | 47310 | 147274 | 23876 | 21887 | 23409 | 69171 | - - - | - - - | - - - | - - - | 23876 | 21887 | 23409 | 69171 | 56931 | 54835 | 53825 | 165592 | # # # | # # # | # # # | # # # | 0.89 | 0.899 | 0.879 | 0.889 | # # # | # # # | # # # | - - - | 0.904 | 0.914 | 0.896 | 0.904 | - - - | 0.47 | 1.48 | 1.45 | 1.41 | 1.44 | 1.37 | 1.42 | 19.73 | 19.52 | 21.21 | 0 | - - - | - - - | - - - | - - - | 56931 | 54835 | 53825 | 165592 | Over-range | 25985 | 23991 | 25669 | 75705 | 10255 | 9826 | 10532 | 30764 | 50475 | 49148 | 47125 | 146748 | 50475 | 49148 | 47125 | 146748 | - - - | - - - | - - - | - - -
5/10/2026 | 9:45:00 PM | 283.41 | 281.26 | 281.1 | 491.11 | 485.39 | 488.39 | 198.7344 | 192.7778 | 189.1997 | 5.256 | 1.439 | 1.435 | 1.433 | 1.613 | 1.613 | 1.723 | Over-range | 60 | 50021 | 48695 | 46647 | 145364 | - - - | - - - | - - - | - - - | 50021 | 48695 | 46647 | 145364 | 23837 | 21812 | 23366 | 69015 | - - - | - - - | - - - | - - - | 23837 | 21812 | 23366 | 69015 | 56323 | 54220 | 53183 | 163726 | # # # | # # # | # # # | # # # | 0.888 | 0.898 | 0.877 | 0.888 | # # # | # # # | # # # | - - - | 0.902 | 0.912 | 0.893 | 0.903 | - - - | 0.475 | 1.48 | 1.45 | 1.4 | 1.44 | 1.37 | 1.42 | 19.62 | 19.41 | 21.08 | 0 | - - - | - - - | - - - | - - - | 56323 | 54220 | 53183 | 163726 | Over-range | 25887 | 23846 | 25542 | 75336 | 10095 | 9636 | 10315 | 30205 | 49819 | 48526 | 46493 | 144838 | 49819 | 48526 | 46493 | 144838 | - - - | - - - | - - - | - - -
5/10/2026 | 10:00:00 PM | 283.86 | 281.6 | 281.5 | 491.79 | 485.99 | 489.18 | 197.34 | 190.928 | 187.7884 | 5.2094 | 1.438 | 1.434 | 1.432 | 1.611 | 1.614 | 1.726 | Over-range | 60.02 | 49710 | 48231 | 46269 | 144210 | - - - | - - - | - - - | - - - | 49710 | 48231 | 46269 | 144210 | 23827 | 21774 | 23437 | 69038 | - - - | - - - | - - - | - - - | 23827 | 21774 | 23437 | 69038 | 56016 | 53765 | 52863 | 162644 | # # # | # # # | # # # | # # # | 0.887 | 0.897 | 0.875 | 0.887 | # # # | # # # | # # # | - - - | 0.901 | 0.911 | 0.891 | 0.901 | - - - | 0.479 | 1.48 | 1.44 | 1.41 | 1.44 | 1.37 | 1.42 | 19.51 | 19.31 | 21.01 | 0 | - - - | - - - | - - - | - - - | 56016 | 53765 | 52863 | 162644 | Over-range | 25821 | 23757 | 25567 | 75209 | 9950 | 9502 | 10215 | 29836 | 49525 | 48067 | 46092 | 143684 | 49525 | 48067 | 46092 | 143684 | - - - | - - - | - - - | - - -
5/10/2026 | 10:15:00 PM | 283.18 | 280.88 | 280.89 | 490.52 | 484.84 | 488.1 | 196.2733 | 189.9627 | 187.3203 | 5.1593 | 1.437 | 1.433 | 1.431 | 1.609 | 1.62 | 1.725 | Over-range | 60 | 49331 | 47822 | 46050 | 143204 | - - - | - - - | - - - | - - - | 49331 | 47822 | 46050 | 143204 | 23627 | 21698 | 23337 | 68662 | - - - | - - - | - - - | - - - | 23627 | 21698 | 23337 | 68662 | 55580 | 53356 | 52615 | 161551 | # # # | # # # | # # # | # # # | 0.888 | 0.896 | 0.875 | 0.886 | # # # | # # # | # # # | - - - | 0.901 | 0.91 | 0.891 | 0.901 | - - - | 0.48 | 1.48 | 1.45 | 1.4 | 1.44 | 1.38 | 1.41 | 19.5 | 19.31 | 20.98 | 0 | - - - | - - - | - - - | - - - | 55580 | 53356 | 52615 | 161551 | Over-range | 25604 | 23661 | 25450 | 74776 | 9867 | 9437 | 10153 | 29613 | 49155 | 47654 | 45869 | 142678 | 49155 | 47654 | 45869 | 142678 | - - - | - - - | - - - | - - -
5/10/2026 | 10:30:00 PM | 283.19 | 280.87 | 280.74 | 490.62 | 484.66 | 487.95 | 196.6474 | 190.0305 | 186.8158 | 5.1795 | 1.437 | 1.433 | 1.431 | 1.61 | 1.613 | 1.729 | Over-range | 60.01 | 49396 | 47887 | 45871 | 143154 | - - - | - - - | - - - | - - - | 49396 | 47887 | 45871 | 143154 | 23741 | 21608 | 23313 | 68661 | - - - | - - - | - - - | - - - | 23741 | 21608 | 23313 | 68661 | 55689 | 53374 | 52446 | 161510 | # # # | # # # | # # # | # # # | 0.887 | 0.897 | 0.875 | 0.886 | # # # | # # # | # # # | - - - | 0.901 | 0.911 | 0.891 | 0.901 | - - - | 0.48 | 1.5 | 1.46 | 1.42 | 1.45 | 1.39 | 1.44 | 19.48 | 19.27 | 21.02 | 0 | - - - | - - - | - - - | - - - | 55689 | 53374 | 52446 | 161510 | Over-range | 25716 | 23572 | 25427 | 74782 | 9882 | 9419 | 10150 | 29630 | 49206 | 47728 | 45698 | 142632 | 49206 | 47728 | 45698 | 142632 | - - - | - - - | - - - | - - -
5/10/2026 | 10:45:00 PM | 283.79 | 281.3 | 281.25 | 491.51 | 485.4 | 488.98 | 196.5626 | 189.1214 | 186.6045 | 5.1849 | 1.437 | 1.434 | 1.431 | 1.603 | 1.612 | 1.731 | Over-range | 60.01 | 49498 | 47723 | 45815 | 143037 | - - - | - - - | - - - | - - - | 49498 | 47723 | 45815 | 143037 | 23771 | 21586 | 23506 | 68862 | - - - | - - - | - - - | - - - | 23771 | 21586 | 23506 | 68862 | 55782 | 53200 | 52482 | 161464 | # # # | # # # | # # # | # # # | 0.887 | 0.897 | 0.873 | 0.886 | # # # | # # # | # # # | - - - | 0.901 | 0.911 | 0.889 | 0.9 | - - - | 0.481 | 1.52 | 1.48 | 1.46 | 1.47 | 1.42 | 1.47 | 19.34 | 19.16 | 20.97 | 0 | - - - | - - - | - - - | - - - | 55782 | 53200 | 52482 | 161464 | Over-range | 25721 | 23511 | 25599 | 74909 | 9824 | 9318 | 10138 | 29483 | 49298 | 47570 | 45643 | 142511 | 49298 | 47570 | 45643 | 142511 | - - - | - - - | - - - | - - -
5/10/2026 | 11:00:00 PM | 284.11 | 281.68 | 281.56 | 492.13 | 486.01 | 489.48 | 196.594 | 189.2844 | 186.4149 | 5.1691 | 1.438 | 1.434 | 1.431 | 1.603 | 1.608 | 1.728 | Over-range | 60.02 | 49548 | 47842 | 45833 | 143223 | - - - | - - - | - - - | - - - | 49548 | 47842 | 45833 | 143223 | 23863 | 21623 | 23517 | 69004 | - - - | - - - | - - - | - - - | 23863 | 21623 | 23517 | 69004 | 55853 | 53317 | 52487 | 161657 | # # # | # # # | # # # | # # # | 0.887 | 0.897 | 0.873 | 0.886 | # # # | # # # | # # # | - - - | 0.9 | 0.911 | 0.889 | 0.9 | - - - | 0.482 | 1.53 | 1.49 | 1.48 | 1.48 | 1.43 | 1.48 | 19.19 | 19.05 | 20.83 | 0 | - - - | - - - | - - - | - - - | 55853 | 53317 | 52487 | 161657 | Over-range | 25780 | 23534 | 25578 | 74968 | 9753 | 9288 | 10057 | 29303 | 49357 | 47681 | 45661 | 142698 | 49357 | 47681 | 45661 | 142698 | - - - | - - - | - - - | - - -
5/10/2026 | 11:15:00 PM | 284.29 | 281.75 | 281.64 | 492.38 | 486.07 | 489.75 | 196.9365 | 188.9432 | 186.4148 | 5.1774 | 1.438 | 1.435 | 1.431 | 1.597 | 1.605 | 1.731 | Over-range | 60.02 | 49690 | 47791 | 45790 | 143272 | - - - | - - - | - - - | - - - | 49690 | 47791 | 45790 | 143272 | 23895 | 21554 | 23631 | 69080 | - - - | - - - | - - - | - - - | 23895 | 21554 | 23631 | 69080 | 55988 | 53234 | 52501 | 161723 | # # # | # # # | # # # | # # # | 0.887 | 0.898 | 0.872 | 0.886 | # # # | # # # | # # # | - - - | 0.901 | 0.911 | 0.888 | 0.9 | - - - | 0.482 | 1.55 | 1.51 | 1.49 | 1.5 | 1.45 | 1.5 | 19.1 | 18.98 | 20.85 | 0 | - - - | - - - | - - - | - - - | 55988 | 53234 | 52501 | 161723 | Over-range | 25798 | 23449 | 25684 | 75017 | 9724 | 9233 | 10060 | 29249 | 49506 | 47618 | 45624 | 142747 | 49506 | 47618 | 45624 | 142747 | - - - | - - - | - - - | - - -
5/10/2026 | 11:30:00 PM | 284.74 | 282.18 | 282.11 | 493.12 | 486.85 | 490.55 | 197.1017 | 188.947 | 186.8526 | 5.1937 | 1.44 | 1.436 | 1.432 | 1.593 | 1.607 | 1.73 | Over-range | 60.01 | 49831 | 47837 | 45952 | 143620 | - - - | - - - | - - - | - - - | 49831 | 47837 | 45952 | 143620 | 23920 | 21651 | 23773 | 69344 | - - - | - - - | - - - | - - - | 23920 | 21651 | 23773 | 69344 | 56122 | 53316 | 52712 | 162150 | # # # | # # # | # # # | # # # | 0.888 | 0.897 | 0.872 | 0.886 | # # # | # # # | # # # | - - - | 0.901 | 0.91 | 0.887 | 0.9 | - - - | 0.483 | 1.59 | 1.54 | 1.52 | 1.53 | 1.48 | 1.54 | 19.08 | 18.96 | 20.85 | 0 | - - - | - - - | - - - | - - - | 56122 | 53316 | 52712 | 162150 | Over-range | 25817 | 23541 | 25827 | 75273 | 9713 | 9242 | 10092 | 29279 | 49659 | 47657 | 45772 | 143087 | 49659 | 47657 | 45772 | 143087 | - - - | - - - | - - - | - - -
5/10/2026 | 11:45:00 PM | 285.05 | 282.5 | 282.33 | 493.72 | 487.3 | 490.98 | 197.3809 | 189.2096 | 186.5656 | 5.1802 | 1.44 | 1.435 | 1.432 | 1.597 | 1.603 | 1.732 | Over-range | 60.02 | 49917 | 47981 | 45906 | 143804 | - - - | - - - | - - - | - - - | 49917 | 47981 | 45906 | 143804 | 24058 | 21666 | 23765 | 69489 | - - - | - - - | - - - | - - - | 24058 | 21666 | 23765 | 69489 | 56262 | 53451 | 52673 | 162387 | # # # | # # # | # # # | # # # | 0.887 | 0.898 | 0.872 | 0.886 | # # # | # # # | # # # | - - - | 0.9 | 0.911 | 0.887 | 0.9 | - - - | 0.483 | 1.59 | 1.54 | 1.53 | 1.54 | 1.49 | 1.55 | 19.06 | 18.99 | 20.86 | 0 | - - - | - - - | - - - | - - - | 56262 | 53451 | 52673 | 162387 | Over-range | 25958 | 23554 | 25828 | 75430 | 9747 | 9241 | 10112 | 29343 | 49688 | 47842 | 45740 | 143270 | 49688 | 47842 | 45740 | 143270 | - - - | - - - | - - - | - - -
5/11/2026 | 12:00:00 AM | 284.71 | 282.13 | 282.02 | 493.09 | 486.71 | 490.44 | 197.5912 | 189.4365 | 187.0455 | 5.212 | 1.44 | 1.435 | 1.432 | 1.595 | 1.606 | 1.732 | Over-range | 60.01 | 49938 | 47967 | 45984 | 143889 | - - - | - - - | - - - | - - - | 49938 | 47967 | 45984 | 143889 | 23982 | 21654 | 23773 | 69409 | - - - | - - - | - - - | - - - | 23982 | 21654 | 23773 | 69409 | 56254 | 53445 | 52749 | 162448 | # # # | # # # | # # # | # # # | 0.888 | 0.898 | 0.872 | 0.886 | # # # | # # # | # # # | - - - | 0.901 | 0.911 | 0.888 | 0.9 | - - - | 0.482 | 1.6 | 1.55 | 1.54 | 1.54 | 1.5 | 1.55 | 19.14 | 19.09 | 20.96 | 0 | - - - | - - - | - - - | - - - | 56254 | 53445 | 52749 | 162448 | Over-range | 25899 | 23570 | 25844 | 75402 | 9777 | 9307 | 10137 | 29457 | 49743 | 47783 | 45821 | 143347 | 49743 | 47783 | 45821 | 143347 | - - - | - - - | - - - | - - -
5/11/2026 | 12:15:00 AM | 283.44 | 280.78 | 280.69 | 490.82 | 484.35 | 488.23 | 197.5245 | 189.0896 | 186.9122 | 5.2151 | 1.438 | 1.434 | 1.431 | 1.594 | 1.605 | 1.734 | Over-range | 60 | 49753 | 47701 | 45763 | 143217 | - - - | - - - | - - - | - - - | 49753 | 47701 | 45763 | 143217 | 23747 | 21399 | 23578 | 68725 | - - - | - - - | - - - | - - - | 23747 | 21399 | 23578 | 68725 | 55986 | 53093 | 52464 | 161543 | # # # | # # # | # # # | # # # | 0.889 | 0.898 | 0.872 | 0.887 | # # # | # # # | # # # | - - - | 0.902 | 0.912 | 0.888 | 0.901 | - - - | 0.48 | 1.57 | 1.53 | 1.51 | 1.52 | 1.49 | 1.53 | 19.17 | 19.1 | 20.98 | 0 | - - - | - - - | - - - | - - - | 55986 | 53093 | 52464 | 161543 | Over-range | 25671 | 23313 | 25656 | 74733 | 9751 | 9249 | 10114 | 29357 | 49553 | 47536 | 45593 | 142681 | 49553 | 47536 | 45593 | 142681 | - - - | - - - | - - - | - - -
5/11/2026 | 12:30:00 AM | 283.69 | 281.11 | 281.01 | 491.31 | 484.95 | 488.69 | 196.7973 | 188.6997 | 186.448 | 5.1938 | 1.438 | 1.433 | 1.43 | 1.596 | 1.606 | 1.732 | Over-range | 60 | 49589 | 47626 | 45707 | 142922 | - - - | - - - | - - - | - - - | 49589 | 47626 | 45707 | 142922 | 23748 | 21463 | 23558 | 68769 | - - - | - - - | - - - | - - - | 23748 | 21463 | 23558 | 68769 | 55830 | 53045 | 52393 | 161267 | # # # | # # # | # # # | # # # | 0.888 | 0.898 | 0.872 | 0.886 | # # # | # # # | # # # | - - - | 0.901 | 0.911 | 0.888 | 0.9 | - - - | 0.481 | 1.56 | 1.53 | 1.51 | 1.51 | 1.48 | 1.52 | 19.1 | 19.03 | 20.85 | 0 | - - - | - - - | - - - | - - - | 55830 | 53045 | 52393 | 161267 | Over-range | 25649 | 23357 | 25610 | 74703 | 9690 | 9214 | 10045 | 29179 | 49395 | 47467 | 45533 | 142394 | 49395 | 47467 | 45533 | 142394 | - - - | - - - | - - - | - - -
5/11/2026 | 12:45:00 AM | 283.9 | 281.4 | 281.23 | 491.76 | 485.43 | 489.02 | 197.6151 | 189.7718 | 186.9986 | 5.2222 | 1.438 | 1.434 | 1.43 | 1.602 | 1.605 | 1.732 | Over-range | 60 | 49805 | 47957 | 45896 | 143658 | - - - | - - - | - - - | - - - | 49805 | 47957 | 45896 | 143658 | 23887 | 21538 | 23587 | 69012 | - - - | - - - | - - - | - - - | 23887 | 21538 | 23587 | 69012 | 56102 | 53402 | 52590 | 162094 | # # # | # # # | # # # | # # # | 0.888 | 0.898 | 0.873 | 0.886 | # # # | # # # | # # # | - - - | 0.901 | 0.912 | 0.889 | 0.901 | - - - | 0.48 | 1.58 | 1.53 | 1.52 | 1.52 | 1.48 | 1.53 | 19.25 | 19.23 | 20.99 | 0 | - - - | - - - | - - - | - - - | 56102 | 53402 | 52590 | 162094 | Over-range | 25824 | 23493 | 25675 | 75078 | 9813 | 9380 | 10140 | 29561 | 49616 | 47783 | 45722 | 143121 | 49616 | 47783 | 45722 | 143121 | - - - | - - - | - - - | - - -
5/11/2026 | 1:00:00 AM | 284.15 | 281.61 | 281.41 | 492.19 | 485.73 | 489.4 | 198.2045 | 190.1384 | 187.3543 | 5.2422 | 1.439 | 1.434 | 1.431 | 1.601 | 1.604 | 1.735 | Over-range | 60.02 | 50012 | 48106 | 46005 | 144123 | - - - | - - - | - - - | - - - | 50012 | 48106 | 46005 | 144123 | 23952 | 21549 | 23648 | 69149 | - - - | - - - | - - - | - - - | 23952 | 21549 | 23648 | 69149 | 56320 | 53544 | 52723 | 162588 | # # # | # # # | # # # | # # # | 0.888 | 0.898 | 0.873 | 0.886 | # # # | # # # | # # # | - - - | 0.901 | 0.912 | 0.889 | 0.901 | - - - | 0.48 | 1.59 | 1.53 | 1.51 | 1.52 | 1.48 | 1.53 | 19.26 | 19.24 | 21.05 | 0 | - - - | - - - | - - - | - - - | 56320 | 53544 | 52723 | 162588 | Over-range | 25899 | 23511 | 25755 | 75255 | 9851 | 9401 | 10202 | 29692 | 49809 | 47941 | 45833 | 143584 | 49809 | 47941 | 45833 | 143584 | - - - | - - - | - - - | - - -
5/11/2026 | 1:15:00 AM | 284.09 | 281.52 | 281.48 | 491.98 | 485.74 | 489.45 | 198.221 | 190.2759 | 188.2279 | 5.2223 | 1.439 | 1.434 | 1.431 | 1.597 | 1.611 | 1.73 | Over-range | 60.01 | 50057 | 48079 | 46257 | 144393 | - - - | - - - | - - - | - - - | 50057 | 48079 | 46257 | 144393 | 23842 | 21653 | 23721 | 69216 | - - - | - - - | - - - | - - - | 23842 | 21653 | 23721 | 69216 | 56312 | 53566 | 52981 | 162859 | # # # | # # # | # # # | # # # | 0.889 | 0.898 | 0.873 | 0.887 | # # # | # # # | # # # | - - - | 0.902 | 0.911 | 0.889 | 0.901 | - - - | 0.479 | 1.58 | 1.53 | 1.54 | 1.53 | 1.49 | 1.54 | 19.27 | 19.3 | 21.04 | 0 | - - - | - - - | - - - | - - - | 56312 | 53566 | 52981 | 162859 | Over-range | 25794 | 23618 | 25831 | 75325 | 9844 | 9431 | 10224 | 29715 | 49867 | 47902 | 46075 | 143844 | 49867 | 47902 | 46075 | 143844 | - - - | - - - | - - - | - - -
5/11/2026 | 1:30:00 AM | 284.17 | 281.64 | 281.57 | 492.15 | 485.95 | 489.59 | 197.7268 | 189.9294 | 187.5626 | 5.2183 | 1.438 | 1.433 | 1.431 | 1.6 | 1.609 | 1.729 | Over-range | 60.01 | 49908 | 48008 | 46104 | 144020 | - - - | - - - | - - - | - - - | 49908 | 48008 | 46104 | 144020 | 23878 | 21639 | 23680 | 69197 | - - - | - - - | - - - | - - - | 23878 | 21639 | 23680 | 69197 | 56187 | 53492 | 52812 | 162492 | # # # | # # # | # # # | # # # | 0.888 | 0.898 | 0.873 | 0.886 | # # # | # # # | # # # | - - - | 0.901 | 0.911 | 0.889 | 0.901 | - - - | 0.481 | 1.58 | 1.54 | 1.53 | 1.53 | 1.49 | 1.54 | 19.24 | 19.28 | 20.95 | 0 | - - - | - - - | - - - | - - - | 56187 | 53492 | 52812 | 162492 | Over-range | 25811 | 23593 | 25760 | 75245 | 9799 | 9401 | 10139 | 29554 | 49716 | 47834 | 45922 | 143471 | 49716 | 47834 | 45922 | 143471 | - - - | - - - | - - - | - - -
5/11/2026 | 1:45:00 AM | 284.38 | 281.76 | 281.79 | 492.41 | 486.21 | 490.02 | 198.3534 | 190.0624 | 188.4608 | 5.2383 | 1.438 | 1.433 | 1.43 | 1.597 | 1.614 | 1.733 | Over-range | 60.01 | 50137 | 48031 | 46311 | 144480 | - - - | - - - | - - - | - - - | 50137 | 48031 | 46311 | 144480 | 23865 | 21688 | 23857 | 69410 | - - - | - - - | - - - | - - - | 23865 | 21688 | 23857 | 69410 | 56408 | 53551 | 53106 | 163065 | # # # | # # # | # # # | # # # | 0.889 | 0.897 | 0.872 | 0.886 | # # # | # # # | # # # | - - - | 0.902 | 0.911 | 0.888 | 0.901 | - - - | 0.48 | 1.58 | 1.54 | 1.53 | 1.53 | 1.5 | 1.54 | 19.41 | 19.45 | 21.17 | 0 | - - - | - - - | - - - | - - - | 56408 | 53551 | 53106 | 163065 | Over-range | 25847 | 23680 | 25991 | 75602 | 9925 | 9505 | 10313 | 29965 | 49951 | 47854 | 46119 | 143923 | 49951 | 47854 | 46119 | 143923 | - - - | - - - | - - - | - - -
5/11/2026 | 2:00:00 AM | 284.59 | 281.97 | 281.91 | 492.83 | 486.47 | 490.28 | 199.5573 | 191.1592 | 189.0198 | 5.2611 | 1.438 | 1.433 | 1.43 | 1.599 | 1.61 | 1.734 | Over-range | 60.01 | 50483 | 48405 | 46491 | 145380 | - - - | - - - | - - - | - - - | 50483 | 48405 | 46491 | 145380 | 24014 | 21680 | 23872 | 69566 | - - - | - - - | - - - | - - - | 24014 | 21680 | 23872 | 69566 | 56792 | 53900 | 53287 | 163979 | # # # | # # # | # # # | # # # | 0.889 | 0.898 | 0.873 | 0.887 | # # # | # # # | # # # | - - - | 0.902 | 0.912 | 0.889 | 0.901 | - - - | 0.478 | 1.61 | 1.53 | 1.53 | 1.53 | 1.5 | 1.55 | 19.44 | 19.51 | 21.24 | 0 | - - - | - - - | - - - | - - - | 56792 | 53900 | 53287 | 163979 | Over-range | 26015 | 23711 | 26039 | 75854 | 10004 | 9601 | 10400 | 30240 | 50288 | 48241 | 46294 | 144823 | 50288 | 48241 | 46294 | 144823 | - - - | - - - | - - - | - - -
5/11/2026 | 2:15:00 AM | 284.56 | 281.97 | 281.96 | 492.76 | 486.54 | 490.29 | 201.1867 | 193.1937 | 190.9992 | 5.2919 | 1.439 | 1.433 | 1.431 | 1.599 | 1.612 | 1.729 | Over-range | 60 | 50962 | 48959 | 47101 | 147022 | - - - | - - - | - - - | - - - | 50962 | 48959 | 47101 | 147022 | 24040 | 21806 | 23898 | 69743 | - - - | - - - | - - - | - - - | 24040 | 21806 | 23898 | 69743 | 57249 | 54474 | 53853 | 165576 | # # # | # # # | # # # | # # # | 0.89 | 0.899 | 0.875 | 0.888 | # # # | # # # | # # # | - - - | 0.904 | 0.913 | 0.891 | 0.903 | - - - | 0.474 | 1.62 | 1.55 | 1.55 | 1.55 | 1.51 | 1.56 | 19.48 | 19.57 | 21.26 | 0 | - - - | - - - | - - - | - - - | 57249 | 54474 | 53853 | 165576 | Over-range | 26083 | 23885 | 26108 | 76157 | 10118 | 9746 | 10512 | 30591 | 50772 | 48784 | 46906 | 146461 | 50772 | 48784 | 46906 | 146461 | - - - | - - - | - - - | - - -
5/11/2026 | 2:30:00 AM | 284.77 | 282.19 | 282.13 | 493.16 | 486.86 | 490.6 | 201.5461 | 193.3865 | 191.1124 | 5.3087 | 1.439 | 1.433 | 1.431 | 1.599 | 1.608 | 1.731 | Over-range | 60.01 | 51087 | 49061 | 47143 | 147291 | - - - | - - - | - - - | - - - | 51087 | 49061 | 47143 | 147291 | 24101 | 21812 | 23953 | 69866 | - - - | - - - | - - - | - - - | 24101 | 21812 | 23953 | 69866 | 57393 | 54570 | 53917 | 165881 | # # # | # # # | # # # | # # # | 0.89 | 0.899 | 0.874 | 0.888 | # # # | # # # | # # # | - - - | 0.904 | 0.913 | 0.891 | 0.903 | - - - | 0.474 | 1.61 | 1.58 | 1.56 | 1.55 | 1.52 | 1.57 | 19.48 | 19.55 | 21.29 | 0 | - - - | - - - | - - - | - - - | 57393 | 54570 | 53917 | 165881 | Over-range | 26154 | 23896 | 26165 | 76301 | 10158 | 9758 | 10529 | 30669 | 50901 | 48872 | 46957 | 146730 | 50901 | 48872 | 46957 | 146730 | - - - | - - - | - - - | - - -
5/11/2026 | 2:45:00 AM | 284.84 | 282.15 | 282.05 | 493.25 | 486.69 | 490.61 | 201.4102 | 192.7755 | 190.3366 | 5.325 | 1.438 | 1.433 | 1.43 | 1.597 | 1.603 | 1.734 | Over-range | 60.01 | 51054 | 48941 | 46896 | 146891 | - - - | - - - | - - - | - - - | 51054 | 48941 | 46896 | 146891 | 24149 | 21690 | 23950 | 69789 | - - - | - - - | - - - | - - - | 24149 | 21690 | 23950 | 69789 | 57369 | 54392 | 53683 | 165444 | # # # | # # # | # # # | # # # | 0.89 | 0.9 | 0.874 | 0.888 | # # # | # # # | # # # | - - - | 0.903 | 0.914 | 0.89 | 0.902 | - - - | 0.475 | 1.63 | 1.59 | 1.58 | 1.57 | 1.54 | 1.59 | 19.35 | 19.39 | 21.19 | 0 | - - - | - - - | - - - | - - - | 57369 | 54392 | 53683 | 165444 | Over-range | 26166 | 23734 | 26128 | 76125 | 10073 | 9636 | 10443 | 30404 | 50862 | 48759 | 46712 | 146332 | 50862 | 48759 | 46712 | 146332 | - - - | - - - | - - - | - - -
5/11/2026 | 3:00:00 AM | 284.75 | 282.11 | 282.05 | 493.09 | 486.7 | 490.54 | 200.8914 | 192.7301 | 190.1989 | 5.3348 | 1.438 | 1.433 | 1.43 | 1.598 | 1.605 | 1.728 | Over-range | 60.01 | 50906 | 48905 | 46907 | 146719 | - - - | - - - | - - - | - - - | 50906 | 48905 | 46907 | 146719 | 24101 | 21732 | 23883 | 69716 | - - - | - - - | - - - | - - - | 24101 | 21732 | 23883 | 69716 | 57203 | 54371 | 53645 | 165220 | # # # | # # # | # # # | # # # | 0.89 | 0.9 | 0.874 | 0.888 | # # # | # # # | # # # | - - - | 0.903 | 0.913 | 0.89 | 0.902 | - - - | 0.475 | 1.63 | 1.57 | 1.58 | 1.56 | 1.54 | 1.59 | 19.25 | 19.32 | 21.01 | 0 | - - - | - - - | - - - | - - - | 57203 | 54371 | 53645 | 165220 | Over-range | 26092 | 23759 | 26029 | 75969 | 9995 | 9601 | 10350 | 30180 | 50722 | 48725 | 46722 | 146168 | 50722 | 48725 | 46722 | 146168 | - - - | - - - | - - - | - - -
5/11/2026 | 3:15:00 AM | 284.88 | 282.3 | 282.14 | 493.4 | 486.95 | 490.69 | 200.5351 | 192.5548 | 189.4869 | 5.3185 | 1.438 | 1.433 | 1.43 | 1.601 | 1.601 | 1.728 | Over-range | 59.99 | 50792 | 48902 | 46743 | 146438 | - - - | - - - | - - - | - - - | 50792 | 48902 | 46743 | 146438 | 24181 | 21723 | 23821 | 69726 | - - - | - - - | - - - | - - - | 24181 | 21723 | 23821 | 69726 | 57128 | 54358 | 53462 | 164948 | # # # | # # # | # # # | # # # | 0.889 | 0.9 | 0.874 | 0.888 | # # # | # # # | # # # | - - - | 0.902 | 0.913 | 0.89 | 0.902 | - - - | 0.476 | 1.63 | 1.59 | 1.59 | 1.57 | 1.55 | 1.6 | 19.2 | 19.24 | 20.95 | 0 | - - - | - - - | - - - | - - - | 57128 | 54358 | 53462 | 164948 | Over-range | 26149 | 23735 | 25948 | 75920 | 9950 | 9563 | 10287 | 30035 | 50602 | 48731 | 46555 | 145889 | 50602 | 48731 | 46555 | 145889 | - - - | - - - | - - - | - - -
5/11/2026 | 3:30:00 AM | 284.76 | 282.15 | 282.05 | 493.15 | 486.74 | 490.53 | 200.1902 | 192.2734 | 189.1868 | 5.3153 | 1.438 | 1.433 | 1.43 | 1.601 | 1.601 | 1.726 | Over-range | 60 | 50687 | 48812 | 46672 | 146171 | - - - | - - - | - - - | - - - | 50687 | 48812 | 46672 | 146171 | 24131 | 21679 | 23769 | 69579 | - - - | - - - | - - - | - - - | 24131 | 21679 | 23769 | 69579 | 57007 | 54250 | 53361 | 164617 | # # # | # # # | # # # | # # # | 0.889 | 0.9 | 0.875 | 0.888 | # # # | # # # | # # # | - - - | 0.902 | 0.913 | 0.89 | 0.902 | - - - | 0.476 | 1.65 | 1.59 | 1.59 | 1.58 | 1.56 | 1.61 | 19.12 | 19.14 | 20.79 | 0 | - - - | - - - | - - - | - - - | 57007 | 54250 | 53361 | 164617 | Over-range | 26088 | 23673 | 25867 | 75716 | 9912 | 9510 | 10205 | 29859 | 50508 | 48635 | 46498 | 145640 | 50508 | 48635 | 46498 | 145640 | - - - | - - - | - - - | - - -
5/11/2026 | 3:45:00 AM | 284.69 | 282.2 | 282.03 | 493.14 | 486.82 | 490.4 | 199.8062 | 192.5551 | 188.7907 | 5.3607 | 1.438 | 1.433 | 1.43 | 1.605 | 1.599 | 1.721 | Over-range | 60.02 | 50542 | 48893 | 46618 | 146053 | - - - | - - - | - - - | - - - | 50542 | 48893 | 46618 | 146053 | 24161 | 21736 | 23651 | 69548 | - - - | - - - | - - - | - - - | 24161 | 21736 | 23651 | 69548 | 56883 | 54340 | 53245 | 164468 | # # # | # # # | # # # | # # # | 0.888 | 0.9 | 0.875 | 0.888 | # # # | # # # | # # # | - - - | 0.902 | 0.913 | 0.891 | 0.902 | - - - | 0.476 | 1.65 | 1.6 | 1.6 | 1.58 | 1.56 | 1.61 | 19.07 | 19.08 | 20.66 | 0 | - - - | - - - | - - - | - - - | 56883 | 54340 | 53245 | 164468 | Over-range | 26099 | 23713 | 25726 | 75620 | 9870 | 9478 | 10122 | 29689 | 50345 | 48726 | 46449 | 145519 | 50345 | 48726 | 46449 | 145519 | - - - | - - - | - - - | - - -
5/11/2026 | 4:00:00 AM | 284.68 | 282.13 | 282.03 | 493.05 | 486.74 | 490.43 | 199.3144 | 191.9608 | 188.5125 | 5.4947 | 1.438 | 1.433 | 1.43 | 1.602 | 1.602 | 1.72 | Over-range | 60.01 | 50447 | 48709 | 46530 | 145686 | - - - | - - - | - - - | - - - | 50447 | 48709 | 46530 | 145686 | 24062 | 21724 | 23674 | 69461 | - - - | - - - | - - - | - - - | 24062 | 21724 | 23674 | 69461 | 56741 | 54157 | 53166 | 164065 | # # # | # # # | # # # | # # # | 0.889 | 0.899 | 0.875 | 0.888 | # # # | # # # | # # # | - - - | 0.902 | 0.913 | 0.89 | 0.902 | - - - | 0.477 | 1.65 | 1.59 | 1.6 | 1.58 | 1.56 | 1.61 | 18.96 | 18.99 | 20.56 | 0 | - - - | - - - | - - - | - - - | 56741 | 54157 | 53166 | 164065 | Over-range | 25974 | 23674 | 25722 | 75451 | 9780 | 9407 | 10058 | 29463 | 50257 | 48548 | 46355 | 145160 | 50257 | 48548 | 46355 | 145160 | - - - | - - - | - - - | - - -
5/11/2026 | 4:15:00 AM | 284.51 | 282 | 281.89 | 492.79 | 486.52 | 490.13 | 199.2522 | 192.2789 | 188.2761 | 5.4806 | 1.438 | 1.434 | 1.431 | 1.603 | 1.597 | 1.715 | Over-range | 60.02 | 50386 | 48800 | 46501 | 145687 | - - - | - - - | - - - | - - - | 50386 | 48800 | 46501 | 145687 | 24088 | 21705 | 23563 | 69356 | - - - | - - - | - - - | - - - | 24088 | 21705 | 23563 | 69356 | 56690 | 54223 | 53072 | 163985 | # # # | # # # | # # # | # # # | 0.889 | 0.9 | 0.876 | 0.888 | # # # | # # # | # # # | - - - | 0.902 | 0.913 | 0.891 | 0.902 | - - - | 0.476 | 1.67 | 1.61 | 1.63 | 1.6 | 1.59 | 1.64 | 18.83 | 18.85 | 20.37 | 0 | - - - | - - - | - - - | - - - | 56690 | 54223 | 53072 | 163985 | Over-range | 25980 | 23637 | 25580 | 75276 | 9734 | 9361 | 9954 | 29261 | 50200 | 48633 | 46342 | 145174 | 50200 | 48633 | 46342 | 145174 | - - - | - - - | - - - | - - -
5/11/2026 | 4:30:00 AM | 284.2 | 281.77 | 281.71 | 492.27 | 486.24 | 489.71 | 198.7099 | 192.2713 | 188.3687 | 5.4816 | 1.438 | 1.434 | 1.431 | 1.604 | 1.601 | 1.71 | Over-range | 60.01 | 50214 | 48733 | 46552 | 145500 | - - - | - - - | - - - | - - - | 50214 | 48733 | 46552 | 145500 | 23965 | 21752 | 23476 | 69193 | - - - | - - - | - - - | - - - | 23965 | 21752 | 23476 | 69193 | 56474 | 54177 | 53066 | 163717 | # # # | # # # | # # # | # # # | 0.889 | 0.9 | 0.877 | 0.889 | # # # | # # # | # # # | - - - | 0.902 | 0.913 | 0.892 | 0.902 | - - - | 0.476 | 1.68 | 1.63 | 1.65 | 1.61 | 1.61 | 1.66 | 18.78 | 18.79 | 20.22 | 0 | - - - | - - - | - - - | - - - | 56474 | 54177 | 53066 | 163717 | Over-range | 25843 | 23669 | 25473 | 75054 | 9673 | 9329 | 9886 | 29075 | 50038 | 48564 | 46389 | 144991 | 50038 | 48564 | 46389 | 144991 | - - - | - - - | - - - | - - -
5/11/2026 | 4:45:00 AM | 284.31 | 281.81 | 281.68 | 492.45 | 486.19 | 489.78 | 136.8271 | 128.4217 | 128.4569 | 3.6035 | 1.438 | 1.433 | 1.431 | 1.847 | 1.851 | 1.92 | Over-range | 60.01 | 33125 | 30297 | 29747 | 93169 | - - - | - - - | - - - | - - - | 33125 | 30297 | 29747 | 93169 | 9403 | 8000 | 10757 | 28160 | - - - | - - - | - - - | - - - | 9403 | 8000 | 10757 | 28160 | 36833 | 33770 | 34089 | 104692 | # # # | # # # | # # # | # # # | 0.899 | 0.897 | 0.873 | 0.89 | # # # | # # # | # # # | - - - | 0.948 | 0.953 | 0.933 | 0.945 | - - - | 0.302 | 1.7 | 1.66 | 1.68 | 1.64 | 1.64 | 1.69 | 36.59 | 39.64 | 41.49 | 0 | - - - | - - - | - - - | - - - | 36833 | 33770 | 34089 | 104692 | Over-range | 16082 | 14914 | 16644 | 47744 | 10888 | 10426 | 11138 | 32725 | 33008 | 30204 | 29661 | 92873 | 33008 | 30204 | 29661 | 92873 | - - - | - - - | - - - | - - -
5/11/2026 | 5:00:00 AM | 284.12 | 281.6 | 281.4 | 492.15 | 485.73 | 489.35 | 99.5048 | 88.5028 | 91.9082 | 2.3359 | 1.437 | 1.433 | 1.431 | 1.954 | 1.96 | 2 | Over-range | 60.01 | 25711 | 22310 | 22531 | 70551 | - - - | - - - | - - - | - - - | 25711 | 22310 | 22531 | 70551 | 2726 | 1753 | 4911 | 9390 | - - - | - - - | - - - | - - - | 2726 | 1753 | 4911 | 9390 | 28242 | 24899 | 25841 | 78982 | # # # | # # # | # # # | # # # | 0.91 | 0.896 | 0.872 | 0.893 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.977 | 0.99 | - - - | 0.133 | 1.74 | 1.71 | 1.72 | 1.67 | 1.69 | 1.73 | 44.59 | 49.21 | 51.09 | 0 | - - - | - - - | - - - | - - - | 28242 | 24899 | 25841 | 78982 | Over-range | 11679 | 11053 | 12650 | 35493 | 11356 | 10913 | 11658 | 34229 | 25617 | 22255 | 22470 | 70341 | 25617 | 22255 | 22470 | 70341 | - - - | - - - | - - - | - - -
5/11/2026 | 5:15:00 AM | 283.45 | 280.87 | 280.72 | 490.92 | 484.49 | 488.21 | 104.1859 | 93.581 | 96.7774 | 2.5096 | 1.437 | 1.433 | 1.431 | 1.925 | 1.924 | 1.96 | Over-range | 60 | 26977 | 23689 | 23887 | 74553 | - - - | - - - | - - - | - - - | 26977 | 23689 | 23887 | 74553 | 2821 | 1932 | 4940 | 9693 | - - - | - - - | - - - | - - - | 2821 | 1932 | 4940 | 9693 | 29502 | 26259 | 27146 | 82908 | # # # | # # # | # # # | # # # | 0.914 | 0.902 | 0.88 | 0.899 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.979 | 0.99 | - - - | 0.13 | 1.79 | 1.76 | 1.79 | 1.71 | 1.75 | 1.79 | 43.33 | 47.31 | 49.28 | 0 | - - - | - - - | - - - | - - - | 29502 | 26259 | 27146 | 82908 | Over-range | 11934 | 11326 | 12890 | 36252 | 11595 | 11160 | 11906 | 34932 | 26895 | 23648 | 23820 | 74363 | 26895 | 23648 | 23820 | 74363 | - - - | - - - | - - - | - - -
5/11/2026 | 5:30:00 AM | 283.07 | 280.57 | 280.37 | 490.34 | 483.97 | 487.55 | 109.8955 | 99.4865 | 102.1321 | 2.6311 | 1.437 | 1.434 | 1.431 | 1.891 | 1.894 | 1.925 | Over-range | 60.01 | 28551 | 25327 | 25385 | 79263 | - - - | - - - | - - - | - - - | 28551 | 25327 | 25385 | 79263 | 3022 | 2054 | 5031 | 10107 | - - - | - - - | - - - | - - - | 3022 | 2054 | 5031 | 10107 | 31082 | 27893 | 28615 | 87591 | # # # | # # # | # # # | # # # | 0.919 | 0.908 | 0.887 | 0.905 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.981 | 0.991 | - - - | 0.128 | 1.84 | 1.8 | 1.85 | 1.76 | 1.8 | 1.85 | 41.97 | 45.54 | 47.53 | 0 | - - - | - - - | - - - | - - - | 31082 | 27893 | 28615 | 87591 | Over-range | 12280 | 11683 | 13202 | 37263 | 11902 | 11501 | 12206 | 35866 | 28469 | 25292 | 25325 | 79087 | 28469 | 25292 | 25325 | 79087 | - - - | - - - | - - - | - - -
5/11/2026 | 5:45:00 AM | 282.69 | 280.11 | 280.01 | 489.57 | 483.23 | 486.95 | 112.2323 | 101.6272 | 104.7119 | 2.7115 | 1.438 | 1.434 | 1.432 | 1.884 | 1.875 | 1.913 | Over-range | 60 | 29173 | 25878 | 26048 | 81099 | - - - | - - - | - - - | - - - | 29173 | 25878 | 26048 | 81099 | 3018 | 2137 | 5124 | 10279 | - - - | - - - | - - - | - - - | 3018 | 2137 | 5124 | 10279 | 31699 | 28446 | 29299 | 89444 | # # # | # # # | # # # | # # # | 0.92 | 0.91 | 0.889 | 0.907 | # # # | # # # | # # # | - - - | 0.995 | 0.997 | 0.981 | 0.991 | - - - | 0.127 | 1.96 | 1.9 | 1.97 | 1.86 | 1.92 | 1.97 | 41.42 | 44.93 | 46.94 | 0 | - - - | - - - | - - - | - - - | 31699 | 28446 | 29299 | 89444 | Over-range | 12394 | 11809 | 13410 | 37714 | 12021 | 11614 | 12392 | 36286 | 29106 | 25836 | 26003 | 80945 | 29106 | 25836 | 26003 | 80945 | - - - | - - - | - - - | - - -
5/11/2026 | 6:00:00 AM | 282.42 | 279.86 | 279.71 | 489.16 | 482.76 | 486.45 | 114.5785 | 103.5896 | 106.2898 | 2.729 | 1.438 | 1.435 | 1.432 | 1.872 | 1.874 | 1.912 | Over-range | 60.01 | 29805 | 26400 | 26425 | 82629 | - - - | - - - | - - - | - - - | 29805 | 26400 | 26425 | 82629 | 3149 | 2048 | 5228 | 10424 | - - - | - - - | - - - | - - - | 3149 | 2048 | 5228 | 10424 | 32334 | 28972 | 29713 | 91020 | # # # | # # # | # # # | # # # | 0.922 | 0.911 | 0.889 | 0.908 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.981 | 0.991 | - - - | 0.126 | 1.97 | 1.92 | 1.98 | 1.87 | 1.93 | 1.99 | 40.85 | 44.56 | 46.77 | 0 | - - - | - - - | - - - | - - - | 32334 | 28972 | 29713 | 91020 | Over-range | 12532 | 11933 | 13582 | 38159 | 12130 | 11755 | 12535 | 36708 | 29747 | 26363 | 26376 | 82486 | 29747 | 26363 | 26376 | 82486 | - - - | - - - | - - - | - - -
5/11/2026 | 6:15:00 AM | 281.96 | 279.54 | 279.4 | 488.43 | 482.29 | 485.75 | 117.3553 | 107.0543 | 109.0094 | 2.7798 | 1.439 | 1.435 | 1.433 | 1.848 | 1.853 | 1.885 | Over-range | 59.99 | 30551 | 27359 | 27216 | 85126 | - - - | - - - | - - - | - - - | 30551 | 27359 | 27216 | 85126 | 3280 | 2109 | 5155 | 10544 | - - - | - - - | - - - | - - - | 3280 | 2109 | 5155 | 10544 | 33062 | 29905 | 30436 | 93403 | # # # | # # # | # # # | # # # | 0.924 | 0.915 | 0.894 | 0.911 | # # # | # # # | # # # | - - - | 0.994 | 0.997 | 0.982 | 0.991 | - - - | 0.124 | 2 | 1.94 | 2.01 | 1.9 | 1.96 | 2.02 | 40.02 | 43.4 | 45.66 | 0 | - - - | - - - | - - - | - - - | 33062 | 29905 | 30436 | 93403 | Over-range | 12634 | 12071 | 13620 | 38429 | 12201 | 11885 | 12607 | 36955 | 30492 | 27331 | 27181 | 85004 | 30492 | 27331 | 27181 | 85004 | - - - | - - - | - - - | - - -

## Energy and Cost
Energy and Cost
Date | Time | Ep (15 min) | Ep+ (15 min) | Ep- (15 min) | Eq (15 min) | Eq/q1 (15 min) | Eq/q2 (15 min) | Eq/q3 (15 min) | Eq/q4 (15 min) | Es (15 min) | Es+ (15 min) | Es- (15 min)
|  | kWh | kWh | kWh | kvarh | kvarh | kvarh | kvarh | kvarh | kVAh | kVAh | kVAh
5/1/2026 | 12:45:00 PM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5/1/2026 | 1:00:00 PM | 13.798 | 13.798 | 0 | 1.96 | 1.96 | 0 | 0 | 0 | 15.855 | 15.855 | 0
5/1/2026 | 1:15:00 PM | 27.952 | 27.952 | 0 | 3.98 | 3.98 | 0 | 0 | 0 | 32.116 | 32.116 | 0
5/1/2026 | 1:30:00 PM | 42.208 | 42.208 | 0 | 6.015 | 6.015 | 0 | 0 | 0 | 48.497 | 48.497 | 0
5/1/2026 | 1:45:00 PM | 56.355 | 56.355 | 0 | 8.017 | 8.017 | 0 | 0 | 0 | 64.708 | 64.708 | 0
5/1/2026 | 2:00:00 PM | 70.801 | 70.801 | 0 | 10.088 | 10.088 | 0 | 0 | 0 | 81.32 | 81.32 | 0
5/1/2026 | 2:15:00 PM | 85.048 | 85.048 | 0 | 12.09 | 12.09 | 0 | 0 | 0 | 97.603 | 97.603 | 0
5/1/2026 | 2:30:00 PM | 99.73 | 99.73 | 0 | 14.181 | 14.181 | 0 | 0 | 0 | 114.451 | 114.451 | 0
5/1/2026 | 2:45:00 PM | 114.163 | 114.163 | 0 | 16.212 | 16.212 | 0 | 0 | 0 | 130.972 | 130.972 | 0
5/1/2026 | 3:00:00 PM | 128.848 | 128.848 | 0 | 18.282 | 18.282 | 0 | 0 | 0 | 147.794 | 147.794 | 0
5/1/2026 | 3:15:00 PM | 143.583 | 143.583 | 0 | 20.363 | 20.363 | 0 | 0 | 0 | 164.681 | 164.681 | 0
5/1/2026 | 3:30:00 PM | 158.071 | 158.071 | 0 | 22.384 | 22.384 | 0 | 0 | 0 | 181.241 | 181.241 | 0
5/1/2026 | 3:45:00 PM | 172.963 | 172.963 | 0 | 24.475 | 24.475 | 0 | 0 | 0 | 198.28 | 198.28 | 0
5/1/2026 | 4:00:00 PM | 187.774 | 187.774 | 0 | 26.55 | 26.55 | 0 | 0 | 0 | 215.214 | 215.214 | 0
5/1/2026 | 4:15:00 PM | 202.44 | 202.44 | 0 | 28.589 | 28.589 | 0 | 0 | 0 | 231.96 | 231.96 | 0
5/1/2026 | 4:30:00 PM | 217.321 | 217.321 | 0 | 30.669 | 30.669 | 0 | 0 | 0 | 248.967 | 248.967 | 0
5/1/2026 | 4:45:00 PM | 232.017 | 232.017 | 0 | 32.703 | 32.703 | 0 | 0 | 0 | 265.715 | 265.715 | 0
5/1/2026 | 5:00:00 PM | 247 | 247 | 0 | 34.799 | 34.799 | 0 | 0 | 0 | 282.85 | 282.85 | 0
5/1/2026 | 5:15:00 PM | 261.846 | 261.846 | 0 | 36.862 | 36.862 | 0 | 0 | 0 | 299.78 | 299.78 | 0
5/1/2026 | 5:30:00 PM | 276.596 | 276.596 | 0 | 38.898 | 38.898 | 0 | 0 | 0 | 316.571 | 316.571 | 0
5/1/2026 | 5:45:00 PM | 291.709 | 291.709 | 0 | 40.998 | 40.998 | 0 | 0 | 0 | 333.792 | 333.792 | 0
5/1/2026 | 6:00:00 PM | 306.41 | 306.41 | 0 | 43.005 | 43.005 | 0 | 0 | 0 | 350.484 | 350.484 | 0
5/1/2026 | 6:15:00 PM | 321.413 | 321.413 | 0 | 45.106 | 45.106 | 0 | 0 | 0 | 367.62 | 367.62 | 0
5/1/2026 | 6:30:00 PM | 336.138 | 336.138 | 0 | 47.148 | 47.148 | 0 | 0 | 0 | 384.411 | 384.411 | 0
5/1/2026 | 6:45:00 PM | 351.044 | 351.044 | 0 | 49.246 | 49.246 | 0 | 0 | 0 | 401.463 | 401.463 | 0
5/1/2026 | 7:00:00 PM | 366.099 | 366.099 | 0 | 51.378 | 51.378 | 0 | 0 | 0 | 418.706 | 418.706 | 0
5/1/2026 | 7:15:00 PM | 380.901 | 380.901 | 0 | 53.462 | 53.462 | 0 | 0 | 0 | 435.615 | 435.615 | 0
5/1/2026 | 7:30:00 PM | 396.033 | 396.033 | 0 | 55.621 | 55.621 | 0 | 0 | 0 | 452.961 | 452.961 | 0
5/1/2026 | 7:45:00 PM | 410.899 | 410.899 | 0 | 57.718 | 57.718 | 0 | 0 | 0 | 469.952 | 469.952 | 0
5/1/2026 | 8:00:00 PM | 426.094 | 426.094 | 0 | 59.895 | 59.895 | 0 | 0 | 0 | 487.385 | 487.385 | 0
5/1/2026 | 8:15:00 PM | 441.131 | 441.131 | 0 | 62.032 | 62.032 | 0 | 0 | 0 | 504.616 | 504.616 | 0
5/1/2026 | 8:30:00 PM | 456.125 | 456.125 | 0 | 64.15 | 64.15 | 0 | 0 | 0 | 521.762 | 521.762 | 0
5/1/2026 | 8:45:00 PM | 471.337 | 471.337 | 0 | 66.317 | 66.317 | 0 | 0 | 0 | 539.187 | 539.187 | 0
5/1/2026 | 9:00:00 PM | 486.27 | 486.27 | 0 | 68.409 | 68.409 | 0 | 0 | 0 | 556.235 | 556.235 | 0
5/1/2026 | 9:15:00 PM | 501.552 | 501.552 | 0 | 70.58 | 70.58 | 0 | 0 | 0 | 573.733 | 573.733 | 0
5/1/2026 | 9:30:00 PM | 516.775 | 516.775 | 0 | 72.724 | 72.724 | 0 | 0 | 0 | 591.113 | 591.113 | 0
5/1/2026 | 9:45:00 PM | 532.096 | 532.096 | 0 | 74.871 | 74.871 | 0 | 0 | 0 | 608.592 | 608.592 | 0
5/1/2026 | 10:00:00 PM | 547.567 | 547.567 | 0 | 77.053 | 77.053 | 0 | 0 | 0 | 626.269 | 626.269 | 0
5/1/2026 | 10:15:00 PM | 562.719 | 562.719 | 0 | 79.165 | 79.165 | 0 | 0 | 0 | 643.538 | 643.538 | 0
5/1/2026 | 10:30:00 PM | 578.216 | 578.216 | 0 | 81.349 | 81.349 | 0 | 0 | 0 | 661.248 | 661.248 | 0
5/1/2026 | 10:45:00 PM | 593.551 | 593.551 | 0 | 83.486 | 83.486 | 0 | 0 | 0 | 678.732 | 678.732 | 0
5/1/2026 | 11:00:00 PM | 609.111 | 609.111 | 0 | 85.644 | 85.644 | 0 | 0 | 0 | 696.462 | 696.462 | 0
5/1/2026 | 11:15:00 PM | 624.854 | 624.854 | 0 | 87.841 | 87.841 | 0 | 0 | 0 | 714.42 | 714.42 | 0
5/1/2026 | 11:30:00 PM | 640.323 | 640.323 | 0 | 89.961 | 89.961 | 0 | 0 | 0 | 731.996 | 731.996 | 0
5/1/2026 | 11:45:00 PM | 656.302 | 656.302 | 0 | 92.183 | 92.183 | 0 | 0 | 0 | 750.203 | 750.203 | 0
5/2/2026 | 12:00:00 AM | 672.16 | 672.16 | 0 | 94.341 | 94.341 | 0 | 0 | 0 | 768.168 | 768.168 | 0
5/2/2026 | 12:15:00 AM | 688.326 | 688.326 | 0 | 96.577 | 96.577 | 0 | 0 | 0 | 786.593 | 786.593 | 0
5/2/2026 | 12:30:00 AM | 703.861 | 703.861 | 0 | 98.745 | 98.745 | 0 | 0 | 0 | 804.362 | 804.362 | 0
5/2/2026 | 12:45:00 AM | 719.21 | 719.21 | 0 | 100.882 | 100.882 | 0 | 0 | 0 | 821.909 | 821.909 | 0
5/2/2026 | 1:00:00 AM | 734.826 | 734.826 | 0 | 103.082 | 103.082 | 0 | 0 | 0 | 839.795 | 839.795 | 0
5/2/2026 | 1:15:00 AM | 750.122 | 750.122 | 0 | 105.201 | 105.201 | 0 | 0 | 0 | 857.248 | 857.248 | 0
5/2/2026 | 1:30:00 AM | 765.826 | 765.826 | 0 | 107.41 | 107.41 | 0 | 0 | 0 | 875.238 | 875.238 | 0
5/2/2026 | 1:45:00 AM | 781.062 | 781.062 | 0 | 109.513 | 109.513 | 0 | 0 | 0 | 892.605 | 892.605 | 0
5/2/2026 | 2:00:00 AM | 796.577 | 796.577 | 0 | 111.679 | 111.679 | 0 | 0 | 0 | 910.341 | 910.341 | 0
5/2/2026 | 2:15:00 AM | 812 | 812 | 0 | 113.815 | 113.815 | 0 | 0 | 0 | 927.928 | 927.928 | 0
5/2/2026 | 2:30:00 AM | 827.519 | 827.519 | 0 | 115.967 | 115.967 | 0 | 0 | 0 | 945.628 | 945.628 | 0
5/2/2026 | 2:45:00 AM | 842.951 | 842.951 | 0 | 118.094 | 118.094 | 0 | 0 | 0 | 963.216 | 963.216 | 0
5/2/2026 | 3:00:00 AM | 857.928 | 857.928 | 0 | 120.112 | 120.112 | 0 | 0 | 0 | 980.212 | 980.212 | 0
5/2/2026 | 3:15:00 AM | 873.325 | 873.325 | 0 | 122.24 | 122.24 | 0 | 0 | 0 | 997.766 | 997.766 | 0
5/2/2026 | 3:30:00 AM | 888.255 | 888.255 | 0 | 124.254 | 124.254 | 0 | 0 | 0 | 1014.717 | 1014.717 | 0
5/2/2026 | 3:45:00 AM | 903.573 | 903.573 | 0 | 126.362 | 126.362 | 0 | 0 | 0 | 1032.189 | 1032.189 | 0
5/2/2026 | 4:00:00 AM | 918.567 | 918.567 | 0 | 128.405 | 128.405 | 0 | 0 | 0 | 1049.266 | 1049.266 | 0
5/2/2026 | 4:15:00 AM | 933.446 | 933.446 | 0 | 130.422 | 130.422 | 0 | 0 | 0 | 1066.191 | 1066.191 | 0
5/2/2026 | 4:30:00 AM | 948.661 | 948.661 | 0 | 132.521 | 132.521 | 0 | 0 | 0 | 1083.568 | 1083.568 | 0
5/2/2026 | 4:45:00 AM | 963.069 | 963.069 | 0 | 134.465 | 134.465 | 0 | 0 | 0 | 1099.939 | 1099.939 | 0
5/2/2026 | 5:00:00 AM | 977.671 | 977.671 | 0 | 136.472 | 136.472 | 0 | 0 | 0 | 1116.598 | 1116.598 | 0
5/2/2026 | 5:15:00 AM | 992.282 | 992.282 | 0 | 138.496 | 138.496 | 0 | 0 | 0 | 1133.309 | 1133.309 | 0
5/2/2026 | 5:30:00 AM | 1006.255 | 1006.255 | 0 | 140.388 | 140.388 | 0 | 0 | 0 | 1149.211 | 1149.211 | 0
5/2/2026 | 5:45:00 AM | 1019.99 | 1019.99 | 0 | 142.262 | 142.262 | 0 | 0 | 0 | 1164.88 | 1164.88 | 0
5/2/2026 | 6:00:00 AM | 1033.801 | 1033.801 | 0 | 144.169 | 144.169 | 0 | 0 | 0 | 1180.697 | 1180.697 | 0
5/2/2026 | 6:15:00 AM | 1047.049 | 1047.049 | 0 | 145.967 | 145.967 | 0 | 0 | 0 | 1195.792 | 1195.792 | 0
5/2/2026 | 6:30:00 AM | 1060.43 | 1060.43 | 0 | 147.798 | 147.798 | 0 | 0 | 0 | 1211.07 | 1211.07 | 0
5/2/2026 | 6:45:00 AM | 1073.841 | 1073.841 | 0 | 149.626 | 149.626 | 0 | 0 | 0 | 1226.367 | 1226.367 | 0
5/2/2026 | 7:00:00 AM | 1087.193 | 1087.193 | 0 | 151.437 | 151.437 | 0 | 0 | 0 | 1241.575 | 1241.575 | 0
5/2/2026 | 7:15:00 AM | 1100.506 | 1100.506 | 0 | 153.236 | 153.236 | 0 | 0 | 0 | 1256.737 | 1256.737 | 0
5/2/2026 | 7:30:00 AM | 1113.817 | 1113.817 | 0 | 155.033 | 155.033 | 0 | 0 | 0 | 1271.895 | 1271.895 | 0
5/2/2026 | 7:45:00 AM | 1126.866 | 1126.866 | 0 | 156.778 | 156.778 | 0 | 0 | 0 | 1286.715 | 1286.715 | 0
5/2/2026 | 8:00:00 AM | 1139.689 | 1139.689 | 0 | 158.492 | 158.492 | 0 | 0 | 0 | 1301.294 | 1301.294 | 0
5/2/2026 | 8:15:00 AM | 1152.413 | 1152.413 | 0 | 160.182 | 160.182 | 0 | 0 | 0 | 1315.738 | 1315.738 | 0
5/2/2026 | 8:30:00 AM | 1165.421 | 1165.421 | 0 | 161.939 | 161.939 | 0 | 0 | 0 | 1330.578 | 1330.578 | 0
5/2/2026 | 8:45:00 AM | 1178.402 | 1178.402 | 0 | 163.696 | 163.696 | 0 | 0 | 0 | 1345.385 | 1345.385 | 0
5/2/2026 | 9:00:00 AM | 1191.36 | 1191.36 | 0 | 165.455 | 165.455 | 0 | 0 | 0 | 1360.167 | 1360.167 | 0
5/2/2026 | 9:15:00 AM | 1203.853 | 1203.853 | 0 | 167.125 | 167.125 | 0 | 0 | 0 | 1374.391 | 1374.391 | 0
5/2/2026 | 9:30:00 AM | 1216.139 | 1216.139 | 0 | 168.752 | 168.752 | 0 | 0 | 0 | 1388.355 | 1388.355 | 0
5/2/2026 | 9:45:00 AM | 1228.79 | 1228.79 | 0 | 170.473 | 170.473 | 0 | 0 | 0 | 1402.839 | 1402.839 | 0
5/2/2026 | 10:00:00 AM | 1241.371 | 1241.371 | 0 | 172.198 | 172.198 | 0 | 0 | 0 | 1417.267 | 1417.267 | 0
5/2/2026 | 10:15:00 AM | 1253.905 | 1253.905 | 0 | 173.92 | 173.92 | 0 | 0 | 0 | 1431.645 | 1431.645 | 0
5/2/2026 | 10:30:00 AM | 1266.338 | 1266.338 | 0 | 175.631 | 175.631 | 0 | 0 | 0 | 1445.908 | 1445.908 | 0
5/2/2026 | 10:45:00 AM | 1278.681 | 1278.681 | 0 | 177.312 | 177.312 | 0 | 0 | 0 | 1460.035 | 1460.035 | 0
5/2/2026 | 11:00:00 AM | 1291.116 | 1291.116 | 0 | 179.018 | 179.018 | 0 | 0 | 0 | 1474.29 | 1474.29 | 0
5/2/2026 | 11:15:00 AM | 1303.679 | 1303.679 | 0 | 180.745 | 180.745 | 0 | 0 | 0 | 1488.7 | 1488.7 | 0
5/2/2026 | 11:30:00 AM | 1316.315 | 1316.315 | 0 | 182.487 | 182.487 | 0 | 0 | 0 | 1503.204 | 1503.204 | 0
5/2/2026 | 11:45:00 AM | 1329.468 | 1329.468 | 0 | 184.354 | 184.354 | 0 | 0 | 0 | 1518.382 | 1518.382 | 0
5/2/2026 | 12:00:00 PM | 1342.785 | 1342.785 | 0 | 186.253 | 186.253 | 0 | 0 | 0 | 1533.767 | 1533.767 | 0
5/2/2026 | 12:15:00 PM | 1356.553 | 1356.553 | 0 | 188.238 | 188.238 | 0 | 0 | 0 | 1549.711 | 1549.711 | 0
5/2/2026 | 12:30:00 PM | 1370.136 | 1370.136 | 0 | 190.175 | 190.175 | 0 | 0 | 0 | 1565.396 | 1565.396 | 0
5/2/2026 | 12:45:00 PM | 1384.199 | 1384.199 | 0 | 192.195 | 192.195 | 0 | 0 | 0 | 1581.673 | 1581.673 | 0
5/2/2026 | 1:00:00 PM | 1397.987 | 1397.987 | 0 | 194.166 | 194.166 | 0 | 0 | 0 | 1597.594 | 1597.594 | 0
5/2/2026 | 1:15:00 PM | 1412.299 | 1412.299 | 0 | 196.224 | 196.224 | 0 | 0 | 0 | 1614.114 | 1614.114 | 0
5/2/2026 | 1:30:00 PM | 1426.713 | 1426.713 | 0 | 198.301 | 198.301 | 0 | 0 | 0 | 1630.759 | 1630.759 | 0
5/2/2026 | 1:45:00 PM | 1440.896 | 1440.896 | 0 | 200.322 | 200.322 | 0 | 0 | 0 | 1647.094 | 1647.094 | 0
5/2/2026 | 2:00:00 PM | 1455.549 | 1455.549 | 0 | 202.434 | 202.434 | 0 | 0 | 0 | 1664.017 | 1664.017 | 0
5/2/2026 | 2:15:00 PM | 1470.094 | 1470.094 | 0 | 204.504 | 204.504 | 0 | 0 | 0 | 1680.755 | 1680.755 | 0
5/2/2026 | 2:30:00 PM | 1484.83 | 1484.83 | 0 | 206.621 | 206.621 | 0 | 0 | 0 | 1697.749 | 1697.749 | 0
5/2/2026 | 2:45:00 PM | 1499.67 | 1499.67 | 0 | 208.747 | 208.747 | 0 | 0 | 0 | 1714.855 | 1714.855 | 0
5/2/2026 | 3:00:00 PM | 1514.379 | 1514.379 | 0 | 210.821 | 210.821 | 0 | 0 | 0 | 1731.732 | 1731.732 | 0
5/2/2026 | 3:15:00 PM | 1529.468 | 1529.468 | 0 | 212.969 | 212.969 | 0 | 0 | 0 | 1749.096 | 1749.096 | 0
5/2/2026 | 3:30:00 PM | 1544.61 | 1544.61 | 0 | 215.11 | 215.11 | 0 | 0 | 0 | 1766.503 | 1766.503 | 0
5/2/2026 | 3:45:00 PM | 1559.618 | 1559.618 | 0 | 217.203 | 217.203 | 0 | 0 | 0 | 1783.678 | 1783.678 | 0
5/2/2026 | 4:00:00 PM | 1574.982 | 1574.982 | 0 | 219.368 | 219.368 | 0 | 0 | 0 | 1801.329 | 1801.329 | 0
5/2/2026 | 4:15:00 PM | 1590.113 | 1590.113 | 0 | 221.478 | 221.478 | 0 | 0 | 0 | 1818.665 | 1818.665 | 0
5/2/2026 | 4:30:00 PM | 1605.45 | 1605.45 | 0 | 223.644 | 223.644 | 0 | 0 | 0 | 1836.284 | 1836.284 | 0
5/2/2026 | 4:45:00 PM | 1620.798 | 1620.798 | 0 | 225.808 | 225.808 | 0 | 0 | 0 | 1853.917 | 1853.917 | 0
5/2/2026 | 5:00:00 PM | 1635.739 | 1635.739 | 0 | 227.872 | 227.872 | 0 | 0 | 0 | 1871.012 | 1871.012 | 0
5/2/2026 | 5:15:00 PM | 1651 | 1651 | 0 | 230.006 | 230.006 | 0 | 0 | 0 | 1888.511 | 1888.511 | 0
5/2/2026 | 5:30:00 PM | 1666.203 | 1666.203 | 0 | 232.134 | 232.134 | 0 | 0 | 0 | 1905.94 | 1905.94 | 0
5/2/2026 | 5:45:00 PM | 1681.084 | 1681.084 | 0 | 234.197 | 234.197 | 0 | 0 | 0 | 1922.969 | 1922.969 | 0
5/2/2026 | 6:00:00 PM | 1696.235 | 1696.235 | 0 | 236.315 | 236.315 | 0 | 0 | 0 | 1940.356 | 1940.356 | 0
5/2/2026 | 6:15:00 PM | 1710.985 | 1710.985 | 0 | 238.356 | 238.356 | 0 | 0 | 0 | 1957.23 | 1957.23 | 0
5/2/2026 | 6:30:00 PM | 1725.969 | 1725.969 | 0 | 240.452 | 240.452 | 0 | 0 | 0 | 1974.444 | 1974.444 | 0
5/2/2026 | 6:45:00 PM | 1740.544 | 1740.544 | 0 | 242.466 | 242.466 | 0 | 0 | 0 | 1991.132 | 1991.132 | 0
5/2/2026 | 7:00:00 PM | 1755.443 | 1755.443 | 0 | 244.554 | 244.554 | 0 | 0 | 0 | 2008.25 | 2008.25 | 0
5/2/2026 | 7:15:00 PM | 1770.127 | 1770.127 | 0 | 246.604 | 246.604 | 0 | 0 | 0 | 2025.072 | 2025.072 | 0
5/2/2026 | 7:30:00 PM | 1784.839 | 1784.839 | 0 | 248.661 | 248.661 | 0 | 0 | 0 | 2041.945 | 2041.945 | 0
5/2/2026 | 7:45:00 PM | 1799.598 | 1799.598 | 0 | 250.735 | 250.735 | 0 | 0 | 0 | 2058.886 | 2058.886 | 0
5/2/2026 | 8:00:00 PM | 1814.075 | 1814.075 | 0 | 252.763 | 252.763 | 0 | 0 | 0 | 2075.489 | 2075.489 | 0
5/2/2026 | 8:15:00 PM | 1828.748 | 1828.748 | 0 | 254.849 | 254.849 | 0 | 0 | 0 | 2092.37 | 2092.37 | 0
5/2/2026 | 8:30:00 PM | 1842.956 | 1842.956 | 0 | 256.828 | 256.828 | 0 | 0 | 0 | 2108.628 | 2108.628 | 0
5/2/2026 | 8:45:00 PM | 1857.632 | 1857.632 | 0 | 258.906 | 258.906 | 0 | 0 | 0 | 2125.515 | 2125.515 | 0
5/2/2026 | 9:00:00 PM | 1871.835 | 1871.835 | 0 | 260.899 | 260.899 | 0 | 0 | 0 | 2141.83 | 2141.83 | 0
5/2/2026 | 9:15:00 PM | 1885.835 | 1885.835 | 0 | 262.866 | 262.866 | 0 | 0 | 0 | 2157.913 | 2157.913 | 0
5/2/2026 | 9:30:00 PM | 1900.171 | 1900.171 | 0 | 264.917 | 264.917 | 0 | 0 | 0 | 2174.457 | 2174.457 | 0
5/2/2026 | 9:45:00 PM | 1913.875 | 1913.875 | 0 | 266.837 | 266.837 | 0 | 0 | 0 | 2190.204 | 2190.204 | 0
5/2/2026 | 10:00:00 PM | 1927.392 | 1927.392 | 0 | 268.732 | 268.732 | 0 | 0 | 0 | 2205.734 | 2205.734 | 0
5/2/2026 | 10:15:00 PM | 1940.887 | 1940.887 | 0 | 270.638 | 270.638 | 0 | 0 | 0 | 2221.265 | 2221.265 | 0
5/2/2026 | 10:30:00 PM | 1954.651 | 1954.651 | 0 | 272.609 | 272.609 | 0 | 0 | 0 | 2237.18 | 2237.18 | 0
5/2/2026 | 10:45:00 PM | 1967.608 | 1967.608 | 0 | 274.413 | 274.413 | 0 | 0 | 0 | 2252.074 | 2252.074 | 0
5/2/2026 | 11:00:00 PM | 1980.405 | 1980.405 | 0 | 276.189 | 276.189 | 0 | 0 | 0 | 2266.763 | 2266.763 | 0
5/2/2026 | 11:15:00 PM | 1992.98 | 1992.98 | 0 | 277.93 | 277.93 | 0 | 0 | 0 | 2281.206 | 2281.206 | 0
5/2/2026 | 11:30:00 PM | 2005.443 | 2005.443 | 0 | 279.661 | 279.661 | 0 | 0 | 0 | 2295.522 | 2295.522 | 0
5/2/2026 | 11:45:00 PM | 2018.062 | 2018.062 | 0 | 281.426 | 281.426 | 0 | 0 | 0 | 2310.041 | 2310.041 | 0
5/3/2026 | 12:00:00 AM | 2030.643 | 2030.643 | 0 | 283.194 | 283.194 | 0 | 0 | 0 | 2324.558 | 2324.558 | 0
5/3/2026 | 12:15:00 AM | 2043.147 | 2043.147 | 0 | 284.962 | 284.962 | 0 | 0 | 0 | 2339.005 | 2339.005 | 0
5/3/2026 | 12:30:00 AM | 2055.551 | 2055.551 | 0 | 286.713 | 286.713 | 0 | 0 | 0 | 2353.348 | 2353.348 | 0
5/3/2026 | 12:45:00 AM | 2067.42 | 2067.42 | 0 | 288.344 | 288.344 | 0 | 0 | 0 | 2366.974 | 2366.974 | 0
5/3/2026 | 1:00:00 AM | 2079.256 | 2079.256 | 0 | 289.991 | 289.991 | 0 | 0 | 0 | 2380.599 | 2380.599 | 0
5/3/2026 | 1:15:00 AM | 2091.417 | 2091.417 | 0 | 291.711 | 291.711 | 0 | 0 | 0 | 2394.657 | 2394.657 | 0
5/3/2026 | 1:30:00 AM | 2103.564 | 2103.564 | 0 | 293.426 | 293.426 | 0 | 0 | 0 | 2408.708 | 2408.708 | 0
5/3/2026 | 1:45:00 AM | 2115.262 | 2115.262 | 0 | 295.05 | 295.05 | 0 | 0 | 0 | 2422.193 | 2422.193 | 0
5/3/2026 | 2:00:00 AM | 2126.928 | 2126.928 | 0 | 296.668 | 296.668 | 0 | 0 | 0 | 2435.626 | 2435.626 | 0
5/3/2026 | 2:15:00 AM | 2138.873 | 2138.873 | 0 | 298.369 | 298.369 | 0 | 0 | 0 | 2449.49 | 2449.49 | 0
5/3/2026 | 2:30:00 AM | 2150.747 | 2150.747 | 0 | 300.056 | 300.056 | 0 | 0 | 0 | 2463.27 | 2463.27 | 0
5/3/2026 | 2:45:00 AM | 2162.118 | 2162.118 | 0 | 301.652 | 301.652 | 0 | 0 | 0 | 2476.414 | 2476.414 | 0
5/3/2026 | 3:00:00 AM | 2173.856 | 2173.856 | 0 | 303.336 | 303.336 | 0 | 0 | 0 | 2490.069 | 2490.069 | 0
5/3/2026 | 3:15:00 AM | 2184.905 | 2184.905 | 0 | 304.862 | 304.862 | 0 | 0 | 0 | 2502.788 | 2502.788 | 0
5/3/2026 | 3:30:00 AM | 2196.415 | 2196.415 | 0 | 306.499 | 306.499 | 0 | 0 | 0 | 2516.137 | 2516.137 | 0
5/3/2026 | 3:45:00 AM | 2207.825 | 2207.825 | 0 | 308.128 | 308.128 | 0 | 0 | 0 | 2529.381 | 2529.381 | 0
5/3/2026 | 4:00:00 AM | 2218.707 | 2218.707 | 0 | 309.642 | 309.642 | 0 | 0 | 0 | 2541.928 | 2541.928 | 0
5/3/2026 | 4:15:00 AM | 2229.832 | 2229.832 | 0 | 311.212 | 311.212 | 0 | 0 | 0 | 2554.8 | 2554.8 | 0
5/3/2026 | 4:30:00 AM | 2241.044 | 2241.044 | 0 | 312.804 | 312.804 | 0 | 0 | 0 | 2567.807 | 2567.807 | 0
5/3/2026 | 4:45:00 AM | 2252.335 | 2252.335 | 0 | 314.414 | 314.414 | 0 | 0 | 0 | 2580.931 | 2580.931 | 0
5/3/2026 | 5:00:00 AM | 2263.506 | 2263.506 | 0 | 316.017 | 316.017 | 0 | 0 | 0 | 2593.923 | 2593.923 | 0
5/3/2026 | 5:15:00 AM | 2274.272 | 2274.272 | 0 | 317.533 | 317.533 | 0 | 0 | 0 | 2606.389 | 2606.389 | 0
5/3/2026 | 5:30:00 AM | 2284.872 | 2284.872 | 0 | 319.014 | 319.014 | 0 | 0 | 0 | 2618.636 | 2618.636 | 0
5/3/2026 | 5:45:00 AM | 2295.9 | 2295.9 | 0 | 320.597 | 320.597 | 0 | 0 | 0 | 2631.469 | 2631.469 | 0
5/3/2026 | 6:00:00 AM | 2306.809 | 2306.809 | 0 | 322.149 | 322.149 | 0 | 0 | 0 | 2644.139 | 2644.139 | 0
5/3/2026 | 6:15:00 AM | 2316.994 | 2316.994 | 0 | 323.553 | 323.553 | 0 | 0 | 0 | 2655.865 | 2655.865 | 0
5/3/2026 | 6:30:00 AM | 2327.861 | 2327.861 | 0 | 325.112 | 325.112 | 0 | 0 | 0 | 2668.518 | 2668.518 | 0
5/3/2026 | 6:45:00 AM | 2333.221 | 2333.221 | 0 | 325.582 | 325.582 | 0 | 0 | 0 | 2674.347 | 2674.347 | 0
5/3/2026 | 7:00:00 AM | 2337.485 | 2337.485 | 0 | 325.845 | 325.845 | 0 | 0 | 0 | 2678.844 | 2678.844 | 0
5/3/2026 | 7:15:00 AM | 2341.955 | 2341.955 | 0 | 326.16 | 326.16 | 0 | 0 | 0 | 2683.589 | 2683.589 | 0
5/3/2026 | 7:30:00 AM | 2346.768 | 2346.768 | 0 | 326.554 | 326.554 | 0 | 0 | 0 | 2688.74 | 2688.74 | 0
5/3/2026 | 7:45:00 AM | 2351.656 | 2351.656 | 0 | 326.964 | 326.964 | 0 | 0 | 0 | 2693.977 | 2693.977 | 0
5/3/2026 | 8:00:00 AM | 2356.599 | 2356.599 | 0 | 327.383 | 327.383 | 0 | 0 | 0 | 2699.28 | 2699.28 | 0
5/3/2026 | 8:15:00 AM | 2361.648 | 2361.648 | 0 | 327.825 | 327.825 | 0 | 0 | 0 | 2704.708 | 2704.708 | 0
5/3/2026 | 8:30:00 AM | 2366.795 | 2366.795 | 0 | 328.292 | 328.292 | 0 | 0 | 0 | 2710.26 | 2710.26 | 0
5/3/2026 | 8:45:00 AM | 2372.113 | 2372.113 | 0 | 328.798 | 328.798 | 0 | 0 | 0 | 2716.025 | 2716.025 | 0
5/3/2026 | 9:00:00 AM | 2381.216 | 2381.216 | 0 | 329.8 | 329.8 | 0 | 0 | 0 | 2725.982 | 2725.982 | 0
5/3/2026 | 9:15:00 AM | 2407.661 | 2407.661 | 0 | 332.926 | 332.926 | 0 | 0 | 0 | 2754.689 | 2754.689 | 0
5/3/2026 | 9:30:00 AM | 2432.548 | 2432.548 | 0 | 335.83 | 335.83 | 0 | 0 | 0 | 2781.767 | 2781.767 | 0
5/3/2026 | 9:45:00 AM | 2451.284 | 2451.284 | 0 | 338.133 | 338.133 | 0 | 0 | 0 | 2802.451 | 2802.451 | 0
5/3/2026 | 10:00:00 AM | 2467.145 | 2467.145 | 0 | 340.099 | 340.099 | 0 | 0 | 0 | 2820.101 | 2820.101 | 0
5/3/2026 | 10:15:00 AM | 2481.963 | 2481.963 | 0 | 341.999 | 341.999 | 0 | 0 | 0 | 2836.741 | 2836.741 | 0
5/3/2026 | 10:30:00 AM | 2495.859 | 2495.859 | 0 | 343.807 | 343.807 | 0 | 0 | 0 | 2852.41 | 2852.41 | 0
5/3/2026 | 10:45:00 AM | 2509.509 | 2509.509 | 0 | 345.622 | 345.622 | 0 | 0 | 0 | 2867.868 | 2867.868 | 0
5/3/2026 | 11:00:00 AM | 2523.147 | 2523.147 | 0 | 347.459 | 347.459 | 0 | 0 | 0 | 2883.358 | 2883.358 | 0
5/3/2026 | 11:15:00 AM | 2536.905 | 2536.905 | 0 | 349.328 | 349.328 | 0 | 0 | 0 | 2899.017 | 2899.017 | 0
5/3/2026 | 11:30:00 AM | 2551.017 | 2551.017 | 0 | 351.283 | 351.283 | 0 | 0 | 0 | 2915.122 | 2915.122 | 0
5/3/2026 | 11:45:00 AM | 2565.131 | 2565.131 | 0 | 353.233 | 353.233 | 0 | 0 | 0 | 2931.233 | 2931.233 | 0
5/3/2026 | 12:00:00 PM | 2579.471 | 2579.471 | 0 | 355.241 | 355.241 | 0 | 0 | 0 | 2947.639 | 2947.639 | 0
5/3/2026 | 12:15:00 PM | 2593.898 | 2593.898 | 0 | 357.271 | 357.271 | 0 | 0 | 0 | 2964.153 | 2964.153 | 0
5/3/2026 | 12:30:00 PM | 2608.062 | 2608.062 | 0 | 359.237 | 359.237 | 0 | 0 | 0 | 2980.32 | 2980.32 | 0
5/3/2026 | 12:45:00 PM | 2622.576 | 2622.576 | 0 | 361.28 | 361.28 | 0 | 0 | 0 | 2996.938 | 2996.938 | 0
5/3/2026 | 1:00:00 PM | 2636.788 | 2636.788 | 0 | 363.248 | 363.248 | 0 | 0 | 0 | 3013.149 | 3013.149 | 0
5/3/2026 | 1:15:00 PM | 2651.457 | 2651.457 | 0 | 365.321 | 365.321 | 0 | 0 | 0 | 3029.945 | 3029.945 | 0
5/3/2026 | 1:30:00 PM | 2666.006 | 2666.006 | 0 | 367.363 | 367.363 | 0 | 0 | 0 | 3046.578 | 3046.578 | 0
5/3/2026 | 1:45:00 PM | 2680.581 | 2680.581 | 0 | 369.404 | 369.404 | 0 | 0 | 0 | 3063.224 | 3063.224 | 0
5/3/2026 | 2:00:00 PM | 2695.447 | 2695.447 | 0 | 371.503 | 371.503 | 0 | 0 | 0 | 3080.218 | 3080.218 | 0
5/3/2026 | 2:15:00 PM | 2710.104 | 2710.104 | 0 | 373.55 | 373.55 | 0 | 0 | 0 | 3096.938 | 3096.938 | 0
5/3/2026 | 2:30:00 PM | 2725.225 | 2725.225 | 0 | 375.692 | 375.692 | 0 | 0 | 0 | 3114.243 | 3114.243 | 0
5/3/2026 | 2:45:00 PM | 2740.006 | 2740.006 | 0 | 377.754 | 377.754 | 0 | 0 | 0 | 3131.087 | 3131.087 | 0
5/3/2026 | 3:00:00 PM | 2755.196 | 2755.196 | 0 | 379.903 | 379.903 | 0 | 0 | 0 | 3148.442 | 3148.442 | 0
5/3/2026 | 3:15:00 PM | 2770.164 | 2770.164 | 0 | 381.983 | 381.983 | 0 | 0 | 0 | 3165.48 | 3165.48 | 0
5/3/2026 | 3:30:00 PM | 2785.645 | 2785.645 | 0 | 384.143 | 384.143 | 0 | 0 | 0 | 3183.088 | 3183.088 | 0
5/3/2026 | 3:45:00 PM | 2801.259 | 2801.259 | 0 | 386.319 | 386.319 | 0 | 0 | 0 | 3200.835 | 3200.835 | 0
5/3/2026 | 4:00:00 PM | 2816.734 | 2816.734 | 0 | 388.438 | 388.438 | 0 | 0 | 0 | 3218.354 | 3218.354 | 0
5/3/2026 | 4:15:00 PM | 2832.635 | 2832.635 | 0 | 390.637 | 390.637 | 0 | 0 | 0 | 3236.39 | 3236.39 | 0
5/3/2026 | 4:30:00 PM | 2848.294 | 2848.294 | 0 | 392.776 | 392.776 | 0 | 0 | 0 | 3254.112 | 3254.112 | 0
5/3/2026 | 4:45:00 PM | 2864.195 | 2864.195 | 0 | 394.948 | 394.948 | 0 | 0 | 0 | 3272.108 | 3272.108 | 0
5/3/2026 | 5:00:00 PM | 2880.333 | 2880.333 | 0 | 397.155 | 397.155 | 0 | 0 | 0 | 3290.38 | 3290.38 | 0
5/3/2026 | 5:15:00 PM | 2896.185 | 2896.185 | 0 | 399.294 | 399.294 | 0 | 0 | 0 | 3308.261 | 3308.261 | 0
5/3/2026 | 5:30:00 PM | 2912.402 | 2912.402 | 0 | 401.502 | 401.502 | 0 | 0 | 0 | 3326.598 | 3326.598 | 0
5/3/2026 | 5:45:00 PM | 2928.423 | 2928.423 | 0 | 403.652 | 403.652 | 0 | 0 | 0 | 3344.637 | 3344.637 | 0
5/3/2026 | 6:00:00 PM | 2944.782 | 2944.782 | 0 | 405.879 | 405.879 | 0 | 0 | 0 | 3363.113 | 3363.113 | 0
5/3/2026 | 6:15:00 PM | 2961.071 | 2961.071 | 0 | 408.086 | 408.086 | 0 | 0 | 0 | 3381.546 | 3381.546 | 0
5/3/2026 | 6:30:00 PM | 2977.076 | 2977.076 | 0 | 410.23 | 410.23 | 0 | 0 | 0 | 3399.61 | 3399.61 | 0
5/3/2026 | 6:45:00 PM | 2993.389 | 2993.389 | 0 | 412.445 | 412.445 | 0 | 0 | 0 | 3418.072 | 3418.072 | 0
5/3/2026 | 7:00:00 PM | 3009.631 | 3009.631 | 0 | 414.651 | 414.651 | 0 | 0 | 0 | 3436.464 | 3436.464 | 0
5/3/2026 | 7:15:00 PM | 3025.564 | 3025.564 | 0 | 416.789 | 416.789 | 0 | 0 | 0 | 3454.45 | 3454.45 | 0
5/3/2026 | 7:30:00 PM | 3041.72 | 3041.72 | 0 | 418.981 | 418.981 | 0 | 0 | 0 | 3472.739 | 3472.739 | 0
5/3/2026 | 7:45:00 PM | 3057.723 | 3057.723 | 0 | 421.159 | 421.159 | 0 | 0 | 0 | 3490.844 | 3490.844 | 0
5/3/2026 | 8:00:00 PM | 3073.664 | 3073.664 | 0 | 423.324 | 423.324 | 0 | 0 | 0 | 3508.879 | 3508.879 | 0
5/3/2026 | 8:15:00 PM | 3089.691 | 3089.691 | 0 | 425.513 | 425.513 | 0 | 0 | 0 | 3527.053 | 3527.053 | 0
5/3/2026 | 8:30:00 PM | 3105.455 | 3105.455 | 0 | 427.653 | 427.653 | 0 | 0 | 0 | 3544.913 | 3544.913 | 0
5/3/2026 | 8:45:00 PM | 3121.383 | 3121.383 | 0 | 429.827 | 429.827 | 0 | 0 | 0 | 3563.012 | 3563.012 | 0
5/3/2026 | 9:00:00 PM | 3136.789 | 3136.789 | 0 | 431.891 | 431.891 | 0 | 0 | 0 | 3580.451 | 3580.451 | 0
5/3/2026 | 9:15:00 PM | 3152.512 | 3152.512 | 0 | 434.034 | 434.034 | 0 | 0 | 0 | 3598.308 | 3598.308 | 0
5/3/2026 | 9:30:00 PM | 3167.946 | 3167.946 | 0 | 436.118 | 436.118 | 0 | 0 | 0 | 3615.801 | 3615.801 | 0
5/3/2026 | 9:45:00 PM | 3183.537 | 3183.537 | 0 | 438.255 | 438.255 | 0 | 0 | 0 | 3633.556 | 3633.556 | 0
5/3/2026 | 10:00:00 PM | 3198.827 | 3198.827 | 0 | 440.354 | 440.354 | 0 | 0 | 0 | 3650.983 | 3650.983 | 0
5/3/2026 | 10:15:00 PM | 3213.787 | 3213.787 | 0 | 442.382 | 442.382 | 0 | 0 | 0 | 3667.999 | 3667.999 | 0
5/3/2026 | 10:30:00 PM | 3229.081 | 3229.081 | 0 | 444.506 | 444.506 | 0 | 0 | 0 | 3685.488 | 3685.488 | 0
5/3/2026 | 10:45:00 PM | 3243.8 | 3243.8 | 0 | 446.519 | 446.519 | 0 | 0 | 0 | 3702.261 | 3702.261 | 0
5/3/2026 | 11:00:00 PM | 3258.846 | 3258.846 | 0 | 448.609 | 448.609 | 0 | 0 | 0 | 3719.484 | 3719.484 | 0
5/3/2026 | 11:15:00 PM | 3273.583 | 3273.583 | 0 | 450.632 | 450.632 | 0 | 0 | 0 | 3736.309 | 3736.309 | 0
5/3/2026 | 11:30:00 PM | 3288.397 | 3288.397 | 0 | 452.681 | 452.681 | 0 | 0 | 0 | 3753.245 | 3753.245 | 0
5/3/2026 | 11:45:00 PM | 3303.176 | 3303.176 | 0 | 454.744 | 454.744 | 0 | 0 | 0 | 3770.173 | 3770.173 | 0
5/4/2026 | 12:00:00 AM | 3317.516 | 3317.516 | 0 | 456.73 | 456.73 | 0 | 0 | 0 | 3786.578 | 3786.578 | 0
5/4/2026 | 12:15:00 AM | 3331.785 | 3331.785 | 0 | 458.709 | 458.709 | 0 | 0 | 0 | 3802.916 | 3802.916 | 0
5/4/2026 | 12:30:00 AM | 3345.512 | 3345.512 | 0 | 460.59 | 460.59 | 0 | 0 | 0 | 3818.615 | 3818.615 | 0
5/4/2026 | 12:45:00 AM | 3358.978 | 3358.978 | 0 | 462.419 | 462.419 | 0 | 0 | 0 | 3833.99 | 3833.99 | 0
5/4/2026 | 1:00:00 AM | 3372.349 | 3372.349 | 0 | 464.254 | 464.254 | 0 | 0 | 0 | 3849.299 | 3849.299 | 0
5/4/2026 | 1:15:00 AM | 3385.8 | 3385.8 | 0 | 466.107 | 466.107 | 0 | 0 | 0 | 3864.711 | 3864.711 | 0
5/4/2026 | 1:30:00 AM | 3399.193 | 3399.193 | 0 | 467.951 | 467.951 | 0 | 0 | 0 | 3880.057 | 3880.057 | 0
5/4/2026 | 1:45:00 AM | 3412.357 | 3412.357 | 0 | 469.766 | 469.766 | 0 | 0 | 0 | 3895.142 | 3895.142 | 0
5/4/2026 | 2:00:00 AM | 3425.407 | 3425.407 | 0 | 471.574 | 471.574 | 0 | 0 | 0 | 3910.125 | 3910.125 | 0
5/4/2026 | 2:15:00 AM | 3438.148 | 3438.148 | 0 | 473.312 | 473.312 | 0 | 0 | 0 | 3924.689 | 3924.689 | 0
5/4/2026 | 2:30:00 AM | 3450.444 | 3450.444 | 0 | 474.976 | 474.976 | 0 | 0 | 0 | 3938.714 | 3938.714 | 0
5/4/2026 | 2:45:00 AM | 3463.167 | 3463.167 | 0 | 476.748 | 476.748 | 0 | 0 | 0 | 3953.345 | 3953.345 | 0
5/4/2026 | 3:00:00 AM | 3475.701 | 3475.701 | 0 | 478.499 | 478.499 | 0 | 0 | 0 | 3967.779 | 3967.779 | 0
5/4/2026 | 3:15:00 AM | 3487.535 | 3487.535 | 0 | 480.113 | 480.113 | 0 | 0 | 0 | 3981.32 | 3981.32 | 0
5/4/2026 | 3:30:00 AM | 3499.384 | 3499.384 | 0 | 481.741 | 481.741 | 0 | 0 | 0 | 3994.916 | 3994.916 | 0
5/4/2026 | 3:45:00 AM | 3511.246 | 3511.246 | 0 | 483.398 | 483.398 | 0 | 0 | 0 | 4008.614 | 4008.614 | 0
5/4/2026 | 4:00:00 AM | 3523.025 | 3523.025 | 0 | 485.054 | 485.054 | 0 | 0 | 0 | 4022.227 | 4022.227 | 0
5/4/2026 | 4:15:00 AM | 3534.718 | 3534.718 | 0 | 486.698 | 486.698 | 0 | 0 | 0 | 4035.764 | 4035.764 | 0
5/4/2026 | 4:30:00 AM | 3546.361 | 3546.361 | 0 | 488.336 | 488.336 | 0 | 0 | 0 | 4049.241 | 4049.241 | 0
5/4/2026 | 4:45:00 AM | 3557.804 | 3557.804 | 0 | 489.928 | 489.928 | 0 | 0 | 0 | 4062.436 | 4062.436 | 0
5/4/2026 | 5:00:00 AM | 3569.084 | 3569.084 | 0 | 491.494 | 491.494 | 0 | 0 | 0 | 4075.453 | 4075.453 | 0
5/4/2026 | 5:15:00 AM | 3580.36 | 3580.36 | 0 | 493.035 | 493.035 | 0 | 0 | 0 | 4088.414 | 4088.414 | 0
5/4/2026 | 5:30:00 AM | 3591.768 | 3591.768 | 0 | 494.601 | 494.601 | 0 | 0 | 0 | 4101.541 | 4101.541 | 0
5/4/2026 | 5:45:00 AM | 3603.175 | 3603.175 | 0 | 496.175 | 496.175 | 0 | 0 | 0 | 4114.708 | 4114.708 | 0
5/4/2026 | 6:00:00 AM | 3614.568 | 3614.568 | 0 | 497.744 | 497.744 | 0 | 0 | 0 | 4127.857 | 4127.857 | 0
5/4/2026 | 6:15:00 AM | 3625.929 | 3625.929 | 0 | 499.291 | 499.291 | 0 | 0 | 0 | 4140.937 | 4140.937 | 0
5/4/2026 | 6:30:00 AM | 3636.907 | 3636.907 | 0 | 500.751 | 500.751 | 0 | 0 | 0 | 4153.512 | 4153.512 | 0
5/4/2026 | 6:45:00 AM | 3647.717 | 3647.717 | 0 | 502.181 | 502.181 | 0 | 0 | 0 | 4165.868 | 4165.868 | 0
5/4/2026 | 7:00:00 AM | 3659.016 | 3659.016 | 0 | 503.718 | 503.718 | 0 | 0 | 0 | 4178.864 | 4178.864 | 0
5/4/2026 | 7:15:00 AM | 3670.318 | 3670.318 | 0 | 505.256 | 505.256 | 0 | 0 | 0 | 4191.862 | 4191.862 | 0
5/4/2026 | 7:30:00 AM | 3681.659 | 3681.659 | 0 | 506.793 | 506.793 | 0 | 0 | 0 | 4204.886 | 4204.886 | 0
5/4/2026 | 7:45:00 AM | 3693.032 | 3693.032 | 0 | 508.341 | 508.341 | 0 | 0 | 0 | 4217.947 | 4217.947 | 0
5/4/2026 | 8:00:00 AM | 3704.448 | 3704.448 | 0 | 509.891 | 509.891 | 0 | 0 | 0 | 4231.054 | 4231.054 | 0
5/4/2026 | 8:15:00 AM | 3715.93 | 3715.93 | 0 | 511.455 | 511.455 | 0 | 0 | 0 | 4244.257 | 4244.257 | 0
5/4/2026 | 8:30:00 AM | 3727.503 | 3727.503 | 0 | 513.035 | 513.035 | 0 | 0 | 0 | 4257.552 | 4257.552 | 0
5/4/2026 | 8:45:00 AM | 3739.291 | 3739.291 | 0 | 514.649 | 514.649 | 0 | 0 | 0 | 4271.099 | 4271.099 | 0
5/4/2026 | 9:00:00 AM | 3751.329 | 3751.329 | 0 | 516.293 | 516.293 | 0 | 0 | 0 | 4284.907 | 4284.907 | 0
5/4/2026 | 9:15:00 AM | 3763.688 | 3763.688 | 0 | 518.002 | 518.002 | 0 | 0 | 0 | 4299.127 | 4299.127 | 0
5/4/2026 | 9:30:00 AM | 3776.574 | 3776.574 | 0 | 519.81 | 519.81 | 0 | 0 | 0 | 4314.001 | 4314.001 | 0
5/4/2026 | 9:45:00 AM | 3789.281 | 3789.281 | 0 | 521.564 | 521.564 | 0 | 0 | 0 | 4328.561 | 4328.561 | 0
5/4/2026 | 10:00:00 AM | 3802.838 | 3802.838 | 0 | 523.481 | 523.481 | 0 | 0 | 0 | 4344.181 | 4344.181 | 0
5/4/2026 | 10:15:00 AM | 3816.33 | 3816.33 | 0 | 525.356 | 525.356 | 0 | 0 | 0 | 4359.663 | 4359.663 | 0
5/4/2026 | 10:30:00 AM | 3830.179 | 3830.179 | 0 | 527.29 | 527.29 | 0 | 0 | 0 | 4375.571 | 4375.571 | 0
5/4/2026 | 10:45:00 AM | 3844.21 | 3844.21 | 0 | 529.233 | 529.233 | 0 | 0 | 0 | 4391.654 | 4391.654 | 0
5/4/2026 | 11:00:00 AM | 3858.338 | 3858.338 | 0 | 531.17 | 531.17 | 0 | 0 | 0 | 4407.787 | 4407.787 | 0
5/4/2026 | 11:15:00 AM | 3872.908 | 3872.908 | 0 | 533.178 | 533.178 | 0 | 0 | 0 | 4424.415 | 4424.415 | 0
5/4/2026 | 11:30:00 AM | 3887.448 | 3887.448 | 0 | 535.152 | 535.152 | 0 | 0 | 0 | 4440.935 | 4440.935 | 0
5/4/2026 | 11:45:00 AM | 3902.377 | 3902.377 | 0 | 537.189 | 537.189 | 0 | 0 | 0 | 4457.916 | 4457.916 | 0
5/4/2026 | 12:00:00 PM | 3917.624 | 3917.624 | 0 | 539.268 | 539.268 | 0 | 0 | 0 | 4475.22 | 4475.22 | 0
5/4/2026 | 12:15:00 PM | 3932.491 | 3932.491 | 0 | 541.258 | 541.258 | 0 | 0 | 0 | 4492.057 | 4492.057 | 0
5/4/2026 | 12:30:00 PM | 3947.085 | 3947.085 | 0 | 543.244 | 543.244 | 0 | 0 | 0 | 4508.702 | 4508.702 | 0
5/4/2026 | 12:45:00 PM | 3960.512 | 3960.512 | 0 | 545.051 | 545.051 | 0 | 0 | 0 | 4524.017 | 4524.017 | 0
5/4/2026 | 1:00:00 PM | 3974.001 | 3974.001 | 0 | 546.883 | 546.883 | 0 | 0 | 0 | 4539.445 | 4539.445 | 0
5/4/2026 | 1:15:00 PM | 3987.526 | 3987.526 | 0 | 548.737 | 548.737 | 0 | 0 | 0 | 4554.953 | 4554.953 | 0
5/4/2026 | 1:30:00 PM | 4000.707 | 4000.707 | 0 | 550.52 | 550.52 | 0 | 0 | 0 | 4570.019 | 4570.019 | 0
5/4/2026 | 1:45:00 PM | 4014.347 | 4014.347 | 0 | 552.419 | 552.419 | 0 | 0 | 0 | 4585.696 | 4585.696 | 0
5/4/2026 | 2:00:00 PM | 4027.663 | 4027.663 | 0 | 554.213 | 554.213 | 0 | 0 | 0 | 4600.898 | 4600.898 | 0
5/4/2026 | 2:15:00 PM | 4041.445 | 4041.445 | 0 | 556.092 | 556.092 | 0 | 0 | 0 | 4616.716 | 4616.716 | 0
5/4/2026 | 2:30:00 PM | 4055.116 | 4055.116 | 0 | 557.924 | 557.924 | 0 | 0 | 0 | 4632.323 | 4632.323 | 0
5/4/2026 | 2:45:00 PM | 4069.047 | 4069.047 | 0 | 559.791 | 559.791 | 0 | 0 | 0 | 4648.219 | 4648.219 | 0
5/4/2026 | 3:00:00 PM | 4083.103 | 4083.103 | 0 | 561.684 | 561.684 | 0 | 0 | 0 | 4664.272 | 4664.272 | 0
5/4/2026 | 3:15:00 PM | 4097.007 | 4097.007 | 0 | 563.52 | 563.52 | 0 | 0 | 0 | 4680.075 | 4680.075 | 0
5/4/2026 | 3:30:00 PM | 4111.315 | 4111.315 | 0 | 565.433 | 565.433 | 0 | 0 | 0 | 4696.404 | 4696.404 | 0
5/4/2026 | 3:45:00 PM | 4125.208 | 4125.208 | 0 | 567.256 | 567.256 | 0 | 0 | 0 | 4712.197 | 4712.197 | 0
5/4/2026 | 4:00:00 PM | 4139.457 | 4139.457 | 0 | 569.173 | 569.173 | 0 | 0 | 0 | 4728.459 | 4728.459 | 0
5/4/2026 | 4:15:00 PM | 4153.223 | 4153.223 | 0 | 571.014 | 571.014 | 0 | 0 | 0 | 4744.14 | 4744.14 | 0
5/4/2026 | 4:30:00 PM | 4167.42 | 4167.42 | 0 | 572.937 | 572.937 | 0 | 0 | 0 | 4760.347 | 4760.347 | 0
5/4/2026 | 4:45:00 PM | 4181.469 | 4181.469 | 0 | 574.819 | 574.819 | 0 | 0 | 0 | 4776.361 | 4776.361 | 0
5/4/2026 | 5:00:00 PM | 4195.548 | 4195.548 | 0 | 576.719 | 576.719 | 0 | 0 | 0 | 4792.435 | 4792.435 | 0
5/4/2026 | 5:15:00 PM | 4209.968 | 4209.968 | 0 | 578.653 | 578.653 | 0 | 0 | 0 | 4808.838 | 4808.838 | 0
5/4/2026 | 5:30:00 PM | 4224.013 | 4224.013 | 0 | 580.528 | 580.528 | 0 | 0 | 0 | 4824.812 | 4824.812 | 0
5/4/2026 | 5:45:00 PM | 4238.408 | 4238.408 | 0 | 582.48 | 582.48 | 0 | 0 | 0 | 4841.244 | 4841.244 | 0
5/4/2026 | 6:00:00 PM | 4252.301 | 4252.301 | 0 | 584.321 | 584.321 | 0 | 0 | 0 | 4857.024 | 4857.024 | 0
5/4/2026 | 6:15:00 PM | 4266.685 | 4266.685 | 0 | 586.28 | 586.28 | 0 | 0 | 0 | 4873.474 | 4873.474 | 0
5/4/2026 | 6:30:00 PM | 4280.736 | 4280.736 | 0 | 588.177 | 588.177 | 0 | 0 | 0 | 4889.49 | 4889.49 | 0
5/4/2026 | 6:45:00 PM | 4295 | 4295 | 0 | 590.109 | 590.109 | 0 | 0 | 0 | 4905.784 | 4905.784 | 0
5/4/2026 | 7:00:00 PM | 4308.945 | 4308.945 | 0 | 592.013 | 592.013 | 0 | 0 | 0 | 4921.734 | 4921.734 | 0
5/4/2026 | 7:15:00 PM | 4322.996 | 4322.996 | 0 | 593.918 | 593.918 | 0 | 0 | 0 | 4937.786 | 4937.786 | 0
5/4/2026 | 7:30:00 PM | 4337.15 | 4337.15 | 0 | 595.85 | 595.85 | 0 | 0 | 0 | 4953.984 | 4953.984 | 0
5/4/2026 | 7:45:00 PM | 4350.881 | 4350.881 | 0 | 597.702 | 597.702 | 0 | 0 | 0 | 4969.654 | 4969.654 | 0
5/4/2026 | 8:00:00 PM | 4365.009 | 4365.009 | 0 | 599.641 | 599.641 | 0 | 0 | 0 | 4985.828 | 4985.828 | 0
5/4/2026 | 8:15:00 PM | 4378.791 | 4378.791 | 0 | 601.524 | 601.524 | 0 | 0 | 0 | 5001.588 | 5001.588 | 0
5/4/2026 | 8:30:00 PM | 4392.628 | 4392.628 | 0 | 603.42 | 603.42 | 0 | 0 | 0 | 5017.443 | 5017.443 | 0
5/4/2026 | 8:45:00 PM | 4406.571 | 4406.571 | 0 | 605.35 | 605.35 | 0 | 0 | 0 | 5033.464 | 5033.464 | 0
5/4/2026 | 9:00:00 PM | 4420.022 | 4420.022 | 0 | 607.172 | 607.172 | 0 | 0 | 0 | 5048.841 | 5048.841 | 0
5/4/2026 | 9:15:00 PM | 4433.163 | 4433.163 | 0 | 608.965 | 608.965 | 0 | 0 | 0 | 5063.899 | 5063.899 | 0
5/4/2026 | 9:30:00 PM | 4446.765 | 4446.765 | 0 | 610.883 | 610.883 | 0 | 0 | 0 | 5079.603 | 5079.603 | 0
5/4/2026 | 9:45:00 PM | 4460.023 | 4460.023 | 0 | 612.725 | 612.725 | 0 | 0 | 0 | 5094.863 | 5094.863 | 0
5/4/2026 | 10:00:00 PM | 4473.017 | 4473.017 | 0 | 614.509 | 614.509 | 0 | 0 | 0 | 5109.768 | 5109.768 | 0
5/4/2026 | 10:15:00 PM | 4487.348 | 4487.348 | 0 | 616.506 | 616.506 | 0 | 0 | 0 | 5126.096 | 5126.096 | 0
5/4/2026 | 10:30:00 PM | 4502.755 | 4502.755 | 0 | 618.675 | 618.675 | 0 | 0 | 0 | 5143.698 | 5143.698 | 0
5/4/2026 | 10:45:00 PM | 4518.314 | 4518.314 | 0 | 620.859 | 620.859 | 0 | 0 | 0 | 5161.446 | 5161.446 | 0
5/4/2026 | 11:00:00 PM | 4533.683 | 4533.683 | 0 | 622.992 | 622.992 | 0 | 0 | 0 | 5178.92 | 5178.92 | 0
5/4/2026 | 11:15:00 PM | 4549.294 | 4549.294 | 0 | 625.182 | 625.182 | 0 | 0 | 0 | 5196.73 | 5196.73 | 0
5/4/2026 | 11:30:00 PM | 4564.64 | 4564.64 | 0 | 627.313 | 627.313 | 0 | 0 | 0 | 5214.215 | 5214.215 | 0
5/4/2026 | 11:45:00 PM | 4580.15 | 4580.15 | 0 | 629.489 | 629.489 | 0 | 0 | 0 | 5231.921 | 5231.921 | 0
5/5/2026 | 12:00:00 AM | 4595.624 | 4595.624 | 0 | 631.67 | 631.67 | 0 | 0 | 0 | 5249.598 | 5249.598 | 0
5/5/2026 | 12:15:00 AM | 4610.931 | 4610.931 | 0 | 633.819 | 633.819 | 0 | 0 | 0 | 5267.094 | 5267.094 | 0
5/5/2026 | 12:30:00 AM | 4626.453 | 4626.453 | 0 | 636.024 | 636.024 | 0 | 0 | 0 | 5284.89 | 5284.89 | 0
5/5/2026 | 12:45:00 AM | 4641.663 | 4641.663 | 0 | 638.156 | 638.156 | 0 | 0 | 0 | 5302.278 | 5302.278 | 0
5/5/2026 | 1:00:00 AM | 4657.147 | 4657.147 | 0 | 640.368 | 640.368 | 0 | 0 | 0 | 5320.058 | 5320.058 | 0
5/5/2026 | 1:15:00 AM | 4672.167 | 4672.167 | 0 | 642.48 | 642.48 | 0 | 0 | 0 | 5337.234 | 5337.234 | 0
5/5/2026 | 1:30:00 AM | 4687.506 | 4687.506 | 0 | 644.67 | 644.67 | 0 | 0 | 0 | 5354.849 | 5354.849 | 0
5/5/2026 | 1:45:00 AM | 4702.563 | 4702.563 | 0 | 646.811 | 646.811 | 0 | 0 | 0 | 5372.118 | 5372.118 | 0
5/5/2026 | 2:00:00 AM | 4717.49 | 4717.49 | 0 | 648.931 | 648.931 | 0 | 0 | 0 | 5389.214 | 5389.214 | 0
5/5/2026 | 2:15:00 AM | 4732.633 | 4732.633 | 0 | 651.106 | 651.106 | 0 | 0 | 0 | 5406.602 | 5406.602 | 0
5/5/2026 | 2:30:00 AM | 4747.412 | 4747.412 | 0 | 653.197 | 653.197 | 0 | 0 | 0 | 5423.505 | 5423.505 | 0
5/5/2026 | 2:45:00 AM | 4762.41 | 4762.41 | 0 | 655.341 | 655.341 | 0 | 0 | 0 | 5440.704 | 5440.704 | 0
5/5/2026 | 3:00:00 AM | 4777.061 | 4777.061 | 0 | 657.403 | 657.403 | 0 | 0 | 0 | 5457.445 | 5457.445 | 0
5/5/2026 | 3:15:00 AM | 4791.969 | 4791.969 | 0 | 659.527 | 659.527 | 0 | 0 | 0 | 5474.525 | 5474.525 | 0
5/5/2026 | 3:30:00 AM | 4806.715 | 4806.715 | 0 | 661.611 | 661.611 | 0 | 0 | 0 | 5491.378 | 5491.378 | 0
5/5/2026 | 3:45:00 AM | 4821.495 | 4821.495 | 0 | 663.708 | 663.708 | 0 | 0 | 0 | 5508.285 | 5508.285 | 0
5/5/2026 | 4:00:00 AM | 4836.335 | 4836.335 | 0 | 665.813 | 665.813 | 0 | 0 | 0 | 5525.265 | 5525.265 | 0
5/5/2026 | 4:15:00 AM | 4850.743 | 4850.743 | 0 | 667.828 | 667.828 | 0 | 0 | 0 | 5541.695 | 5541.695 | 0
5/5/2026 | 4:30:00 AM | 4865.431 | 4865.431 | 0 | 669.93 | 669.93 | 0 | 0 | 0 | 5558.548 | 5558.548 | 0
5/5/2026 | 4:45:00 AM | 4879.661 | 4879.661 | 0 | 671.935 | 671.935 | 0 | 0 | 0 | 5574.821 | 5574.821 | 0
5/5/2026 | 5:00:00 AM | 4893.563 | 4893.563 | 0 | 673.862 | 673.862 | 0 | 0 | 0 | 5590.659 | 5590.659 | 0
5/5/2026 | 5:15:00 AM | 4907.826 | 4907.826 | 0 | 675.865 | 675.865 | 0 | 0 | 0 | 5606.986 | 5606.986 | 0
5/5/2026 | 5:30:00 AM | 4921.831 | 4921.831 | 0 | 677.801 | 677.801 | 0 | 0 | 0 | 5622.984 | 5622.984 | 0
5/5/2026 | 5:45:00 AM | 4935.503 | 4935.503 | 0 | 679.667 | 679.667 | 0 | 0 | 0 | 5638.568 | 5638.568 | 0
5/5/2026 | 6:00:00 AM | 4949.048 | 4949.048 | 0 | 681.504 | 681.504 | 0 | 0 | 0 | 5653.977 | 5653.977 | 0
5/5/2026 | 6:15:00 AM | 4962.478 | 4962.478 | 0 | 683.291 | 683.291 | 0 | 0 | 0 | 5669.21 | 5669.21 | 0
5/5/2026 | 6:30:00 AM | 4975.854 | 4975.854 | 0 | 685.058 | 685.058 | 0 | 0 | 0 | 5684.367 | 5684.367 | 0
5/5/2026 | 6:45:00 AM | 4989.14 | 4989.14 | 0 | 686.808 | 686.808 | 0 | 0 | 0 | 5699.412 | 5699.412 | 0
5/5/2026 | 7:00:00 AM | 5002.22 | 5002.22 | 0 | 688.515 | 688.515 | 0 | 0 | 0 | 5714.201 | 5714.201 | 0
5/5/2026 | 7:15:00 AM | 5015.242 | 5015.242 | 0 | 690.21 | 690.21 | 0 | 0 | 0 | 5728.911 | 5728.911 | 0
5/5/2026 | 7:30:00 AM | 5028.349 | 5028.349 | 0 | 691.919 | 691.919 | 0 | 0 | 0 | 5743.729 | 5743.729 | 0
5/5/2026 | 7:45:00 AM | 5041.624 | 5041.624 | 0 | 693.662 | 693.662 | 0 | 0 | 0 | 5758.752 | 5758.752 | 0
5/5/2026 | 8:00:00 AM | 5055.109 | 5055.109 | 0 | 695.448 | 695.448 | 0 | 0 | 0 | 5774.03 | 5774.03 | 0
5/5/2026 | 8:15:00 AM | 5068.752 | 5068.752 | 0 | 697.258 | 697.258 | 0 | 0 | 0 | 5789.502 | 5789.502 | 0
5/5/2026 | 8:30:00 AM | 5082.348 | 5082.348 | 0 | 699.056 | 699.056 | 0 | 0 | 0 | 5804.905 | 5804.905 | 0
5/5/2026 | 8:45:00 AM | 5096.352 | 5096.352 | 0 | 700.939 | 700.939 | 0 | 0 | 0 | 5820.81 | 5820.81 | 0
5/5/2026 | 9:00:00 AM | 5110.388 | 5110.388 | 0 | 702.82 | 702.82 | 0 | 0 | 0 | 5836.731 | 5836.731 | 0
5/5/2026 | 9:15:00 AM | 5124.792 | 5124.792 | 0 | 704.764 | 704.764 | 0 | 0 | 0 | 5853.081 | 5853.081 | 0
5/5/2026 | 9:30:00 AM | 5139.668 | 5139.668 | 0 | 706.772 | 706.772 | 0 | 0 | 0 | 5869.93 | 5869.93 | 0
5/5/2026 | 9:45:00 AM | 5154.912 | 5154.912 | 0 | 708.792 | 708.792 | 0 | 0 | 0 | 5887.095 | 5887.095 | 0
5/5/2026 | 10:00:00 AM | 5170.877 | 5170.877 | 0 | 710.895 | 710.895 | 0 | 0 | 0 | 5905.03 | 5905.03 | 0
5/5/2026 | 10:15:00 AM | 5187.251 | 5187.251 | 0 | 713.043 | 713.043 | 0 | 0 | 0 | 5923.39 | 5923.39 | 0
5/5/2026 | 10:30:00 AM | 5203.775 | 5203.775 | 0 | 715.165 | 715.165 | 0 | 0 | 0 | 5941.827 | 5941.827 | 0
5/5/2026 | 10:45:00 AM | 5221.184 | 5221.184 | 0 | 717.417 | 717.417 | 0 | 0 | 0 | 5961.245 | 5961.245 | 0
5/5/2026 | 11:00:00 AM | 5238.706 | 5238.706 | 0 | 719.674 | 719.674 | 0 | 0 | 0 | 5980.78 | 5980.78 | 0
5/5/2026 | 11:15:00 AM | 5255.822 | 5255.822 | 0 | 721.843 | 721.843 | 0 | 0 | 0 | 5999.893 | 5999.893 | 0
5/5/2026 | 11:30:00 AM | 5272.109 | 5272.109 | 0 | 723.906 | 723.906 | 0 | 0 | 0 | 6018.071 | 6018.071 | 0
5/5/2026 | 11:45:00 AM | 5287.663 | 5287.663 | 0 | 725.892 | 725.892 | 0 | 0 | 0 | 6035.553 | 6035.553 | 0
5/5/2026 | 12:00:00 PM | 5302.832 | 5302.832 | 0 | 727.86 | 727.86 | 0 | 0 | 0 | 6052.641 | 6052.641 | 0
5/5/2026 | 12:15:00 PM | 5317.947 | 5317.947 | 0 | 729.805 | 729.805 | 0 | 0 | 0 | 6069.648 | 6069.648 | 0
5/5/2026 | 12:30:00 PM | 5333.177 | 5333.177 | 0 | 731.802 | 731.802 | 0 | 0 | 0 | 6086.828 | 6086.828 | 0
5/5/2026 | 12:45:00 PM | 5348.162 | 5348.162 | 0 | 733.737 | 733.737 | 0 | 0 | 0 | 6103.685 | 6103.685 | 0
5/5/2026 | 1:00:00 PM | 5363.648 | 5363.648 | 0 | 735.762 | 735.762 | 0 | 0 | 0 | 6121.153 | 6121.153 | 0
5/5/2026 | 1:15:00 PM | 5378.816 | 5378.816 | 0 | 737.69 | 737.69 | 0 | 0 | 0 | 6138.2 | 6138.2 | 0
5/5/2026 | 1:30:00 PM | 5394.245 | 5394.245 | 0 | 739.709 | 739.709 | 0 | 0 | 0 | 6155.625 | 6155.625 | 0
5/5/2026 | 1:45:00 PM | 5409.215 | 5409.215 | 0 | 741.654 | 741.654 | 0 | 0 | 0 | 6172.495 | 6172.495 | 0
5/5/2026 | 2:00:00 PM | 5424.303 | 5424.303 | 0 | 743.65 | 743.65 | 0 | 0 | 0 | 6189.565 | 6189.565 | 0
5/5/2026 | 2:15:00 PM | 5439.318 | 5439.318 | 0 | 745.611 | 745.611 | 0 | 0 | 0 | 6206.507 | 6206.507 | 0
5/5/2026 | 2:30:00 PM | 5454.3 | 5454.3 | 0 | 747.58 | 747.58 | 0 | 0 | 0 | 6223.442 | 6223.442 | 0
5/5/2026 | 2:45:00 PM | 5469.432 | 5469.432 | 0 | 749.569 | 749.569 | 0 | 0 | 0 | 6240.554 | 6240.554 | 0
5/5/2026 | 3:00:00 PM | 5484.334 | 5484.334 | 0 | 751.509 | 751.509 | 0 | 0 | 0 | 6257.362 | 6257.362 | 0
5/5/2026 | 3:15:00 PM | 5499.553 | 5499.553 | 0 | 753.492 | 753.492 | 0 | 0 | 0 | 6274.577 | 6274.577 | 0
5/5/2026 | 3:30:00 PM | 5514.454 | 5514.454 | 0 | 755.404 | 755.404 | 0 | 0 | 0 | 6291.348 | 6291.348 | 0
5/5/2026 | 3:45:00 PM | 5529.859 | 5529.859 | 0 | 757.379 | 757.379 | 0 | 0 | 0 | 6308.733 | 6308.733 | 0
5/5/2026 | 4:00:00 PM | 5544.944 | 5544.944 | 0 | 759.289 | 759.289 | 0 | 0 | 0 | 6325.706 | 6325.706 | 0
5/5/2026 | 4:15:00 PM | 5560.341 | 5560.341 | 0 | 761.251 | 761.251 | 0 | 0 | 0 | 6343.059 | 6343.059 | 0
5/5/2026 | 4:30:00 PM | 5575.594 | 5575.594 | 0 | 763.182 | 763.182 | 0 | 0 | 0 | 6360.231 | 6360.231 | 0
5/5/2026 | 4:45:00 PM | 5590.824 | 5590.824 | 0 | 765.118 | 765.118 | 0 | 0 | 0 | 6377.373 | 6377.373 | 0
5/5/2026 | 5:00:00 PM | 5606.582 | 5606.582 | 0 | 767.106 | 767.106 | 0 | 0 | 0 | 6395.096 | 6395.096 | 0
5/5/2026 | 5:15:00 PM | 5622.103 | 5622.103 | 0 | 769.043 | 769.043 | 0 | 0 | 0 | 6412.49 | 6412.49 | 0
5/5/2026 | 5:30:00 PM | 5637.911 | 5637.911 | 0 | 771.043 | 771.043 | 0 | 0 | 0 | 6430.261 | 6430.261 | 0
5/5/2026 | 5:45:00 PM | 5653.361 | 5653.361 | 0 | 772.976 | 772.976 | 0 | 0 | 0 | 6447.588 | 6447.588 | 0
5/5/2026 | 6:00:00 PM | 5669 | 5669 | 0 | 774.987 | 774.987 | 0 | 0 | 0 | 6465.2 | 6465.2 | 0
5/5/2026 | 6:15:00 PM | 5684.701 | 5684.701 | 0 | 776.99 | 776.99 | 0 | 0 | 0 | 6482.862 | 6482.862 | 0
5/5/2026 | 6:30:00 PM | 5700.181 | 5700.181 | 0 | 778.952 | 778.952 | 0 | 0 | 0 | 6500.284 | 6500.284 | 0
5/5/2026 | 6:45:00 PM | 5715.918 | 5715.918 | 0 | 780.983 | 780.983 | 0 | 0 | 0 | 6518.055 | 6518.055 | 0
5/5/2026 | 7:00:00 PM | 5731.395 | 5731.395 | 0 | 782.95 | 782.95 | 0 | 0 | 0 | 6535.483 | 6535.483 | 0
5/5/2026 | 7:15:00 PM | 5747.163 | 5747.163 | 0 | 784.983 | 784.983 | 0 | 0 | 0 | 6553.285 | 6553.285 | 0
5/5/2026 | 7:30:00 PM | 5762.524 | 5762.524 | 0 | 786.949 | 786.949 | 0 | 0 | 0 | 6570.561 | 6570.561 | 0
5/5/2026 | 7:45:00 PM | 5778.219 | 5778.219 | 0 | 789.024 | 789.024 | 0 | 0 | 0 | 6588.293 | 6588.293 | 0
5/5/2026 | 8:00:00 PM | 5793.499 | 5793.499 | 0 | 791.029 | 791.029 | 0 | 0 | 0 | 6605.544 | 6605.544 | 0
5/5/2026 | 8:15:00 PM | 5808.846 | 5808.846 | 0 | 793.038 | 793.038 | 0 | 0 | 0 | 6622.895 | 6622.895 | 0
5/5/2026 | 8:30:00 PM | 5824.117 | 5824.117 | 0 | 795.039 | 795.039 | 0 | 0 | 0 | 6640.194 | 6640.194 | 0
5/5/2026 | 8:45:00 PM | 5839.023 | 5839.023 | 0 | 796.977 | 796.977 | 0 | 0 | 0 | 6657.052 | 6657.052 | 0
5/5/2026 | 9:00:00 PM | 5854.298 | 5854.298 | 0 | 798.987 | 798.987 | 0 | 0 | 0 | 6674.386 | 6674.386 | 0
5/5/2026 | 9:15:00 PM | 5868.941 | 5868.941 | 0 | 800.873 | 800.873 | 0 | 0 | 0 | 6690.925 | 6690.925 | 0
5/5/2026 | 9:30:00 PM | 5884.048 | 5884.048 | 0 | 802.876 | 802.876 | 0 | 0 | 0 | 6708.095 | 6708.095 | 0
5/5/2026 | 9:45:00 PM | 5898.688 | 5898.688 | 0 | 804.793 | 804.793 | 0 | 0 | 0 | 6724.682 | 6724.682 | 0
5/5/2026 | 10:00:00 PM | 5913.295 | 5913.295 | 0 | 806.749 | 806.749 | 0 | 0 | 0 | 6741.315 | 6741.315 | 0
5/5/2026 | 10:15:00 PM | 5927.985 | 5927.985 | 0 | 808.735 | 808.735 | 0 | 0 | 0 | 6758.072 | 6758.072 | 0
5/5/2026 | 10:30:00 PM | 5942.493 | 5942.493 | 0 | 810.668 | 810.668 | 0 | 0 | 0 | 6774.567 | 6774.567 | 0
5/5/2026 | 10:45:00 PM | 5957.465 | 5957.465 | 0 | 812.699 | 812.699 | 0 | 0 | 0 | 6791.661 | 6791.661 | 0
5/5/2026 | 11:00:00 PM | 5971.956 | 5971.956 | 0 | 814.618 | 814.618 | 0 | 0 | 0 | 6808.115 | 6808.115 | 0
5/5/2026 | 11:15:00 PM | 5987.127 | 5987.127 | 0 | 816.672 | 816.672 | 0 | 0 | 0 | 6825.419 | 6825.419 | 0
5/5/2026 | 11:30:00 PM | 6002.699 | 6002.699 | 0 | 818.756 | 818.756 | 0 | 0 | 0 | 6843.053 | 6843.053 | 0
5/5/2026 | 11:45:00 PM | 6020.261 | 6020.261 | 0 | 821.105 | 821.105 | 0 | 0 | 0 | 6862.819 | 6862.819 | 0
5/6/2026 | 12:00:00 AM | 6038.876 | 6038.876 | 0 | 823.591 | 823.591 | 0 | 0 | 0 | 6883.689 | 6883.689 | 0
5/6/2026 | 12:15:00 AM | 6057.575 | 6057.575 | 0 | 826.065 | 826.065 | 0 | 0 | 0 | 6904.634 | 6904.634 | 0
5/6/2026 | 12:30:00 AM | 6076.724 | 6076.724 | 0 | 828.6 | 828.6 | 0 | 0 | 0 | 6926.064 | 6926.064 | 0
5/6/2026 | 12:45:00 AM | 6096.137 | 6096.137 | 0 | 831.178 | 831.178 | 0 | 0 | 0 | 6947.773 | 6947.773 | 0
5/6/2026 | 1:00:00 AM | 6115.449 | 6115.449 | 0 | 833.717 | 833.717 | 0 | 0 | 0 | 6969.337 | 6969.337 | 0
5/6/2026 | 1:15:00 AM | 6134.662 | 6134.662 | 0 | 836.237 | 836.237 | 0 | 0 | 0 | 6990.761 | 6990.761 | 0
5/6/2026 | 1:30:00 AM | 6153.804 | 6153.804 | 0 | 838.733 | 838.733 | 0 | 0 | 0 | 7012.083 | 7012.083 | 0
5/6/2026 | 1:45:00 AM | 6173.235 | 6173.235 | 0 | 841.29 | 841.29 | 0 | 0 | 0 | 7033.748 | 7033.748 | 0
5/6/2026 | 2:00:00 AM | 6193.004 | 6193.004 | 0 | 843.88 | 843.88 | 0 | 0 | 0 | 7055.751 | 7055.751 | 0
5/6/2026 | 2:15:00 AM | 6213.675 | 6213.675 | 0 | 846.586 | 846.586 | 0 | 0 | 0 | 7078.724 | 7078.724 | 0
5/6/2026 | 2:30:00 AM | 6235.486 | 6235.486 | 0 | 849.409 | 849.409 | 0 | 0 | 0 | 7102.873 | 7102.873 | 0
5/6/2026 | 2:45:00 AM | 6258.441 | 6258.441 | 0 | 852.313 | 852.313 | 0 | 0 | 0 | 7128.167 | 7128.167 | 0
5/6/2026 | 3:00:00 AM | 6283.368 | 6283.368 | 0 | 855.457 | 855.457 | 0 | 0 | 0 | 7155.595 | 7155.595 | 0
5/6/2026 | 3:15:00 AM | 6309.221 | 6309.221 | 0 | 858.657 | 858.657 | 0 | 0 | 0 | 7183.9 | 7183.9 | 0
5/6/2026 | 3:30:00 AM | 6335.747 | 6335.747 | 0 | 861.949 | 861.949 | 0 | 0 | 0 | 7212.9 | 7212.9 | 0
5/6/2026 | 3:45:00 AM | 6362.465 | 6362.465 | 0 | 865.237 | 865.237 | 0 | 0 | 0 | 7242.057 | 7242.057 | 0
5/6/2026 | 4:00:00 AM | 6389.182 | 6389.182 | 0 | 868.472 | 868.472 | 0 | 0 | 0 | 7271.135 | 7271.135 | 0
5/6/2026 | 4:15:00 AM | 6416.527 | 6416.527 | 0 | 871.775 | 871.775 | 0 | 0 | 0 | 7300.857 | 7300.857 | 0
5/6/2026 | 4:30:00 AM | 6443.911 | 6443.911 | 0 | 875.081 | 875.081 | 0 | 0 | 0 | 7330.628 | 7330.628 | 0
5/6/2026 | 4:45:00 AM | 6471.518 | 6471.518 | 0 | 878.413 | 878.413 | 0 | 0 | 0 | 7360.618 | 7360.618 | 0
5/6/2026 | 5:00:00 AM | 6499.325 | 6499.325 | 0 | 881.751 | 881.751 | 0 | 0 | 0 | 7390.79 | 7390.79 | 0
5/6/2026 | 5:15:00 AM | 6527.804 | 6527.804 | 0 | 885.126 | 885.126 | 0 | 0 | 0 | 7421.627 | 7421.627 | 0
5/6/2026 | 5:30:00 AM | 6556.22 | 6556.22 | 0 | 888.468 | 888.468 | 0 | 0 | 0 | 7452.371 | 7452.371 | 0
5/6/2026 | 5:45:00 AM | 6584.611 | 6584.611 | 0 | 891.794 | 891.794 | 0 | 0 | 0 | 7483.073 | 7483.073 | 0
5/6/2026 | 6:00:00 AM | 6612.948 | 6612.948 | 0 | 895.083 | 895.083 | 0 | 0 | 0 | 7513.703 | 7513.703 | 0
5/6/2026 | 6:15:00 AM | 6641.18 | 6641.18 | 0 | 898.323 | 898.323 | 0 | 0 | 0 | 7544.183 | 7544.183 | 0
5/6/2026 | 6:30:00 AM | 6669.413 | 6669.413 | 0 | 901.564 | 901.564 | 0 | 0 | 0 | 7574.666 | 7574.666 | 0
5/6/2026 | 6:45:00 AM | 6697.651 | 6697.651 | 0 | 904.805 | 904.805 | 0 | 0 | 0 | 7605.134 | 7605.134 | 0
5/6/2026 | 7:00:00 AM | 6725.907 | 6725.907 | 0 | 908.056 | 908.056 | 0 | 0 | 0 | 7635.627 | 7635.627 | 0
5/6/2026 | 7:15:00 AM | 6754.121 | 6754.121 | 0 | 911.29 | 911.29 | 0 | 0 | 0 | 7666.061 | 7666.061 | 0
5/6/2026 | 7:30:00 AM | 6782.328 | 6782.328 | 0 | 914.525 | 914.525 | 0 | 0 | 0 | 7696.483 | 7696.483 | 0
5/6/2026 | 7:45:00 AM | 6810.571 | 6810.571 | 0 | 917.768 | 917.768 | 0 | 0 | 0 | 7726.951 | 7726.951 | 0
5/6/2026 | 8:00:00 AM | 6838.809 | 6838.809 | 0 | 921.008 | 921.008 | 0 | 0 | 0 | 7757.398 | 7757.398 | 0
5/6/2026 | 8:15:00 AM | 6867.085 | 6867.085 | 0 | 924.266 | 924.266 | 0 | 0 | 0 | 7787.879 | 7787.879 | 0
5/6/2026 | 8:30:00 AM | 6895.722 | 6895.722 | 0 | 927.625 | 927.625 | 0 | 0 | 0 | 7818.791 | 7818.791 | 0
5/6/2026 | 8:45:00 AM | 6924.514 | 6924.514 | 0 | 931.026 | 931.026 | 0 | 0 | 0 | 7849.893 | 7849.893 | 0
5/6/2026 | 9:00:00 AM | 6953.611 | 6953.611 | 0 | 934.484 | 934.484 | 0 | 0 | 0 | 7881.329 | 7881.329 | 0
5/6/2026 | 9:15:00 AM | 6982.926 | 6982.926 | 0 | 937.968 | 937.968 | 0 | 0 | 0 | 7913.001 | 7913.001 | 0
5/6/2026 | 9:30:00 AM | 7012.426 | 7012.426 | 0 | 941.485 | 941.485 | 0 | 0 | 0 | 7944.872 | 7944.872 | 0
5/6/2026 | 9:45:00 AM | 7041.913 | 7041.913 | 0 | 944.987 | 944.987 | 0 | 0 | 0 | 7976.732 | 7976.732 | 0
5/6/2026 | 10:00:00 AM | 7070.9 | 7070.9 | 0 | 948.409 | 948.409 | 0 | 0 | 0 | 8008.053 | 8008.053 | 0
5/6/2026 | 10:15:00 AM | 7098.815 | 7098.815 | 0 | 951.552 | 951.552 | 0 | 0 | 0 | 8038.171 | 8038.171 | 0
5/6/2026 | 10:30:00 AM | 7124.395 | 7124.395 | 0 | 954.464 | 954.464 | 0 | 0 | 0 | 8065.831 | 8065.831 | 0
5/6/2026 | 10:45:00 AM | 7148.256 | 7148.256 | 0 | 957.243 | 957.243 | 0 | 0 | 0 | 8091.721 | 8091.721 | 0
5/6/2026 | 11:00:00 AM | 7170.844 | 7170.844 | 0 | 959.873 | 959.873 | 0 | 0 | 0 | 8116.252 | 8116.252 | 0
5/6/2026 | 11:15:00 AM | 7192.807 | 7192.807 | 0 | 962.449 | 962.449 | 0 | 0 | 0 | 8140.167 | 8140.167 | 0
5/6/2026 | 11:30:00 AM | 7214.497 | 7214.497 | 0 | 965.003 | 965.003 | 0 | 0 | 0 | 8163.808 | 8163.808 | 0
5/6/2026 | 11:45:00 AM | 7236.285 | 7236.285 | 0 | 967.622 | 967.622 | 0 | 0 | 0 | 8187.631 | 8187.631 | 0
5/6/2026 | 12:00:00 PM | 7257.965 | 7257.965 | 0 | 970.231 | 970.231 | 0 | 0 | 0 | 8211.335 | 8211.335 | 0
5/6/2026 | 12:15:00 PM | 7279.429 | 7279.429 | 0 | 972.792 | 972.792 | 0 | 0 | 0 | 8234.778 | 8234.778 | 0
5/6/2026 | 12:30:00 PM | 7300.689 | 7300.689 | 0 | 975.357 | 975.357 | 0 | 0 | 0 | 8258.02 | 8258.02 | 0
5/6/2026 | 12:45:00 PM | 7322.622 | 7322.622 | 0 | 977.991 | 977.991 | 0 | 0 | 0 | 8281.978 | 8281.978 | 0
5/6/2026 | 1:00:00 PM | 7345.297 | 7345.297 | 0 | 980.756 | 980.756 | 0 | 0 | 0 | 8306.773 | 8306.773 | 0
5/6/2026 | 1:15:00 PM | 7368.444 | 7368.444 | 0 | 983.586 | 983.586 | 0 | 0 | 0 | 8332.083 | 8332.083 | 0
5/6/2026 | 1:30:00 PM | 7391.813 | 7391.813 | 0 | 986.43 | 986.43 | 0 | 0 | 0 | 8357.624 | 8357.624 | 0
5/6/2026 | 1:45:00 PM | 7415.414 | 7415.414 | 0 | 989.293 | 989.293 | 0 | 0 | 0 | 8383.417 | 8383.417 | 0
5/6/2026 | 2:00:00 PM | 7439.317 | 7439.317 | 0 | 992.177 | 992.177 | 0 | 0 | 0 | 8409.511 | 8409.511 | 0
5/6/2026 | 2:15:00 PM | 7463.247 | 7463.247 | 0 | 995.074 | 995.074 | 0 | 0 | 0 | 8435.629 | 8435.629 | 0
5/6/2026 | 2:30:00 PM | 7488.05 | 7488.05 | 0 | 998.072 | 998.072 | 0 | 0 | 0 | 8462.676 | 8462.676 | 0
5/6/2026 | 2:45:00 PM | 7513.633 | 7513.633 | 0 | 1001.144 | 1001.144 | 0 | 0 | 0 | 8490.575 | 8490.575 | 0
5/6/2026 | 3:00:00 PM | 7538.844 | 7538.844 | 0 | 1004.185 | 1004.185 | 0 | 0 | 0 | 8518.065 | 8518.065 | 0
5/6/2026 | 3:15:00 PM | 7564.583 | 7564.583 | 0 | 1007.247 | 1007.247 | 0 | 0 | 0 | 8546.095 | 8546.095 | 0
5/6/2026 | 3:30:00 PM | 7590.995 | 7590.995 | 0 | 1010.348 | 1010.348 | 0 | 0 | 0 | 8574.803 | 8574.803 | 0
5/6/2026 | 3:45:00 PM | 7617.217 | 7617.217 | 0 | 1013.452 | 1013.452 | 0 | 0 | 0 | 8603.311 | 8603.311 | 0
5/6/2026 | 4:00:00 PM | 7643.236 | 7643.236 | 0 | 1016.537 | 1016.537 | 0 | 0 | 0 | 8631.613 | 8631.613 | 0
5/6/2026 | 4:15:00 PM | 7669.681 | 7669.681 | 0 | 1019.634 | 1019.634 | 0 | 0 | 0 | 8660.351 | 8660.351 | 0
5/6/2026 | 4:30:00 PM | 7695.978 | 7695.978 | 0 | 1022.725 | 1022.725 | 0 | 0 | 0 | 8688.948 | 8688.948 | 0
5/6/2026 | 4:45:00 PM | 7721.505 | 7721.505 | 0 | 1025.739 | 1025.739 | 0 | 0 | 0 | 8716.712 | 8716.712 | 0
5/6/2026 | 5:00:00 PM | 7747.128 | 7747.128 | 0 | 1028.77 | 1028.77 | 0 | 0 | 0 | 8744.582 | 8744.582 | 0
5/6/2026 | 5:15:00 PM | 7773.463 | 7773.463 | 0 | 1031.849 | 1031.849 | 0 | 0 | 0 | 8773.206 | 8773.206 | 0
5/6/2026 | 5:30:00 PM | 7800.671 | 7800.671 | 0 | 1034.999 | 1034.999 | 0 | 0 | 0 | 8802.704 | 8802.704 | 0
5/6/2026 | 5:45:00 PM | 7828.426 | 7828.426 | 0 | 1038.192 | 1038.192 | 0 | 0 | 0 | 8832.743 | 8832.743 | 0
5/6/2026 | 6:00:00 PM | 7856.56 | 7856.56 | 0 | 1041.4 | 1041.4 | 0 | 0 | 0 | 8863.147 | 8863.147 | 0
5/6/2026 | 6:15:00 PM | 7884.523 | 7884.523 | 0 | 1044.622 | 1044.622 | 0 | 0 | 0 | 8893.411 | 8893.411 | 0
5/6/2026 | 6:30:00 PM | 7912.107 | 7912.107 | 0 | 1047.833 | 1047.833 | 0 | 0 | 0 | 8923.302 | 8923.302 | 0
5/6/2026 | 6:45:00 PM | 7939.23 | 7939.23 | 0 | 1051.008 | 1051.008 | 0 | 0 | 0 | 8952.727 | 8952.727 | 0
5/6/2026 | 7:00:00 PM | 7965.979 | 7965.979 | 0 | 1054.159 | 1054.159 | 0 | 0 | 0 | 8981.807 | 8981.807 | 0
5/6/2026 | 7:15:00 PM | 7993.641 | 7993.641 | 0 | 1057.402 | 1057.402 | 0 | 0 | 0 | 9011.816 | 9011.816 | 0
5/6/2026 | 7:30:00 PM | 8022.576 | 8022.576 | 0 | 1060.769 | 1060.769 | 0 | 0 | 0 | 9043.098 | 9043.098 | 0
5/6/2026 | 7:45:00 PM | 8051.435 | 8051.435 | 0 | 1064.119 | 1064.119 | 0 | 0 | 0 | 9074.322 | 9074.322 | 0
5/6/2026 | 8:00:00 PM | 8079.997 | 8079.997 | 0 | 1067.435 | 1067.435 | 0 | 0 | 0 | 9105.257 | 9105.257 | 0
5/6/2026 | 8:15:00 PM | 8108.885 | 8108.885 | 0 | 1070.782 | 1070.782 | 0 | 0 | 0 | 9136.526 | 9136.526 | 0
5/6/2026 | 8:30:00 PM | 8137.605 | 8137.605 | 0 | 1074.116 | 1074.116 | 0 | 0 | 0 | 9167.627 | 9167.627 | 0
5/6/2026 | 8:45:00 PM | 8166.044 | 8166.044 | 0 | 1077.441 | 1077.441 | 0 | 0 | 0 | 9198.458 | 9198.458 | 0
5/6/2026 | 9:00:00 PM | 8193.912 | 8193.912 | 0 | 1080.758 | 1080.758 | 0 | 0 | 0 | 9228.759 | 9228.759 | 0
5/6/2026 | 9:15:00 PM | 8221.64 | 8221.64 | 0 | 1084.083 | 1084.083 | 0 | 0 | 0 | 9258.932 | 9258.932 | 0
5/6/2026 | 9:30:00 PM | 8249.382 | 8249.382 | 0 | 1087.393 | 1087.393 | 0 | 0 | 0 | 9289.104 | 9289.104 | 0
5/6/2026 | 9:45:00 PM | 8277.04 | 8277.04 | 0 | 1090.694 | 1090.694 | 0 | 0 | 0 | 9319.204 | 9319.204 | 0
5/6/2026 | 10:00:00 PM | 8305.376 | 8305.376 | 0 | 1094.03 | 1094.03 | 0 | 0 | 0 | 9349.96 | 9349.96 | 0
5/6/2026 | 10:15:00 PM | 8335.387 | 8335.387 | 0 | 1097.496 | 1097.496 | 0 | 0 | 0 | 9382.378 | 9382.378 | 0
5/6/2026 | 10:30:00 PM | 8361.764 | 8361.764 | 0 | 1100.699 | 1100.699 | 0 | 0 | 0 | 9411.134 | 9411.134 | 0
5/6/2026 | 10:45:00 PM | 8384.434 | 8384.434 | 0 | 1103.409 | 1103.409 | 0 | 0 | 0 | 9435.891 | 9435.891 | 0
5/6/2026 | 11:00:00 PM | 8406.671 | 8406.671 | 0 | 1106.062 | 1106.062 | 0 | 0 | 0 | 9460.191 | 9460.191 | 0
5/6/2026 | 11:15:00 PM | 8428.548 | 8428.548 | 0 | 1108.682 | 1108.682 | 0 | 0 | 0 | 9484.082 | 9484.082 | 0
5/6/2026 | 11:30:00 PM | 8450.192 | 8450.192 | 0 | 1111.299 | 1111.299 | 0 | 0 | 0 | 9507.747 | 9507.747 | 0
5/6/2026 | 11:45:00 PM | 8471.828 | 8471.828 | 0 | 1113.913 | 1113.913 | 0 | 0 | 0 | 9531.415 | 9531.415 | 0
5/7/2026 | 12:00:00 AM | 8493.474 | 8493.474 | 0 | 1116.537 | 1116.537 | 0 | 0 | 0 | 9555.098 | 9555.098 | 0
5/7/2026 | 12:15:00 AM | 8515.122 | 8515.122 | 0 | 1119.168 | 1119.168 | 0 | 0 | 0 | 9578.794 | 9578.794 | 0
5/7/2026 | 12:30:00 AM | 8536.464 | 8536.464 | 0 | 1121.741 | 1121.741 | 0 | 0 | 0 | 9602.125 | 9602.125 | 0
5/7/2026 | 12:45:00 AM | 8557.834 | 8557.834 | 0 | 1124.368 | 1124.368 | 0 | 0 | 0 | 9625.555 | 9625.555 | 0
5/7/2026 | 1:00:00 AM | 8579.273 | 8579.273 | 0 | 1127.017 | 1127.017 | 0 | 0 | 0 | 9649.066 | 9649.066 | 0
5/7/2026 | 1:15:00 AM | 8600.673 | 8600.673 | 0 | 1129.662 | 1129.662 | 0 | 0 | 0 | 9672.53 | 9672.53 | 0
5/7/2026 | 1:30:00 AM | 8622.13 | 8622.13 | 0 | 1132.321 | 1132.321 | 0 | 0 | 0 | 9696.054 | 9696.054 | 0
5/7/2026 | 1:45:00 AM | 8645.366 | 8645.366 | 0 | 1135.151 | 1135.151 | 0 | 0 | 0 | 9721.472 | 9721.472 | 0
5/7/2026 | 2:00:00 AM | 8671.763 | 8671.763 | 0 | 1138.363 | 1138.363 | 0 | 0 | 0 | 9750.238 | 9750.238 | 0
5/7/2026 | 2:15:00 AM | 8699.321 | 8699.321 | 0 | 1141.714 | 1141.714 | 0 | 0 | 0 | 9780.204 | 9780.204 | 0
5/7/2026 | 2:30:00 AM | 8727.348 | 8727.348 | 0 | 1145.117 | 1145.117 | 0 | 0 | 0 | 9810.64 | 9810.64 | 0
5/7/2026 | 2:45:00 AM | 8755.822 | 8755.822 | 0 | 1148.601 | 1148.601 | 0 | 0 | 0 | 9841.558 | 9841.558 | 0
5/7/2026 | 3:00:00 AM | 8784.644 | 8784.644 | 0 | 1152.127 | 1152.127 | 0 | 0 | 0 | 9872.829 | 9872.829 | 0
5/7/2026 | 3:15:00 AM | 8813.632 | 8813.632 | 0 | 1155.672 | 1155.672 | 0 | 0 | 0 | 9904.281 | 9904.281 | 0
5/7/2026 | 3:30:00 AM | 8858.746 | 8858.746 | 0 | 1171.215 | 1171.215 | 0 | 0 | 0 | 9953.515 | 9953.515 | 0
5/7/2026 | 3:45:00 AM | 8910.856 | 8910.856 | 0 | 1190.487 | 1190.487 | 0 | 0 | 0 | 10010.305 | 10010.305 | 0
5/7/2026 | 4:00:00 AM | 8959.517 | 8959.517 | 0 | 1209.406 | 1209.406 | 0 | 0 | 0 | 10063.602 | 10063.602 | 0
5/7/2026 | 4:15:00 AM | 9005.276 | 9005.276 | 0 | 1227.945 | 1227.945 | 0 | 0 | 0 | 10113.906 | 10113.906 | 0
5/7/2026 | 4:30:00 AM | 9049.845 | 9049.845 | 0 | 1246.32 | 1246.32 | 0 | 0 | 0 | 10162.999 | 10162.999 | 0
5/7/2026 | 4:45:00 AM | 9093.598 | 9093.598 | 0 | 1264.594 | 1264.594 | 0 | 0 | 0 | 10211.283 | 10211.283 | 0
5/7/2026 | 5:00:00 AM | 9137.16 | 9137.16 | 0 | 1282.855 | 1282.855 | 0 | 0 | 0 | 10259.385 | 10259.385 | 0
5/7/2026 | 5:15:00 AM | 9180.801 | 9180.801 | 0 | 1301.054 | 1301.054 | 0 | 0 | 0 | 10307.523 | 10307.523 | 0
5/7/2026 | 5:30:00 AM | 9224.681 | 9224.681 | 0 | 1319.246 | 1319.246 | 0 | 0 | 0 | 10355.893 | 10355.893 | 0
5/7/2026 | 5:45:00 AM | 9268.389 | 9268.389 | 0 | 1337.324 | 1337.324 | 0 | 0 | 0 | 10404.06 | 10404.06 | 0
5/7/2026 | 6:00:00 AM | 9311.754 | 9311.754 | 0 | 1355.32 | 1355.32 | 0 | 0 | 0 | 10451.857 | 10451.857 | 0
5/7/2026 | 6:15:00 AM | 9355.04 | 9355.04 | 0 | 1373.198 | 1373.198 | 0 | 0 | 0 | 10499.528 | 10499.528 | 0
5/7/2026 | 6:30:00 AM | 9398.355 | 9398.355 | 0 | 1390.967 | 1390.967 | 0 | 0 | 0 | 10547.184 | 10547.184 | 0
5/7/2026 | 6:45:00 AM | 9441.658 | 9441.658 | 0 | 1408.68 | 1408.68 | 0 | 0 | 0 | 10594.806 | 10594.806 | 0
5/7/2026 | 7:00:00 AM | 9484.928 | 9484.928 | 0 | 1426.389 | 1426.389 | 0 | 0 | 0 | 10642.388 | 10642.388 | 0
5/7/2026 | 7:15:00 AM | 9528.601 | 9528.601 | 0 | 1444.213 | 1444.213 | 0 | 0 | 0 | 10690.413 | 10690.413 | 0
5/7/2026 | 7:30:00 AM | 9572.55 | 9572.55 | 0 | 1462.122 | 1462.122 | 0 | 0 | 0 | 10738.743 | 10738.743 | 0
5/7/2026 | 7:45:00 AM | 9615.798 | 9615.798 | 0 | 1479.929 | 1479.929 | 0 | 0 | 0 | 10786.345 | 10786.345 | 0
5/7/2026 | 8:00:00 AM | 9658.455 | 9658.455 | 0 | 1497.649 | 1497.649 | 0 | 0 | 0 | 10833.344 | 10833.344 | 0
5/7/2026 | 8:15:00 AM | 9701.138 | 9701.138 | 0 | 1515.34 | 1515.34 | 0 | 0 | 0 | 10880.352 | 10880.352 | 0
5/7/2026 | 8:30:00 AM | 9743.728 | 9743.728 | 0 | 1532.989 | 1532.989 | 0 | 0 | 0 | 10927.254 | 10927.254 | 0
5/7/2026 | 8:45:00 AM | 9786.171 | 9786.171 | 0 | 1550.704 | 1550.704 | 0 | 0 | 0 | 10974.048 | 10974.048 | 0
5/7/2026 | 9:00:00 AM | 9828.484 | 9828.484 | 0 | 1568.371 | 1568.371 | 0 | 0 | 0 | 11020.69 | 11020.69 | 0
5/7/2026 | 9:15:00 AM | 9870.8 | 9870.8 | 0 | 1586.006 | 1586.006 | 0 | 0 | 0 | 11067.331 | 11067.331 | 0
5/7/2026 | 9:30:00 AM | 9913.135 | 9913.135 | 0 | 1603.607 | 1603.607 | 0 | 0 | 0 | 11113.981 | 11113.981 | 0
5/7/2026 | 9:45:00 AM | 9955.424 | 9955.424 | 0 | 1621.191 | 1621.191 | 0 | 0 | 0 | 11160.588 | 11160.588 | 0
5/7/2026 | 10:00:00 AM | 9997.814 | 9997.814 | 0 | 1638.765 | 1638.765 | 0 | 0 | 0 | 11207.293 | 11207.293 | 0
5/7/2026 | 10:15:00 AM | 10040.304 | 10040.304 | 0 | 1656.33 | 1656.33 | 0 | 0 | 0 | 11254.1 | 11254.1 | 0
5/7/2026 | 10:30:00 AM | 10082.927 | 10082.927 | 0 | 1673.912 | 1673.912 | 0 | 0 | 0 | 11301.051 | 11301.051 | 0
5/7/2026 | 10:45:00 AM | 10125.592 | 10125.592 | 0 | 1691.469 | 1691.469 | 0 | 0 | 0 | 11348.026 | 11348.026 | 0
5/7/2026 | 11:00:00 AM | 10168.496 | 10168.496 | 0 | 1709.027 | 1709.027 | 0 | 0 | 0 | 11395.23 | 11395.23 | 0
5/7/2026 | 11:15:00 AM | 10211.872 | 10211.872 | 0 | 1726.681 | 1726.681 | 0 | 0 | 0 | 11442.935 | 11442.935 | 0
5/7/2026 | 11:30:00 AM | 10255.659 | 10255.659 | 0 | 1744.46 | 1744.46 | 0 | 0 | 0 | 11491.101 | 11491.101 | 0
5/7/2026 | 11:45:00 AM | 10299.662 | 10299.662 | 0 | 1762.322 | 1762.322 | 0 | 0 | 0 | 11539.505 | 11539.505 | 0
5/7/2026 | 12:00:00 PM | 10343.685 | 10343.685 | 0 | 1780.168 | 1780.168 | 0 | 0 | 0 | 11587.922 | 11587.922 | 0
5/7/2026 | 12:15:00 PM | 10387.333 | 10387.333 | 0 | 1797.932 | 1797.932 | 0 | 0 | 0 | 11635.954 | 11635.954 | 0
5/7/2026 | 12:30:00 PM | 10430.697 | 10430.697 | 0 | 1815.655 | 1815.655 | 0 | 0 | 0 | 11683.689 | 11683.689 | 0
5/7/2026 | 12:45:00 PM | 10473.697 | 10473.697 | 0 | 1833.326 | 1833.326 | 0 | 0 | 0 | 11731.06 | 11731.06 | 0
5/7/2026 | 1:00:00 PM | 10516.571 | 10516.571 | 0 | 1850.976 | 1850.976 | 0 | 0 | 0 | 11778.301 | 11778.301 | 0
5/7/2026 | 1:15:00 PM | 10559.492 | 10559.492 | 0 | 1868.633 | 1868.633 | 0 | 0 | 0 | 11825.59 | 11825.59 | 0
5/7/2026 | 1:30:00 PM | 10602.222 | 10602.222 | 0 | 1886.221 | 1886.221 | 0 | 0 | 0 | 11872.674 | 11872.674 | 0
5/7/2026 | 1:45:00 PM | 10644.732 | 10644.732 | 0 | 1903.812 | 1903.812 | 0 | 0 | 0 | 11919.541 | 11919.541 | 0
5/7/2026 | 2:00:00 PM | 10686.862 | 10686.862 | 0 | 1921.365 | 1921.365 | 0 | 0 | 0 | 11966.017 | 11966.017 | 0
5/7/2026 | 2:15:00 PM | 10728.215 | 10728.215 | 0 | 1938.848 | 1938.848 | 0 | 0 | 0 | 12011.703 | 12011.703 | 0
5/7/2026 | 2:30:00 PM | 10769.549 | 10769.549 | 0 | 1956.344 | 1956.344 | 0 | 0 | 0 | 12057.378 | 12057.378 | 0
5/7/2026 | 2:45:00 PM | 10810.805 | 10810.805 | 0 | 1973.807 | 1973.807 | 0 | 0 | 0 | 12102.967 | 12102.967 | 0
5/7/2026 | 3:00:00 PM | 10851.288 | 10851.288 | 0 | 1991.099 | 1991.099 | 0 | 0 | 0 | 12147.734 | 12147.734 | 0
5/7/2026 | 3:15:00 PM | 10891.468 | 10891.468 | 0 | 2008.356 | 2008.356 | 0 | 0 | 0 | 12192.197 | 12192.197 | 0
5/7/2026 | 3:30:00 PM | 10931.901 | 10931.901 | 0 | 2025.722 | 2025.722 | 0 | 0 | 0 | 12236.952 | 12236.952 | 0
5/7/2026 | 3:45:00 PM | 10972.244 | 10972.244 | 0 | 2043.113 | 2043.113 | 0 | 0 | 0 | 12281.643 | 12281.643 | 0
5/7/2026 | 4:00:00 PM | 11012.316 | 11012.316 | 0 | 2060.421 | 2060.421 | 0 | 0 | 0 | 12326.049 | 12326.049 | 0
5/7/2026 | 4:15:00 PM | 11051.719 | 11051.719 | 0 | 2077.634 | 2077.634 | 0 | 0 | 0 | 12369.751 | 12369.751 | 0
5/7/2026 | 4:30:00 PM | 11090.907 | 11090.907 | 0 | 2094.796 | 2094.796 | 0 | 0 | 0 | 12413.222 | 12413.222 | 0
5/7/2026 | 4:45:00 PM | 11130.293 | 11130.293 | 0 | 2112.036 | 2112.036 | 0 | 0 | 0 | 12456.918 | 12456.918 | 0
5/7/2026 | 5:00:00 PM | 11169.549 | 11169.549 | 0 | 2129.254 | 2129.254 | 0 | 0 | 0 | 12500.485 | 12500.485 | 0
5/7/2026 | 5:15:00 PM | 11208.378 | 11208.378 | 0 | 2146.449 | 2146.449 | 0 | 0 | 0 | 12543.618 | 12543.618 | 0
5/7/2026 | 5:30:00 PM | 11247.031 | 11247.031 | 0 | 2163.622 | 2163.622 | 0 | 0 | 0 | 12586.565 | 12586.565 | 0
5/7/2026 | 5:45:00 PM | 11285.629 | 11285.629 | 0 | 2180.824 | 2180.824 | 0 | 0 | 0 | 12629.473 | 12629.473 | 0
5/7/2026 | 6:00:00 PM | 11323.981 | 11323.981 | 0 | 2198.018 | 2198.018 | 0 | 0 | 0 | 12672.147 | 12672.147 | 0
5/7/2026 | 6:15:00 PM | 11362.297 | 11362.297 | 0 | 2215.319 | 2215.319 | 0 | 0 | 0 | 12714.856 | 12714.856 | 0
5/7/2026 | 6:30:00 PM | 11400.54 | 11400.54 | 0 | 2232.64 | 2232.64 | 0 | 0 | 0 | 12757.504 | 12757.504 | 0
5/7/2026 | 6:45:00 PM | 11438.753 | 11438.753 | 0 | 2249.979 | 2249.979 | 0 | 0 | 0 | 12800.136 | 12800.136 | 0
5/7/2026 | 7:00:00 PM | 11476.877 | 11476.877 | 0 | 2267.327 | 2267.327 | 0 | 0 | 0 | 12842.688 | 12842.688 | 0
5/7/2026 | 7:15:00 PM | 11503.358 | 11503.358 | 0 | 2276.016 | 2276.016 | 0 | 0 | 0 | 12872.229 | 12872.229 | 0
5/7/2026 | 7:30:00 PM | 11522.038 | 11522.038 | 0 | 2278.411 | 2278.411 | 0 | 0 | 0 | 12892.968 | 12892.968 | 0
5/7/2026 | 7:45:00 PM | 11542.096 | 11542.096 | 0 | 2280.997 | 2280.997 | 0 | 0 | 0 | 12915.202 | 12915.202 | 0
5/7/2026 | 8:00:00 PM | 11563.03 | 11563.03 | 0 | 2283.6 | 2283.6 | 0 | 0 | 0 | 12938.262 | 12938.262 | 0
5/7/2026 | 8:15:00 PM | 11584.807 | 11584.807 | 0 | 2286.267 | 2286.267 | 0 | 0 | 0 | 12962.188 | 12962.188 | 0
5/7/2026 | 8:30:00 PM | 11607.386 | 11607.386 | 0 | 2289.001 | 2289.001 | 0 | 0 | 0 | 12986.95 | 12986.95 | 0
5/7/2026 | 8:45:00 PM | 11630.686 | 11630.686 | 0 | 2291.796 | 2291.796 | 0 | 0 | 0 | 13012.484 | 13012.484 | 0
5/7/2026 | 9:00:00 PM | 11654.63 | 11654.63 | 0 | 2294.647 | 2294.647 | 0 | 0 | 0 | 13038.681 | 13038.681 | 0
5/7/2026 | 9:15:00 PM | 11678.955 | 11678.955 | 0 | 2297.526 | 2297.526 | 0 | 0 | 0 | 13065.244 | 13065.244 | 0
5/7/2026 | 9:30:00 PM | 11703.507 | 11703.507 | 0 | 2300.401 | 2300.401 | 0 | 0 | 0 | 13092.03 | 13092.03 | 0
5/7/2026 | 9:45:00 PM | 11728.117 | 11728.117 | 0 | 2303.287 | 2303.287 | 0 | 0 | 0 | 13118.883 | 13118.883 | 0
5/7/2026 | 10:00:00 PM | 11753.179 | 11753.179 | 0 | 2306.22 | 2306.22 | 0 | 0 | 0 | 13146.175 | 13146.175 | 0
5/7/2026 | 10:15:00 PM | 11778.388 | 11778.388 | 0 | 2309.171 | 2309.171 | 0 | 0 | 0 | 13173.629 | 13173.629 | 0
5/7/2026 | 10:30:00 PM | 11803.156 | 11803.156 | 0 | 2312.087 | 2312.087 | 0 | 0 | 0 | 13200.638 | 13200.638 | 0
5/7/2026 | 10:45:00 PM | 11827.413 | 11827.413 | 0 | 2314.949 | 2314.949 | 0 | 0 | 0 | 13227.104 | 13227.104 | 0
5/7/2026 | 11:00:00 PM | 11851.19 | 11851.19 | 0 | 2317.813 | 2317.813 | 0 | 0 | 0 | 13253.153 | 13253.153 | 0
5/7/2026 | 11:15:00 PM | 11874.248 | 11874.248 | 0 | 2320.626 | 2320.626 | 0 | 0 | 0 | 13278.459 | 13278.459 | 0
5/7/2026 | 11:30:00 PM | 11897.064 | 11897.064 | 0 | 2323.425 | 2323.425 | 0 | 0 | 0 | 13303.512 | 13303.512 | 0
5/7/2026 | 11:45:00 PM | 11919.536 | 11919.536 | 0 | 2326.198 | 2326.198 | 0 | 0 | 0 | 13328.224 | 13328.224 | 0
5/8/2026 | 12:00:00 AM | 11941.66 | 11941.66 | 0 | 2328.906 | 2328.906 | 0 | 0 | 0 | 13352.501 | 13352.501 | 0
5/8/2026 | 12:15:00 AM | 11963.842 | 11963.842 | 0 | 2331.665 | 2331.665 | 0 | 0 | 0 | 13376.887 | 13376.887 | 0
5/8/2026 | 12:30:00 AM | 11985.612 | 11985.612 | 0 | 2334.374 | 2334.374 | 0 | 0 | 0 | 13400.834 | 13400.834 | 0
5/8/2026 | 12:45:00 AM | 12006.921 | 12006.921 | 0 | 2337.029 | 2337.029 | 0 | 0 | 0 | 13424.279 | 13424.279 | 0
5/8/2026 | 1:00:00 AM | 12027.673 | 12027.673 | 0 | 2339.626 | 2339.626 | 0 | 0 | 0 | 13447.146 | 13447.146 | 0
5/8/2026 | 1:15:00 AM | 12047.917 | 12047.917 | 0 | 2342.179 | 2342.179 | 0 | 0 | 0 | 13469.522 | 13469.522 | 0
5/8/2026 | 1:30:00 AM | 12067.388 | 12067.388 | 0 | 2344.621 | 2344.621 | 0 | 0 | 0 | 13491.047 | 13491.047 | 0
5/8/2026 | 1:45:00 AM | 12086.344 | 12086.344 | 0 | 2347.017 | 2347.017 | 0 | 0 | 0 | 13512.051 | 13512.051 | 0
5/8/2026 | 2:00:00 AM | 12104.576 | 12104.576 | 0 | 2349.358 | 2349.358 | 0 | 0 | 0 | 13532.36 | 13532.36 | 0
5/8/2026 | 2:15:00 AM | 12122.13 | 12122.13 | 0 | 2351.595 | 2351.595 | 0 | 0 | 0 | 13551.908 | 13551.908 | 0
5/8/2026 | 2:30:00 AM | 12139.483 | 12139.483 | 0 | 2353.864 | 2353.864 | 0 | 0 | 0 | 13571.363 | 13571.363 | 0
5/8/2026 | 2:45:00 AM | 12156.15 | 12156.15 | 0 | 2356.029 | 2356.029 | 0 | 0 | 0 | 13590.044 | 13590.044 | 0
5/8/2026 | 3:00:00 AM | 12172.646 | 12172.646 | 0 | 2358.203 | 2358.203 | 0 | 0 | 0 | 13608.608 | 13608.608 | 0
5/8/2026 | 3:15:00 AM | 12188.823 | 12188.823 | 0 | 2360.332 | 2360.332 | 0 | 0 | 0 | 13626.813 | 13626.813 | 0
5/8/2026 | 3:30:00 AM | 12204.822 | 12204.822 | 0 | 2362.441 | 2362.441 | 0 | 0 | 0 | 13644.83 | 13644.83 | 0
5/8/2026 | 3:45:00 AM | 12220.765 | 12220.765 | 0 | 2364.564 | 2364.564 | 0 | 0 | 0 | 13662.827 | 13662.827 | 0
5/8/2026 | 4:00:00 AM | 12236.158 | 12236.158 | 0 | 2366.586 | 2366.586 | 0 | 0 | 0 | 13680.164 | 13680.164 | 0
5/8/2026 | 4:15:00 AM | 12251.772 | 12251.772 | 0 | 2368.683 | 2368.683 | 0 | 0 | 0 | 13697.837 | 13697.837 | 0
5/8/2026 | 4:30:00 AM | 12266.774 | 12266.774 | 0 | 2370.665 | 2370.665 | 0 | 0 | 0 | 13714.769 | 13714.769 | 0
5/8/2026 | 4:45:00 AM | 12281.734 | 12281.734 | 0 | 2372.679 | 2372.679 | 0 | 0 | 0 | 13731.728 | 13731.728 | 0
5/8/2026 | 5:00:00 AM | 12296.263 | 12296.263 | 0 | 2374.619 | 2374.619 | 0 | 0 | 0 | 13748.187 | 13748.187 | 0
5/8/2026 | 5:15:00 AM | 12310.844 | 12310.844 | 0 | 2376.561 | 2376.561 | 0 | 0 | 0 | 13764.686 | 13764.686 | 0
5/8/2026 | 5:30:00 AM | 12325.014 | 12325.014 | 0 | 2378.438 | 2378.438 | 0 | 0 | 0 | 13780.697 | 13780.697 | 0
5/8/2026 | 5:45:00 AM | 12338.912 | 12338.912 | 0 | 2380.285 | 2380.285 | 0 | 0 | 0 | 13796.435 | 13796.435 | 0
5/8/2026 | 6:00:00 AM | 12352.598 | 12352.598 | 0 | 2382.101 | 2382.101 | 0 | 0 | 0 | 13811.937 | 13811.937 | 0
5/8/2026 | 6:15:00 AM | 12366.144 | 12366.144 | 0 | 2383.892 | 2383.892 | 0 | 0 | 0 | 13827.275 | 13827.275 | 0
5/8/2026 | 6:30:00 AM | 12379.73 | 12379.73 | 0 | 2385.682 | 2385.682 | 0 | 0 | 0 | 13842.665 | 13842.665 | 0
5/8/2026 | 6:45:00 AM | 12392.98 | 12392.98 | 0 | 2387.445 | 2387.445 | 0 | 0 | 0 | 13857.719 | 13857.719 | 0
5/8/2026 | 7:00:00 AM | 12406.203 | 12406.203 | 0 | 2389.204 | 2389.204 | 0 | 0 | 0 | 13872.746 | 13872.746 | 0
5/8/2026 | 7:15:00 AM | 12419.048 | 12419.048 | 0 | 2390.895 | 2390.895 | 0 | 0 | 0 | 13887.317 | 13887.317 | 0
5/8/2026 | 7:30:00 AM | 12431.793 | 12431.793 | 0 | 2392.572 | 2392.572 | 0 | 0 | 0 | 13901.76 | 13901.76 | 0
5/8/2026 | 7:45:00 AM | 12444.456 | 12444.456 | 0 | 2394.249 | 2394.249 | 0 | 0 | 0 | 13916.136 | 13916.136 | 0
5/8/2026 | 8:00:00 AM | 12457.192 | 12457.192 | 0 | 2395.956 | 2395.956 | 0 | 0 | 0 | 13930.64 | 13930.64 | 0
5/8/2026 | 8:15:00 AM | 12470.227 | 12470.227 | 0 | 2397.72 | 2397.72 | 0 | 0 | 0 | 13945.51 | 13945.51 | 0
5/8/2026 | 8:30:00 AM | 12483.839 | 12483.839 | 0 | 2399.597 | 2399.597 | 0 | 0 | 0 | 13961.088 | 13961.088 | 0
5/8/2026 | 8:45:00 AM | 12496.902 | 12496.902 | 0 | 2401.348 | 2401.348 | 0 | 0 | 0 | 13975.936 | 13975.936 | 0
5/8/2026 | 9:00:00 AM | 12510.192 | 12510.192 | 0 | 2403.152 | 2403.152 | 0 | 0 | 0 | 13991.099 | 13991.099 | 0
5/8/2026 | 9:15:00 AM | 12523.824 | 12523.824 | 0 | 2405.034 | 2405.034 | 0 | 0 | 0 | 14006.698 | 14006.698 | 0
5/8/2026 | 9:30:00 AM | 12537.064 | 12537.064 | 0 | 2406.822 | 2406.822 | 0 | 0 | 0 | 14021.755 | 14021.755 | 0
5/8/2026 | 9:45:00 AM | 12550.96 | 12550.96 | 0 | 2408.764 | 2408.764 | 0 | 0 | 0 | 14037.691 | 14037.691 | 0
5/8/2026 | 10:00:00 AM | 12564.632 | 12564.632 | 0 | 2410.65 | 2410.65 | 0 | 0 | 0 | 14053.306 | 14053.306 | 0
5/8/2026 | 10:15:00 AM | 12578.727 | 12578.727 | 0 | 2412.609 | 2412.609 | 0 | 0 | 0 | 14069.431 | 14069.431 | 0
5/8/2026 | 10:30:00 AM | 12592.856 | 12592.856 | 0 | 2414.561 | 2414.561 | 0 | 0 | 0 | 14085.554 | 14085.554 | 0
5/8/2026 | 10:45:00 AM | 12607.402 | 12607.402 | 0 | 2416.566 | 2416.566 | 0 | 0 | 0 | 14102.116 | 14102.116 | 0
5/8/2026 | 11:00:00 AM | 12622.312 | 12622.312 | 0 | 2418.628 | 2418.628 | 0 | 0 | 0 | 14119.086 | 14119.086 | 0
5/8/2026 | 11:15:00 AM | 12637.072 | 12637.072 | 0 | 2420.627 | 2420.627 | 0 | 0 | 0 | 14135.806 | 14135.806 | 0
5/8/2026 | 11:30:00 AM | 12652.283 | 12652.283 | 0 | 2422.724 | 2422.724 | 0 | 0 | 0 | 14153.085 | 14153.085 | 0
5/8/2026 | 11:45:00 AM | 12667.444 | 12667.444 | 0 | 2424.802 | 2424.802 | 0 | 0 | 0 | 14170.287 | 14170.287 | 0
5/8/2026 | 12:00:00 PM | 12682.539 | 12682.539 | 0 | 2426.853 | 2426.853 | 0 | 0 | 0 | 14187.385 | 14187.385 | 0
5/8/2026 | 12:15:00 PM | 12697.824 | 12697.824 | 0 | 2428.951 | 2428.951 | 0 | 0 | 0 | 14204.731 | 14204.731 | 0
5/8/2026 | 12:30:00 PM | 12712.95 | 12712.95 | 0 | 2431.01 | 2431.01 | 0 | 0 | 0 | 14221.879 | 14221.879 | 0
5/8/2026 | 12:45:00 PM | 12728.222 | 12728.222 | 0 | 2433.1 | 2433.1 | 0 | 0 | 0 | 14239.2 | 14239.2 | 0
5/8/2026 | 1:00:00 PM | 12743.849 | 12743.849 | 0 | 2435.243 | 2435.243 | 0 | 0 | 0 | 14256.906 | 14256.906 | 0
5/8/2026 | 1:15:00 PM | 12759.31 | 12759.31 | 0 | 2437.339 | 2437.339 | 0 | 0 | 0 | 14274.379 | 14274.379 | 0
5/8/2026 | 1:30:00 PM | 12775.275 | 12775.275 | 0 | 2439.507 | 2439.507 | 0 | 0 | 0 | 14292.419 | 14292.419 | 0
5/8/2026 | 1:45:00 PM | 12791.298 | 12791.298 | 0 | 2441.681 | 2441.681 | 0 | 0 | 0 | 14310.528 | 14310.528 | 0
5/8/2026 | 2:00:00 PM | 12807.821 | 12807.821 | 0 | 2443.859 | 2443.859 | 0 | 0 | 0 | 14329.048 | 14329.048 | 0
5/8/2026 | 2:15:00 PM | 12824.606 | 12824.606 | 0 | 2446.082 | 2446.082 | 0 | 0 | 0 | 14347.868 | 14347.868 | 0
5/8/2026 | 2:30:00 PM | 12841.541 | 12841.541 | 0 | 2448.334 | 2448.334 | 0 | 0 | 0 | 14366.862 | 14366.862 | 0
5/8/2026 | 2:45:00 PM | 12858.547 | 12858.547 | 0 | 2450.603 | 2450.603 | 0 | 0 | 0 | 14385.954 | 14385.954 | 0
5/8/2026 | 3:00:00 PM | 12875.502 | 12875.502 | 0 | 2452.858 | 2452.858 | 0 | 0 | 0 | 14404.964 | 14404.964 | 0
5/8/2026 | 3:15:00 PM | 12892.527 | 12892.527 | 0 | 2455.121 | 2455.121 | 0 | 0 | 0 | 14424.041 | 14424.041 | 0
5/8/2026 | 3:30:00 PM | 12909.66 | 12909.66 | 0 | 2457.399 | 2457.399 | 0 | 0 | 0 | 14443.251 | 14443.251 | 0
5/8/2026 | 3:45:00 PM | 12927.049 | 12927.049 | 0 | 2459.711 | 2459.711 | 0 | 0 | 0 | 14462.73 | 14462.73 | 0
5/8/2026 | 4:00:00 PM | 12944.492 | 12944.492 | 0 | 2462.028 | 2462.028 | 0 | 0 | 0 | 14482.271 | 14482.271 | 0
5/8/2026 | 4:15:00 PM | 12962.082 | 12962.082 | 0 | 2464.323 | 2464.323 | 0 | 0 | 0 | 14501.882 | 14501.882 | 0
5/8/2026 | 4:30:00 PM | 12979.829 | 12979.829 | 0 | 2466.632 | 2466.632 | 0 | 0 | 0 | 14521.656 | 14521.656 | 0
5/8/2026 | 4:45:00 PM | 12997.875 | 12997.875 | 0 | 2468.979 | 2468.979 | 0 | 0 | 0 | 14541.751 | 14541.751 | 0
5/8/2026 | 5:00:00 PM | 13016.127 | 13016.127 | 0 | 2471.358 | 2471.358 | 0 | 0 | 0 | 14562.078 | 14562.078 | 0
5/8/2026 | 5:15:00 PM | 13034.615 | 13034.615 | 0 | 2473.757 | 2473.757 | 0 | 0 | 0 | 14582.628 | 14582.628 | 0
5/8/2026 | 5:30:00 PM | 13053.611 | 13053.611 | 0 | 2476.199 | 2476.199 | 0 | 0 | 0 | 14603.687 | 14603.687 | 0
5/8/2026 | 5:45:00 PM | 13072.923 | 13072.923 | 0 | 2478.679 | 2478.679 | 0 | 0 | 0 | 14625.078 | 14625.078 | 0
5/8/2026 | 6:00:00 PM | 13092.437 | 13092.437 | 0 | 2481.19 | 2481.19 | 0 | 0 | 0 | 14646.683 | 14646.683 | 0
5/8/2026 | 6:15:00 PM | 13113.191 | 13113.191 | 0 | 2483.816 | 2483.816 | 0 | 0 | 0 | 14669.566 | 14669.566 | 0
5/8/2026 | 6:30:00 PM | 13134.317 | 13134.317 | 0 | 2486.476 | 2486.476 | 0 | 0 | 0 | 14692.84 | 14692.84 | 0
5/8/2026 | 6:45:00 PM | 13155.633 | 13155.633 | 0 | 2489.148 | 2489.148 | 0 | 0 | 0 | 14716.311 | 14716.311 | 0
5/8/2026 | 7:00:00 PM | 13177.206 | 13177.206 | 0 | 2491.852 | 2491.852 | 0 | 0 | 0 | 14740.073 | 14740.073 | 0
5/8/2026 | 7:15:00 PM | 13199.094 | 13199.094 | 0 | 2494.591 | 2494.591 | 0 | 0 | 0 | 14764.186 | 14764.186 | 0
5/8/2026 | 7:30:00 PM | 13221.52 | 13221.52 | 0 | 2497.373 | 2497.373 | 0 | 0 | 0 | 14788.864 | 14788.864 | 0
5/8/2026 | 7:45:00 PM | 13244.314 | 13244.314 | 0 | 2500.185 | 2500.185 | 0 | 0 | 0 | 14813.94 | 14813.94 | 0
5/8/2026 | 8:00:00 PM | 13267.474 | 13267.474 | 0 | 2503.028 | 2503.028 | 0 | 0 | 0 | 14839.396 | 14839.396 | 0
5/8/2026 | 8:15:00 PM | 13290.651 | 13290.651 | 0 | 2505.861 | 2505.861 | 0 | 0 | 0 | 14864.862 | 14864.862 | 0
5/8/2026 | 8:30:00 PM | 13313.801 | 13313.801 | 0 | 2508.693 | 2508.693 | 0 | 0 | 0 | 14890.312 | 14890.312 | 0
5/8/2026 | 8:45:00 PM | 13336.903 | 13336.903 | 0 | 2511.506 | 2511.506 | 0 | 0 | 0 | 14915.705 | 14915.705 | 0
5/8/2026 | 9:00:00 PM | 13359.747 | 13359.747 | 0 | 2514.273 | 2514.273 | 0 | 0 | 0 | 14940.805 | 14940.805 | 0
5/8/2026 | 9:15:00 PM | 13382.615 | 13382.615 | 0 | 2517.044 | 2517.044 | 0 | 0 | 0 | 14965.911 | 14965.911 | 0
5/8/2026 | 9:30:00 PM | 13405.381 | 13405.381 | 0 | 2519.802 | 2519.802 | 0 | 0 | 0 | 14990.909 | 14990.909 | 0
5/8/2026 | 9:45:00 PM | 13428.108 | 13428.108 | 0 | 2522.575 | 2522.575 | 0 | 0 | 0 | 15015.883 | 15015.883 | 0
5/8/2026 | 10:00:00 PM | 13450.742 | 13450.742 | 0 | 2525.336 | 2525.336 | 0 | 0 | 0 | 15040.753 | 15040.753 | 0
5/8/2026 | 10:15:00 PM | 13473.332 | 13473.332 | 0 | 2528.107 | 2528.107 | 0 | 0 | 0 | 15065.599 | 15065.599 | 0
5/8/2026 | 10:30:00 PM | 13496.697 | 13496.697 | 0 | 2530.941 | 2530.941 | 0 | 0 | 0 | 15091.183 | 15091.183 | 0
5/8/2026 | 10:45:00 PM | 13519.565 | 13519.565 | 0 | 2533.697 | 2533.697 | 0 | 0 | 0 | 15116.195 | 15116.195 | 0
5/8/2026 | 11:00:00 PM | 13542.56 | 13542.56 | 0 | 2536.508 | 2536.508 | 0 | 0 | 0 | 15141.397 | 15141.397 | 0
5/8/2026 | 11:15:00 PM | 13565.286 | 13565.286 | 0 | 2539.299 | 2539.299 | 0 | 0 | 0 | 15166.348 | 15166.348 | 0
5/8/2026 | 11:30:00 PM | 13587.782 | 13587.782 | 0 | 2542.081 | 2542.081 | 0 | 0 | 0 | 15191.074 | 15191.074 | 0
5/8/2026 | 11:45:00 PM | 13609.724 | 13609.724 | 0 | 2544.768 | 2544.768 | 0 | 0 | 0 | 15215.144 | 15215.144 | 0
5/9/2026 | 12:00:00 AM | 13631.697 | 13631.697 | 0 | 2547.5 | 2547.5 | 0 | 0 | 0 | 15239.3 | 15239.3 | 0
5/9/2026 | 12:15:00 AM | 13653.447 | 13653.447 | 0 | 2550.226 | 2550.226 | 0 | 0 | 0 | 15263.241 | 15263.241 | 0
5/9/2026 | 12:30:00 AM | 13675.012 | 13675.012 | 0 | 2552.932 | 2552.932 | 0 | 0 | 0 | 15286.987 | 15286.987 | 0
5/9/2026 | 12:45:00 AM | 13696.191 | 13696.191 | 0 | 2555.559 | 2555.559 | 0 | 0 | 0 | 15310.252 | 15310.252 | 0
5/9/2026 | 1:00:00 AM | 13717.585 | 13717.585 | 0 | 2558.252 | 2558.252 | 0 | 0 | 0 | 15333.821 | 15333.821 | 0
5/9/2026 | 1:15:00 AM | 13738.875 | 13738.875 | 0 | 2560.935 | 2560.935 | 0 | 0 | 0 | 15357.27 | 15357.27 | 0
5/9/2026 | 1:30:00 AM | 13760.188 | 13760.188 | 0 | 2563.623 | 2563.623 | 0 | 0 | 0 | 15380.744 | 15380.744 | 0
5/9/2026 | 1:45:00 AM | 13781.132 | 13781.132 | 0 | 2566.234 | 2566.234 | 0 | 0 | 0 | 15403.766 | 15403.766 | 0
5/9/2026 | 2:00:00 AM | 13802.353 | 13802.353 | 0 | 2568.907 | 2568.907 | 0 | 0 | 0 | 15427.138 | 15427.138 | 0
5/9/2026 | 2:15:00 AM | 13823.662 | 13823.662 | 0 | 2571.603 | 2571.603 | 0 | 0 | 0 | 15450.61 | 15450.61 | 0
5/9/2026 | 2:30:00 AM | 13845.108 | 13845.108 | 0 | 2574.304 | 2574.304 | 0 | 0 | 0 | 15474.217 | 15474.217 | 0
5/9/2026 | 2:45:00 AM | 13866.681 | 13866.681 | 0 | 2576.991 | 2576.991 | 0 | 0 | 0 | 15497.898 | 15497.898 | 0
5/9/2026 | 3:00:00 AM | 13888.211 | 13888.211 | 0 | 2579.69 | 2579.69 | 0 | 0 | 0 | 15521.579 | 15521.579 | 0
5/9/2026 | 3:15:00 AM | 13909.787 | 13909.787 | 0 | 2582.407 | 2582.407 | 0 | 0 | 0 | 15545.323 | 15545.323 | 0
5/9/2026 | 3:30:00 AM | 13931.36 | 13931.36 | 0 | 2585.122 | 2585.122 | 0 | 0 | 0 | 15569.073 | 15569.073 | 0
5/9/2026 | 3:45:00 AM | 13952.48 | 13952.48 | 0 | 2587.752 | 2587.752 | 0 | 0 | 0 | 15592.28 | 15592.28 | 0
5/9/2026 | 4:00:00 AM | 13973.722 | 13973.722 | 0 | 2590.434 | 2590.434 | 0 | 0 | 0 | 15615.689 | 15615.689 | 0
5/9/2026 | 4:15:00 AM | 13994.956 | 13994.956 | 0 | 2593.123 | 2593.123 | 0 | 0 | 0 | 15639.097 | 15639.097 | 0
5/9/2026 | 4:30:00 AM | 14016.063 | 14016.063 | 0 | 2595.781 | 2595.781 | 0 | 0 | 0 | 15662.347 | 15662.347 | 0
5/9/2026 | 4:45:00 AM | 14037.032 | 14037.032 | 0 | 2598.409 | 2598.409 | 0 | 0 | 0 | 15685.407 | 15685.407 | 0
5/9/2026 | 5:00:00 AM | 14058.19 | 14058.19 | 0 | 2601.095 | 2601.095 | 0 | 0 | 0 | 15708.729 | 15708.729 | 0
5/9/2026 | 5:15:00 AM | 14079.367 | 14079.367 | 0 | 2603.772 | 2603.772 | 0 | 0 | 0 | 15732.054 | 15732.054 | 0
5/9/2026 | 5:30:00 AM | 14100.485 | 14100.485 | 0 | 2606.434 | 2606.434 | 0 | 0 | 0 | 15755.29 | 15755.29 | 0
5/9/2026 | 5:45:00 AM | 14121.349 | 14121.349 | 0 | 2609.039 | 2609.039 | 0 | 0 | 0 | 15778.216 | 15778.216 | 0
5/9/2026 | 6:00:00 AM | 14142.462 | 14142.462 | 0 | 2611.7 | 2611.7 | 0 | 0 | 0 | 15801.447 | 15801.447 | 0
5/9/2026 | 6:15:00 AM | 14163.627 | 14163.627 | 0 | 2614.36 | 2614.36 | 0 | 0 | 0 | 15824.721 | 15824.721 | 0
5/9/2026 | 6:30:00 AM | 14184.78 | 14184.78 | 0 | 2617.019 | 2617.019 | 0 | 0 | 0 | 15847.982 | 15847.982 | 0
5/9/2026 | 6:45:00 AM | 14205.832 | 14205.832 | 0 | 2619.64 | 2619.64 | 0 | 0 | 0 | 15871.074 | 15871.074 | 0
5/9/2026 | 7:00:00 AM | 14227.379 | 14227.379 | 0 | 2622.342 | 2622.342 | 0 | 0 | 0 | 15894.727 | 15894.727 | 0
5/9/2026 | 7:15:00 AM | 14248.922 | 14248.922 | 0 | 2625.038 | 2625.038 | 0 | 0 | 0 | 15918.375 | 15918.375 | 0
5/9/2026 | 7:30:00 AM | 14270.604 | 14270.604 | 0 | 2627.753 | 2627.753 | 0 | 0 | 0 | 15942.17 | 15942.17 | 0
5/9/2026 | 7:45:00 AM | 14292.481 | 14292.481 | 0 | 2630.492 | 2630.492 | 0 | 0 | 0 | 15966.173 | 15966.173 | 0
5/9/2026 | 8:00:00 AM | 14314.632 | 14314.632 | 0 | 2633.253 | 2633.253 | 0 | 0 | 0 | 15990.464 | 15990.464 | 0
5/9/2026 | 8:15:00 AM | 14337.357 | 14337.357 | 0 | 2636.059 | 2636.059 | 0 | 0 | 0 | 16015.335 | 16015.335 | 0
5/9/2026 | 8:30:00 AM | 14360.653 | 14360.653 | 0 | 2638.905 | 2638.905 | 0 | 0 | 0 | 16040.805 | 16040.805 | 0
5/9/2026 | 8:45:00 AM | 14384.731 | 14384.731 | 0 | 2641.814 | 2641.814 | 0 | 0 | 0 | 16067.066 | 16067.066 | 0
5/9/2026 | 9:00:00 AM | 14409.689 | 14409.689 | 0 | 2644.783 | 2644.783 | 0 | 0 | 0 | 16094.182 | 16094.182 | 0
5/9/2026 | 9:15:00 AM | 14435.104 | 14435.104 | 0 | 2647.795 | 2647.795 | 0 | 0 | 0 | 16121.755 | 16121.755 | 0
5/9/2026 | 9:30:00 AM | 14460.743 | 14460.743 | 0 | 2650.822 | 2650.822 | 0 | 0 | 0 | 16149.551 | 16149.551 | 0
5/9/2026 | 9:45:00 AM | 14486.973 | 14486.973 | 0 | 2653.933 | 2653.933 | 0 | 0 | 0 | 16177.997 | 16177.997 | 0
5/9/2026 | 10:00:00 AM | 14513.095 | 14513.095 | 0 | 2656.987 | 2656.987 | 0 | 0 | 0 | 16206.254 | 16206.254 | 0
5/9/2026 | 10:15:00 AM | 14539.21 | 14539.21 | 0 | 2660.043 | 2660.043 | 0 | 0 | 0 | 16234.512 | 16234.512 | 0
5/9/2026 | 10:30:00 AM | 14565.582 | 14565.582 | 0 | 2663.158 | 2663.158 | 0 | 0 | 0 | 16263.091 | 16263.091 | 0
5/9/2026 | 10:45:00 AM | 14591.685 | 14591.685 | 0 | 2666.213 | 2666.213 | 0 | 0 | 0 | 16291.342 | 16291.342 | 0
5/9/2026 | 11:00:00 AM | 14617.786 | 14617.786 | 0 | 2669.267 | 2669.267 | 0 | 0 | 0 | 16319.598 | 16319.598 | 0
5/9/2026 | 11:15:00 AM | 14644.274 | 14644.274 | 0 | 2672.381 | 2672.381 | 0 | 0 | 0 | 16348.284 | 16348.284 | 0
5/9/2026 | 11:30:00 AM | 14670.662 | 14670.662 | 0 | 2675.458 | 2675.458 | 0 | 0 | 0 | 16376.817 | 16376.817 | 0
5/9/2026 | 11:45:00 AM | 14697.499 | 14697.499 | 0 | 2678.607 | 2678.607 | 0 | 0 | 0 | 16405.869 | 16405.869 | 0
5/9/2026 | 12:00:00 PM | 14724.19 | 14724.19 | 0 | 2681.704 | 2681.704 | 0 | 0 | 0 | 16434.715 | 16434.715 | 0
5/9/2026 | 12:15:00 PM | 14751.451 | 14751.451 | 0 | 2684.889 | 2684.889 | 0 | 0 | 0 | 16464.191 | 16464.191 | 0
5/9/2026 | 12:30:00 PM | 14778.823 | 14778.823 | 0 | 2688.088 | 2688.088 | 0 | 0 | 0 | 16493.803 | 16493.803 | 0
5/9/2026 | 12:45:00 PM | 14805.997 | 14805.997 | 0 | 2691.23 | 2691.23 | 0 | 0 | 0 | 16523.15 | 16523.15 | 0
5/9/2026 | 1:00:00 PM | 14833.386 | 14833.386 | 0 | 2694.427 | 2694.427 | 0 | 0 | 0 | 16552.763 | 16552.763 | 0
5/9/2026 | 1:15:00 PM | 14860.955 | 14860.955 | 0 | 2697.656 | 2697.656 | 0 | 0 | 0 | 16582.587 | 16582.587 | 0
5/9/2026 | 1:30:00 PM | 14888.596 | 14888.596 | 0 | 2700.89 | 2700.89 | 0 | 0 | 0 | 16612.486 | 16612.486 | 0
5/9/2026 | 1:45:00 PM | 14916.061 | 14916.061 | 0 | 2704.067 | 2704.067 | 0 | 0 | 0 | 16642.153 | 16642.153 | 0
5/9/2026 | 2:00:00 PM | 14943.679 | 14943.679 | 0 | 2707.26 | 2707.26 | 0 | 0 | 0 | 16672.002 | 16672.002 | 0
5/9/2026 | 2:15:00 PM | 14971.575 | 14971.575 | 0 | 2710.479 | 2710.479 | 0 | 0 | 0 | 16702.144 | 16702.144 | 0
5/9/2026 | 2:30:00 PM | 14999.789 | 14999.789 | 0 | 2713.728 | 2713.728 | 0 | 0 | 0 | 16732.598 | 16732.598 | 0
5/9/2026 | 2:45:00 PM | 15027.803 | 15027.803 | 0 | 2716.931 | 2716.931 | 0 | 0 | 0 | 16762.81 | 16762.81 | 0
5/9/2026 | 3:00:00 PM | 15056.008 | 15056.008 | 0 | 2720.181 | 2720.181 | 0 | 0 | 0 | 16793.257 | 16793.257 | 0
5/9/2026 | 3:15:00 PM | 15084.191 | 15084.191 | 0 | 2723.425 | 2723.425 | 0 | 0 | 0 | 16823.674 | 16823.674 | 0
5/9/2026 | 3:30:00 PM | 15112.378 | 15112.378 | 0 | 2726.67 | 2726.67 | 0 | 0 | 0 | 16854.102 | 16854.102 | 0
5/9/2026 | 3:45:00 PM | 15140.571 | 15140.571 | 0 | 2729.929 | 2729.929 | 0 | 0 | 0 | 16884.552 | 16884.552 | 0
5/9/2026 | 4:00:00 PM | 15168.777 | 15168.777 | 0 | 2733.182 | 2733.182 | 0 | 0 | 0 | 16915.016 | 16915.016 | 0
5/9/2026 | 4:15:00 PM | 15196.984 | 15196.984 | 0 | 2736.421 | 2736.421 | 0 | 0 | 0 | 16945.465 | 16945.465 | 0
5/9/2026 | 4:30:00 PM | 15225.197 | 15225.197 | 0 | 2739.674 | 2739.674 | 0 | 0 | 0 | 16975.934 | 16975.934 | 0
5/9/2026 | 4:45:00 PM | 15253.514 | 15253.514 | 0 | 2742.961 | 2742.961 | 0 | 0 | 0 | 17006.527 | 17006.527 | 0
5/9/2026 | 5:00:00 PM | 15281.879 | 15281.879 | 0 | 2746.253 | 2746.253 | 0 | 0 | 0 | 17037.176 | 17037.176 | 0
5/9/2026 | 5:15:00 PM | 15310.18 | 15310.18 | 0 | 2749.524 | 2749.524 | 0 | 0 | 0 | 17067.757 | 17067.757 | 0
5/9/2026 | 5:30:00 PM | 15338.602 | 15338.602 | 0 | 2752.829 | 2752.829 | 0 | 0 | 0 | 17098.468 | 17098.468 | 0
5/9/2026 | 5:45:00 PM | 15367.026 | 15367.026 | 0 | 2756.135 | 2756.135 | 0 | 0 | 0 | 17129.177 | 17129.177 | 0
5/9/2026 | 6:00:00 PM | 15395.348 | 15395.348 | 0 | 2759.411 | 2759.411 | 0 | 0 | 0 | 17159.766 | 17159.766 | 0
5/9/2026 | 6:15:00 PM | 15423.624 | 15423.624 | 0 | 2762.672 | 2762.672 | 0 | 0 | 0 | 17190.298 | 17190.298 | 0
5/9/2026 | 6:30:00 PM | 15452.367 | 15452.367 | 0 | 2765.995 | 2765.995 | 0 | 0 | 0 | 17221.328 | 17221.328 | 0
5/9/2026 | 6:45:00 PM | 15481.543 | 15481.543 | 0 | 2769.359 | 2769.359 | 0 | 0 | 0 | 17252.807 | 17252.807 | 0
5/9/2026 | 7:00:00 PM | 15510.715 | 15510.715 | 0 | 2772.715 | 2772.715 | 0 | 0 | 0 | 17284.271 | 17284.271 | 0
5/9/2026 | 7:15:00 PM | 15539.776 | 15539.776 | 0 | 2776.037 | 2776.037 | 0 | 0 | 0 | 17315.599 | 17315.599 | 0
5/9/2026 | 7:30:00 PM | 15568.834 | 15568.834 | 0 | 2779.366 | 2779.366 | 0 | 0 | 0 | 17346.926 | 17346.926 | 0
5/9/2026 | 7:45:00 PM | 15597.897 | 15597.897 | 0 | 2782.709 | 2782.709 | 0 | 0 | 0 | 17378.277 | 17378.277 | 0
5/9/2026 | 8:00:00 PM | 15640.421 | 15640.421 | 0 | 2795.883 | 2795.883 | 0 | 0 | 0 | 17424.434 | 17424.434 | 0
5/9/2026 | 8:15:00 PM | 15692.46 | 15692.46 | 0 | 2814.631 | 2814.631 | 0 | 0 | 0 | 17480.937 | 17480.937 | 0
5/9/2026 | 8:30:00 PM | 15741.992 | 15741.992 | 0 | 2833.056 | 2833.056 | 0 | 0 | 0 | 17534.936 | 17534.936 | 0
5/9/2026 | 8:45:00 PM | 15787.32 | 15787.32 | 0 | 2850.941 | 2850.941 | 0 | 0 | 0 | 17584.655 | 17584.655 | 0
5/9/2026 | 9:00:00 PM | 15831.197 | 15831.197 | 0 | 2868.616 | 2868.616 | 0 | 0 | 0 | 17632.884 | 17632.884 | 0
5/9/2026 | 9:15:00 PM | 15874.711 | 15874.711 | 0 | 2886.265 | 2886.265 | 0 | 0 | 0 | 17680.774 | 17680.774 | 0
5/9/2026 | 9:30:00 PM | 15918.14 | 15918.14 | 0 | 2903.96 | 2903.96 | 0 | 0 | 0 | 17728.611 | 17728.611 | 0
5/9/2026 | 9:45:00 PM | 15960.479 | 15960.479 | 0 | 2921.673 | 2921.673 | 0 | 0 | 0 | 17775.446 | 17775.446 | 0
5/9/2026 | 10:00:00 PM | 16000.428 | 16000.428 | 0 | 2939.139 | 2939.139 | 0 | 0 | 0 | 17819.873 | 17819.873 | 0
5/9/2026 | 10:15:00 PM | 16040.573 | 16040.573 | 0 | 2956.579 | 2956.579 | 0 | 0 | 0 | 17864.481 | 17864.481 | 0
5/9/2026 | 10:30:00 PM | 16081.492 | 16081.492 | 0 | 2974.128 | 2974.128 | 0 | 0 | 0 | 17909.885 | 17909.885 | 0
5/9/2026 | 10:45:00 PM | 16123.477 | 16123.477 | 0 | 2991.799 | 2991.799 | 0 | 0 | 0 | 17956.339 | 17956.339 | 0
5/9/2026 | 11:00:00 PM | 16166.208 | 16166.208 | 0 | 3009.587 | 3009.587 | 0 | 0 | 0 | 18003.546 | 18003.546 | 0
5/9/2026 | 11:15:00 PM | 16209.042 | 16209.042 | 0 | 3027.427 | 3027.427 | 0 | 0 | 0 | 18050.87 | 18050.87 | 0
5/9/2026 | 11:30:00 PM | 16251.912 | 16251.912 | 0 | 3045.289 | 3045.289 | 0 | 0 | 0 | 18098.236 | 18098.236 | 0
5/9/2026 | 11:45:00 PM | 16294.689 | 16294.689 | 0 | 3063.163 | 3063.163 | 0 | 0 | 0 | 18145.522 | 18145.522 | 0
5/10/2026 | 12:00:00 AM | 16337.395 | 16337.395 | 0 | 3081.06 | 3081.06 | 0 | 0 | 0 | 18192.742 | 18192.742 | 0
5/10/2026 | 12:15:00 AM | 16379.841 | 16379.841 | 0 | 3098.939 | 3098.939 | 0 | 0 | 0 | 18239.703 | 18239.703 | 0
5/10/2026 | 12:30:00 AM | 16422.109 | 16422.109 | 0 | 3116.865 | 3116.865 | 0 | 0 | 0 | 18286.516 | 18286.516 | 0
5/10/2026 | 12:45:00 AM | 16464.107 | 16464.107 | 0 | 3134.814 | 3134.814 | 0 | 0 | 0 | 18333.085 | 18333.085 | 0
5/10/2026 | 1:00:00 AM | 16506.057 | 16506.057 | 0 | 3152.767 | 3152.767 | 0 | 0 | 0 | 18379.615 | 18379.615 | 0
5/10/2026 | 1:15:00 AM | 16547.988 | 16547.988 | 0 | 3170.725 | 3170.725 | 0 | 0 | 0 | 18426.131 | 18426.131 | 0
5/10/2026 | 1:30:00 AM | 16589.827 | 16589.827 | 0 | 3188.66 | 3188.66 | 0 | 0 | 0 | 18472.544 | 18472.544 | 0
5/10/2026 | 1:45:00 AM | 16631.557 | 16631.557 | 0 | 3206.618 | 3206.618 | 0 | 0 | 0 | 18518.866 | 18518.866 | 0
5/10/2026 | 2:00:00 AM | 16672.907 | 16672.907 | 0 | 3224.573 | 3224.573 | 0 | 0 | 0 | 18564.826 | 18564.826 | 0
5/10/2026 | 2:15:00 AM | 16713.897 | 16713.897 | 0 | 3242.48 | 3242.48 | 0 | 0 | 0 | 18610.429 | 18610.429 | 0
5/10/2026 | 2:30:00 AM | 16754.532 | 16754.532 | 0 | 3260.353 | 3260.353 | 0 | 0 | 0 | 18655.678 | 18655.678 | 0
5/10/2026 | 2:45:00 AM | 16777.523 | 16777.523 | 0 | 3265.575 | 3265.575 | 0 | 0 | 0 | 18681.291 | 18681.291 | 0
5/10/2026 | 3:00:00 AM | 16798.921 | 16798.921 | 0 | 3268.31 | 3268.31 | 0 | 0 | 0 | 18704.921 | 18704.921 | 0
5/10/2026 | 3:15:00 AM | 16821.641 | 16821.641 | 0 | 3271.181 | 3271.181 | 0 | 0 | 0 | 18729.954 | 18729.954 | 0
5/10/2026 | 3:30:00 AM | 16845.242 | 16845.242 | 0 | 3274.144 | 3274.144 | 0 | 0 | 0 | 18755.961 | 18755.961 | 0
5/10/2026 | 3:45:00 AM | 16869.994 | 16869.994 | 0 | 3277.206 | 3277.206 | 0 | 0 | 0 | 18783.164 | 18783.164 | 0
5/10/2026 | 4:00:00 AM | 16895.319 | 16895.319 | 0 | 3280.319 | 3280.319 | 0 | 0 | 0 | 18810.933 | 18810.933 | 0
5/10/2026 | 4:15:00 AM | 16921.009 | 16921.009 | 0 | 3283.468 | 3283.468 | 0 | 0 | 0 | 18839.059 | 18839.059 | 0
5/10/2026 | 4:30:00 AM | 16946.902 | 16946.902 | 0 | 3286.641 | 3286.641 | 0 | 0 | 0 | 18867.372 | 18867.372 | 0
5/10/2026 | 4:45:00 AM | 16972.582 | 16972.582 | 0 | 3289.762 | 3289.762 | 0 | 0 | 0 | 18895.423 | 18895.423 | 0
5/10/2026 | 5:00:00 AM | 17016.486 | 17016.486 | 0 | 3306.329 | 3306.329 | 0 | 0 | 0 | 18943.618 | 18943.618 | 0
5/10/2026 | 5:15:00 AM | 17061.388 | 17061.388 | 0 | 3324.714 | 3324.714 | 0 | 0 | 0 | 18993.126 | 18993.126 | 0
5/10/2026 | 5:30:00 AM | 17103.451 | 17103.451 | 0 | 3342.716 | 3342.716 | 0 | 0 | 0 | 19039.716 | 19039.716 | 0
5/10/2026 | 5:45:00 AM | 17144.643 | 17144.643 | 0 | 3360.583 | 3360.583 | 0 | 0 | 0 | 19085.417 | 19085.417 | 0
5/10/2026 | 6:00:00 AM | 17185.517 | 17185.517 | 0 | 3378.474 | 3378.474 | 0 | 0 | 0 | 19130.842 | 19130.842 | 0
5/10/2026 | 6:15:00 AM | 17226.279 | 17226.279 | 0 | 3396.381 | 3396.381 | 0 | 0 | 0 | 19176.179 | 19176.179 | 0
5/10/2026 | 6:30:00 AM | 17267.263 | 17267.263 | 0 | 3414.284 | 3414.284 | 0 | 0 | 0 | 19221.74 | 19221.74 | 0
5/10/2026 | 6:45:00 AM | 17308.621 | 17308.621 | 0 | 3432.258 | 3432.258 | 0 | 0 | 0 | 19267.697 | 19267.697 | 0
5/10/2026 | 7:00:00 AM | 17349.626 | 17349.626 | 0 | 3450.202 | 3450.202 | 0 | 0 | 0 | 19313.296 | 19313.296 | 0
5/10/2026 | 7:15:00 AM | 17390.568 | 17390.568 | 0 | 3468.134 | 3468.134 | 0 | 0 | 0 | 19358.829 | 19358.829 | 0
5/10/2026 | 7:30:00 AM | 17431.211 | 17431.211 | 0 | 3486.01 | 3486.01 | 0 | 0 | 0 | 19404.052 | 19404.052 | 0
5/10/2026 | 7:45:00 AM | 17471.804 | 17471.804 | 0 | 3503.848 | 3503.848 | 0 | 0 | 0 | 19449.213 | 19449.213 | 0
5/10/2026 | 8:00:00 AM | 17512.367 | 17512.367 | 0 | 3521.671 | 3521.671 | 0 | 0 | 0 | 19494.337 | 19494.337 | 0
5/10/2026 | 8:15:00 AM | 17552.696 | 17552.696 | 0 | 3539.429 | 3539.429 | 0 | 0 | 0 | 19539.208 | 19539.208 | 0
5/10/2026 | 8:30:00 AM | 17593.035 | 17593.035 | 0 | 3557.15 | 3557.15 | 0 | 0 | 0 | 19584.066 | 19584.066 | 0
5/10/2026 | 8:45:00 AM | 17633.802 | 17633.802 | 0 | 3574.92 | 3574.92 | 0 | 0 | 0 | 19629.365 | 19629.365 | 0
5/10/2026 | 9:00:00 AM | 17674.69 | 17674.69 | 0 | 3592.65 | 3592.65 | 0 | 0 | 0 | 19674.775 | 19674.775 | 0
5/10/2026 | 9:15:00 AM | 17715.711 | 17715.711 | 0 | 3610.346 | 3610.346 | 0 | 0 | 0 | 19720.299 | 19720.299 | 0
5/10/2026 | 9:30:00 AM | 17756.965 | 17756.965 | 0 | 3628.024 | 3628.024 | 0 | 0 | 0 | 19766.038 | 19766.038 | 0
5/10/2026 | 9:45:00 AM | 17798.449 | 17798.449 | 0 | 3645.702 | 3645.702 | 0 | 0 | 0 | 19812.015 | 19812.015 | 0
5/10/2026 | 10:00:00 AM | 17840.391 | 17840.391 | 0 | 3663.396 | 3663.396 | 0 | 0 | 0 | 19858.44 | 19858.44 | 0
5/10/2026 | 10:15:00 AM | 17882.411 | 17882.411 | 0 | 3681.032 | 3681.032 | 0 | 0 | 0 | 19904.924 | 19904.924 | 0
5/10/2026 | 10:30:00 AM | 17924.609 | 17924.609 | 0 | 3698.663 | 3698.663 | 0 | 0 | 0 | 19951.589 | 19951.589 | 0
5/10/2026 | 10:45:00 AM | 17966.672 | 17966.672 | 0 | 3716.234 | 3716.234 | 0 | 0 | 0 | 19998.107 | 19998.107 | 0
5/10/2026 | 11:00:00 AM | 18008.284 | 18008.284 | 0 | 3733.719 | 3733.719 | 0 | 0 | 0 | 20044.153 | 20044.153 | 0
5/10/2026 | 11:15:00 AM | 18049.929 | 18049.929 | 0 | 3751.173 | 3751.173 | 0 | 0 | 0 | 20090.222 | 20090.222 | 0
5/10/2026 | 11:30:00 AM | 18091.279 | 18091.279 | 0 | 3768.571 | 3768.571 | 0 | 0 | 0 | 20135.992 | 20135.992 | 0
5/10/2026 | 11:45:00 AM | 18132.677 | 18132.677 | 0 | 3785.936 | 3785.936 | 0 | 0 | 0 | 20181.795 | 20181.795 | 0
5/10/2026 | 12:00:00 PM | 18173.173 | 18173.173 | 0 | 3803.336 | 3803.336 | 0 | 0 | 0 | 20226.756 | 20226.756 | 0
5/10/2026 | 12:15:00 PM | 18212.747 | 18212.747 | 0 | 3820.703 | 3820.703 | 0 | 0 | 0 | 20270.817 | 20270.817 | 0
5/10/2026 | 12:30:00 PM | 18251.069 | 18251.069 | 0 | 3837.957 | 3837.957 | 0 | 0 | 0 | 20313.64 | 20313.64 | 0
5/10/2026 | 12:45:00 PM | 18289.516 | 18289.516 | 0 | 3855.224 | 3855.224 | 0 | 0 | 0 | 20356.595 | 20356.595 | 0
5/10/2026 | 1:00:00 PM | 18328.52 | 18328.52 | 0 | 3872.537 | 3872.537 | 0 | 0 | 0 | 20400.111 | 20400.111 | 0
5/10/2026 | 1:15:00 PM | 18367.919 | 18367.919 | 0 | 3889.909 | 3889.909 | 0 | 0 | 0 | 20444.034 | 20444.034 | 0
5/10/2026 | 1:30:00 PM | 18407.938 | 18407.938 | 0 | 3907.322 | 3907.322 | 0 | 0 | 0 | 20488.57 | 20488.57 | 0
5/10/2026 | 1:45:00 PM | 18448.23 | 18448.23 | 0 | 3924.711 | 3924.711 | 0 | 0 | 0 | 20533.351 | 20533.351 | 0
5/10/2026 | 2:00:00 PM | 18488.157 | 18488.157 | 0 | 3942.005 | 3942.005 | 0 | 0 | 0 | 20577.735 | 20577.735 | 0
5/10/2026 | 2:15:00 PM | 18528.07 | 18528.07 | 0 | 3959.324 | 3959.324 | 0 | 0 | 0 | 20622.122 | 20622.122 | 0
5/10/2026 | 2:30:00 PM | 18567.624 | 18567.624 | 0 | 3976.581 | 3976.581 | 0 | 0 | 0 | 20666.136 | 20666.136 | 0
5/10/2026 | 2:45:00 PM | 18606.378 | 18606.378 | 0 | 3993.699 | 3993.699 | 0 | 0 | 0 | 20709.317 | 20709.317 | 0
5/10/2026 | 3:00:00 PM | 18645.006 | 18645.006 | 0 | 4010.831 | 4010.831 | 0 | 0 | 0 | 20752.384 | 20752.384 | 0
5/10/2026 | 3:15:00 PM | 18683.486 | 18683.486 | 0 | 4027.977 | 4027.977 | 0 | 0 | 0 | 20795.321 | 20795.321 | 0
5/10/2026 | 3:30:00 PM | 18722.396 | 18722.396 | 0 | 4045.183 | 4045.183 | 0 | 0 | 0 | 20838.704 | 20838.704 | 0
5/10/2026 | 3:45:00 PM | 18761.634 | 18761.634 | 0 | 4062.389 | 4062.389 | 0 | 0 | 0 | 20882.416 | 20882.416 | 0
5/10/2026 | 4:00:00 PM | 18800.831 | 18800.831 | 0 | 4079.601 | 4079.601 | 0 | 0 | 0 | 20926.078 | 20926.078 | 0
5/10/2026 | 4:15:00 PM | 18839.815 | 18839.815 | 0 | 4096.796 | 4096.796 | 0 | 0 | 0 | 20969.523 | 20969.523 | 0
5/10/2026 | 4:30:00 PM | 18878.949 | 18878.949 | 0 | 4113.999 | 4113.999 | 0 | 0 | 0 | 21013.112 | 21013.112 | 0
5/10/2026 | 4:45:00 PM | 18917.804 | 18917.804 | 0 | 4131.128 | 4131.128 | 0 | 0 | 0 | 21056.409 | 21056.409 | 0
5/10/2026 | 5:00:00 PM | 18956.399 | 18956.399 | 0 | 4148.211 | 4148.211 | 0 | 0 | 0 | 21099.435 | 21099.435 | 0
5/10/2026 | 5:15:00 PM | 18995.156 | 18995.156 | 0 | 4165.344 | 4165.344 | 0 | 0 | 0 | 21142.64 | 21142.64 | 0
5/10/2026 | 5:30:00 PM | 19034.043 | 19034.043 | 0 | 4182.489 | 4182.489 | 0 | 0 | 0 | 21185.971 | 21185.971 | 0
5/10/2026 | 5:45:00 PM | 19072.863 | 19072.863 | 0 | 4199.616 | 4199.616 | 0 | 0 | 0 | 21229.223 | 21229.223 | 0
5/10/2026 | 6:00:00 PM | 19111.321 | 19111.321 | 0 | 4216.689 | 4216.689 | 0 | 0 | 0 | 21272.095 | 21272.095 | 0
5/10/2026 | 6:15:00 PM | 19150.335 | 19150.335 | 0 | 4233.891 | 4233.891 | 0 | 0 | 0 | 21315.554 | 21315.554 | 0
5/10/2026 | 6:30:00 PM | 19189.179 | 19189.179 | 0 | 4251.079 | 4251.079 | 0 | 0 | 0 | 21358.852 | 21358.852 | 0
5/10/2026 | 6:45:00 PM | 19227.996 | 19227.996 | 0 | 4268.284 | 4268.284 | 0 | 0 | 0 | 21402.131 | 21402.131 | 0
5/10/2026 | 7:00:00 PM | 19266.727 | 19266.727 | 0 | 4285.529 | 4285.529 | 0 | 0 | 0 | 21445.342 | 21445.342 | 0
5/10/2026 | 7:15:00 PM | 19305.369 | 19305.369 | 0 | 4302.811 | 4302.811 | 0 | 0 | 0 | 21488.48 | 21488.48 | 0
5/10/2026 | 7:30:00 PM | 19344.184 | 19344.184 | 0 | 4320.154 | 4320.154 | 0 | 0 | 0 | 21531.814 | 21531.814 | 0
5/10/2026 | 7:45:00 PM | 19382.955 | 19382.955 | 0 | 4337.545 | 4337.545 | 0 | 0 | 0 | 21575.123 | 21575.123 | 0
5/10/2026 | 8:00:00 PM | 19421.594 | 19421.594 | 0 | 4354.951 | 4354.951 | 0 | 0 | 0 | 21618.312 | 21618.312 | 0
5/10/2026 | 8:15:00 PM | 19460.137 | 19460.137 | 0 | 4372.306 | 4372.306 | 0 | 0 | 0 | 21661.4 | 21661.4 | 0
5/10/2026 | 8:30:00 PM | 19498.399 | 19498.399 | 0 | 4389.664 | 4389.664 | 0 | 0 | 0 | 21704.216 | 21704.216 | 0
5/10/2026 | 8:45:00 PM | 19536.371 | 19536.371 | 0 | 4407.003 | 4407.003 | 0 | 0 | 0 | 21746.753 | 21746.753 | 0
5/10/2026 | 9:00:00 PM | 19574.145 | 19574.145 | 0 | 4424.349 | 4424.349 | 0 | 0 | 0 | 21789.104 | 21789.104 | 0
5/10/2026 | 9:15:00 PM | 19611.509 | 19611.509 | 0 | 4441.684 | 4441.684 | 0 | 0 | 0 | 21831.052 | 21831.052 | 0
5/10/2026 | 9:30:00 PM | 19648.328 | 19648.328 | 0 | 4458.976 | 4458.976 | 0 | 0 | 0 | 21872.45 | 21872.45 | 0
5/10/2026 | 9:45:00 PM | 19684.669 | 19684.669 | 0 | 4476.23 | 4476.23 | 0 | 0 | 0 | 21913.381 | 21913.381 | 0
5/10/2026 | 10:00:00 PM | 19720.721 | 19720.721 | 0 | 4493.49 | 4493.49 | 0 | 0 | 0 | 21954.042 | 21954.042 | 0
5/10/2026 | 10:15:00 PM | 19756.522 | 19756.522 | 0 | 4510.655 | 4510.655 | 0 | 0 | 0 | 21994.43 | 21994.43 | 0
5/10/2026 | 10:30:00 PM | 19792.311 | 19792.311 | 0 | 4527.82 | 4527.82 | 0 | 0 | 0 | 22034.808 | 22034.808 | 0
5/10/2026 | 10:45:00 PM | 19828.07 | 19828.07 | 0 | 4545.036 | 4545.036 | 0 | 0 | 0 | 22075.174 | 22075.174 | 0
5/10/2026 | 11:00:00 PM | 19863.875 | 19863.875 | 0 | 4562.287 | 4562.287 | 0 | 0 | 0 | 22115.588 | 22115.588 | 0
5/10/2026 | 11:15:00 PM | 19899.694 | 19899.694 | 0 | 4579.557 | 4579.557 | 0 | 0 | 0 | 22156.018 | 22156.018 | 0
5/10/2026 | 11:30:00 PM | 19935.599 | 19935.599 | 0 | 4596.893 | 4596.893 | 0 | 0 | 0 | 22196.556 | 22196.556 | 0
5/10/2026 | 11:45:00 PM | 19971.55 | 19971.55 | 0 | 4614.265 | 4614.265 | 0 | 0 | 0 | 22237.153 | 22237.153 | 0
5/11/2026 | 12:00:00 AM | 20007.522 | 20007.522 | 0 | 4631.617 | 4631.617 | 0 | 0 | 0 | 22277.765 | 22277.765 | 0
5/11/2026 | 12:15:00 AM | 20043.326 | 20043.326 | 0 | 4648.799 | 4648.799 | 0 | 0 | 0 | 22318.151 | 22318.151 | 0
5/11/2026 | 12:30:00 AM | 20079.057 | 20079.057 | 0 | 4665.991 | 4665.991 | 0 | 0 | 0 | 22358.467 | 22358.467 | 0
5/11/2026 | 12:45:00 AM | 20114.971 | 20114.971 | 0 | 4683.244 | 4683.244 | 0 | 0 | 0 | 22398.991 | 22398.991 | 0
5/11/2026 | 1:00:00 AM | 20151.002 | 20151.002 | 0 | 4700.531 | 4700.531 | 0 | 0 | 0 | 22439.638 | 22439.638 | 0
5/11/2026 | 1:15:00 AM | 20187.1 | 20187.1 | 0 | 4717.835 | 4717.835 | 0 | 0 | 0 | 22480.353 | 22480.353 | 0
5/11/2026 | 1:30:00 AM | 20223.105 | 20223.105 | 0 | 4735.134 | 4735.134 | 0 | 0 | 0 | 22520.976 | 22520.976 | 0
5/11/2026 | 1:45:00 AM | 20259.225 | 20259.225 | 0 | 4752.487 | 4752.487 | 0 | 0 | 0 | 22561.742 | 22561.742 | 0
5/11/2026 | 2:00:00 AM | 20295.57 | 20295.57 | 0 | 4769.878 | 4769.878 | 0 | 0 | 0 | 22602.737 | 22602.737 | 0
5/11/2026 | 2:15:00 AM | 20332.326 | 20332.326 | 0 | 4787.314 | 4787.314 | 0 | 0 | 0 | 22644.131 | 22644.131 | 0
5/11/2026 | 2:30:00 AM | 20369.148 | 20369.148 | 0 | 4804.781 | 4804.781 | 0 | 0 | 0 | 22685.601 | 22685.601 | 0
5/11/2026 | 2:45:00 AM | 20405.871 | 20405.871 | 0 | 4822.228 | 4822.228 | 0 | 0 | 0 | 22726.962 | 22726.962 | 0
5/11/2026 | 3:00:00 AM | 20442.551 | 20442.551 | 0 | 4839.657 | 4839.657 | 0 | 0 | 0 | 22768.267 | 22768.267 | 0
5/11/2026 | 3:15:00 AM | 20479.16 | 20479.16 | 0 | 4857.088 | 4857.088 | 0 | 0 | 0 | 22809.504 | 22809.504 | 0
5/11/2026 | 3:30:00 AM | 20515.703 | 20515.703 | 0 | 4874.483 | 4874.483 | 0 | 0 | 0 | 22850.658 | 22850.658 | 0
5/11/2026 | 3:45:00 AM | 20552.216 | 20552.216 | 0 | 4891.87 | 4891.87 | 0 | 0 | 0 | 22891.775 | 22891.775 | 0
5/11/2026 | 4:00:00 AM | 20588.638 | 20588.638 | 0 | 4909.235 | 4909.235 | 0 | 0 | 0 | 22932.791 | 22932.791 | 0
5/11/2026 | 4:15:00 AM | 20625.06 | 20625.06 | 0 | 4926.574 | 4926.574 | 0 | 0 | 0 | 22973.787 | 22973.787 | 0
5/11/2026 | 4:30:00 AM | 20661.435 | 20661.435 | 0 | 4943.873 | 4943.873 | 0 | 0 | 0 | 23014.717 | 23014.717 | 0
5/11/2026 | 4:45:00 AM | 20684.727 | 20684.727 | 0 | 4950.913 | 4950.913 | 0 | 0 | 0 | 23040.89 | 23040.89 | 0
5/11/2026 | 5:00:00 AM | 20702.365 | 20702.365 | 0 | 4953.26 | 4953.26 | 0 | 0 | 0 | 23060.635 | 23060.635 | 0
5/11/2026 | 5:15:00 AM | 20721.003 | 20721.003 | 0 | 4955.683 | 4955.683 | 0 | 0 | 0 | 23081.362 | 23081.362 | 0
5/11/2026 | 5:30:00 AM | 20740.819 | 20740.819 | 0 | 4958.21 | 4958.21 | 0 | 0 | 0 | 23103.26 | 23103.26 | 0
5/11/2026 | 5:45:00 AM | 20761.093 | 20761.093 | 0 | 4960.78 | 4960.78 | 0 | 0 | 0 | 23125.621 | 23125.621 | 0
5/11/2026 | 6:00:00 AM | 20781.75 | 20781.75 | 0 | 4963.386 | 4963.386 | 0 | 0 | 0 | 23148.376 | 23148.376 | 0
5/11/2026 | 6:15:00 AM | 20803.032 | 20803.032 | 0 | 4966.022 | 4966.022 | 0 | 0 | 0 | 23171.727 | 23171.727 | 0